## Zone substations
Zone Substation |  | On-load Capacity - Nameplate Rating (MVA) | Hot or Cold Spare Capacity - Nameplate Rating (MVA) | Total Capacity - Nameplate Rating (MVA) | Cyclic N-1 Rating (MVA) | Hours Load is ≥ 95% of MD | Station Power Factor at MD | Load Transfers (MVA) | Generation Capacity <1MW (MW) (Note 3) | Generation Capacity >1MW (1MW) | Actual Demand (MVA) | 50% PoE Forecast Demand (MVA) |  |  |  |  | % Load Above N-1 Rating (2021) | Energy at Risk (MWh) (N-1 50% PoE) |  |  |  |  | Hours at Risk (N-1 50% PoE)
[11 empty] | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 |  | 2021 | 2022 | 2023 | 2024 | 2025 | 2021 | 2022 | 2023 | 2024 | 2025
BTS 22kV
BK | S | 23 | 10 | 33 | 27.2 |  | 0.98148 |  | 1.902 |  | 15.3447 | 14.7735 | 15.3339 | 15.4358 | 15.609 | 15.9758 | -
| W | 23 | 10 | 33 | 28.6 |  | 0.99214 |  |  |  | 13.5914 | 14.6351 | 14.6149 | 15.1693 | 15.2701 | 15.4414 | -
C | S | 22.5 |  | 22.5 | 17 |  | 0.99673 |  | 1.233 |  | 12.0927 | 12.822 | 13.8955 | 13.8955 | 14.0159 | 14.2767 | -
| W | 22.5 |  | 22.5 | 17 |  | 0.99525 |  |  |  | 11.1205 | 11.0927 | 12.841 | 13.9161 | 13.9161 | 14.0367 | -
F | S | 20 |  | 20 | 13 | 3 | 0.98929 | 1 | 2.197 |  | 14.878 | 14.8188 | 14.8188 | 15.0007 | 15.405 | 16.0115 | 13.99% | 7.7993 | 7.7993 | 9.7031 | 15.0814 | 26.2574 | 11.5 | 11.5 | 13.5 | 18.25 | 26.5
| W | 20 |  | 20 | 15.3 | 3 | 0.99562 |  |  |  | 14.7236 | 14.8751 | 14.7245 | 14.7245 | 14.9052 | 15.307 | -
BTS 66kV
BQ | S | 55 | 55 | 110 | 64.9 | 3 | 0.99999 | 15.2 | 2.122 | 12.4 | 72.0068 | 71.5704 | 72.2004 | 72.9304 | 74.5104 | 76.6704 | 10.28% | 20.989 | 26.3624 | 33.9865 | 55.8725 | 103.193 | 8.5 | 10.25 | 12.25 | 18.75 | 31.25
| W | 55 | 55 | 110 | 72.3 | 11 | 0.99998 | 15.2 | 2.122 |  | 52.5943 | 57.5911 | 57.8311 | 58.3312 | 59.2112 | 60.6812 | -
VM | S | 57 | 27 | 84 | 62.8 |  | 0.99475 | 21.5 | 0.98 |  | 48.9707 | 50.5455 | 53.9735 | 56.8687 | 57.8639 | 58.6983 | -
| W | 57 | 27 | 84 | 69.2 |  | 0.99997 | 21.5 | 0.98 |  | 37.9175 | 40.3813 | 41.3214 | 45.2515 | 47.1016 | 47.3616 | -
WA | S | 57 | 27 | 84 | 67.1 |  | 0.98149 | 12.2 | 0.179 |  | 49.8344 | 45.3087 | 45.0438 | 45.2577 | 45.9607 | 47.163 | -
| W | 57 | 27 | 84 | 73.7 |  | 0.99993 |  | 0.179 |  | 39.7387 | 37.4825 | 33.6723 | 34.1623 | 34.4723 | 35.1724 | -
MP | S | 165 |  | 165 | 124 |  | 0.99971 |  | 0.583 | 1.15 | 104.5744 | 93.0672 | 93.9074 | 95.1778 | 97.2584 | 100.2893 | -
| W | 165 |  | 165 | 123.4 |  | 0.99154 |  |  |  | 77.1804 | 77.9495 | 70.7587 | 71.979 | 73.1388 | 75.0248 | -
DLF 22kV
TP | S | [10 empty] | Note 6 | Note 6 | Note 6 | Note 6 | Note 6 | -
| W | [10 empty] | Note 6 | Note 6 | Note 6 | Note 6 | Note 6 | -
FBTS 66kV
AP | S | 60 | 27 | 87 | 70 |  | 0.99331 | 17 | 2.36 |  | 50.9339 | 47.2057 | 47.4372 | 48.7963 | 49.35 | 50.7896 | -
| W | 60 | 27 | 87 | 71.3 |  | 0.99974 |  | 2.36 |  | 38.9102 | 40.4506 | 40.3105 | 41.3208 | 42.101 | 42.6712 | -
E | S | 13.5 |  | 13.5 | 0 |  | 0.92046 |  | 0.057 |  | 2.8487 | 3.1506 | 3.1941 | 3.2484 | 3.3353 | 3.4439 | 100%
| W | 13.5 |  | 13.5 | 0 |  | 0.91287 |  | 0.057 |  | 2.6817 | 2.7167 | 2.7386 | 2.7715 | 2.8372 | 2.9139 | 100%
FB | S | 90 |  | 90 | 63.7 |  | 0.99854 | 3.4 | 0.27 |  | 25.7138 | 24.7562 | 25.1067 | 25.4972 | 26.2183 | 27.0996 | -
| W | 90 |  | 90 | 62 |  | 0.99997 |  | 0.27 |  | 23.7289 | 21.1106 | 21.2906 | 21.5907 | 22.0407 | 22.7107 | -
MG | S | 60 | 27 | 87 | 64.3 |  | 0.9519 |  | 0.418 |  | 37.1102 | 34.2685 | 34.8778 | 36.0649 | 36.9053 | 38.4076 | -
| W | 60 | 27 | 87 | 75 |  | 0.99687 |  | 0.418 |  | 24.1353 | 24.9681 | 25.2389 | 25.7806 | 26.4929 | 27.4559 | -
PM | S | 27 |  | 27 | 17.4 |  | 0.96779 | 2.1 | 0.836 |  | 13.4415 | 15.5923 | 16.0986 | 16.8426 | 16.9149 | 17.1732 | -
| W | 27 |  | 27 | 19.7 |  | 0.95935 | 2.1 | 0.836 |  | 13.5346 | 14.6036 | 14.6036 | 15.4688 | 15.8023 | 15.9066 | -
SB | S | 110 |  | 110 | 59.7 |  | 0.9749 |  | 0.296 | 6 | 42.8246 | 42.9888 | 52.4667 | 56.3748 | 57.1235 | 57.8313 | -
| W | 110 |  | 110 | 63.6 |  | 0.97817 |  | 0.296 |  | 31.6244 | 32.9084 | 37.8053 | 44.1437 | 46.1474 | 46.1372 | -
SO | S | 60 | 27 | 87 | 63.7 |  | 0.97187 | 8.4 | 0.295 |  | 38.9656 | 34.6547 | 35.9615 | 37.1344 | 38.2148 | 39.2746 | -
| W | 60 | 27 | 87 | 71.7 |  | 0.96224 |  | 0.295 |  | 26.8745 | 33.526 | 33.8378 | 35.5629 | 36.5086 | 37.579 | -
WG | S | 81 |  | 81 | 67.6 |  | 0.98189 |  | 0.268 |  | 42.0468 | 41.6339 | 42.6218 | 43.8643 | 45.4225 | 47.2048 | -
| W | 81 |  | 81 | 71.9 |  | 0.97931 |  | 0.268 |  | 37.9538 | 37.1589 | 37.8022 | 38.7723 | 39.9875 | 41.4681 | -
RTS 66kV
AR | S | 60 |  | 60 | 32.9 | 4 | 0.99832 | 3.3 | 1.718 |  | 37.3408 | 33.2859 | 32.9653 | 32.795 | 32.9854 | 33.5663 | 1.173%
| W | 60 |  | 60 | 35.8 | 6 | 0.99415 | 3.3 | 1.718 |  | 30.3615 | 28.2954 | 27.8529 | 27.6416 | 27.6617 | 28.0138 | -
B | S | 54 |  | 54 | 29 | 5 | 0.99796 | 8.3 | 1.052 | 6.2 | 26.544 | 33.7587 | 33.909 | 34.2998 | 34.4702 | 34.7407 | 16.41% | 55.7651 | 60.5932 | 74.4668 | 81.0811 | 92.4298 | 34.5 | 36.75 | 42.75 | 45.25 | 49.75
| W | 54 |  | 54 | 32.2 | 8 | 0.99975 | 8.3 | 1.052 | 6.2 | 24.0273 | 31.1677 | 30.9376 | 31.3978 | 31.7078 | 31.7778 | -
BC | S | 57 | 30 | 87 | 71.6 |  | 0.97705 |  | 1.771 |  | 50.3926 | 44.1534 | 43.7952 | 43.7133 | 44.1329 | 44.9824 | -
| W | 57 | 30 | 87 | 70.6 |  | 0.99326 |  | 1.771 |  | 40.933 | 44.0869 | 43.4325 | 43.0802 | 42.9996 | 43.4124 | -
CL | S | 60 | 27 | 87 | 71.7 |  | 0.98249 |  | 2.91 |  | 54.4859 | 51.3695 | 51.339 | 52.2754 | 52.7843 | 53.2118 | -
| W | 60 | 27 | 87 | 70.7 |  | 0.99105 |  | 2.91 |  | 36.9995 | 37.0616 | 36.5773 | 37.3038 | 38.0908 | 38.4944 | -
CW | S | 54 |  | 54 | 34.4 |  | 0.97994 |  | 1.691 |  | 30.964 | 25.6546 | 27.2772 | 29.063 | 29.8283 | 30.1651 | -
| W | 54 |  | 54 | 38.2 |  | 0.98191 |  | 1.691 |  | 25.2279 | 23.4645 | 23.108 | 25.3078 | 26.6216 | 26.9373 | -
FR | S | 90 |  | 90 | 61.3 |  | 0.96458 | 24.8 | 0.21 |  | 49.1115 | 48.4773 | 50.6648 | 51.5253 | 51.6289 | 52.9767 | -
| W | 90 |  | 90 | 72.1 |  | 0.95738 | 24.8 | 0.21 |  | 37.4554 | 38.1249 | 39.0231 | 40.9451 | 41.2062 | 41.342 | -
MP | S | 165 |  | 165 | 124 |  | 0.99971 |  | 0.583 | 1.15 | 104.5744 | Note 5 | Note 5 | Note 5 | Note 5 | Note 5 | -
| W | 165 |  | 165 | 123.4 |  | 0.99154 |  | 0.583 | 1.15 | 77.1804 | Note 5 | Note 5 | Note 5 | Note 5 | Note 5 | -
NR | S | 83 |  | 83 | 65.2 |  | 0.97162 | 7.4 | 2.514 | 2.6 | 57.3002 | 54.7127 | 55.3919 | 56.8946 | 56.9769 | 57.6047 | -
| W | 83 |  | 83 | 71.7 |  | 0.99193 |  | 2.514 | 2.6 | 40.7222 | 42.7851 | 42.4423 | 44.1057 | 44.8013 | 44.9425 | -
SK | S | 60 | 27 | 87 | 63.2 |  | 0.95537 |  | 0.757 | 6.2 | 48.5352 | 51.6552 | 55.2663 | 55.5489 | 55.4757 | 55.9153 | -
| W | 60 | 27 | 87 | 72.9 |  | 0.99124 |  | 0.757 | 6.2 | 35.7963 | 41.4228 | 43.3597 | 45.105 | 44.9839 | 45.0445 | -
TK | S | 60 | 27 | 87 | 52.5 | 3 | 0.98034 | 16.2 | 1.7 |  | 61.8226 | 48.6666 | 49.1868 | 49.4316 | 49.452 | 49.9723 | -
| W | 60 | 27 | 87 | 54.7 | 9 | 0.98498 | 16.2 | 1.7 |  | 39.0928 | 40.8332 | 40.4271 | 41.3002 | 41.3408 | 41.5337 | -
WP | S | 110 |  | 110 | 71.6525 |  | 0.99971 |  |  |  | Note 8 | 18.1853 | 19.5457 | 19.5257 | 19.6757 | 20.0058 | -
| W | 110 |  | 110 | 71.6525 |  | 0.99154 |  |  |  | Note 8 | Note 8 | 15.2188 | 15.8743 | 15.8541 | 15.9752 | -
RTS 22kV
R | S | 40 |  | 40 | 30.1 |  | 0.99932 |  | 0.742 |  | 25.5553 | 26.6381 | 35.174 | 41.7084 | 42.9092 | 43.1994 | -
| W | 40 |  | 40 | 36 |  | 0.98342 |  |  |  | 20.959 | 19.8187 | 27.0689 | 35.7427 | 39.9119 | 40.3084 | -
RP | S | 20 |  | 20 | 9.45 | 4 | 0.92961 |  |  |  | 9.0916 | 9.4556 | 9.703 | Note 7 | Note 7 | Note 7 | 0.05891%
| W | 20 |  | 20 | 10.2 | 5 | 0.91182 |  |  |  | 8.1974 | 7.5673 | Note 7 | Note 7 | Note 7 | Note 7 | -
WMTS 66kV
JA | S | 165 |  | 165 | 127.8 |  | 0.99204 | 63 | 0.257 |  | 101.0046 | 103.4936 | 108.574 | 110.7513 | 111.1445 | 112.5053 | -
| W | 165 |  | 165 | 127.4 |  | 0.99757 | 63 | 0.257 |  | 78.5884 | 77.1276 | 79.7439 | 84.4153 | 85.4879 | 85.5781 | -
LQ | S | 120 | 60 | 180 | 131.8 |  | 0.99713 | 37 | 0.03 |  | 80.1482 | 87.6519 | 89.9285 | 90.0889 | 91.1721 | 93.3282 | -
| W | 120 | 60 | 180 | 142.2 |  | 0.95115 |  | 0.03 |  | 72.3808 | 71.629 | 73.2061 | 74.6044 | 74.8988 | 76.0132 | -
NC | S | 60 |  | 60 | 31.9 |  | 0.98666 | 4.8 | 6.841 |  | 35.6935 | 31.794 | 31.2872 | 30.9832 | 31.2467 | 31.9663 | -
| W | 60 |  | 60 | 40.2 |  | 0.99398 |  | 6.841 |  | 29.3808 | 29.0751 | 28.4111 | 28.059 | 28.069 | 28.562 | -
DA | S | 40.5 |  | 40.5 | 29.2 |  | 0.94374 | 15.5 | 0.526 | 2 | 28.7062 | Note 4 | Note 4 | 43.3807 | 44.1966 | 44.7476 | -
| W | 40.5 |  | 40.5 | 32.6 |  | 0.95057 | 15.5 | 0.526 | 2 | 22.5534 | Note 4 | Note 4 | 35.3471 | 36.4202 | 36.7147 | -
WB | S | 60 |  | 60 | 17.1 | 4 | 0.99928 | 2.7 | 3.642 |  | 24.0057 | 22.296 | 22.1559 | 22.266 | 22.6963 | 23.4268 | 30.39% | 127 | 111 | 110 | 130 | 178 | 97 | 83 | 80 | 90 | 121
| W | 60 |  | 60 | 18.4 | 2 | 0.99833 | 2.7 | 3.642 |  | 21.2469 | 22.6578 | 22.3172 | 22.177 | 22.2872 | 22.7179 | 23.14%
WMTS 22kV
DA | S | 40.5 |  | 40.5 | 29.2 |  | 0.94374 | 15.5 | 0.526 | 2 | 28.7062 | 22.0149 | 25.3257 | Note 4 | Note 4 | Note 4 | -
| W | 40.5 |  | 40.5 | 32.6 |  | 0.95057 | 15.5 | 0.526 | 2 | 22.5534 | 24.3399 | 21.7129 | Note 4 | Note 4 | Note 4 | -
J | S | 30 | 10 | 40 | 15.4 | [6 empty] | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | -
| W | 30 | 10 | 40 | 17.2 | [6 empty] | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | -
LS | S | 30 |  | 30 | 24.2 |  | 0.99578 |  | 0.594 |  | 20.8635 | 21.0551 | Note 2 | Note 2 | Note 2 | Note 2 | -
| W | 30 |  | 30 | 27 |  | 0.99869 |  | 0.594 |  | 18.1349 | 18.0258 | Note 2 | Note 2 | Note 2 | Note 2 | -
TSTS 66kV
L | S | 60 |  | 60 | 32.1 | 4 | 0.99378 | 13.4 | 5.478 |  | 46.1258 | 41.8504 | 41.6089 | 41.1762 | 41.3372 | 42.0818 | 30.37% | 134.5427 | 126.6441 | 113.2736 | 118.133 | 142.3848 | 39.5 | 37.75 | 35 | 36 | 40.75
| W | 60 |  | 60 | 36.4 | 8 | 0.99977 | 13.4 | 5.478 |  | 29.0189 | 29.7769 | 29.7669 | 29.5568 | 29.4968 | 29.9269 | -
Q | S | 60 |  | 60 | 27.2 | 4 | 0.9929 | 5.8 | 3.998 |  | 39.9633 | 34.7265 | 34.1726 | 33.8603 | 34.0416 | 34.6459 | 27.67% | 109 | 91 | 82 | 87 | 106 | 41 | 36 | 33 | 35 | 40
| W | 60 |  | 60 | 31.5 | 8 | 0.9908 | 5.8 | 3.998 |  | 28.0353 | 28.381 | 27.7855 | 27.4626 | 27.4424 | 27.836 | -
SVTS 66kV
RD | S | 60 |  | 60 | 24.9 | 3 | 0.98591 | 3.6 | 3.907 |  | 38.326 | 33.208 | 32.569 | 32.1835 | 32.3255 | 32.8935 | 33.37% | 99 | 81 | 72 | 75 | 90 | 36 | 31 | 28 | 30 | 34
| W | 60 |  | 60 | 28.7 | 8 | 0.99033 | 3.6 | 3.907 |  | 24.4312 | 23.8507 | 23.2751 | 22.9015 | 22.8611 | 23.1944 | -
Note 1: J offloaded to JA and VM
Note 2: LS offload to BQ and VM planned
Note 3: Generation capacity <1MW is mostly solar PV
Note 4: DA transfer to WMTS66 planned
Note 5: Refer BTS66 for 2021 onwards
Note 6: TP offloaded to JA
Note 7: RP offload to WP planned
Note 8: WP commissioned mid 2020

## Sub transmission lines
Subtransmission line |  | Line Rating (MVA) | Hours Load is 95% of MD | Power Factor at MD | Load Transfers (MVA) | Generation Capacity (MW) (Note 1) | Historical Demand Worst case N-1 Scenario (MVA) | Forecast Demand Worst case N-1 Scenario (MVA) |  |  |  |  | % Load Above N-1 Rating (2021) | Energy at Risk (MWh) (N-1 50% PoE) |  |  |  |  | Hours at Risk (N-1 50% PoE)
[7 empty] | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 |  | 2021 | 2022 | 2023 | 2024 | 2025 | 2021 | 2022 | 2023 | 2024 | 2025
BTS 22kV
BTS-BK185 | S | 10.5 |  | 0.95092 |  |  | 8.15 | 7.8 | 8.1 | 8.2 | 8.3 | 8.45 | -
| W | 10.5 |  | 0.97183 |  |  | 7.1 | 7.65 | 7.65 | 7.95 | 8 | 8.1 | -
BTS-BK187 | S | 10.3 |  | 0.95062 |  |  | 8.1 | 7.75 | 8.1 | 8.2 | 8.3 | 8.45 | -
| W | 10.3 |  | 0.97163 |  |  | 7.05 | 7.6 | 7.65 | 7.95 | 8 | 8.05 | -
BTS-BK194 | S | 10.3 |  | 1 |  |  | 8.15 | 7.8 | 8.1 | 8.2 | 8.3 | 8.45 | -
| W | 10.3 |  | 1 |  |  | 7.1 | 7.65 | 7.65 | 7.95 | 8 | 8.1 | -
BTS-C186 | S | 9.9 |  | 1 |  |  | 6.2 | 6.6 | 7.1 | 7.1 | 7.2 | 7.3 | -
| W | 11.2 |  | 0.98246 |  |  | 5.7 | 5.7 | 6.5 | 7.1 | 7.1 | 7.2 | -
BTS-C191 | S | 9.9 |  | 1 |  |  | 6.2 | 6.6 | 7.1 | 7.1 | 7.2 | 7.3 | -
| W | 11.2 |  | 0.98246 |  |  | 5.7 | 5.7 | 6.5 | 7.1 | 7.1 | 7.1 | -
BTS-C196 | S | 9.9 |  | 1 |  |  | 6.2 | 6.6 | 7.1 | 7.1 | 7.2 | 7.3 | -
| W | 11.2 |  | 0.98246 |  |  | 5.7 | 5.7 | 6.6 | 7.1 | 7.1 | 7.2 | -
BTS-F179 | S | 12 | 3 | 0.96753 |  |  | 15.4 | 15.3 | 15.2 | 15.4 | 15.9 | 16.5 | 27.5% | 51.7725 | 45.0503 | 50.9728 | 72.2391 | 113.9523 | 67.75 | 56.5 | 61 | 80.25 | 120.5
| W | 12.6 | 3 | 0.98026 |  |  | 15.2 | 15.3 | 15.1 | 15.1 | 15.3 | 15.8 | 21.43%
BTS-F182 | S | 12 |  | 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | -
| W | 12.6 |  | 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | -
BTS-F189 | S | 14.1 | 3 | 0.97386 |  |  | 15.3 | 15.3 | 15.3 | 15.4 | 15.9 | 16.6 | 8.511% | 3.6618 | 3.1295 | 3.6564 | 7.6704 | 16.7168 | 8.5 | 8.25 | 9 | 12.5 | 19.5
| W | 14.8 | 3 | 0.98013 |  |  | 15.1 | 15.3 | 15.1 | 15.1 | 15.3 | 15.8 | 3.378%
BTS 66kV
BTS-BQ1 | S | 125.7 |  | 0.973 |  |  | 118.5 | 114.6 | 116.5 | 118.7 | 119.7 | 123.3 | -
| W | 128 |  | 0.99458 |  |  | 92.3 | 94.4 | 91.4 | 93.7 | 95.1 | 96.5 | -
BTS-BQ3 | S | 145.2 |  | 0.97406 |  |  | 111.8 | 108.1 | 109.9 | 112 | 112.9 | 116.4 | -
| W | 153.2 |  | 0.99426 |  |  | 87.1 | 89.1 | 86.3 | 88.4 | 89.8 | 91.1 | -
BTS-VM1 | S | 125.7 |  | 0.9741 |  |  | 100.4 | 97.1 | 98.9 | 100.9 | 101.7 | 104.8 | -
| W | 128 |  | 0.99488 |  |  | 78.1 | 79.7 | 77.2 | 79.4 | 80.6 | 81.8 | -
BQ-WP2 | S | 137.5 |  | 0.98246 |  |  | 51.3 | 47.9 | 48.8 | 49.2 | 49.7 | 51.8 | -
| W | 146.9 |  | 0.99739 |  |  | 38.3 | 38.5 | 35.1 | 35.8 | 36.4 | 37.2 | -
BQ-WP3 | S | 137.5 |  | 0.98246 |  |  | 51.3 | 47.9 | 48.8 | 49.2 | 49.7 | 51.8 | -
| W | 146.9 |  | 0.99739 |  |  | 38.3 | 38.5 | 35.1 | 35.8 | 36.4 | 37.2 | -
BTS-WP | S | 125.7 |  | 0.97543 |  |  | 109.9 | 105.8 | 107.4 | 109.5 | 110.4 | 113.9 | -
| W | 128 |  | 0.99413 |  |  | 85.2 | 86.9 | 83.6 | 85.6 | 86.9 | 88.3 | -
VM-BQ1 | S | 162.3 |  | 0.96208 |  |  | 50.1 | 48.5 | 50.5 | 51.9 | 52.2 | 53.7 | -
| W | 173.7 |  | 0.99476 |  |  | 38.2 | 38.2 | 37.2 | 39.4 | 40.1 | 40.5 | -
VM-BQ3 | S | 125.7 |  | 0.964 |  |  | 50 | 48.4 | 50.4 | 51.8 | 52 | 53.6 | -
| W | 128 |  | 0.99476 |  |  | 38.2 | 38.1 | 37.1 | 39.4 | 40.1 | 40.5 | -
WP-MP1 | S | 78.3 |  | 0.9548 |  |  | 53.1 | 48.8 | 49.7 | 50.1 | 51.2 | 53 | -
| W | 84.6 |  | 0.98458 |  |  | 38.9 | 39.2 | 35.6 | 36.2 | 36.9 | 37.8 | -
WP-MP2 | S | 80 |  | 0.95489 |  |  | 53.2 | 48.9 | 49.8 | 50.2 | 51.2 | 53.1 | -
| W | 85.7 |  | 0.98458 |  |  | 38.9 | 39.3 | 35.7 | 36.3 | 36.9 | 37.8 | -
WP-MP3 | S | 83.9 |  | 0.9548 |  |  | 53.1 | 48.7 | 49.6 | 50.1 | 51.1 | 52.9 | -
| W | 91.5 |  | 0.98201 |  |  | 38.9 | 39.2 | 35.6 | 36.2 | 36.9 | 37.7 | -
VM-WA1 | S | 37.7 |  | 0.89818 |  |  | 27.5 | 23.8 | 25.1 | 24.4 | 24.2 | 24.8 | -
| W | 40 |  | 1 |  |  | 19.5 | 18.5 | 16.7 | 17 | 17.1 | 17.4 | -
VM-WA2 | S | 37.7 |  | 0.8968 |  |  | 28.1 | 24.3 | 25.3 | 24.8 | 24.7 | 25.3 | -
| W | 40 |  | 0.995 |  |  | 20 | 19 | 17.1 | 17.4 | 17.5 | 17.8 | -
VM-WA3 | S | 37.7 |  | 0.98291 |  |  | 23.4 | 21.9 | 21.1 | 21.4 | 22.2 | 22.8 | -
| W | 40 |  | 0.985 |  |  | 20 | 18.5 | 16.7 | 17 | 17.1 | 17.4 | -
FBTS 66kV
FBTS-AP | S | 135.5 |  | 0.93906 |  |  | 91.9 | 84.8 | 85.7 | 88.6 | 89.9 | 93.5 | -
| W | 137.2 |  | 0.99526 |  |  | 63.3 | 65.8 | 65.8 | 67.3 | 68.9 | 70.8 | -
FBTS-MG | S | 100.6 |  | 0.9377 |  |  | 91.5 | 84.6 | 85.4 | 88.9 | 90.3 | 93.1 | -
| W | 125.7 |  | 0.99368 |  |  | 63.3 | 65.8 | 65.7 | 67.7 | 68.9 | 70.8 | -
MG-AP | S | 91.4 |  | 0.95825 |  |  | 52.7 | 48.8 | 49 | 50.8 | 51.3 | 52.6 | -
| W | 91.4 |  | 0.98731 |  |  | 39.4 | 41.1 | 40.8 | 42.2 | 42.6 | 43.6 | -
FBTS-E | S | 66.3 |  | 0.92857 |  |  | 16.8 | 19.5 | 20.1 | 21 | 21.1 | 21.5 | -
| W | 86.3 |  | 0.91667 |  |  | 16.8 | 18 | 18 | 19 | 19.4 | 19.7 | -
FBTS-PM | S | 66.3 |  | 0.94545 |  |  | 16.5 | 19 | 19.6 | 20.4 | 20.5 | 20.9 | -
| W | 86.3 |  | 0.93293 |  |  | 16.4 | 17.6 | 17.5 | 18.5 | 18.9 | 19.1 | -
E-PM | S | 74.3 |  | 0.93525 |  |  | 13.9 | 16.3 | 16.9 | 17.7 | 17.7 | 18.1 | -
| W | 94.4 |  | 0.92199 |  |  | 14.1 | 15.3 | 15.3 | 16.2 | 16.6 | 16.7 | -
FBTS-FB | S | 135.5 |  | 0.95374 |  |  | 73.5 | 74.1 | 75.8 | 77.3 | 80.3 | 83.2 | -
| W | 142.3 |  | 0.97083 |  |  | 61.7 | 59.3 | 60.1 | 61.6 | 63.3 | 65.6 | -
FBTS-WG | S | 88 |  | 0.95374 |  |  | 73.5 | 74.1 | 75.4 | 77.4 | 79.9 | 83.5 | -
| W | 112 |  | 0.96759 |  |  | 61.7 | 59.4 | 60.2 | 61.4 | 63.3 | 65.9 | -
FB-WG | S | 89.7 |  | 0.95064 |  |  | 46.6 | 48.2 | 49.5 | 50.5 | 52.8 | 54.7 | -
| W | 94.3 |  | 0.95767 |  |  | 37.8 | 37.9 | 38.6 | 39.8 | 40.9 | 42.6 | -
FBTS-SB | S | 117.7 |  | 0.94582 |  |  | 84.9 | 80.8 | 93.3 | 98.8 | 101 | 102.9 | -
| W | 130.3 |  | 0.95425 |  |  | 61.2 | 68.7 | 74.6 | 83.2 | 86.6 | 87.8 | -
FBTS-SO | S | 109.2 |  | 0.9436 |  |  | 85.1 | 81 | 93.4 | 99 | 101.1 | 103.1 | -
| W | 134.9 |  | 0.95114 |  |  | 61.4 | 68.9 | 74.8 | 83.6 | 87 | 88 | -
SB-SO | S | 130.3 |  | 0.96339 |  |  | 43.7 | 44.5 | 54.9 | 59 | 60 | 60.9 | -
| W | 137.2 |  | 0.97006 |  |  | 33.4 | 34.4 | 39.1 | 45.9 | 48.2 | 48.1 | -
DLF 22kV
DLF64-TP278 | S | 11.1 |  | 0.94118 |  |  | 3.4 | 0.5 | 0.7 | 0.4 | 0.1 | 0.1 | -
| W | 11.6 |  | 0.91176 |  |  | 3.4 | 3.4 | 0.3 | 0.5 | 0.3 | 0.7 | -
DLF5-TP53 | S | 11.1 |  | 0.94118 |  |  | 3.4 | 0.5 | 0.7 | 0.4 | 0.1 | 0.1 | -
| W | 11.6 |  | 0.91176 |  |  | 3.4 | 3.4 | 0.3 | 0.4 | 0.3 | 0.7 | -
RTS 22kV
RTS-R134 | S | 19.9 |  | 0.9898 |  |  | 9.8 | 9.8 | 12.6 | 14.8 | 15.1 | 15.2 | -
| W | 19.9 |  | 0.9881 |  |  | 8.4 | 7.9 | 10.2 | 13.2 | 14.6 | 14.8 | -
RTS-R135 | S | 16.5 |  | 0.99398 |  |  | 16.6 | 16.7 | 21.5 | 25.2 | 25.7 | 25.8 | 1.212%
| W | 17.1 |  | 0.97902 |  |  | 14.3 | 13.5 | 17.4 | 22.4 | 24.9 | 25.2 | -
RTS-R136 | S | 16.5 |  | 0.99394 |  |  | 16.5 | 16.6 | 21.3 | 24.9 | 25.5 | 25.6 | 0.6061%
| W | 17.1 |  | 0.97183 |  |  | 14.2 | 13.4 | 17.3 | 22.2 | 24.6 | 25 | -
RTS-RP123 | S | 11.4 |  | 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | -
| W | 11.4 |  | 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | -
RTS-RP124 | S | 9.4 |  | 0.92391 |  |  | 9.2 | 9.7 | Note 5 | Note 5 | Note 5 | Note 5 | 3.191%
| W | 9.4 |  | 0.90361 |  |  | 8.3 | 7.6 | Note 5 | Note 5 | Note 5 | Note 5 | -
RTS-RP125 | S | 9.2 | 7 | 0.91489 |  |  | 9.4 | 9.8 | Note 5 | Note 5 | Note 5 | Note 5 | 6.522% | 2.0467 | 4.4984 | 4.4984 | 5.4617 | 9.2921 | 7.5 | 10.5 | 10.5 | 13.75 | 29.5
| W | 10.1 | 5 | 0.89412 |  |  | 8.5 | 7.7 | Note 5 | Note 5 | Note 5 | Note 5 | -
RTS 66kV
RTS-AR | S | 94.3 |  | 0.91116 |  |  | 92.3 | 80.7 | 80 | 80.1 | 80.7 | 82.1 | -
| W | 123.4 |  | 0.94444 |  |  | 73.8 | 75.9 | 74.5 | 73.8 | 73.5 | 74.7 | -
RTS-TK | S | 116.6 |  | 0.92824 |  |  | 64.1 | 50.9 | 50.9 | 50.9 | 50.8 | 52.4 | -
| W | 122.3 |  | 0.97743 |  |  | 44.3 | 45.1 | 44.6 | 44.7 | 44.7 | 45.2 | -
RTS-TK/BC | S | 135.5 |  | 0.94269 |  |  | 120.4 | 99.2 | 99.4 | 98.5 | 98.9 | 100.2 | -
| W | 137.2 |  | 0.96831 |  |  | 85.2 | 87.5 | 86.6 | 86.9 | 87.4 | 87.8 | -
BC-AR | S | 84.6 |  | 0.87287 |  |  | 52.7 | 46.1 | 45.8 | 46 | 46.4 | 47.2 | -
| W | 91.4 |  | 0.9381 |  |  | 42 | 45.8 | 45 | 44.6 | 44.4 | 45 | -
TK-BC | S | 91.4 |  | 0.94333 |  |  | 90 | 78.3 | 77.7 | 77.5 | 78.1 | 80.7 | -
| W | 91.4 |  | 0.96399 |  |  | 72.2 | 72.8 | 71.6 | 71 | 70.9 | 71.9 | -
RTS-CL | S | 135.4 |  | 0.95481 |  |  | 101.8 | 94.8 | 96.3 | 98.5 | 99.2 | 100.1 | -
| W | 142.3 |  | 0.96562 |  |  | 66.9 | 67.9 | 68.5 | 70.8 | 72.7 | 74.2 | -
K-CL | S | 91.4 |  | 0.93945 |  |  | 57.8 | 53.8 | 53.8 | 55.3 | 55.8 | 56.7 | -
| W | 91.4 |  | 0.97113 |  |  | 38.1 | 38 | 37.6 | 38.3 | 39.3 | 39.6 | -
RTS-CW | S | 120 |  | 0.91928 |  |  | 121.4 | 120.3 | 123.1 | 128.1 | 128.7 | 130.3 | 0.25%
| W | 142.9 |  | 0.9637 |  |  | 90.9 | 98.5 | 98.4 | 102.4 | 105.2 | 106.2 | -
RTS-NR | S | 117.2 |  | 0.91646 |  |  | 118.5 | 117 | 119.8 | 125 | 125.2 | 126.8 | -
| W | 142.9 |  | 0.96089 |  |  | 89.5 | 97.1 | 96.6 | 101.4 | 103.9 | 104.4 | -
B-CW | S | 85.7 |  | 0.94498 |  |  | 83.6 | 88.5 | 89.4 | 91.5 | 91.7 | 92.3 | 3.267%
| W | 91.4 |  | 0.98254 |  |  | 63 | 71.6 | 72 | 73.5 | 74.5 | 75.1 | -
B-NR | S | 85.7 |  | 0.95883 |  |  | 58.3 | 59.6 | 61.4 | 64.6 | 64.7 | 65.7 | -
| W | 91.4 |  | 0.97751 |  |  | 48.9 | 54 | 53.6 | 56.3 | 58.1 | 58.6 | -
RTS-SK | S | 102.9 |  | 0.93396 |  |  | 74.2 | 75.8 | 80.8 | 81.2 | 81 | 81.5 | -
| W | 108 |  | 0.97851 |  |  | 60.5 | 66 | 68.4 | 70.9 | 71.7 | 71.6 | -
RTS-FR1 | S | 82.3 |  | 0.92593 |  |  | 24.3 | 37.4 | 39.8 | 40.3 | 40.5 | 41.8 | -
| W | 87.4 |  | 0.95699 |  |  | 18.6 | 19.2 | 29.9 | 31.4 | 31.7 | 31.8 | -
RTS-FR2 | S | 82.3 |  | 0.92245 |  |  | 24.5 | 37.5 | 40.3 | 40.7 | 40.9 | 42.1 | -
| W | 86.9 |  | 0.95722 |  |  | 18.7 | 19.3 | 30 | 31.7 | 31.8 | 31.9 | -
RTS-FR3 | S | 67.4 |  | 0.92593 |  |  | 24.3 | 37.4 | 40.1 | 40.5 | 40.7 | 41.9 | -
| W | 76 |  | 0.95699 |  |  | 18.6 | 19.2 | 29.9 | 31.5 | 31.7 | 31.8 | -
FR-MP1 | S | Note 3 |  | Note 3 |  |  | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | -
| W | Note 3 |  | Note 3 |  |  | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | -
FR-WP1 | S | 84.6 |  | 0.81818 |  |  | 1.1 | 13.3 | 14.9 | 14.9 | 14.9 | 15.1 | -
| W | 78.3 |  | 0.82353 |  |  | 1.7 | 1.8 | 10.6 | 11.4 | 11.4 | 11.4 | -
FR-MP2 | S | Note 3 |  | Note 3 |  |  | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | -
| W | Note 3 |  | Note 3 |  |  | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | -
FR-WP2 | S | 80 |  | 0.35 |  |  | 2 | 11.7 | 12.6 | 12.6 | 12.7 | 13 | -
| W | 85.7 |  | 0.76923 |  |  | 1.3 | 1.4 | 9.5 | 9.8 | 9.8 | 9.9 | -
BQ-FR3 | S | Note 3 |  | Note 3 |  |  | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | -
| W | Note 3 |  | Note 3 |  |  | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | -
FR-WP3 | S | 81.7 |  | 0.35 |  |  | 2 | 11.5 | 12.3 | 12.2 | 12.3 | 12.6 | -
| W | 88 |  | 0.84615 |  |  | 1.3 | 1.5 | 9.3 | 9.5 | 9.7 | 9.7 | -
BQ-MP3 | S | Note 3 |  | Note 3 |  |  | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | -
| W | Note 3 |  | Note 3 |  |  | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | Note 3 | -
SVTS 66kV
SVTS-RD | S | 116.6 |  | 0.9593 |  |  | 108.1 | 94.5 | 95.1 | 95.6 | 97.6 | 99.5 | -
| W | 122.3 |  | 0.97395 |  |  | 69.1 | 66.6 | 66 | 66.9 | 70 | 70.8 | -
TSTS 66kV
TSTS-L | S | 106.9 | 2 | 0.90698 |  |  | 129 | 115.7 | 115.3 | 114 | 114.6 | 116.1 | 8.232% | 9.8187 | 9.0318 | 6.6448 | 7.7004 | 10.6485 | 2.75 | 2.5 | 2.25 | 2.25 | 2.75
| W | 108.6 | 5 | 0.96438 |  |  | 78.6 | 80.5 | 80.1 | 79.8 | 80.5 | 81.1 | -
HB-Q | S | 94.9 |  | 0.93164 |  |  | 90.7 | 80.5 | 79.6 | 78.4 | 78.9 | 80.3 | -
| W | 108.6 |  | 0.97251 |  |  | 58.2 | 59.9 | 58.9 | 58.3 | 58.4 | 59.1 | -
L-Q | S | 95.4 |  | 0.95378 |  |  | 71.4 | 64.4 | 64.4 | 63.8 | 64.2 | 64.7 | -
| W | 108.6 |  | 0.9765 |  |  | 46.8 | 47.6 | 47.3 | 47.3 | 47.8 | 48.1 | -
WMTS 22kV
WMTS-BS216 | S | Note 4 |  | Note 4 |  |  | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | -
| W | Note 4 |  | Note 4 |  |  | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | -
WMTS-BS218 | S | Note 10 |  | Note 10 |  |  | Note 10 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | -
| W | Note 10 |  | Note 10 |  |  | Note 10 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | -
WMTS-DA213 | S | 71.4 |  | 0.88673 |  |  | 30.9 | 34.5 | 46.8 | 49.4 | 50.3 | 50.8 | -
| W | 87.4 |  | 0.91489 |  |  | 23.5 | 25 | 33.6 | 38.8 | 40.3 | 40.5 | -
WMTS-DA222 | S | 71.4 |  | 0.88673 |  |  | 30.9 | 34.5 | 46.8 | 49.4 | 50.3 | 50.8 | -
| W | 87.4 |  | 0.91489 |  |  | 23.5 | 25 | 33.6 | 38.7 | 40.3 | 40.5 | -
WMTS-J220 | S | 25.5 |  | 0.97826 |  |  | 13.8 | 14.5 | 14.2 | 14.4 | 14.4 | 14.8 | -
| W | 26.7 |  | 0.94697 |  |  | 13.2 | 13.3 | 12.9 | 12.7 | 12.9 | 13.2 | -
WMTS-LS214 | S | 19.1 |  | 0.98936 |  |  | 9.4 | 9.7 | 9.8 | 10 | 10.4 | 14.8 | -
| W | 19.1 |  | 0.98718 |  |  | 7.8 | 7.8 | 7.9 | 8.1 | 8.3 | 8.8 | -
WMTS-LS226 | S | 19.1 |  | 0.91447 |  |  | 15.2 | 15 | 14.7 | 14.8 | 14.8 | 15.2 | -
| W | 19.1 |  | 0.91971 |  |  | 13.7 | 13.7 | 13.3 | 13.4 | 13.2 | 13.5 | -
BS-J324 | S | Note 4 |  | Note 4 |  |  | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | -
| W | Note 4 |  | Note 4 |  |  | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | -
LS-J325 | S | 21.3 |  | 0.96377 |  |  | 13.8 | 14.5 | 14.2 | 14.4 | 14.4 | 14.7 | -
| W | 25.9 |  | 0.93233 |  |  | 13.3 | 13.3 | 12.9 | 12.7 | 12.9 | 13.2 | -
WMTS 66kV
WMTS-JA1 | S | 145.2 |  | 0.93785 |  |  | 72.4 | 76.2 | 79.9 | 81.2 | 82.1 | 84.1 | -
| W | 153.2 |  | 0.92411 |  |  | 59.3 | 59.5 | 61.3 | 63.9 | 65 | 65.7 | -
WMTS-JA3 | S | 114.6 |  | 0.95626 |  |  | 66.3 | 69.8 | 73.3 | 74.5 | 75.5 | 77.4 | -
| W | 121.2 |  | 0.93796 |  |  | 54.8 | 54.8 | 56.5 | 58.8 | 59.5 | 60.4 | -
WMTS-VM1 | S | 130.3 |  | 0.97978 |  |  | 44.5 | 47.3 | 49.3 | 50 | 50.8 | 52 | -
| W | 164.6 |  | 0.95756 |  |  | 37.7 | 37.6 | 38.7 | 40.1 | 40.4 | 41.1 | -
WMTS-VM2 | S | 144 |  | 0.95732 |  |  | 32.8 | 34.9 | 36.4 | 36.9 | 37.5 | 38.4 | -
| W | 155.4 |  | 0.92446 |  |  | 27.8 | 27.8 | 28.6 | 29.6 | 29.8 | 30.4 | -
WMTS-VM3 | S | 144 |  | 0.94867 |  |  | 52.6 | 55.8 | 58.4 | 59.1 | 60 | 61.4 | -
| W | 155.4 |  | 0.92809 |  |  | 44.5 | 44.5 | 45.7 | 47.4 | 47.8 | 48.6 | -
VM-LQ1 | S | 76.6 |  | 0.98485 |  |  | 39.6 | 43.9 | 44.4 | 45.1 | 45.3 | 47 | -
| W | 86.9 |  | 0.94901 |  |  | 35.3 | 34.2 | 35 | 35.8 | 35.8 | 35.8 | -
VM-LQ3 | S | 76.6 |  | 0.9217 |  |  | 44.7 | 49.5 | 51.6 | 50.8 | 52.5 | 52.8 | -
| W | 86.9 |  | 0.80899 |  |  | 44.5 | 45.2 | 46.2 | 47 | 47 | 49.1 | -
VM-JA | S | 91.4 |  | 0.96482 |  |  | 79.6 | 83 | 87.5 | 89.4 | 90.5 | 92.8 | -
| W | 98.3 |  | 0.95963 |  |  | 64.4 | 64.5 | 66.7 | 69.8 | 70.7 | 71.6 | -
JA-LQ2 | S | 76.6 |  | 0.92377 |  |  | 44.6 | 49.4 | 51.5 | 50.7 | 52.4 | 52.8 | -
| W | 86.9 |  | 0.81124 |  |  | 44.5 | 45.3 | 46.3 | 47.1 | 47.1 | 49.2 | -
JA-WP | S | 120.5 |  | 0 |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | -
| W | 128 |  | 0 |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | -
WMTS-NC | S | 54.9 |  | 0.94222 |  |  | 62.3 | 56.3 | 55.5 | 55.1 | 55.6 | 57.3 | 2.55%
| W | 70.3 |  | 0.95701 |  |  | 53.5 | 52.6 | 51.3 | 50.9 | 51.1 | 52 | -
WMTS-WB | S | 54.9 |  | 0.93185 |  |  | 63.1 | 56.7 | 55.8 | 55.5 | 56.2 | 57.7 | 3.279%
| W | 70.3 |  | 0.95131 |  |  | 53.4 | 52.7 | 51.7 | 50.9 | 51.2 | 52.3 | -
WB-NC | S | 74.3 |  | 0.92553 |  |  | 37.6 | 33.1 | 32.4 | 32.2 | 32.5 | 33.4 | -
| W | 97.2 |  | 0.95349 |  |  | 30.1 | 29.9 | 29.2 | 28.6 | 28.8 | 29.2 | -
Note 1: Generation capacity is specified at the location (sub-transmission line/ loop) where the generation is connected to the network.
Note 2: Forecast demand worst case N-1 scenario refers to the expected load that the sub-transmission line would supply in the event of the worst case outage of a sub-transmission line within the loop system.
Note 3: Cut in of new WP Zone substation requires new BTS-WP & JA-WP and creates new WP-MP1, 2 & 3 and FR-WP1, 2 & 3 from FR-MP1 & 2 and BQ-MP3; and also creates new BQ-WP2 & 3 from BQ-FR3 and BQ-MP3
Note 4: WMTS-BS216 & 218 to be used for supply new HV customer. J-LS cable to be retired
Note 5: No load on lines RTS-RP124 and RTS-RP125 after planned RP offload to WP