## Zone substations
Zone Substation |  | On-load Capacity - Nameplate Rating (MVA) | Hot or Cold Spare Capacity - Nameplate Rating (MVA) (note 1) | Total Capacity - Nameplate Rating (MVA) | Cyclic N-1 Rating (MVA) | Hours Load is ≥ 95% of MD (note 2) | Station Power Factor at MD | Load Transfers (MVA) | Generation Capacity <1MW (MW) (notes 3 & 4) | Generation Capacity >1MW (1MW) | Actual Demand (MVA) | 50% PoE Forecast Demand (MVA) |  |  |  |  | % Load Above N-1 Rating (2021) | Energy at Risk (MWh) (N-1 50% PoE) |  |  |  |  | Hours at Risk (N-1 50% PoE)
[11 empty] | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 |  | 2021 | 2022 | 2023 | 2024 | 2025 | 2021 | 2022 | 2023 | 2024 | 2025
ATS 66kV
LV | S | 99 |  | 99 | 79.8 | 2 | 0.99995 | 3.2 | 45.928 | - | 104.7713 | 90.8442 | 94.9744 | 98.0845 | 101.4147 | 105.3249 | 13.84% | 44 | 96 | 152 | 229 | 340 | 11 | 17 | 23 | 29 | 38
| W | 99 |  | 99 | 95.4 | 7 | 0.99996 |  | 45.928 | - | 76.0393 | 78.2728 | 70.3026 | 73.0027 | 75.4727 | 78.3029 | -
WBE | S | 99 |  | 99 | 82.8 | 3 | 0.99775 | 3.8 | 39.963 | 13.9 | 109.5848 | 102.1397 | 107.2512 | 111.4507 | 115.9709 | 121.2026 | 23.36% | 222 | 384 | 557 | 795 | 1129 | 31 | 43 | 57 | 72 | 89
| W | 99 |  | 99 | 92.2 | 4 | 0.99888 |  | 39.963 | 13.9 | 75.864 | 81.3008 | 75.9848 | 79.0082 | 82.0716 | 85.4754 | -
ATS/BLTS 66kV
AC | S | 40 |  | 40 | 30 | - | 0.95251 | 0 | 0.1 | - | 2.2571 | 2.3937 | 2.7401 | 2.8346 | 2.8556 | 2.8976 | -
| W | 40 |  | 40 | 30 | - | 0.96079 |  | 0.1 | - | 2.1615 | 2.2169 | 2.3731 | 2.7165 | 2.7686 | 2.7998 | -
AL | S | 30 |  | 30 | 0 | 4 | 0.99892 | 22 | 4.054 | - | 20.2066 | 20.0818 | 20.8526 | 21.3331 | 21.5634 | 21.9538 | 100% | 40733 | 41918 | 42891 | 43353 | 44137 | 8760 | 8760 | 8760 | 8760 | 8760
| W | 30 |  | 30 | 0 | - | 0.98666 |  | 4.054 | - | 17.0701 | 17.4021 | 17.6859 | 18.6082 | 18.7704 | 19.0238 | 100%
BMH | S | 27 |  | 27 | 19.1 | 3 | 0.99998 | 3.1 | 9.472 | - | 29.2 | 27.9506 | 29.2106 | 30.1907 | 31.2307 | 32.4707 | 46.34% | 262 | 380 | 511 | 697 | 989 | 106 | 150 | 218 | 307 | 432
| W | 27 |  | 27 | 20.2 | 8 | 0.97157 |  | 9.472 | - | 19.9689 | 21.0793 | 21.9027 | 22.7467 | 23.5187 | 24.3936 | 4.353%
LVN11 | S | 30 |  | 30 | 0 | 808 |  |  |  | - | 12.5 | 12.9231 | 12.7956 | 12.663 | 12.6773 | 12.7 | 100%
| W | 30 |  | 30 | 0 | 312 |  |  |  | - | 12.5 | 12.996 | 12.9119 | 13.0364 | 12.9253 | 12.9 | 100%
LVN22 | S | 99 |  | 99 | 79.7 | - | 0.99229 |  | 5.439 | - | 68.3217 | 71.9952 | 73.6277 | 74.6657 | 75.9759 | 77.8503 | -
| W | 99 |  | 99 | 85 | - | 0.99695 |  | 5.439 | - | 64.3007 | 65.9916 | 67.0749 | 68.3689 | 69.402 | 70.7862 | -
BATS 66kV
ART | S | 20 |  | 20 | 13.6 | 4 | 0.99991 | 2.2863 | 5.134 | 6.9 | 15.3734 | 13.8413 | 13.9113 | 13.9113 | 13.9813 | 14.1413 | 1.774%
| W | 20 |  | 20 | 15.2 | 4 | 0.99208 | 0 | 5.134 | 6.9 | 12.5635 | 13.8699 | 13.9505 | 14.0211 | 14.0211 | 14.0916 | -
BAN | S | 120 |  | 120 | 96.4 | - | 0.97281 | 4.7631 | 23.805 | 6.1 | 84.6328 | 82.801 | 84.9494 | 86.7072 | 88.8145 | 91.518 | -
| W | 120 |  | 120 | 104.4 | - | 0.99995 | 0 | 23.805 | 6.1 | 77.1178 | 78.4239 | 80.554 | 82.6441 | 84.3542 | 86.4043 | -
BAS | S | 99 |  | 99 | 76 | 4 | 0.99175 | 0 | 27.74 | 7.15 | 83.561 | 79.3649 | 81.8655 | 83.5091 | 85.3341 | 87.7843 | 4.427%
| W | 99 |  | 99 | 84.6 | 9 | 0.99593 | 12.5747 | 27.74 | 7.15 | 72.5469 | 73.1173 | 75.0351 | 76.9228 | 78.5193 | 80.4772 | -
BETS 66kV | [7 empty] | 0
BGO | S | 66 |  | 66 | 38.5 | 4 | 0.99977 | 21.5 | 13.143 | - | 45.2903 | 46.6109 | 48.3914 | 49.2516 | 49.8817 | 51.032 | 21.07% | 87 | 146 | 183 | 215 | 281 | 31 | 47 | 56 | 62 | 75
| W | 66 |  | 66 | 45.4 | 11 | 0.99989 | 0 | 13.143 | - | 34.8793 | 37.7343 | 38.6444 | 40.1546 | 40.5146 | 41.0547 | -
CMN | S | 66 |  | 66 | 43 | - | 0.99927 | 0 | 13.146 | - | 29.7615 | 27.7904 | 28.3308 | 28.591 | 28.9212 | 29.4616 | -
| W | 66 |  | 66 | 49.5 | - | 0.98621 | 0 | 13.146 | - | 24.0521 | 24.9238 | 25.2989 | 25.6437 | 25.9175 | 26.323 | -
CTN | S | 39.5 |  | 39.5 | 33.7 | - | 0.9573 | 0 | 7.115 | 7.2 | 20.1054 | 20.9653 | 21.4145 | 21.2682 | 21.1533 | 21.1638 | -
| W | 39.5 |  | 39.5 | 38.4 | - | 0.99761 | 0 | 7.115 | 7.2 | 15.5597 | 17.9328 | 18.5343 | 18.5343 | 18.424 | 18.3739 | -
EHK | S | 54 |  | 54 | 36.4 | 4 | 0.97851 | 14.9753 | 14.17 |  | 52.1997 | 52.7128 | 55.4823 | 56.4021 | 57.6591 | 59.5293 | 44.82% | 984 | 1506 | 1711 | 2016 | 2538 | 211 | 284 | 311 | 351 | 427
| W | 54 |  | 54 | 41 | 3 | 0.99924 | 0 | 14.17 | - | 36.9492 | 39.9302 | 41.5715 | 43.1727 | 43.7231 | 44.9941 | -
MRO | S | 27 |  | 27 | 18.3 | 5 | 0.99806 | 3.7343 | 9.671 | - | 22.0351 | 21.9224 | 22.3833 | 22.4835 | 22.6338 | 22.9043 | 19.79% | 42 | 57 | 61 | 67 | 78 | 33 | 42 | 44 | 47 | 53
| W | 27 |  | 27 | 20.2 | 4 | 0.97822 | 0 | 9.671 | - | 17.4948 | 18.411 | 18.7483 | 18.9732 | 19.0652 | 19.2288 | -
DPTS 66kV | [7 empty] | 0
MLN | S | 99 |  | 99 | 79.8 | 5 | 0.99902 | 0 | 29.043 | - | 79.0239 | 74.1524 | 84.7428 | 91.159 | 94.4322 | 98.4061 | -
| W | 99 |  | 99 | 83.4 | 11 | 0.99692 | 0 | 29.043 | - | 53.4274 | 56.1026 | 60.1551 | 71.3495 | 73.4861 | 75.8133 | -
SU | S | 99 |  | 99 | 93 | 7 | 0.99984 | 16.1947 | 22.019 | - | 92.1427 | 90.2748 | 103.0969 | 106.3274 | 107.7076 | 109.7479 | -
| W | 99 |  | 99 | 99 | 4 | 0.99785 | 0 | 22.019 | - | 65.7524 | 68.6274 | 77.3962 | 85.193 | 86.0147 | 87.077 | -
TNA | S | 66 |  | 66 | 47.6 | 6 | 0.99906 | 16.3852 | 21.184 | 8.8 | 44.3122 | 65.1115 | 72.7186 | 80.476 | 82.9082 | 85.2505 | 36.79% | 729 | 2124 | 6626 | 10742 | 13520 | 34.25 | 92.75 | 300 | 638 | 829
| W | 66 |  | 66 | 47.6 | 3 | 0.99791 | 0 | 21.184 | 8.8 | 39.2496 | 52.0185 | 55.0949 | 62.8311 | 67.5609 | 68.9338 | 9.283%
FBTS 66kV | [7 empty] | 0
DLF | S | 66 |  | 66 | 42 | - | 0.98683 | 0 | 0.064 | - | 19.9782 | 19.0003 | 19.2131 | 19.7096 | 20.5 | 21.3816 | -
| W | 66 |  | 66 | 49.3 | - | 0.99134 |  | 0.064 | - | 19.0633 | 14.6771 | 14.0819 | 14.2131 | 14.5964 | 15.2117 | -
GTS 66kV | [7 empty] | 0
CLC | S | 79 |  | 79 | 49.2 | - | 0.99966 | 0 | 8.586 | - | 41.4844 | 41.5842 | 42.1444 | 42.2544 | 42.4245 | 42.8546 | -
| W | 79 |  | 79 | 54.8 | - | 0.99907 | 0 | 8.586 | - | 36.4392 | 38.3657 | 38.746 | 39.0764 | 39.2065 | 39.4767 | -
CRO | S | 60 |  | 60 | 34.3 | 3 | 0.99038 | 5.9825 | 9.393 | - | 29.9713 | 34.8451 | 45.9014 | 48.2035 | 48.4156 | 48.8397 | 1.589%
| W | 60 |  | 60 | 38 | 11 | 0.9757 | 0 | 9.393 | - | 26.387 | 27.5085 | 35.3695 | 45.9056 | 46.0798 | 46.3565 | -
DDL | S | 66 |  | 66 | 39.7 | 2 | 0.9982 | 6.0968 | 24.752 | 1.1 | 64.0752 | 60.6391 | 63.7346 | 66.9103 | 68.8839 | 70.6871 | 52.74% | 219 | 290 | 379 | 446 | 524 | 26 | 33 | 43 | 52 | 67
| W | 66 |  | 66 | 47.2 | 3.75 | 0.99898 | 0 | 24.752 | 1.1 | 48.1552 | 42.8637 | 44.3152 | 47.4484 | 49.6706 | 50.7117 | -
FNS | S | 99 |  | 99 | 87.2 | - | 0.98225 | 0 | 9.764 | 1 | 38.1224 | 39.8067 | 50.1605 | 53.1842 | 56.1061 | 57.7146 | -
| W | 99 |  | 99 | 98.6 | - | 0.98969 | 0 | 9.764 | 1 | 30.2021 | 31.9696 | 36.9914 | 44.7514 | 46.7318 | 49.7024 | -
GB | S | 37.5 |  | 37.5 | 37.6 | - | 0.93863 | 0 | 1.248 | - | 14.4859 | 14.0737 | 17.8878 | 18.5803 | 18.6655 | 18.8359 | -
| W | 37.5 |  | 37.5 | 37.6 | - | 0.96041 | 0 | 1.248 | - | 12.4474 | 12.6196 | 13.7129 | 17.0135 | 17.0968 | 17.2114 | -
GCY | S | 66 |  | 66 | 37.8 | 4 | 0.96384 | 17.5284 | 5.386 | 5.5 | 51.1295 | 50.0603 | 51.4091 | 52.291 | 53.2662 | 54.5631 | 32.43% | 207 | 273 | 324 | 386 | 484 | 54 | 66 | 75 | 88 | 107
| W | 66 |  | 66 | 43.9 | 3 | 0.98392 | 0 | 5.386 | 5.5 | 33.2068 | 39.8916 | 40.786 | 41.66 | 42.3613 | 43.2049 | -
GL | S | 80 |  | 80 | 47.6 | 3 | 0.98794 | 7.5067 | 18.069 | - | 64.8947 | 58.799 | 60.4084 | 62.2607 | 63.4349 | 64.609 | 23.53% | 103 | 169 | 264 | 346 | 474 | 34 | 56 | 82 | 104 | 139
| W | 80 |  | 80 | 47.6 | 4 | 0.99989 | 0 | 18.069 | - | 51.2196 | 51.2155 | 52.2956 | 54.0258 | 55.446 | 56.3861 | 7.596%
GLE | S | 79.5 |  | 79.5 | 53.3 | - | 0.99727 | 11.8126 | 21.326 | - | 56.8633 | 53.566 | 55.9224 | 58.4594 | 59.7529 | 60.9461 | 0.4991%
| W | 79.5 |  | 79.5 | 59.1 | - | 0.99627 | 0 | 21.326 | - | 48.3867 | 49.0327 | 50.3074 | 53.2684 | 54.8744 | 55.9685 | -
WIN | S | 26.5 |  | 26.5 | 10.5 | - | 0.95317 | 0 | 4.304 | - | 9.3134 | 9.5681 | 9.7674 | 9.9353 | 10.1451 | 10.4284 | -
| W | 26.5 |  | 26.5 | 10.5 | - | 0.93019 | 0 | 4.304 | - | 9.5978 | 9.6002 | 9.8044 | 10.0087 | 10.1807 | 10.3957 | -
WPD | S | 79.5 |  | 79.5 | 56.8 | 2 | 0.99975 | 12.1936 | 25.911 | - | 86.4633 | 80.29 | 83.3007 | 85.4613 | 87.8119 | 90.7726 | 41.36% | 256 | 336 | 401 | 485 | 620 | 31 | 36 | 41 | 51 | 70
| W | 79.5 |  | 79.5 | 62.6 | 5 | 0.99866 | 0 | 25.911 | - | 60.692 | 58.9289 | 60.8215 | 62.724 | 64.4063 | 66.419 | -
HOTS 66kV | [5 empty] | - |  | 0
CHM | S | 33 |  | 33 | 0 | 3 | 0.99451 | 0 | 0.982 | - | 2.8275 | 2.6445 | 2.6144 | 2.5842 | 2.5641 | 2.554 | 100% | 8306 | 8228 | 8134 | 8054 | 8006 | 8760 | 8760 | 8760 | 8760 | 8760
| W | 33 |  | 33 | 0 | 4 | 0.96875 | 0 | 0.982 | - | 2.7252 | 2.7355 | 2.7149 | 2.6839 | 2.6529 | 2.6323 | 100%
HSM | S | 40.5 |  | 40.5 | 39.7 | 3 | 0.99977 | 4 | 14.337 | - | 44.6929 | 42.6498 | 44.5702 | 45.2804 | 45.4904 | 45.9905 | 7.43% | 6 | 21 | 32 | 35 | 45 | 5 | 14 | 18 | 20 | 23
| W | 40.5 |  | 40.5 | 40.4 | 10 | 0.99722 | 0 | 14.337 | - | 31.9616 | 33.2425 | 34.7968 | 36.1105 | 36.3611 | 36.5918 | -
NHL | S | 20 |  | 20 | 13 | - | 0.99734 | 0 | 3.014 | - | 12.3685 | 11.1897 | 11.2098 | 11.1095 | 11.0193 | 11.0092 | -
| W | 20 |  | 20 | 16.2 | - | 0.99192 | 0 | 3.014 | - | 9.0947 | 8.8717 | 8.8414 | 8.8112 | 8.7406 | 8.7003 | -
STL | S | 27 |  | 27 | 18.5 | 4 | 0.99642 | 0 | 4.693 | - | 20.2769 | 21.517 | 21.7077 | 21.6976 | 21.7077 | 21.8984 | 16.31% | 74 | 85 | 84 | 90 | 110 | 105 | 116 | 115 | 121 | 138
| W | 27 |  | 27 | 18.8 | 6 | 0.99777 | 0 | 4.693 | - | 18.4568 | 21.3477 | 21.488 | 21.5782 | 21.5682 | 21.6684 | 13.55%
KGTS 66kV | [7 empty] | 0
CHA | S | 27 |  | 27 | 15.2 | 5 | 0.96366 | 0 | 5.736 | - | 14.5966 | 16.0326 | 16.0534 | 16.0015 | 15.9911 | 16.0845 | 5.478% | 2 | 2 | 2 | 2 | 3 | 6 | 6 | 6 | 6 | 6
| W | 27 |  | 27 | 15.2 | 5 | 0.97953 | 0 | 5.736 | - | 13.9402 | 15.4257 | 15.7728 | 15.7933 | 15.7422 | 15.732 | 1.485%
SHL | S | 40.5 |  | 40.5 | 36.7 | 8 | 0.99878 | 2.6674 | 11.432 | 14.4 | 36.7707 | 37.8061 | 40.0488 | 40.7296 | 41.03 | 41.4806 | 3.014%
| W | 40.5 |  | 40.5 | 40.4 | 4 | 0.99967 | 0 | 11.432 | 14.4 | 27.3356 | 28.6094 | 30.64 | 32.0605 | 32.4206 | 32.6607 | -
KTS 66kV | [7 empty] | 0
GSB | S | 66 |  | 66 | 49.5 | - | 0.99196 | 0 | 9.817 | - | 22.7611 | 23.5089 | 25.6662 | 26.2409 | 26.5332 | 26.9969 | -
| W | 66 |  | 66 | 49.5 | - | 0.99941 | 0 | 9.817 | - | 19.809 | 20.0018 | 23.3338 | 25.475 | 25.7552 | 26.1154 | -
SA | S | 93 |  | 93 | 81.2 | 5 | 0.99595 | 8.3831 | 22.893 | - | 93.4356 | 84.2516 | 86.5309 | 87.9466 | 89.5531 | 91.8324 | 3.758%
| W | 93 |  | 93 | 89.6 | 10 | 0.99604 | 0 | 22.893 | - | 59.0761 | 59.9977 | 61.343 | 62.6783 | 63.8027 | 65.2685 | -
SSE | S | 99 |  | 99 | 89.7 | - | 0.96597 | 14.137 | 11.551 | - | 69.3145 | 69.0911 | 73.9877 | 74.7435 | 75.375 | 76.4723 | -
| W | 99 |  | 99 | 99 | - | 0.96762 | 0 | 11.551 | - | 59.1573 | 61.3879 | 63.9199 | 67.0823 | 67.475 | 68.0951 | -
WND | S | 66 |  | 66 | 37.5 | - | 0.99659 | 0 | 14.595 | 1.5 | 29.2032 | 31.3167 | 33.6346 | 33.9757 | 34.4273 | 35.1096 | -
| W | 66 |  | 66 | 42.7 | - | 0.99971 | 0 | 14.595 | 1.5 | 27.7432 | 28.5584 | 31.2192 | 33.5299 | 33.87 | 34.3201 | -
RCTS 66kV | [7 empty] | 0
BBD | S | 66 |  | 66 | 45.2 | - | 0.97022 | 1.4099 | 0.42 | - | 29.7741 | 32.6421 | 33.4357 | 33.4254 | 33.178 | 33.1059 | -
| W | 66 |  | 66 | 49.5 | - | 0.94649 | 0 | 0.42 | - | 22.1268 | 25.378 | 25.5259 | 26.3923 | 26.1915 | 26.0225 | -
MBN | S | 60 |  | 59 | 37.6 | 9 | 0.998 | 11.5459 | 11.947 | - | 41.43 | 41.3827 | 45.4909 | 48.036 | 48.547 | 49.2284 | 10.06% | 30 | 188 | 376 | 424 | 494 | 22 | 66 | 105 | 114 | 126
| W | 60 |  | 59 | 40.4 | 3 | 0.99904 | 0 | 11.947 | - | 26.0868 | 26.5155 | 28.2772 | 31.8606 | 33.0718 | 33.3721 | -
MDA | S | 66 |  | 66 | 39.7 | 6 | 0.9922 | 15.3183 | 12.167 | - | 50.1732 | 47.2283 | 49.627 | 51.0279 | 51.421 | 52.1466 | 18.96% | 128 | 262 | 372 | 407 | 477 | 46 | 75 | 94 | 100 | 111
| W | 66 |  | 66 | 44.6 | 3 | 0.99435 | 0 | 12.167 | - | 34.7796 | 37.0291 | 37.6727 | 40.5188 | 40.9311 | 41.3435 | -
SHTS 66kV | [7 empty] | 0
CME | S | 40.5 |  | 40.5 | 32.3 | 3 | 0.9999 | 0 | 12.323 | 14.25 | 38.6436 | 35.6335 | 37.5137 | 38.3237 | 38.6538 | 39.2238 | 10.32% | 10 | 35 | 53 | 61 | 79 | 9 | 22 | 28 | 32 | 38
| W | 40.5 |  | 40.5 | 37.3 | 2 | 0.99343 | 0 | 12.323 | 14.25 | 26.4485 | 27.6114 | 28.9502 | 30.279 | 30.5709 | 30.8829 | -
ECA | S | 40.5 |  | 39.5 | 34.6 | - | 0.9997 | 5.4871 | 12.578 | 4.8 | 28.7547 | 32.8597 | 33.5399 | 33.86 | 34.2201 | 34.8303 | - | 19.1 | 6.9 | 6.3 | 8 | 8.9 | 15 | 8 | 8 | 9 | 9
| W | 40.5 |  | 39.5 | 40.4 | - | 0.99524 | 0 | 12.578 | 4.8 | 24.0454 | 24.8281 | 25.22 | 25.6018 | 25.843 | 26.1846 | -
KYM | S | 40.5 |  | 40.5 | 33.8 | - | 0.99988 | 0 | 10.216 | - | 28.5146 | 28.5735 | 29.8336 | 30.1637 | 30.3237 | 30.6737 | -
| W | 40.5 |  | 40.5 | 38.8 | - | 0.94741 | 0 | 10.216 | - | 21.106 | 23.8123 | 24.5828 | 25.3217 | 25.5328 | 25.7333 | -
MNA | S | 66 |  | 66 | 37 | 5 | 0.98989 | 9.2595 | 12.084 | 1 | 45.0924 | 42.6207 | 44.5603 | 45.0857 | 45.4089 | 46.0151 | 15.19% | 62 | 144 | 175 | 195 | 237 | 34 | 61 | 68 | 73 | 83
| W | 66 |  | 66 | 42.5 | 8 | 0.99991 | 0 | 12.084 | 1 | 28.3676 | 29.9027 | 31.5129 | 32.533 | 32.693 | 32.953 | -
NKA | S | 39.5 |  | 39.5 | 30.5 | 6 | 0.9984 | 1.9053 | 10.508 | 9.8 | 28.8204 | 30.0481 | 32.1715 | 33.2031 | 33.3634 | 33.7139 | -
| W | 39.5 |  | 39.5 | 30.5 | 7 | 0.9766 | 0 | 10.508 | 9.8 | 25.6716 | 29.3161 | 30.719 | 32.388 | 32.9 | 33.1458 | -
SHN | S | 66 |  | 66 | 40 | - | 0.99979 | 0 | 11.451 | 5.4 | 35.6737 | 35.8675 | 37.0977 | 38.1479 | 38.528 | 39.1581 | -
| W | 66 |  | 66 | 44.1 | - | 0.99969 | 0 | 11.451 | 5.4 | 25.0491 | 26.6283 | 27.1485 | 28.3189 | 28.859 | 29.1391 | -
SHP | S | 66 |  | 66 | 36.6 | - | 0.99401 | 0 | 5.938 | 19.2 | 23.4784 | 22.897 | 27.062 | 27.4845 | 27.5147 | 27.7159 | -
| W | 66 |  | 66 | 41.9 | - | 0.99994 | 0 | 5.938 | 19.2 | 20.8958 | 19.4411 | 21.2612 | 23.9914 | 24.0114 | 24.1214 | -
STN | S | 79 |  | 79 | 61.9 | - | 0.97891 | 0 | 12.729 | 3.3 | 47.6778 | 49.2896 | 50.587 | 51.2101 | 51.9865 | 53.0795 | -
| W | 79 |  | 79 | 61.9 | - | 0.99573 | 0 | 12.729 | 3.3 | 33.8617 | 34.899 | 35.602 | 36.3653 | 36.767 | 37.3796 | -
TGTS 66kV | [7 empty] | 0
CDN | S | 20 |  | 20 | 17.2 | - | 0.99958 | 0 | 3.594 | - | 13.5302 | 17.5273 | 18.0575 | 18.0075 | 18.0275 | 18.1475 | 1.903%
| W | 20 |  | 20 | 18.2 | - | 0.99968 | 0 | 3.594 | - | 14.7347 | 16.6653 | 17.5256 | 18.0558 | 18.0058 | 18.0258 | -
COB | S | 26 |  | 26 | 15 | 10 | 0.90421 | 4.1535 | 0.896 | - | 13.7279 | 15.8592 | 15.9588 | 15.9035 | 15.8371 | 15.8592 | 5.728% | 3 | 4 | 3 | 3 | 3 | 8 | 10 | 9 | 7 | 8
| W | 26 |  | 26 | 15 | 8 | 0.94976 | 0 | 0.896 | - | 12.5108 | 14.2668 | 14.2984 | 14.3195 | 14.2563 | 14.2458 | -
HTN | S | 39.5 |  | 39.5 | 34.2 | - | 0.99891 | 3.9629 | 7.608 | - | 28.7658 | 27.5101 | 27.7604 | 27.7204 | 27.7204 | 27.9005 | -
| W | 39.5 |  | 39.5 | 38.4 | - | 0.99546 | 0 | 7.608 | - | 25.0663 | 25.4856 | 26.018 | 26.1185 | 26.0984 | 26.1787 | -
KRT | S | 40.5 |  | 40.5 | 33.4 | 8 | 0.99799 | 10 | 5.301 | - | 24.8718 | 35.5015 | 36.0526 | 36.4133 | 36.9143 | 37.6458 | 6.292% | 10 | 17 | 23 | 35 | 61 | 11 | 16 | 21 | 30 | 45
| W | 40.5 |  | 40.5 | 37.6 | 12 | 0.99822 | 0 | 5.301 | - | 23.7157 | 34.9121 | 35.4931 | 36.0441 | 36.4047 | 36.9056 | -
PLD | S | 32 |  | 32 | 22.1 | - | 0.9992 | 0 | 6.422 | - | 15.2898 | 18.885 | 18.9951 | 19.0251 | 19.1352 | 19.3654 | -
| W | 32 |  | 32 | 24 | - | 0.99993 | 0 | 6.422 | - | 16.8595 | 18.7512 | 18.8713 | 18.9813 | 19.0113 | 19.1213 | -
TRG | S | 27 |  | 27 | 19.2 | 1 | 0.99047 | 5.6015 | 5.41 | 7.2 | 19.802 | 24.6247 | 24.7559 | 24.7559 | 24.8468 | 25.0891 | 28.25% | 25 | 28 | 28 | 30 | 35 | 147 | 154 | 155 | 159 | 171
| W | 27 |  | 27 | 19.4 | 1 | 0.99033 | 0 | 5.41 | 7.2 | 20.948 | 24.507 | 24.6281 | 24.7594 | 24.7594 | 24.8503 | 26.32%
WBL | S | 79.5 |  | 79.5 | 64 |  | 0.99774 | 10.4408 | 8.854 | - | 52.6632 | 47.8781 | 48.9806 | 49.5519 | 50.1833 | 51.1354 | -
| W | 79.5 |  | 79.5 | 68.7 |  | 1 | 0 | 8.854 | - | 45.0129 | 45.3502 | 46.1802 | 46.9902 | 47.5702 | 48.3302 | -
WETS 66kV | [7 empty] | 0
OYN | S | 27 |  | 27 | 15.2 | - | 0.90681 | 0 | 2.418 | - | 8.8318 | 8.2487 | 8.2597 | 8.1825 | 8.1053 | 8.0943 | -
| W | 27 |  | 27 | 15.2 | - | 0.77205 | 0 | 2.418 | - | 8.0933 | 8.2378 | 8.2249 | 8.186 | 8.1083 | 8.0694 | -
RVL | S | 19.5 |  | 19.5 | 20.4 | - | 0.99997 | 3.5438 | 2.45 | 7.5 | 20.3192 | 21.2806 | 21.5207 | 21.5307 | 21.5507 | 21.7107 | 4.317%
| W | 19.5 |  | 19.5 | 22.9 | - | 0.99525 | 0 | 2.45 | 7.5 | 12.7116 | 13.0118 | 13.062 | 13.1826 | 13.1926 | 13.2328 | -
WMN | S | 33 | 13.5 | 46.5 | 17.2 | 9 | 0.98194 | 3.4295 | 0.541 | 4.25 | 23.9446 | 25.2458 | 26.3253 | 26.2031 | 26.0809 | 26.0911 | 46.78% | 2339 | 3299 | 3181 | 3066 | 3076 | 1290 | 1561 | 1531 | 1501 | 1504
| W | 33 | 13.5 | 46.5 | 20.2 | 3 | 1 | 0 | 0.541 | 4.25 | 14.2681 | 16.5701 | 17.5401 | 18.1001 | 18.0101 | 17.9601 | -
Note 1: * indicates cold standby transformer
Note 2: Where load is above N-1 rating
Note 3: Generation capacity <1MW is mostly solar PV
Note 4: TNA generation <1MW based on load transfers to TNA

## Sub-transmission lines
Subtransmission line |  | Line Rating (MVA) | Hours Load is 95% of MD | Power Factor at MD | Load Transfers (MVA) | Generation Capacity (MW) | Historical Demand Worst case N-1 Scenario (MVA) | Forecast Demand Worst case N-1 Scenario (MVA) |  |  |  |  | % Load Above N-1 Rating (2021) | Energy at Risk (MWh) (N-1 50% PoE) |  |  |  |  | Hours at Risk (N-1 50% PoE)
[7 empty] | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 |  | 2021 | 2022 | 2023 | 2024 | 2025 | 2021 | 2022 | 2023 | 2024 | 2025
ATS 66kV
ATS-HCP | S | 109.7 | 4 | 0.9368 | 19.8 |  | 125 | 114.1 | 120.2 | 126.1 | 131.1 | 138.3 | 4.011%
| W | 134.9 | 4 | 0.9694 | 40.8 |  | 81.7 | 87.8 | 82.5 | 85.9 | 89.1 | 92.7 | -
ATS-WBE | S | 109.7 | 4 | 0.93291 | 19.8 |  | 125.2 | 114.2 | 120.3 | 126.2 | 131.2 | 138.4 | 4.102%
| W | 134.9 | 4 | 0.96822 | 40.8 |  | 81.8 | 87.9 | 82.5 | 85.9 | 89.1 | 93.7 | -
HCP-WBE | S | 109.7 | 4 | 0.96196 | 19.8 |  | 110.4 | 102.9 | 108.3 | 113.1 | 117.4 | 123.4 | -
| W | 134.9 | 4 | 0.98121 | 40.8 |  | 74.5 | 80.1 | 75.1 | 78.2 | 81 | 84.3 | -
ATS-LV1 | S | 135.5 |  | 0.97619 |  |  | 109.2 | 94.1 | 97.9 | 101.8 | 105.4 | 109.5 | -
| W | 142.3 |  | 0.98718 |  |  | 78 | 80 | 71.9 | 74.8 | 77.2 | 80.3 | -
ATS-LV2 | S | 135.5 |  | 0.97283 |  |  | 110.4 | 94.2 | 98.9 | 102.9 | 106.6 | 110.6 | -
| W | 142.3 |  | 0.98464 |  |  | 78.1 | 80.9 | 71.9 | 74.8 | 77.3 | 81.1 | -
ATS/BLTS 66kV
ATS-AC | S | 102.3 |  | 0.9891 |  |  | 36.7 | 32.3 | 33.1 | 33.1 | 32.9 | 34.3 | -
| W | 108 |  | 0.9969 |  |  | 32.3 | 27 | 27.7 | 29.2 | 29 | 29.3 | -
AC-CPL | S | 102.9 |  | 0.99143 |  | 22.5 | 35 | 30.2 | 30.8 | 30.7 | 30.5 | 31.8 | -
| W | 108 |  | 0.99351 |  | 22.5 | 30.8 | 25.2 | 25.8 | 27 | 26.7 | 27 | -
CPL-AL | S | 91.4 |  | 1 |  | 22.5 | 22 | 24.1 | 24.6 | 24 | 23.4 | 24.2 | -
| W | 91.4 |  | 0.87179 |  | 22.5 | 19.5 | 22.6 | 22.4 | 22.2 | 22.6 | 22.8 | -
AL-BLTS | S | 91.4 |  | 0.9541 |  |  | 30.5 | 23.7 | 25.2 | 26 | 26.5 | 26.7 | -
| W | 91.4 |  | 0.97872 |  |  | 28.2 | 18.5 | 20 | 21.5 | 20.6 | 20.8 | -
ATS-ATD | S | 101.7 |  | 1 |  |  | 7.5 | 11.4 | 14.2 | 18.7 | 22.7 | 22.6 | -
| W | 122.3 |  | 1 |  |  | 15.8 | 15.8 | 20.1 | 23.4 | 27.7 | 27.6 | -
BLTS-ATD | S | 97.2 |  | 0.91045 |  |  | 6.7 | 12.6 | 14.9 | 18.8 | 22.7 | 22.7 | -
| W | 125.7 |  | 1 |  |  | 15.9 | 15.9 | 20.2 | 23.5 | 27.8 | 27.7 | -
ATS-LVN | S | 109.7 |  | 0.97837 |  |  | 83.2 | 87.1 | 88.7 | 89.6 | 91.2 | 92.9 | -
| W | 134.9 |  | 0.98726 |  |  | 78.5 | 80.3 | 81.1 | 82.7 | 83.9 | 85.3 | -
BLTS-LVN | S | 109.7 |  | 0.97368 |  |  | 83.6 | 87.4 | 89.2 | 90.1 | 91.4 | 93.3 | -
| W | 122.3 |  | 0.98357 |  |  | 79.1 | 80.8 | 81.6 | 83.2 | 84.3 | 85.7 | -
ATS-SCI | S | 90.8 |  | 0.78636 |  |  | 44 | 46.3 | 43.8 | 48.3 | 53.3 | 53.3 | -
| W | 116 |  | 0.80525 |  |  | 45.7 | 45.7 | 45.5 | 45.7 | 45.7 | 45.7 | -
BLTS-SCI | S | 97.2 |  | 0.99167 |  |  | 72 | 69.3 | 68.9 | 68.8 | 70 | 69.8 | -
| W | 125.7 |  | 0.99418 |  |  | 68.7 | 68.6 | 68.4 | 68.3 | 68.2 | 69.3 | -
ATS-TYA | S | 102.3 |  | 1 |  |  | 19.2 | 19.9 | 20.3 | 19.4 | 19.3 | 19 | -
| W | 130.3 |  | 0.74879 |  |  | 20.7 | 19.2 | 20 | 18.5 | 18.6 | 18.8 | -
BLTS-TYA | S | 88 |  | 1 |  |  | 19.1 | 19.8 | 20.2 | 19.5 | 19.4 | 19.1 | -
| W | 112 |  | 0.75 |  |  | 20.8 | 19.2 | 20.1 | 18.5 | 18.6 | 18.7 | -
BLTS-BMH | S | 32.6 | 3 | 0.98366 | 3.2 | 14.35 | 30.6 | 29.6 | 30.8 | 31.7 | 32.6 | 34.5 | -
| W | 37.7 | 12 | 0.98446 | 7.5 | 14.35 | 19.3 | 20.6 | 21.7 | 22.5 | 23.4 | 24.4 | -
BATS 66kV
BATS-BAN1 | S | 96 | 6 | 0.92918 | 12.3 | 13.125 | 94.6 | 91.7 | 93.9 | 96 | 98.4 | 102.4 | -
| W | 114.3 | 21 | 0.9862 | 15 | 13.125 | 79.7 | 82.8 | 85.1 | 87.5 | 88.9 | 90.9 | -
BATS-BAN2 | S | 96 | 6 | 0.92455 | 12.3 | 13.125 | 94.1 | 92.1 | 94.2 | 96.4 | 98.8 | 102.8 | -
| W | 114.3 | 21 | 0.98361 | 15 | 13.125 | 79.3 | 82.3 | 85.3 | 87.8 | 89.3 | 91.3 | -
BAN-BGR | S | 46.3 |  | 0.98824 |  | 26.25 | 17 | 15.1 | 15.2 | 15.3 | 15.4 | 15.4 | -
| W | 49.7 |  | 0.98529 |  | 26.25 | 13.6 | 15.4 | 15.5 | 15.6 | 15.5 | 15.6 | -
BGR-ART | S | 45.7 |  | 1 |  | 26.25 | 15.7 | 14.1 | 14.3 | 14.3 | 14.4 | 14.4 | -
| W | 47.4 |  | 0.9845 |  | 26.25 | 12.9 | 14.4 | 14.5 | 14.5 | 14.5 | 14.6 | -
BATS-YSW/BGL | S | 36.6 | 4 | 0.99427 | 3.2 | 14.35 | 34.9 | 33.1 | 35.1 | 36.8 | 37.9 | 39.5 | -
| W | 37.1 | 5 | 0.95089 | 7.5 | 14.35 | 22.4 | 23.9 | 25.2 | 26.5 | 27.6 | 28.9 | -
YSW-BMH | S | 36.6 | 4 | 0.98582 | 3.2 | 14.35 | 28.2 | 26.8 | 28.5 | 29.8 | 30.7 | 32 | -
| W | 37.2 | 5 | 0.98889 | 7.5 | 14.35 | 18 | 19 | 19.7 | 20.5 | 21.2 | 22 | -
BATS-BAS1 | S | 83.5 |  | 0.95172 | 15.3084 |  | 87 | 82.8 | 84.6 | 86.5 | 88.6 | 91.7 | -
| W | 102.9 |  | 0.96904 | 20.3366 |  | 74.3 | 74.9 | 76.9 | 79 | 80.5 | 82.6 | -
BATS-BAS2/BGF | S | 93.2 |  | 0.9485 |  |  | 93.2 | 87.7 | 90.8 | 92.7 | 94.8 | 98 | -
| W | 94.9 |  | 0.96465 |  |  | 79.2 | 79.8 | 81.8 | 85 | 86.6 | 88.7 | -
BETS 66kV
BETS-BGO | S | 109.7 |  | 0.96687 |  |  | 99.6 | 101.5 | 106 | 108.4 | 110.5 | 114.3 | -
| W | 114.3 |  | 0.99299 |  |  | 71.3 | 77.4 | 79.7 | 83.4 | 84.1 | 86.4 | -
BGO-EHK | S | 54.9 | 4 | 0.94516 | 0 |  | 54.7 | 55.2 | 58.1 | 59.4 | 60.3 | 63.1 | 0.5464%
| W | 52.6 | 3 | 0.99189 | 4.8 |  | 37 | 40.2 | 41.7 | 43.9 | 44.4 | 45.6 | -
BETS-EHK | S | 111.4 |  | 0.96112 |  |  | 100.3 | 102.2 | 108.4 | 110.1 | 112.2 | 115.1 | -
| W | 111.4 |  | 0.99166 |  |  | 71.9 | 78.1 | 80.8 | 83.9 | 84.7 | 87 | -
BETS-CMN | S | 64 |  | 0.9849 |  |  | 59.6 | 57 | 58.6 | 59.4 | 59.6 | 61.1 | -
| W | 65.2 |  | 1 |  |  | 44.2 | 46.4 | 47.4 | 48.1 | 48.6 | 49.3 | -
CMN-MRO | S | 26.3 | 6 | 1 | 0 |  | 26.3 | 25.6 | 25.4 | 26.2 | 25.8 | 26.4 | -
| W | 34.9 | 4 | 0.99573 | 0 |  | 23.4 | 24.3 | 25.1 | 25.3 | 25.4 | 26 | -
BETS-MRO | S | 76.6 |  | 0.89818 |  |  | 65.8 | 61.9 | 63.6 | 64.3 | 65.1 | 67.2 | -
| W | 89.2 |  | 0.98698 |  |  | 46.1 | 48.5 | 50.9 | 51.6 | 52.1 | 53 | -
BETS-CTN | S | 26.3 | 6.5 | 0.99554 | 0.4 | 19.8 | 22.4 | 23.6 | 24 | 23.9 | 23.5 | 23.9 | -
| W | 30.3 | 3 | 1 | 0.4 | 19.8 | 17.1 | 20.2 | 21 | 21 | 20.9 | 20.9 | -
CTN-CBW | S | 108.6 |  | 0 |  | 19.8 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | -
| W | 113.2 |  | 0 |  | 19.8 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | -
DPTS 66kV
DPTS-MLN1 | S | 94.3 |  | 0.95529 |  |  | 85 | 78.8 | 91.5 | 99.9 | 103.8 | 109.6 | -
| W | 100.6 |  | 0.97101 |  |  | 55.2 | 58.2 | 62.8 | 75.9 | 79.6 | 82 | -
DPTS-MLN2 | S | 94.3 |  | 0.95719 |  |  | 84.1 | 78.7 | 91.4 | 98.8 | 103.7 | 108.4 | -
| W | 100.6 |  | 0.97283 |  |  | 55.2 | 58.2 | 62.8 | 75.9 | 79.1 | 81.1 | -
DPTS-SU1 | S | 91.4 |  | 0.95603 |  |  | 97.8 | 95.7 | 111 | 116.2 | 117.2 | 121 | 4.705%
| W | 91.4 |  | 0.96637 |  |  | 68.4 | 71.6 | 82 | 90.6 | 92.2 | 93.2 | -
DPTS-SU2 | S | 97.7 |  | 0.96213 |  |  | 97.7 | 94.6 | 109.8 | 113.7 | 115.9 | 117.2 | -
| W | 125.7 |  | 0.96898 |  |  | 67.7 | 70.8 | 81.1 | 89.7 | 91.1 | 92.1 | -
DPTS-TNA1 | S | 102.3 |  | 0.98658 |  |  | 44.7 | 66.9 | 75 | 83.3 | 85.7 | 88.3 | -
| W | 122.3 |  | 0.98737 |  |  | 39.6 | 53.2 | 56 | 64.7 | 69.4 | 71.4 | -
DPTS-TNA2 | S | 102.3 |  | 0.98658 |  |  | 44.7 | 66.9 | 75 | 83.3 | 85.7 | 88.3 | -
| W | 122.3 |  | 0.98737 |  |  | 39.6 | 53.2 | 56 | 64.7 | 69.4 | 71.4 | -
FBTS 66kV
FBTS-DLF1 | S | 87.5 |  | 0.95455 |  |  | 26.4 | 21.6 | 21.8 | 22.4 | 23.1 | 24.3 | -
| W | 87.5 |  | 0.95669 |  |  | 25.4 | 20.6 | 16.6 | 16.7 | 17.1 | 17.7 | -
FBTS-DLF3 | S | 87.5 |  | 0.95094 |  |  | 26.5 | 21.7 | 21.8 | 22.4 | 23.2 | 24.3 | -
| W | 87.5 |  | 0.95669 |  |  | 25.4 | 20.6 | 16.6 | 16.7 | 17.1 | 17.7 | -
GTS 66kV
GTS-BCG | S | 109.7 |  | 0.96047 |  |  | 86 | 80 | 82.7 | 84.6 | 87.5 | 91.1 | -
| W | 134.9 |  | 0.97315 |  |  | 59.6 | 57.9 | 60.2 | 62.1 | 63.5 | 65.3 | -
BCG-WPD | S | 91.4 |  | 0.98828 |  |  | 76.8 | 71.2 | 73.4 | 75.1 | 77.5 | 80.7 | -
| W | 91.4 |  | 0.99057 |  |  | 53 | 51.5 | 53.7 | 55.5 | 56.8 | 58.4 | -
GTS-WPD | S | 91.4 | 3 | 0.96572 | 9.5 |  | 84.6 | 78.8 | 81.4 | 84.4 | 86.1 | 89.6 | -
| W | 91.4 | 5 | 0.97647 | 19.8 |  | 59.5 | 57.8 | 59.3 | 61.1 | 62.5 | 65.2 | -
GTS-WIN | S | 74.3 |  | 0.99598 |  | 66 | 49.8 | 50.4 | 50.8 | 51.1 | 51.8 | 52.3 | -
| W | 87.4 |  | 0.9932 |  | 66 | 44.1 | 46.2 | 46.9 | 47.3 | 48.3 | 49 | -
MGW-CLC | S | 74.3 |  | 0.98701 |  | 66 | 38.5 | 38.6 | 39.1 | 39.2 | 39.4 | 39.8 | -
| W | 86.9 |  | 0.99699 |  | 66 | 33.2 | 35 | 35.3 | 35.6 | 36.3 | 36.6 | -
WIN-MGW | S | 94.9 |  | 0.96526 |  | 66 | 40.3 | 40.8 | 40.7 | 40.8 | 41.6 | 41.5 | -
| W | 99.5 |  | 0.97406 |  | 66 | 34.7 | 36.8 | 37.3 | 37.5 | 38.4 | 38.8 | -
GTS-CRO | S | 91.4 |  | 0.97523 |  |  | 32.3 | 36.8 | 48.9 | 51.4 | 51.7 | 51.6 | -
| W | 91.4 |  | 0.96113 |  |  | 28.3 | 29.8 | 38 | 49.4 | 49.1 | 49.2 | -
FDN-CRO | S | 109.7 |  | 0.9772 |  |  | 30.7 | 35.1 | 47.1 | 49.6 | 49.9 | 49.7 | -
| W | 134.9 |  | 0.95896 |  |  | 26.8 | 27.9 | 35.9 | 47.3 | 47.6 | 47.8 | -
GTS-FDN | S | 102.9 |  | 0.97523 |  |  | 32.3 | 36.8 | 48.9 | 51.5 | 51.7 | 51.6 | -
| W | 134.9 |  | 0.95819 |  |  | 28.7 | 29.9 | 38 | 49.5 | 49.8 | 50 | -
GTS-FNS | S | 88 |  | 0.97523 |  |  | 88.8 | 74.2 | 84.6 | 86.8 | 89.6 | 91.1 | -
| W | 112 |  | 0.97492 |  |  | 63.8 | 65.7 | 70.5 | 77.7 | 79.3 | 81.9 | -
FNS-SRC | S | 109.7 |  | 0.98131 |  |  | 53.5 | 37.8 | 45.4 | 48.1 | 51 | 52.2 | -
| W | 125.7 |  | 0.97253 |  |  | 36.4 | 36.4 | 36.6 | 40.2 | 41.9 | 45.2 | -
GTS-SRC | S | 109.7 |  | 0.97297 |  |  | 88.8 | 74.3 | 84.7 | 86.9 | 89.7 | 91.2 | -
| W | 134.9 |  | 0.97352 |  |  | 64.2 | 65.7 | 70.5 | 77.7 | 79.4 | 82.6 | -
GTS-GB | S | 135.5 |  | 0.90074 |  |  | 135 | 125.5 | 133.7 | 137.6 | 140.1 | 143.2 | -
| W | 142.3 |  | 0.96795 |  |  | 93.6 | 100.8 | 103.9 | 110.3 | 112.7 | 114.4 | -
GB-GL | S | 89.7 | 1 | 0.92388 | 15.9 |  | 115.6 | 107.4 | 111.2 | 114 | 116.2 | 119 | 19.73% | 29.3088 | 46.9248 | 65.087 | 82.8917 | 111.1361 | 4 | 6.25 | 8.5 | 10.5 | 13.25
| W | 100.6 | 2 | 0.98 | 18.5 |  | 80 | 86.6 | 88.5 | 91.3 | 93.6 | 95 | -
GCY-GL | S | 98.3 |  | 0.94785 |  |  | 76.7 | 70.6 | 75.7 | 77.8 | 79 | 80.5 | -
| W | 134.9 |  | 0.98827 |  |  | 59.7 | 60.1 | 62.2 | 66.8 | 68.4 | 69.2 | -
GTS-GCY | S | 102.9 | 1 | 0.91025 | 15.9 |  | 133.7 | 125.8 | 133.1 | 136.3 | 138.8 | 142 | 22.25% | 43.7752 | 91.9425 | 123.2921 | 154.4193 | 200.3447 | 5.75 | 10.5 | 13.5 | 17 | 20.25
| W | 110.3 | 2 | 0.97112 | 18.5 |  | 93.5 | 101.3 | 104.4 | 110.3 | 112.8 | 114.5 | -
GTS-GLE1 | S | 109.7 | 1 | 0.93254 |  |  | 134.9 | 125.3 | 133.3 | 139.5 | 143.7 | 147.6 | 14.22% | 15.1571 | 39.539 | 67.2268 | 92.6489 | 121.7801 | 2.25 | 4 | 6.25 | 8 | 9.5
| W | 133.7 | 1 | 0.96872 |  |  | 95.9 | 95.7 | 98.7 | 106.2 | 110.6 | 112.9 | -
GTS-GLE2 | S | 109.7 | 1 | 0.89539 |  |  | 145.3 | 133.1 | 142.2 | 152.2 | 156.7 | 162.5 | 21.33% | 37.2417 | 79.6326 | 155.8639 | 201.1028 | 270.0747 | 4 | 7.25 | 11.25 | 13.75 | 17
| W | 133.7 | 1 | 0.95161 |  |  | 99.2 | 99.2 | 102.3 | 110.5 | 115.1 | 119.5 | -
GLE-DDL1 | S | 74.3 |  | 0.95442 |  |  | 70.2 | 64.6 | 68 | 71.6 | 74.8 | 77 | -
| W | 86.9 |  | 0.98652 |  |  | 44.5 | 43.6 | 45.1 | 48.2 | 50.5 | 51.4 | -
GLE-DDL2 | S | 74.3 |  | 0.95312 |  |  | 70.4 | 64.8 | 69.3 | 72.9 | 75 | 77.2 | -
| W | 86.9 |  | 0.98876 |  |  | 44.5 | 43.6 | 45.1 | 49 | 51.4 | 52.3 | -
HOTS 66kV
HOTS-STL1 | S | 49.2 |  | 0.96667 |  | 13.125 | 27 | 26.7 | 27.2 | 27.1 | 27.2 | 27.1 | -
| W | 57.2 |  | 0.99606 |  | 13.125 | 25.4 | 27.6 | 28 | 27.9 | 28 | 28.2 | -
HOTS-STL2 | S | 25.7 |  | 0.98462 |  | 13.125 | 26 | 25.9 | 26.6 | 26.5 | 26.6 | 26.2 | 0.7782%
| W | 34.9 |  | 1 |  | 13.125 | 24.2 | 26.8 | 26.8 | 26.7 | 26.9 | 27 | -
STL-ART | S | 38.3 |  | 1 |  | 26.25 | 15.7 | 14.2 | 14.2 | 14.2 | 14.3 | 14.4 | -
| W | 43.4 |  | 0.98438 |  | 26.25 | 12.8 | 14.2 | 14.5 | 14.6 | 14.6 | 14.6 | -
HOTS-HSM1 | S | 49.2 |  | 0.99132 |  |  | 46.1 | 44 | 45.9 | 46.6 | 46.8 | 47.3 | -
| W | 52.6 |  | 1 |  |  | 32.4 | 33.6 | 35.2 | 36.5 | 36.7 | 36.9 | -
HOTS-HSM2 | S | 49.2 |  | 0.99348 |  |  | 46 | 43.9 | 45.8 | 46.6 | 46.8 | 47.3 | -
| W | 52.6 |  | 0.99691 |  |  | 32.4 | 33.6 | 35.1 | 36.4 | 36.7 | 36.9 | -
HOTS-KWF | S | 44 |  | 0.77976 |  | 31.05 | 16.8 | 14.7 | 14.9 | 14.8 | 14.7 | 14.8 | -
| W | 43.4 |  | 0.7541 |  | 31.05 | 12.2 | 11.8 | 11.9 | 12 | 11.9 | 11.9 | -
KWF-NHL | S | 44 |  | 0.99138 |  |  | 11.6 | 10.5 | 10.5 | 10.4 | 10.3 | 10.3 | -
| W | 43.4 |  | 1 |  |  | 8.4 | 8.2 | 8.2 | 8.2 | 8.1 | 8.1 | -
HOTS-CHM | S | 26.2 |  | 0.93333 |  |  | 3 | 2.8 | 2.8 | 2.7 | 2.7 | 2.7 | -
| W | 35.4 |  | 1 |  |  | 2.7 | 2.7 | 2.7 | 2.7 | 2.6 | 2.6 | -
KTS 66kV
SBY-GSB1 | S | 51.4 | 2 | 0.97445 |  |  | 54.8 | 58 | 63.4 | 64.7 | 65.5 | 66.9 | 12.84% | 17.7964 | 81.4122 | 94.8099 | 109.8932 | 140.8081 | 7.5 | 18.25 | 21 | 24 | 29.5
| W | 69.7 | 2 | 0.98984 |  |  | 49.2 | 50.9 | 57.5 | 62.1 | 62.8 | 64.2 | -
SBY-GSB2 | S | 76.6 |  | 0.96527 |  |  | 54.7 | 57.9 | 63.8 | 64.6 | 65.4 | 66.8 | -
| W | 89.2 |  | 0.98574 |  |  | 49.1 | 50.8 | 57.4 | 62 | 63.2 | 64 | -
GSB-WND1 | S | 109.7 |  | 0.98007 |  |  | 30.1 | 32.3 | 34.7 | 35.5 | 35.9 | 36.7 | -
| W | 114.3 |  | 0.99291 |  |  | 28.2 | 29.4 | 32.2 | 34.5 | 34.8 | 35.2 | -
GSB-WND2 | S | 46.3 |  | 0.98371 |  |  | 30.7 | 33 | 36 | 36.2 | 36.7 | 37.5 | -
| W | 49.7 |  | 0.98958 |  |  | 28.8 | 30 | 32.9 | 35.2 | 35.5 | 36.5 | -
KTS-SA1 | S | 116.6 |  | 0.9498 |  |  | 97.6 | 88.1 | 89.8 | 92 | 93.7 | 96.4 | -
| W | 122.3 |  | 0.97167 |  |  | 60 | 61.3 | 63.1 | 63.8 | 64.9 | 67.1 | -
KTS-SA2 | S | 108 |  | 0.94929 |  |  | 98.6 | 88.1 | 90.8 | 92.1 | 93.7 | 96.4 | -
| W | 122.3 |  | 0.97195 |  |  | 60.6 | 61.4 | 63.1 | 63.8 | 65.6 | 67.1 | -
KTS-SSE2 | S | 89.7 |  | 0.90546 |  |  | 75.1 | 75 | 80.8 | 81.4 | 82.1 | 83.6 | -
| W | 100.6 |  | 0.91905 |  |  | 63 | 65.9 | 68.6 | 72 | 73.2 | 73.9 | -
KTS-SSE1 | S | 89.7 |  | 0.9016 |  |  | 75.2 | 75.1 | 80.9 | 82.4 | 83 | 84.6 | -
| W | 100.6 |  | 0.91442 |  |  | 63.1 | 66 | 68.6 | 72.8 | 73.3 | 73.9 | -
KGTS 66kV
KGTS-CHA | S | 31.4 |  | 0.96689 |  |  | 15.1 | 16.8 | 16.9 | 16.8 | 16.8 | 16.9 | -
| W | 43.4 |  | 0.97917 |  |  | 14.4 | 15.9 | 16.3 | 16.2 | 16.2 | 16.4 | -
KGTS-SHL | S | 36 | 2 | 0.94692 | 0.8 | 25 | 47.1 | 48.8 | 52.3 | 53.5 | 54 | 54.8 | 35.56% | 101.1827 | 228.3169 | 299.4611 | 331.7483 | 392.1647 | 31.75 | 62 | 79.25 | 85.75 | 100.5
| W | 36 | 2 | 0.98131 | 1.7 | 25 | 32.1 | 34.2 | 36.9 | 39.9 | 40.4 | 41.4 | -
KGTS-GSF | S | 48.6 | 7 | 0.96145 | 0.8 | 25 | 41.5 | 43.2 | 47.4 | 48.2 | 48.7 | 49 | -
| W | 52.6 | 6 | 0.9863 | 1.7 | 25 | 29.2 | 31 | 33.4 | 35.4 | 35.7 | 36 | -
GSF-SHL | S | 76.6 | 7 | 0.97222 | 0.8 | 25 | 39.6 | 41.1 | 44.7 | 45.3 | 45.8 | 46.2 | -
| W | 89.2 | 6 | 0.98944 | 1.7 | 25 | 28.4 | 30.1 | 32.4 | 34.2 | 34.5 | 34.7 | -
RCTS 66kV
RCTS-MBN | S | 97.2 |  | 0.93206 |  |  | 57.4 | 56.7 | 59.5 | 61.2 | 61.6 | 62.3 | -
| W | 114.3 |  | 0.96825 |  |  | 37.8 | 40.4 | 41.4 | 44.3 | 44.9 | 45.2 | -
MBN-DTN | S | 74.3 |  | 0.92683 |  |  | 28.7 | 37.5 | 37.4 | 37.7 | 37.7 | 37.5 | -
| W | 86.9 |  | 0.93651 |  |  | 25.2 | 28.7 | 28.8 | 28.8 | 28.8 | 28.8 | -
MDA-MBN | S | 74.3 |  | 0.96029 |  |  | 55.4 | 58.2 | 62.3 | 64.3 | 64.7 | 64.6 | -
| W | 86.9 |  | 0.98158 |  |  | 38 | 40.3 | 41.9 | 44.8 | 45.7 | 46 | -
MDA-BNG | S | 104 |  | 0.94595 |  |  | 44.4 | 43.3 | 45.3 | 46.3 | 46.5 | 46.7 | -
| W | 114.3 |  | 0.97697 |  |  | 30.4 | 32.2 | 33.1 | 34.3 | 34.7 | 34.8 | -
RCTS-MDA1 | S | 72 | 2 | 0.93023 |  |  | 94.6 | 91.7 | 95.9 | 98.6 | 99.2 | 100.3 | 27.36% | 273.0632 | 509.5804 | 708.8847 | 758.175 | 852.8827 | 52 | 76.75 | 94.5 | 99 | 106.5
| W | 90.9 | 2 | 0.96635 |  |  | 62.4 | 66.6 | 68 | 72.7 | 73.6 | 74.1 | -
RCTS-MDA2 | S | 104 |  | 0.94078 |  |  | 103 | 100 | 105.3 | 108.1 | 108.7 | 109.7 | -
| W | 114.3 |  | 0.97101 |  |  | 69 | 73.7 | 75.6 | 80.2 | 81.3 | 81.8 | -
RCTS-YSF | S | 84.6 |  | 0.88889 |  |  | 9.9 | 9.3 | 9.2 | 9.1 | 9 | 9 | -
| W | 106.3 |  | 0.76667 |  |  | 9 | 9.5 | 9.4 | 9.3 | 9.2 | 9.2 | -
YSF-HTH | S | 17.7 |  | 0.90526 |  |  | 9.5 | 8.9 | 8.8 | 8.7 | 8.7 | 8.7 | -
| W | 35.4 |  | 0.77273 |  |  | 8.8 | 8.9 | 8.9 | 8.8 | 8.7 | 8.7 | -
RCTS-KSF | S | 84.6 |  | 0.9854 |  | 90 | 27.4 | 28.3 | 28.5 | 28.5 | 28.5 | 28.7 | -
| W | 106.3 |  | 0.94175 |  | 90 | 20.6 | 20.9 | 20.9 | 21 | 20.9 | 21 | -
KSF-RVL | S | 84.6 |  | 0.98155 |  | 90 | 27.1 | 27.9 | 28.2 | 28.1 | 28.2 | 28.3 | -
| W | 106.3 |  | 0.93137 |  | 90 | 20.4 | 20.6 | 20.6 | 20.7 | 20.7 | 20.8 | -
RVL-BSP | S | 84.6 |  | 0.96591 |  |  | 26.4 | 27.3 | 27.4 | 27.4 | 27.4 | 27.6 | -
| W | 106.3 |  | 0.92424 |  |  | 19.8 | 20.1 | 20 | 20.1 | 20.2 | 20.2 | -
BSP-BBD | S | 65.2 |  | 0.94025 |  |  | 31.8 | 35.3 | 36.4 | 36.1 | 35.8 | 35.8 | -
| W | 67.4 |  | 0.92275 |  |  | 23.3 | 27.2 | 27.3 | 28.3 | 28 | 27.9 | -
SHTS 66kV
SHTS-KYM1 | S | 79.4 |  | 0.9716 |  |  | 49.3 | 52.6 | 56.6 | 57 | 57.7 | 58.6 | -
| W | 90.3 |  | 1 |  |  | 37.4 | 38.9 | 40.4 | 42.4 | 42.9 | 43.4 | -
SHTS-KYM2 | S | 79.4 |  | 0.9739 |  |  | 49.8 | 53.2 | 57 | 57.7 | 58.1 | 59 | -
| W | 90.3 |  | 1 |  |  | 37.9 | 39.4 | 40.9 | 42.9 | 43.4 | 43.9 | -
KYM-ECA1 | S | 45.7 |  | 0.97846 |  |  | 32.5 | 38.2 | 39.5 | 39.9 | 40.4 | 41.1 | -
| W | 52.6 |  | 1 |  |  | 25.8 | 26.6 | 27.3 | 27.7 | 27.9 | 28.3 | -
KYM-ECA2 | S | 45.7 |  | 0.98154 |  |  | 32.5 | 39 | 39.6 | 40.8 | 41.2 | 42 | -
| W | 53.2 |  | 1 |  |  | 25.8 | 27.1 | 27.3 | 27.8 | 28 | 28.8 | -
SHP-KYM | S | 104 |  | 0.98701 |  |  | 23.1 | 22.3 | 26.7 | 27.2 | 26.8 | 27.4 | -
| W | 114.3 |  | 1 |  |  | 20.4 | 18.9 | 20.8 | 23.5 | 23.4 | 23.5 | -
SHTS-SHP | S | 101.7 |  | 0.97059 |  |  | 37.4 | 39.3 | 43.1 | 43.6 | 44 | 44.6 | -
| W | 116 |  | 1 |  |  | 29 | 29.6 | 31 | 33 | 33.3 | 33.7 | -
SHTS-MNA | S | 88 |  | 0.94931 |  |  | 86.8 | 86.3 | 89.5 | 90.8 | 91.8 | 93 | -
| W | 114.4 |  | 0.99818 |  |  | 55 | 57.6 | 59.7 | 61.4 | 61.8 | 62.5 | -
STN-MNA | S | 48.6 |  | 0.9619 |  |  | 42 | 43.8 | 44.6 | 45.1 | 45.8 | 46.8 | -
| W | 52.6 |  | 1 |  |  | 29.1 | 30.3 | 30.7 | 31.4 | 31.7 | 32.1 | -
SHTS-STN | S | 91.4 |  | 0.95863 |  |  | 84.6 | 83.9 | 87.2 | 87.9 | 89.4 | 91.1 | -
| W | 91.4 |  | 1 |  |  | 54.8 | 57 | 59.1 | 60.8 | 61.2 | 61.9 | -
SHTS-NKA | S | 91.4 |  | 0.93606 |  | 50 | 78.2 | 74.6 | 80.8 | 84 | 84.6 | 86.4 | -
| W | 91.4 |  | 0.97985 |  | 50 | 54.6 | 60.5 | 64 | 67.5 | 68.8 | 69.8 | -
SHTS-NSF | S | 98.3 |  | 0.94862 |  | 50 | 75.9 | 73.3 | 79.2 | 81.5 | 83.6 | 84.5 | -
| W | 114.3 |  | 0.98168 |  | 50 | 54.6 | 59.5 | 63 | 66.9 | 67.6 | 68.6 | -
NSF-NKA | S | 102.9 |  | 0.97746 |  | 50 | 71 | 68.8 | 73.8 | 75.7 | 77.3 | 77.7 | -
| W | 114.3 |  | 0.99619 |  | 50 | 52.5 | 57 | 60.1 | 63.6 | 64.3 | 65.1 | -
NKA-CME | S | 74.3 |  | 0.9689 |  |  | 41.8 | 37.9 | 40.2 | 41.6 | 41.9 | 42.5 | -
| W | 86.9 |  | 0.97112 |  |  | 27.7 | 29.2 | 30.6 | 32.2 | 32.7 | 32.9 | -
SHTS-SHN1 | S | 88 |  | 0.98087 |  |  | 36.6 | 36.6 | 38.2 | 39.1 | 39.8 | 40.5 | -
| W | 112 |  | 0.98819 |  |  | 25.4 | 26.9 | 27.7 | 29 | 29.5 | 29.7 | -
SHTS-SHN2 | S | 88 |  | 0.98087 |  |  | 36.6 | 36.6 | 38.2 | 39.1 | 39.8 | 40.5 | -
| W | 112 |  | 0.98819 |  |  | 25.4 | 26.9 | 27.7 | 29 | 29.5 | 29.7 | -
TGTS 66kV
TGTS-CDN | S | 76.6 |  | 0.98894 |  |  | 45.2 | 49.2 | 49.9 | 50.4 | 50.1 | 50.6 | -
| W | 85.7 |  | 0.99755 |  |  | 40.8 | 44.1 | 45.1 | 46.3 | 46.5 | 46.6 | -
COB-CDN | S | 49.2 |  | 1 |  |  | 24.3 | 25.7 | 25.6 | 25.6 | 26.6 | 26.5 | -
| W | 57.2 |  | 1 |  |  | 23.1 | 23.7 | 24.8 | 25.2 | 25.9 | 26.1 | -
CDN-CLC | S | 74.3 |  | 0.97512 |  | 66 | 40.2 | 40.4 | 40.8 | 41.6 | 41.2 | 41.6 | -
| W | 86.9 |  | 0.99125 |  | 66 | 34.3 | 36.1 | 36.4 | 37.4 | 37.4 | 37.7 | -
TGTS-COB | S | 109.7 |  | 0.98365 |  |  | 36.7 | 40.2 | 40.3 | 40.3 | 41.1 | 41.1 | -
| W | 116 |  | 0.98567 |  |  | 34.9 | 37 | 38.2 | 38.6 | 39.4 | 39.5 | -
TGTS-HTN | S | 47.4 | 5 | 0.86468 | 2.7 | 43.35 | 43.6 | 40 | 40.6 | 40.5 | 40.6 | 41 | -
| W | 48 | 5 | 0.95614 | 3.4 | 43.35 | 34.2 | 34.8 | 35.7 | 35.8 | 35.8 | 35.9 | -
NRB-HTN | S | 52.6 | 5 | 0.89078 | 2.7 | 43.35 | 29.3 | 28.9 | 29.1 | 29 | 29.3 | 29.2 | -
| W | 53.2 | 5 | 0.98507 | 3.4 | 43.35 | 26.8 | 27 | 27.4 | 27.6 | 27.5 | 27.7 | -
TGTS-NRB | S | 42.2 | 1 | 0.8141 | 2.7 | 43.35 | 46.8 | 44.4 | 45 | 44.9 | 45 | 45.3 | 5.213% | 0.83254 | 1.3912 | 1.2716 | 1.3912 | 1.8013 | 3.25 | 4.5 | 4.25 | 4.5 | 4.75
| W | 42.2 | 1 | 0.94556 | 3.4 | 43.35 | 34.9 | 35.7 | 36.8 | 37 | 36.9 | 37.1 | -
TGTS-KRT1 | S | 44 |  | 0.98824 |  | 16.0667 | 34 | 39.1 | 40 | 40.4 | 41 | 41.9 | -
| W | 44.6 |  | 0.98722 |  | 16.0667 | 31.3 | 37.7 | 38.4 | 39.1 | 39.6 | 40.1 | -
TGTS-KRT2 | S | 97.2 |  | 0.8825 |  | 16.0667 | 40 | 44.5 | 45.4 | 45.8 | 46.3 | 47.3 | -
| W | 116 |  | 0.9073 |  | 16.0667 | 35.6 | 42.7 | 43.5 | 44.2 | 44.6 | 45.3 | -
KRT-PLD1/CWF | S | 40 |  | 0.99387 |  | 18.2 | 16.3 | 20.6 | 20.7 | 20.7 | 20.8 | 21.1 | -
| W | 45.7 |  | 0.99448 |  | 18.2 | 18.1 | 20.3 | 20.5 | 20.8 | 20.7 | 21 | -
KRT-PLD2/YWF | S | 29.7 |  | 0.99412 |  | 30 | 17 | 21.8 | 22.1 | 22.1 | 22.2 | 22.5 | -
| W | 29.7 |  | 0.97449 |  | 30 | 19.6 | 21.6 | 21.7 | 21.9 | 21.9 | 22 | -
KRT-WBL | S | 46.9 |  | 0.92829 |  | 16.0667 | 25.1 | 18.4 | 19 | 19.3 | 19.6 | 20 | -
| W | 47.4 |  | 0.95187 |  | 16.0667 | 18.7 | 18.1 | 18.3 | 18.8 | 18.8 | 18.9 | -
TRG-WBL1 | S | 47.4 |  | 0.96173 |  |  | 39.2 | 42.8 | 43.9 | 44.3 | 45 | 46 | -
| W | 49.7 |  | 0.96875 |  |  | 35.2 | 41.1 | 41.9 | 42.7 | 43.3 | 43.8 | -
TRG-WBL2 | S | 45.7 |  | 0.9916 |  |  | 35.7 | 37.8 | 38.6 | 39 | 39.4 | 40.3 | -
| W | 46.3 |  | 0.99678 |  |  | 31.1 | 36 | 36.7 | 37.4 | 37.8 | 38.4 | -
TGTS-TRG1 | S | 91.5 |  | 0.99558 |  |  | 67.8 | 75.6 | 76.8 | 77.9 | 78.9 | 80.8 | -
| W | 91.5 |  | 0.99842 |  |  | 63.2 | 73 | 74.2 | 75 | 75.8 | 76.5 | -
TGTS-TRG2 | S | 91.5 |  | 0.99705 |  |  | 67.8 | 75.7 | 76.8 | 77.9 | 79 | 80.8 | -
| W | 91.5 |  | 0.99842 |  |  | 63.2 | 73.1 | 74.2 | 75 | 75.8 | 76.5 | -
WETS 66kV
WETS-HTH | S | 17.7 |  | 0.91398 |  |  | 9.3 | 8.7 | 8.7 | 8.7 | 8.6 | 8.6 | -
| W | 35.4 |  | 0.78571 |  |  | 8.4 | 8.6 | 8.7 | 8.7 | 8.6 | 8.5 | -
HTH-OYN | S | 17.7 |  | 0.91209 |  |  | 9.1 | 8.6 | 8.5 | 8.5 | 8.4 | 8.4 | -
| W | 35.4 |  | 0.77381 |  |  | 8.4 | 8.5 | 8.5 | 8.5 | 8.4 | 8.3 | -
WETS-WSF | S | 84.6 |  | 0.95367 |  | 87.8 | 25.9 | 27.4 | 28.5 | 28.4 | 28.2 | 28.4 | -
| W | 106.3 |  | 0.99315 |  | 87.8 | 14.6 | 17.2 | 18.2 | 18.8 | 18.7 | 18.7 | -
WSF-WMN | S | 31.4 |  | 0.95349 |  |  | 25.8 | 27.3 | 28.4 | 28.4 | 28.2 | 28.3 | -
| W | 43.4 |  | 1 |  |  | 14.5 | 17.2 | 18.2 | 18.8 | 18.7 | 18.6 | -
WETS-BSP | S | 84.6 | 10 | 0.96823 | 0 | 88 | 59.8 | 65.1 | 66.4 | 66.2 | 66.1 | 66.1 | -
| W | 106.3 | 1 | 0.98798 | 0.76923 | 88 | 41.6 | 46 | 46.3 | 47.3 | 47.1 | 46.9 | -
Note 1: Generation capacity is specified at the location (sub-transmission line/ loop) where the generation is connected to the network.
Note 2: The demand figures are actuals for summer and forecast for winter.
Note 3: Forecast demand worst case N-1 scenario refers to the expected load that the sub-transmission line would supply in the event of the worst case outage of a sub-transmission line within the loop system.
Note 4: Radial lines are studied with the expected load under system normal (or N) conditions and also under N-1 if normally open loop arrangement exists. Where load does not exceed the N rating, the N-1 risk is shown if this is worse case.