## Zone substations
Zone Substation |  | On-load Capacity - Nameplate Rating (MVA) | Hot or Cold Spare Capacity - Nameplate Rating (MVA) (note 1) | Total Capacity - Nameplate Rating (MVA) | Cyclic N-1 Rating (MVA) | Hours Load is ≥ 95% of MD (note 2) | Station Power Factor at MD | Load Transfers (MVA) | Generation Capacity <1MW (MW) (notes 3 & 4) | Generation Capacity >1MW (1MW) | Actual Demand (MVA) | 50% PoE Forecast Demand (MVA) |  |  |  |  | % Load Above N-1 Rating (2022) | Energy at Risk (MWh) (N-1 50% PoE) |  |  |  |  | Hours at Risk (N-1 50% PoE)
[11 empty] | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2022 | 2023 | 2024 | 2025 | 2026
ATS 66kV
LV | S | 99 |  | 99 | 79.8 | 2.25 |  | 15.661 | 46.5 | - | 81.0124 | 105.2331 | 112.829 | 116.3804 | 116.8724 | 120.5299 | 31.87% | 298.8825 | 557.7633 | 711.6544 | 734.7993 | 931.0588 | 32.75 | 50 | 58.5 | 60 | 76.25
LV | W | 99 |  | 99 | 95.4 | 8.75 |  |  | 45.928 | - | 71.8369 | 87.0359 | 92.2781 | 93.6718 | 95.1389 | 99.2877 | -
WBE | S | 99 |  | 99 | 82.8 | 3 | 0.98572 | 12.079 | 44.8 | 13.9 | 90.3933 | 108.5768 | 115.4221 | 117.2556 | 119.5519 | 124.5399 | 31.13% | 412 | 713 | 810 | 942 | 1269 | 43 | 62 | 68 | 74 | 92
WBE | W | 99 |  | 99 | 92.2 | 5 | 0.99799 |  | 39.963 | 13.9 | 74.669 | 82.6503 | 86.7412 | 88.565 | 91.488 | 96.3109 | -
ATS/BLTS 66kV
AC | S | 40 |  | 40 | 30 |  | 0.91758 | 0 | 0.1 | - | 2.1853 | 3.1182 | 3.5247 | 4.2469 | 4.2604 | 4.3075 | -
AC | W | 40 |  | 40 | 30 |  | 0.96593 |  | 0.1 | - | 2.0707 | 3.2999 | 4.1066 | 4.2868 | 4.3092 | 4.3758 | -
AL | S | 30 |  | 30 | 34.2 |  | 0.96541 | 22 | 4.4 | - | 19.0691 | 21.5149 | 22.5457 | 22.3921 | 22.4052 | 22.8907 | -
AL | W | 30 |  | 30 | 38.6 |  | 0.97658 |  | 4.054 | - | 17.6496 | 19.2343 | 19.4479 | 19.4109 | 19.6368 | 20.2208 | -
BMH | S | 27 |  | 27 | 19.1 | 2 | 0.99791 | 5.144 | 10.2 | - | 24.0216 | 29.9839 | 32.5292 | 34.9459 | 35.3765 | 36.4868 | 56.98% | 424 | 1292 | 1899 | 2235 | 3004 | 246 | 585 | 773 | 878 | 1107
BMH | W | 27 |  | 27 | 20.2 | 5 | 0.99971 |  | 9.472 | - | 22.0015 | 24.367 | 27.1721 | 28.0293 | 28.6407 | 29.7512 | 20.63%
LVN11 | S | 30 |  | 30 | 32.5 |  |  |  |  | - | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | -
LVN11 | W | 30 |  | 30 | 35.9 |  |  |  |  | - | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | -
LVN | S | 99 |  | 99 | 79.7 |  | 0.9852 |  | 7 | - | 66.5536 | 75.3721 | 79.9662 | 83.235 | 83.098 | 84.5535 | -
LVN | W | 99 |  | 99 | 85 |  | 0.99915 |  | 5.439 | - | 64.2038 | 74.2592 | 78.8909 | 79.6049 | 80.2526 | 82.2973 | -
BATS 66kV
ART | S | 20 |  | 20 | 13.6 |  | 0.99802 | 2.2863 | 5.7 | 6.9 | 13.0576 | 13.9425 | 14.4734 | 14.0956 | 13.8618 | 13.9332 | 2.518%
ART | W | 20 |  | 20 | 15.2 |  | 0.99614 | 0 | 5.134 | 6.9 | 13.0868 | 14.3409 | 14.3693 | 14.1144 | 14.0488 | 14.2646 | -
BAN | S | 120 |  | 120 | 96.4 |  | 0.99017 | 4.7631 | 26.2 | 6.1 | 71.2279 | 80.9469 | 84.5165 | 85.5486 | 85.678 | 87.7808 | -
BAN | W | 120 |  | 120 | 104.4 |  | 0.994 | 0 | 23.805 | 6.1 | 74.6434 | 83.4095 | 85.7024 | 86.1619 | 87.5084 | 90.6939 | -
BAS | S | 99 |  | 99 | 76 |  | 0.99886 | 0 | 30.6 | 7.15 | 65.2421 | 79.7547 | 81.6695 | 83.4519 | 83.5848 | 85.6358 | 4.94%
BAS | W | 99 |  | 99 | 84.6 |  | 0.99999 | 12.5747 | 27.74 | 7.15 | 71.8734 | 74.8881 | 77.7481 | 78.3912 | 79.6151 | 82.4998 | -
BETS 66kV | [7 empty] | 0
BGO | S | 66 |  | 66 | 38.5 | 3 | 0.97879 | 21.4 | 14.6 | - | 40.8503 | 44.2979 | 46.0518 | 45.537 | 45.3679 | 46.3115 | 15.06% | 30 | 50 | 44 | 42 | 54 | 11 | 15 | 14 | 14 | 16
BGO | W | 66 |  | 66 | 45.4 | 12 | 0.99813 | 0 | 13.143 | - | 33.0016 | 36.4144 | 36.6149 | 36.1639 | 36.3508 | 37.414 | -
CMN | S | 66 |  | 66 | 43 |  | 0.99635 | 0 | 17 | - | 24.2224 | 28.6737 | 28.8982 | 28.4636 | 28.2611 | 28.7223 | -
CMN | W | 66 |  | 66 | 49.5 |  | 0.98136 | 0 | 13.146 | - | 26.8893 | 25.689 | 25.7041 | 25.5838 | 25.6523 | 26.3433 | -
CTN | S | 39.5 |  | 39.5 | 33.7 |  | 0.96629 | 0 | 7.8 | 7.2 | 18.0645 | 19.3127 | 20.07 | 19.6631 | 19.2529 | 19.2369 | -
CTN | W | 39.5 |  | 39.5 | 38.4 |  | 0.95866 | 0 | 7.115 | 7.2 | 16.806 | 17.7329 | 17.9196 | 17.5219 | 17.3389 | 17.4604 | -
EHK | S | 54 |  | 54 | 36.4 | 3 | 0.97671 | 14.975 | 15.9 |  | 45.8158 | 55.4734 | 57.5202 | 57.9338 | 58.308 | 59.8894 | 52.4% | 1148 | 1588 | 1698 | 1860 | 2513 | 272 | 367 | 393 | 443 | 608
EHK | W | 54 |  | 54 | 41 | 3 | 0.99867 | 0 | 14.17 | - | 39.6461 | 45.848 | 46.9041 | 47.2246 | 48.0909 | 49.881 | 11.82%
MRO | S | 27 |  | 27 | 18.3 | 3 | 0.99527 | 3.734 | 10.3 | - | 19.558 | 23.1013 | 23.335 | 23.7833 | 23.5634 | 23.776 | 26.24% | 57 | 65 | 82 | 73 | 81 | 37 | 41 | 50 | 46 | 49
MRO | W | 27 |  | 27 | 20.2 | 10 | 0.98582 | 0 | 9.671 | - | 17.6062 | 17.8831 | 18.5173 | 18.5968 | 18.6052 | 18.9674 | -
DPTS 66kV | [7 empty] | 0
MLN | S | 99 |  | 99 | 79.8 |  | 0.99997 | 0 | 33.7 | - | 66.6476 | 82.4621 | 84.8629 | 90.6126 | 92.5561 | 97.348 | 3.336%
MLN | W | 99 |  | 99 | 83.4 |  | 0.99971 | 0 | 29.043 | - | 57.9499 | 62.0684 | 67.4165 | 69.8831 | 71.5077 | 76.5594 | -
SU | S | 99 |  | 99 | 93 | 4 | 0.99938 | 12.194 | 24 | - | 77.2236 | 97.7964 | 109.1472 | 108.5975 | 108.3536 | 110.3365 | 5.157% | 5 | 141 | 129 | 124 | 171 | 3 | 26 | 25 | 24 | 30
SU | W | 99 |  | 99 | 99 | 13 | 0.99952 | 0 | 22.019 | - | 68.5454 | 88.1823 | 90.4924 | 90.0253 | 90.3743 | 92.9938 | -
TNA | S | 66 |  | 99 | 95.2 |  | 0.99977 | 16.3852 | 30.1 | 8.8 | 59.2929 | 71.6913 | 91.2663 | 112.9444 | 115.8433 | 119.3189 | -
TNA | W | 66 |  | 99 | 95.2 |  | 0.99953 | 0 | 21.184 | 8.8 | 45.7328 | 59.9143 | 88.058 | 96.337 | 98.4825 | 101.5722 | -
FBTS 66kV | [7 empty] | 0
DLF | S | 66 |  | 66 | 42 |  | 0.99454 | 0 | 0.064 | - | 12.8199 | 16.7172 | 17.1928 | 16.9969 | 16.8939 | 17.3169 | -
DLF | W | 66 |  | 66 | 49.3 |  | 0.99993 |  | 0.064 | - | 9.809 | 13.6234 | 13.8004 | 13.6545 | 13.7295 | 14.241 | -
GTS 66kV | [7 empty] | 0
CLC | S | 79 |  | 79 | 49.2 |  | 0.99925 | 0 | 9.2 | - | 39.8912 | 36.9007 | 37.3357 | 36.6562 | 36.0392 | 36.2106 | -
CLC | W | 79 |  | 79 | 54.8 |  | 0.99974 | 0 | 8.586 | - | 38.6986 | 38.5325 | 38.5301 | 37.8767 | 37.7597 | 38.4028 | -
CRO | S | 60 |  | 60 | 34.3 | 5 | 0.98848 | 10.365 | 9.9 | - | 27.3547 | 38.0134 | 46.9161 | 47.459 | 47.1545 | 47.4694 | 10.83% | 34 | 522 | 590 | 563 | 654 | 26 | 184 | 204 | 200 | 234
CRO | W | 60 |  | 60 | 38 | 7 | 0.99894 | 0 | 9.393 | - | 27.8579 | 41.0618 | 43.5981 | 43.8161 | 43.8374 | 44.4442 | 8.057%
DDL | S | 66 |  | 66 | 39.7 | 2 | 0.99296 | 6.668 | 27.1 | 1.1 | 57.757 | 61.7827 | 65.0099 | 66.7394 | 66.7203 | 68.2033 | 55.62% | 235 | 383 | 449 | 486 | 663 | 38 | 75 | 87 | 99 | 146
DDL | W | 66 |  | 66 | 47.2 | 3 | 0.99963 | 0 | 24.752 | 1.1 | 50.3993 | 52.2579 | 55.3705 | 55.9438 | 56.6154 | 58.4268 | 10.72%
FNS | S | 99 |  | 99 | 87.2 |  | 0.98344 | 0 | 10.8 | 1 | 34.3467 | 45.1506 | 48.6776 | 52.7983 | 52.7784 | 54.3855 | -
FNS | W | 99 |  | 99 | 98.6 |  | 0.98088 | 0 | 9.764 | 1 | 31.7404 | 41.5375 | 45.9332 | 46.8463 | 47.421 | 49.4515 | -
GB | S | 37.5 |  | 37.5 | 37.6 |  | 0.90999 | 0 | 1.4 | - | 14.6851 | 18.9421 | 20.2205 | 27.917 | 28.888 | 29.0328 | -
GB | W | 37.5 |  | 37.5 | 37.6 |  | 0.95666 | 0 | 1.248 | - | 12.6759 | 18.1412 | 21.2443 | 27.2924 | 27.3163 | 27.5482 | -
GCY | S | 66 |  | 66 | 37.8 | 3 | 0.9679 | 16.385 | 5.9 | 5.5 | 35.7116 | 43.8313 | 45.1783 | 47.8349 | 48.0197 | 48.4196 | 15.96% | 28 | 46 | 104 | 109 | 121 | 12 | 18 | 33 | 34 | 37
GCY | W | 66 |  | 66 | 43.9 | 3 | 0.9878 | 0 | 5.386 | 5.5 | 31.7581 | 35.708 | 38.2354 | 39.8102 | 39.7475 | 40.3662 | -
GL | S | 80 |  | 80 | 47.6 | 3 | 0.98978 | 14.328 | 19.4 | - | 53.0947 | 61.3866 | 62.831 | 62.5077 | 61.9142 | 62.7548 | 28.96% | 187 | 255 | 245 | 249 | 364 | 58 | 76 | 73 | 78 | 115
GL | W | 80 |  | 80 | 47.6 | 4 | 0.9975 | 0 | 18.069 | - | 52.9676 | 54.4092 | 55.4152 | 55.3559 | 55.7131 | 57.2753 | 14.31%
GLE | S | 79.5 |  | 79.5 | 53.3 |  | 0.98365 | 11.8126 | 23.5 | - | 50.6253 | 54.8041 | 57.0118 | 57.5421 | 57.2363 | 58.1896 | 2.822%
GLE | W | 79.5 |  | 79.5 | 59.1 |  | 0.99142 | 0 | 21.326 | - | 49.7586 | 52.1908 | 53.6613 | 53.8912 | 54.239 | 55.6823 | -
WIN | S | 20.5 |  | 20.5 | 10.5 |  | 0.87723 | 0 | 4.7 | - | 8.247 | 9.7254 | 9.8541 | 9.7802 | 9.7574 | 9.9537 | -
WIN | W | 20.5 |  | 20.5 | 10.5 |  | 0.92419 | 0 | 4.304 | - | 9.5242 | 10.0983 | 10.1659 | 10.1403 | 10.256 | 10.5656 | -
WPD | S | 79.5 |  | 79.5 | 56.8 | 2 | 0.99535 | 11.432 | 34.6 | - | 72.7848 | 87.0843 | 89.4902 | 90.0793 | 90.2726 | 92.9622 | 53.32% | 472 | 607 | 678 | 778 | 1244 | 75 | 103 | 119 | 145 | 233
WPD | W | 79.5 |  | 79.5 | 62.6 | 4 | 0.99995 | 0 | 25.911 | - | 70.8291 | 71.8039 | 73.2998 | 74.1806 | 75.3962 | 78.5419 | 14.7%
HOTS 66kV | [7 empty] | 0
CHM | S | 33 |  | 33 | 36.9 |  | 0.98665 | 0 | 0.982 | - | 2.5298 | 2.8576 | 2.8272 | 2.7313 | 2.6556 | 2.6398 | -
CHM | W | 33 |  | 33 | 44.1 |  | 0.95714 | 0 | 0.982 | - | 2.5827 | 2.6929 | 2.6357 | 2.5587 | 2.5166 | 2.5289 | -
HSM | S | 40.5 |  | 40.5 | 39.7 | 3 | 0.99952 | 3.811 | 15.7 | - | 37.1476 | 42.7249 | 43.5917 | 45.8706 | 45.3588 | 45.6579 | 7.619% | 8 | 14 | 50 | 40 | 46 | 6 | 11 | 24 | 22 | 23
HSM | W | 40.5 |  | 40.5 | 40.4 | 5 | 0.9976 | 0 | 14.337 | - | 33.2357 | 33.9928 | 36.6482 | 37.0778 | 37.016 | 37.6486 | -
NHL | S | 20 |  | 20 | 13 |  | 0.99885 | 0 | 3.1 | - | 10.698 | 11.296 | 11.275 | 11.3261 | 11.0387 | 10.9938 | -
NHL | W | 20 |  | 20 | 16.2 |  | 0.98944 | 0 | 3.014 | - | 9.0573 | 9.186 | 9.3692 | 9.2133 | 9.0946 | 9.1588 | -
STL | S | 27 |  | 27 | 18.5 | 3 | 0.9865 | 4.6 | 5 | - | 21.0735 | 20.0708 | 20.758 | 20.2934 | 19.9458 | 20.0288 | 8.491% | 4 | 11 | 6 | 3 | 4 | 4 | 4 | 3 | 2 | 3
STL | W | 27 |  | 27 | 18.8 | 5 | 0.97942 | 0 | 4.693 | - | 19.3672 | 19.4863 | 19.4495 | 19.0862 | 18.9901 | 19.2686 | 3.651%
KGTS 66kV | [7 empty] | 0
CHA | S | 27 |  | 27 | 15.2 |  | 0.96461 | 0 | 6.1 | - | 14.3495 | 13.8743 | 13.8643 | 13.4803 | 13.1929 | 13.2122 | -
CHA | W | 27 |  | 27 | 15.2 |  | 0.99999 | 0 | 5.736 | - | 13.1315 | 13.7846 | 13.6163 | 13.3079 | 13.1884 | 13.3389 | -
SHL | S | 40.5 |  | 40.5 | 36.7 |  | 0.99942 | 2.6674 | 12.3 | 14.4 | 34.9153 | 38.1247 | 39.7471 | 39.3499 | 38.8738 | 39.2205 | 3.882%
SHL | W | 40.5 |  | 40.5 | 40.4 |  | 0.9877 | 0 | 11.432 | 14.4 | 28.5049 | 30.6604 | 31.144 | 30.7047 | 30.6778 | 31.2311 | -
KTS 66kV | [7 empty] | 0
GSB | S | 66 |  | 66 | 49.5 |  | 0.99999 | 0 | 10.7 | - | 17.451 | 22.531 | 23.639 | 23.5963 | 23.513 | 24.085 | -
GSB | W | 66 |  | 66 | 49.5 |  | 0.99955 | 0 | 9.817 | - | 20.9108 | 22.7514 | 23.1804 | 23.2809 | 23.5637 | 24.4162 | -
SA | S | 93 |  | 93 | 81.2 | 3 | 0.99998 | 5.906 | 27 | - | 70.0625 | 87.3683 | 89.3469 | 89.9885 | 89.8783 | 91.7623 | 7.596% | 13 | 25 | 30 | 29 | 48 | 5 | 8 | 9 | 8 | 12
SA | W | 93 |  | 93 | 89.6 | 8 | 0.99795 | 0 | 22.893 | - | 63.3077 | 66.2001 | 67.832 | 68.2344 | 69.1077 | 71.3954 | -
SSE | S | 99 |  | 99 | 89.7 |  | 0.96559 | 14.137 | 12.3 | - | 60.2041 | 71.377 | 73.7633 | 73.4659 | 72.5272 | 73.332 | -
SSE | W | 99 |  | 99 | 99 |  | 0.9784 | 0 | 11.551 | - | 59.2689 | 64.0928 | 65.3535 | 64.3827 | 64.1443 | 65.521 | -
WND | S | 66 |  | 66 | 37.5 |  | 0.99865 | 0 | 15.7 | 4.7 | 24.3093 | 26.9394 | 27.589 | 28.0006 | 28.0212 | 28.6645 | -
WND | W | 66 |  | 66 | 42.7 |  | 0.99389 | 0 | 14.595 | 1.5 | 29.1041 | 30.2933 | 31.002 | 31.068 | 31.4757 | 32.5335 | -
RCTS 66kV | [7 empty] | 0
BBD | S | 66 |  | 66 | 45.2 |  | 0.98926 | 1.4099 | 0.7 | - | 29.113 | 31.0417 | 32.3409 | 33.2361 | 32.4674 | 32.3313 | -
BBD | W | 66 |  | 66 | 49.5 |  | 0.95687 | 0 | 0.42 | - | 19.8133 | 22.2489 | 23.7333 | 23.9637 | 23.5591 | 23.5895 | -
MBN | S | 60 |  | 59 | 37.6 | 6 | 0.99935 | 11.546 | 13.8 | - | 39.2545 | 42.3957 | 44.588 | 47.1405 | 47.4149 | 47.9696 | 12.75% | 40 | 103 | 222 | 238 | 272 | 24 | 41 | 69 | 72 | 78
MBN | W | 60 |  | 59 | 40.4 | 3 | 0.99999 | 0 | 11.947 | - | 26.3966 | 28.0632 | 30.8746 | 32.0794 | 32.5258 | 33.1556 | -
MDA | S | 66 |  | 66 | 39.7 | 5 | 0.95657 | 15.318 | 13.8 | - | 42.7245 | 50.0313 | 51.5402 | 50.9166 | 50.0307 | 50.3908 | 26.02% | 219 | 316 | 273 | 219 | 240 | 66 | 86 | 77 | 66 | 70
MDA | W | 66 |  | 66 | 44.6 | 4 | 1 | 0 | 12.167 | - | 36.7787 | 39.3871 | 39.7704 | 38.975 | 38.6194 | 39.1422 | -
SHTS 66kV | [7 empty] | 0
CME | S | 40.5 |  | 40.5 | 32.3 | 1 | 0.99981 | 0 | 13.2 | 14.25 | 28.7923 | 41.6476 | 42.4129 | 42.803 | 42.6471 | 43.2122 | 28.94% | 124 | 158 | 177 | 169 | 198 | 49 | 58 | 62 | 61 | 67
CME | W | 40.5 |  | 40.5 | 37.3 | 2 | 0.99829 | 0 | 12.323 | 14.25 | 23.6115 | 24.7376 | 25.5079 | 25.723 | 25.8042 | 26.4802 | -
ECA | S | 40.5 |  | 40.5 | 34.6 |  | 0.99624 | 5.4871 | 13.6 | 9.6 | 27.5238 | 35.0434 | 36.963 | 37.6509 | 37.3975 | 37.9819 | 1.282%
ECA | W | 40.5 |  | 40.5 | 40.4 |  | 0.99333 | 0 | 12.578 | 4.8 | 26.7367 | 29.8168 | 30.9805 | 30.8922 | 31.0203 | 31.7859 | -
KYM | S | 40.5 |  | 40.5 | 33.8 |  | 0.99474 | 0 | 11 | - | 24.338 | 31.164 | 32.9612 | 32.6884 | 32.4384 | 32.7912 | -
KYM | W | 40.5 |  | 40.5 | 38.8 |  | 0.96799 | 0 | 10.216 | - | 20.5652 | 25.8765 | 26.1597 | 25.8925 | 25.8579 | 26.2789 | -
MNA | S | 66 |  | 66 | 37 | 5 | 0.99525 | 8.1 | 13.3 | 5.8 | 37.3521 | 44.4983 | 45.2531 | 45.649 | 45.3341 | 46.0319 | 20.27% | 131 | 170 | 193 | 174 | 217 | 55 | 65 | 71 | 66 | 77
MNA | W | 66 |  | 66 | 42.5 | 9 | 0.98125 | 0 | 12.084 | 1 | 29.5633 | 30.2559 | 31.106 | 31.1494 | 31.2883 | 32.0711 | -
NKA | S | 39.5 |  | 39.5 | 30.5 |  | 0.97538 | 1.9053 | 11.6 | 14.6 | 26.079 | 29.7711 | 30.313 | 30.39 | 30.0313 | 30.3099 | -
NKA | W | 39.5 |  | 39.5 | 30.5 |  | 0.96722 | 0 | 10.508 | 9.8 | 24.9283 | 27.536 | 28.0534 | 27.7631 | 27.777 | 28.3295 | -
SHN | S | 66 |  | 66 | 40 |  | 0.98406 | 0 | 13.2 | 5.4 | 31.4715 | 36.6672 | 38.0372 | 37.7138 | 37.4294 | 37.9249 | -
SHN | W | 66 |  | 66 | 44.1 |  | 0.99511 | 0 | 11.451 | 5.4 | 27.2445 | 27.7045 | 28.0584 | 27.7793 | 27.7235 | 28.2238 | -
SHP | S | 66 |  | 66 | 36.6 |  | 0.98688 | 0 | 6.5 | 28.8 | 21.8007 | 22.44 | 22.7077 | 22.2794 | 21.9694 | 22.1054 | -
SHP | W | 66 |  | 66 | 41.9 |  | 0.99963 | 0 | 5.938 | 19.2 | 18.6648 | 19.7271 | 19.5366 | 19.2318 | 19.1944 | 19.5043 | -
STN | S | 79 |  | 79 | 61.9 |  | 0.99556 | 0 | 14.1 | 7.4 | 43.7058 | 48.1457 | 48.9943 | 48.4002 | 48.1018 | 48.9508 | -
STN | W | 79 |  | 79 | 61.9 |  | 0.98688 | 0 | 12.729 | 3.3 | 35.4366 | 35.8927 | 35.9248 | 35.6164 | 35.8352 | 36.7946 | -
TGTS 66kV | [7 empty] | 0
CDN | S | 20 |  | 20 | 17.2 |  | 0.99998 | 0 | 3.8 | - | 12.1002 | 14.413 | 14.5174 | 14.2432 | 13.9619 | 13.9624 | -
CDN | W | 20 |  | 20 | 18.2 |  | 0.9998 | 0 | 3.594 | - | 13.665 | 14.6966 | 14.5101 | 14.1956 | 14.1073 | 14.3127 | -
COB | S | 26 |  | 26 | 15 |  | 0.93049 | 4.1535 | 1 | - | 14.0385 | 14.7747 | 14.7888 | 14.4004 | 14.0784 | 14.054 | -
COB | W | 26 |  | 26 | 15 |  | 0.95641 | 0 | 0.896 | - | 13.518 | 14.2339 | 14.0261 | 13.6809 | 13.5472 | 13.68 | -
HTN | S | 39.5 |  | 39.5 | 34.2 |  | 0.99987 | 3.9629 | 8.1 | - | 23.4414 | 28.6239 | 28.5508 | 27.7091 | 27.0539 | 27.0308 | -
HTN | W | 39.5 |  | 39.5 | 38.4 |  | 0.99995 | 0 | 7.608 | - | 24.8532 | 25.6538 | 25.4261 | 24.9124 | 24.7634 | 25.129 | -
KRT | S | 40.5 |  | 40.5 | 33.4 |  | 0.99458 | 10 | 5.9 | - | 27.4598 | 25.776 | 26.261 | 26.0244 | 25.7835 | 26.0638 | -
KRT | W | 40.5 |  | 40.5 | 37.6 |  | 0.99913 | 0 | 5.301 | - | 16.1031 | 27.7057 | 27.6068 | 27.3275 | 27.5248 | 28.269 | -
PLD | S | 32 |  | 32 | 22.1 |  | 0.99166 | 0 | 7.2 | - | 14.238 | 15.3877 | 15.4923 | 15.2164 | 14.9856 | 15.0637 | -
PLD | W | 32 |  | 32 | 24 |  | 0.99388 | 0 | 6.422 | - | 16.7326 | 17.7296 | 17.6181 | 17.3204 | 17.2516 | 17.5329 | -
TRG | S | 46.5 |  | 46.5 | 19.2 | 1 | 0.97763 | 5.144 | 5.9 | 7.2 | 17.6876 | 19.9147 | 20.0404 | 19.6528 | 19.3373 | 19.4476 | 3.723% | 1 | 1 | 1 | 0 | 1 | 19 | 16 | 9 | 8 | 13
TRG | W | 46.5 |  | 46.5 | 19.4 | 1 | 0.98632 | 0 | 5.41 | 7.2 | 19.9935 | 21.0881 | 20.9166 | 20.5096 | 20.4068 | 20.7237 | 8.702%
WBL | S | 79.5 |  | 79.5 | 49.2 |  | 0.95923 | 9.4 | 10 | - | 52.1116 | 49.1177 | 49.9389 | 49.9376 | 49.4944 | 49.9571 | -
WBL | W | 79.5 |  | 79.5 | 54.8 |  | 0.97985 | 0 | 8.854 | - | 44.553 | 49.0729 | 49.5264 | 49.2261 | 49.5772 | 50.95 | -
WETS 66kV | [7 empty] | 0
OYN | S | 27 |  | 27 | 15.2 |  | 0.86461 | 0 | 2.6 | - | 8.0923 | 8.9215 | 8.8753 | 8.5877 | 8.3602 | 8.3212 | -
OYN | W | 27 |  | 27 | 15.2 |  | 0.86422 | 0 | 2.418 | - | 7.5004 | 7.403 | 7.2801 | 7.0777 | 6.9788 | 7.0191 | -
RVL | S | 19.5 |  | 19.5 | 20.4 | 10 | 1.5913 | 4.268 | 2.9 | 7.5 | 20.4313 | 21.4114 | 21.4948 | 21.5178 | 21.1525 | 21.2693 | 4.958%
RVL | W | 19.5 |  | 19.5 | 22.9 | 2 | 1.1974 | 0 | 2.45 | 7.5 | 14.8872 | 13.6963 | 13.9859 | 14.2332 | 14.2713 | 14.1265 | -
WMN | S | 33 | 13.5 | 46.5 | 17.2 | 8 | 0.98977 | 3.811 | 1.4 | 4.25 | 23.8754 | 24.6684 | 25.1521 | 25.5661 | 25.0075 | 24.9625 | 43.42% | 1964 | 2361 | 2730 | 2238 | 2201 | 1226 | 1349 | 1451 | 1312 | 1301
WMN | W | 33 | 13.5 | 46.5 | 20.2 | 4 | 0.99721 | 0 | 0.541 | 4.25 | 16.2047 | 18.7504 | 19.4009 | 19.4261 | 19.1433 | 19.2329 | -
Note 1: * indicates cold standby transformer
Note 2: Where load is above N-1 rating
Note 3: Generation capacity <1MW is mostly solar PV
Note 4: TNA generation <1MW based on load transfers to TNA

## Sub-transmission lines
Subtransmission line |  | Line Rating (MVA) | Hours Load is 95% of MD | Power Factor at MD | Load Transfers (MVA) | Generation Capacity (MW) | Historical Demand Worst case N-1 Scenario (MVA) | Forecast Demand Worst case N-1 Scenario (MVA) |  |  |  |  | % Load Above N-1 Rating (2022) | Energy at Risk (MWh) (N-1 50% PoE) |  |  |  |  | Hours at Risk (N-1 50% PoE)
[7 empty] | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2022 | 2023 | 2024 | 2025 | 2026
ATS 66kV
ATS-HCP | S | 109.7 | 3 | 0.92144 | 12.1 | 6.95 | 103.1 | 124.7 | 133.1 | 134.6 | 138.4 | 143.9 | 13.67% | 43.977 | 131.1363 | 153.0533 | 216.3303 | 328.781 | 6.75 | 15.25 | 16.75 | 20.5 | 26.5
| W | 134.9 | 3 | 0.96882 | 12.1 | 6.95 | 83.4 | 86.7 | 92.9 | 97.4 | 99 | 103 | -
ATS-WBE | S | 109.7 | 3 | 0.91939 | 12.1 | 6.95 | 104.2 | 124.8 | 133.3 | 136.1 | 138.5 | 144 | 13.76% | 44.5457 | 133.6896 | 176.1674 | 217.7191 | 330.3207 | 6.75 | 15.5 | 18 | 20.75 | 26.75
| W | 134.9 | 3 | 0.96647 | 12.1 | 6.95 | 83.5 | 86.8 | 92.9 | 97.4 | 100 | 103 | -
HCP-WBE | S | 109.7 |  | 0.94481 |  |  | 90.6 | 108.5 | 115.7 | 117.1 | 120.5 | 125.4 | -
| W | 134.9 |  | 0.97948 |  |  | 73.1 | 76.3 | 81.8 | 85.9 | 87.6 | 91.2 | -
ATS-LV1 | S | 135.5 |  | 0.9927 |  |  | 82.2 | 106.1 | 114.7 | 118 | 119.5 | 122.4 | -
| W | 142.3 |  | 0.99583 |  |  | 71.9 | 80.1 | 87.6 | 93.1 | 94.4 | 95.9 | -
ATS-LV2 | S | 135.5 |  | 0.99148 |  |  | 82.2 | 107.2 | 115.9 | 119.3 | 119.6 | 123.6 | -
| W | 142.3 |  | 0.9945 |  |  | 72.7 | 80.2 | 87.6 | 93.1 | 95.3 | 96.8 | -
ATS/BLTS 66kV
ATS-AC | S | 102.3 |  | 0.90774 |  |  | 33.6 | 43.3 | 41.4 | 41.9 | 41.1 | 41.4 | -
| W | 108 |  | 0.89952 |  |  | 41.8 | 43.6 | 40.9 | 42.8 | 42.5 | 42 | -
AC-CPL | S | 102.9 |  | 0.90909 |  | 11.25 | 31.9 | 40.9 | 38.7 | 38.7 | 37.9 | 38.2 | -
| W | 108 |  | 0.90025 |  | 11.25 | 40.1 | 41.7 | 38.4 | 39.8 | 39.3 | 38.8 | -
CPL-AL | S | 91.4 |  | 0.90164 |  | 11.25 | 30.5 | 28.8 | 31.6 | 31.9 | 31.4 | 31.6 | -
| W | 91.4 |  | 0.89844 |  | 11.25 | 25.6 | 22.7 | 27.5 | 29 | 29 | 28.6 | -
AL-BLTS | S | 91.4 |  | 0.94675 |  |  | 16.9 | 30.8 | 27 | 27.3 | 27.1 | 27.6 | -
| W | 91.4 |  | 0.93103 |  |  | 29 | 33 | 27.2 | 27.8 | 27.5 | 27.6 | -
ATS-ATD | S | 102.3 |  | 0.94578 |  |  | 16.6 | 18.7 | 24.8 | 34.6 | 54.6 | 60.8 | -
| W | 130.3 |  | 0.88095 |  |  | 12.6 | 13.7 | 20.2 | 26.2 | 36.1 | 56 | -
BLTS-ATD | S | 97.2 |  | 0.97872 |  |  | 14.1 | 18.9 | 24.9 | 34.7 | 54.6 | 60.7 | -
| W | 125.7 |  | 0.63158 |  |  | 9.5 | 11.8 | 20.3 | 26.3 | 36.1 | 56 | -
ATS-LVN | S | 109.7 |  | 0.96989 |  |  | 79.7 | 89.5 | 94.1 | 98 | 97.8 | 99.4 | -
| W | 134.9 |  | 0.99092 |  |  | 77.1 | 80.1 | 87.6 | 92.7 | 93.3 | 94 | -
BLTS-LVN | S | 109.7 |  | 0.97143 |  |  | 80.5 | 88.9 | 94.3 | 97.4 | 97.2 | 98.8 | -
| W | 122.3 |  | 0.99094 |  |  | 77.3 | 81.1 | 87.9 | 92.8 | 93.4 | 94.1 | -
ATS-SCI | S | 90.8 |  | 0.74728 |  |  | 45.9 | 46.3 | 46.8 | 45.8 | 45.1 | 45.3 | -
| W | 116 |  | 0.78638 |  |  | 42.6 | 45.2 | 46.1 | 45.9 | 45 | 44.8 | -
BLTS-SCI | S | 97.2 |  | 0.99452 |  |  | 73 | 88.7 | 89.4 | 87.7 | 86.4 | 87 | -
| W | 125.7 |  | 0.98478 |  |  | 111.7 | 87.3 | 88.8 | 88.3 | 86.8 | 86.3 | -
ATS-TYA | S | 102.3 |  | 0.84229 |  |  | 27.9 | 27.1 | 28.4 | 28.7 | 28 | 28 | -
| W | 130.3 |  | 0.82156 |  |  | 26.9 | 25.3 | 28.1 | 30.1 | 30.1 | 29.5 | -
BLTS-TYA | S | 88 |  | 0.84411 |  |  | 26.3 | 25.7 | 26.9 | 27.3 | 26.6 | 26.6 | -
| W | 112 |  | 0.82239 |  |  | 25.9 | 24.2 | 26.9 | 28.9 | 28.9 | 28.3 | -
BLTS-BMH | S | 32.6 |  | 0.97571 |  | 14.35 | 24.7 | 31.8 | 34.9 | 38.3 | 39.5 | 41.7 | -
| W | 37.7 |  | 0.96916 |  | 14.35 | 22.7 | 22.7 | 25.1 | 29 | 30.1 | 30.7 | -
BATS 66kV
BATS-BAN1 | S | 96 |  | 0.96178 |  | 29.3 | 78.5 | 88.8 | 93.6 | 94.2 | 94 | 97.2 | -
| W | 114.3 |  | 0.95849 |  | 29.3 | 79.5 | 83.1 | 89.3 | 92.5 | 92.7 | 93.9 | -
BATS-BAN2 | S | 96 |  | 0.95897 |  | 29.3 | 78 | 89.1 | 93.9 | 94.6 | 94.4 | 96.7 | -
| W | 114.3 |  | 0.95489 |  | 29.3 | 79.8 | 83.4 | 89.6 | 92 | 92.2 | 94.2 | -
BAN-BGR | S | 46.3 |  | 1 |  | 26.25 | 13.5 | 14.7 | 15.5 | 15.1 | 14.8 | 14.7 | -
| W | 47.4 |  | 0.9854 |  | 26.25 | 13.7 | 14.6 | 15.4 | 15.4 | 15.1 | 15.1 | -
BGR-ART | S | 45.7 |  | 1 |  | 26.25 | 13 | 14 | 14.7 | 14.3 | 14.1 | 14 | -
| W | 47.4 |  | 0.98473 |  | 26.25 | 13.1 | 13.9 | 14.6 | 14.6 | 14.4 | 14.3 | -
BATS-YSW/BGL | S | 36.6 | 0 | 0.99355 | 0 | 14.35 | 31 | 39.5 | 42.3 | 45 | 45.5 | 46.8 | 7.923% | 0.72034 | 3.2339 | 7.9453 | 9.0893 | 12.9287 | 1 | 2.5 | 4.75 | 5 | 6.75
| W | 37.1 | 4 | 0.96617 | 0 | 14.35 | 26.6 | 27.4 | 30.6 | 34.4 | 35.2 | 36.4 | -
YSW-BMH | S | 36.6 |  | 0.98268 |  | 14.35 | 23.1 | 29.8 | 32.2 | 34.2 | 34.6 | 35.5 | -
| W | 37.2 |  | 0.99029 |  | 14.35 | 20.6 | 20.6 | 23.4 | 26.6 | 27.3 | 28.2 | -
BATS-BAS1 | S | 83.5 |  | 0.98171 |  | 3.575 | 65.6 | 79.8 | 81.5 | 83.3 | 83.5 | 86.1 | -
| W | 102.9 |  | 0.98753 |  | 3.575 | 72.2 | 72 | 75 | 77.8 | 78.5 | 79.7 | -
BATS-BAS2/BGF | S | 93.2 |  | 0.97606 |  | 3.575 | 71 | 85.2 | 88.2 | 89.9 | 90.1 | 91.5 | -
| W | 94.9 |  | 0.98715 |  | 3.575 | 77.8 | 77.3 | 80.4 | 83.3 | 83.8 | 85 | -
BETS 66kV
BETS-BGO | S | 109.7 |  | 0.94743 |  |  | 89.4 | 104.1 | 107.3 | 107 | 106.2 | 109.7 | -
| W | 114.3 |  | 0.98377 |  |  | 49.3 | 77.5 | 83.4 | 85.2 | 85.1 | 86.2 | -
BGO-EHK | S | 52 | 10 | 0.9477 | 15 |  | 47.8 | 58.6 | 60.3 | 60.6 | 60.4 | 62.6 | 12.69% | 66.9819 | 115.8302 | 124.6216 | 118.7644 | 183.3926 | 32 | 33.5 | 33.5 | 33.5 | 33.75
| W | 52.6 | 1 | 0.98753 | 15 |  | 40.1 | 42.6 | 46.8 | 48.2 | 48.5 | 49.4 | -
BETS-EHK | S | 111.4 |  | 0.94007 |  |  | 90.1 | 104 | 107.9 | 107.6 | 107.6 | 111.1 | -
| W | 111.4 |  | 0.98577 |  |  | 49.2 | 77.5 | 84 | 85.9 | 85.8 | 86.8 | -
BETS-CMN | S | 64 |  | 0.9959 |  |  | 48.8 | 59.8 | 60 | 60.2 | 59.5 | 61.3 | -
| W | 65.2 |  | 1 |  |  | 48.1 | 47.1 | 47.4 | 48.6 | 48.5 | 48.6 | -
CMN-MRO | S | 26.3 |  | 1 |  |  | 23.9 | 27 | 26.9 | 26.7 | 26.7 | 27.2 | 2.662%
| W | 34.9 |  | 0.98855 |  |  | 26.2 | 25 | 25.6 | 25.4 | 25.2 | 25.3 | -
BETS-MRO | S | 76.6 |  | 0.95802 |  |  | 52.4 | 64.8 | 65.2 | 65.1 | 64 | 65.1 | -
| W | 89.2 |  | 0.97665 |  |  | 51.4 | 50.2 | 51.7 | 52.4 | 52.1 | 52.5 | -
BETS-CTN | S | 26.3 |  | 1 |  | 27 | 19.5 | 21.8 | 22.9 | 22.2 | 21.8 | 21.8 | -
| W | 30.3 |  | 0.97826 |  | 27 | 18.4 | 18.5 | 19.7 | 19.9 | 19.4 | 19.2 | -
CTN-CBW | S | 98.9 |  | 0 |  | 19.8 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | -
| W | 106.3 |  | 0 |  | 19.8 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | -
DPTS 66kV
DPTS-MLN1 | S | 109.7 |  | 0.97848 |  |  | 69.7 | 88.4 | 91.6 | 98.7 | 100.8 | 107.2 | -
| W | 134.9 |  | 0.98662 |  |  | 59.8 | 60.5 | 63.9 | 70.4 | 74 | 75.7 | -
DPTS-MLN2 | S | 109.7 |  | 0.97848 |  |  | 69.7 | 88.3 | 90.6 | 98.7 | 100.7 | 107.1 | -
| W | 134.9 |  | 0.98662 |  |  | 59.8 | 60.5 | 63.3 | 70.4 | 73.3 | 75.7 | -
DPTS-SU1 | S | 109.7 |  | 0.96798 |  |  | 81.2 | 106.1 | 120.6 | 119.8 | 119.4 | 122.3 | -
| W | 133.7 |  | 0.97497 |  |  | 71.9 | 76.9 | 94.8 | 97.2 | 96.8 | 97.2 | -
DPTS-SU2 | S | 109.7 |  | 0.96346 |  |  | 82.1 | 107.4 | 122.1 | 121.3 | 120.8 | 123.8 | -
| W | 133.7 |  | 0.97218 |  |  | 71.9 | 77.8 | 95.9 | 98.3 | 98 | 98.3 | -
DPTS-TNA1 | S | 135.5 |  | 0.95513 |  | 4.4 | 62.4 | 77.8 | 102.1 | 133.9 | 137.2 | 142.4 | -
| W | 142.9 |  | 0.97053 |  | 4.4 | 47.5 | 49 | 63.7 | 97.6 | 109.8 | 112.3 | -
DPTS-TNA2 | S | 135.5 |  | 0.95714 |  | 4.4 | 63 | 77.8 | 102.1 | 133.9 | 137.3 | 142.4 | -
| W | 142.9 |  | 0.97053 |  | 4.4 | 47.5 | 49 | 63.7 | 97.6 | 109.8 | 113.4 | -
FBTS 66kV
FBTS-DLF1 | S | 87.5 |  | 0.98052 |  |  | 15.4 | 19.4 | 19.9 | 19.8 | 19.6 | 20.1 | -
| W | 87.5 |  | 1 |  |  | 12.2 | 15.7 | 16 | 16.2 | 16 | 16.4 | -
FBTS-DLF3 | S | 87.5 |  | 0.98052 |  |  | 15.4 | 19.5 | 19.9 | 19.8 | 19.7 | 20.1 | -
| W | 87.5 |  | 1 |  |  | 12.2 | 15.7 | 16.1 | 16.2 | 16.1 | 16.4 | -
GTS 66kV
GTS-BCG | S | 109.7 |  | 0.99128 |  |  | 68.8 | 82.3 | 84.2 | 84.7 | 84.8 | 87.2 | -
| W | 134.9 |  | 0.97674 |  |  | 68.8 | 64.1 | 66.5 | 67.7 | 69.3 | 70 | -
BCG-WPD | S | 91.4 |  | 1 |  |  | 62.8 | 75.2 | 76.8 | 77.4 | 77.6 | 79.7 | -
| W | 91.4 |  | 0.99512 |  |  | 61.5 | 59.2 | 61.4 | 62.5 | 64.1 | 64.8 | -
GTS-WPD | S | 91.4 |  | 0.99263 |  |  | 67.8 | 81.1 | 84.1 | 83.4 | 83.5 | 87.1 | -
| W | 91.4 |  | 0.97935 |  |  | 67.8 | 64 | 66.4 | 67.6 | 68.2 | 69 | -
GTS-WIN | S | 74.3 |  | 0.98941 |  | 66 | 47.2 | 44.9 | 45.6 | 44.7 | 44.1 | 44.5 | -
| W | 87.4 |  | 0.99363 |  | 66 | 47.1 | 45.7 | 47.6 | 47.8 | 47.1 | 46.7 | -
MGW-CLC | S | 74.3 |  | 0.9973 |  | 66 | 37.1 | 33.8 | 34.2 | 33.6 | 33 | 33.1 | -
| W | 86.9 |  | 0.99444 |  | 66 | 36 | 34.5 | 35.8 | 35.8 | 35.2 | 35.1 | -
WIN-MGW | S | 98.3 |  | 0.96183 |  | 66 | 39.3 | 35.3 | 36 | 35.3 | 34.6 | 34.9 | -
| W | 99.5 |  | 0.9734 |  | 66 | 37.6 | 36 | 37.8 | 37.9 | 37.3 | 36.6 | -
GTS-CRO | S | 91.4 |  | 0.97527 |  |  | 28.3 | 40.7 | 50 | 51.2 | 50.8 | 51 | -
| W | 91.4 |  | 0.9932 |  |  | 29.4 | 29.7 | 44.2 | 46.6 | 46.6 | 46.6 | -
FDN-CRO | S | 109.7 |  | 0.97818 |  |  | 27.5 | 38.8 | 47.9 | 49.1 | 48.8 | 49 | -
| W | 134.9 |  | 0.99281 |  |  | 27.8 | 27.5 | 42.5 | 44.2 | 44.9 | 44.9 | -
GTS-FDN | S | 102.9 |  | 0.97527 |  |  | 28.3 | 40.7 | 50.1 | 51.2 | 50.9 | 51.1 | -
| W | 134.9 |  | 0.9932 |  |  | 29.4 | 29.7 | 44.8 | 46.6 | 47.3 | 47.3 | -
GTS-FNS | S | 88 |  | 0.96552 |  | 10.6 | 75.4 | 84.9 | 88.1 | 91 | 90.3 | 91.8 | -
| W | 112 |  | 0.99878 |  | 10.6 | 81.8 | 80.6 | 89 | 92.6 | 92.3 | 92.7 | -
FNS-SRC | S | 109.7 |  | 0.9633 |  | 9.6 | 43.6 | 44.8 | 44.9 | 48 | 48 | 49.4 | -
| W | 125.7 |  | 0.99626 |  | 9.6 | 53.5 | 51.2 | 52 | 51.8 | 50.8 | 50.9 | -
GTS-SRC | S | 109.7 |  | 0.96159 |  | 9.6 | 75.5 | 84.9 | 88 | 90.9 | 90.2 | 91.8 | -
| W | 134.9 |  | 0.99878 |  | 9.6 | 81.7 | 80.5 | 88.9 | 92.5 | 92.2 | 93.3 | -
GTS-GB | S | 135.5 |  | 0.92669 |  |  | 102.3 | 123 | 128 | 139 | 139.5 | 141.4 | -
| W | 142.3 |  | 0.95842 |  |  | 93.8 | 98.9 | 106.8 | 112.9 | 122.5 | 122.1 | -
GB-GL | S | 89.7 | 1 | 0.9486 | 16.6 |  | 85.6 | 101 | 104.3 | 106.8 | 106.4 | 107.8 | 12.6% | 13.4662 | 20.5463 | 27.5588 | 26.3393 | 30.7618 | 2.25 | 2.75 | 3.5 | 3.25 | 3.75
| W | 100.6 | 2 | 0.9725 | 16.6 |  | 80 | 83.1 | 86.5 | 89.4 | 92.1 | 91.7 | -
GCY-GL | S | 109.7 |  | 0.95209 |  | 2.75 | 64.7 | 75.7 | 78.2 | 84.8 | 85.1 | 86.3 | -
| W | 134.9 |  | 0.97561 |  | 2.75 | 61.5 | 62.6 | 68.2 | 71.9 | 78.4 | 78.1 | -
GTS-GCY | S | 90.3 | 1 | 0.92996 | 16.6 | 2.75 | 102.8 | 123.8 | 128.1 | 139.4 | 139.9 | 141.7 | 37.1% | 148.3183 | 228.4017 | 495.3738 | 560.2904 | 608.4915 | 17.75 | 24.75 | 42.75 | 45.5 | 47.75
| W | 96.6 | 2 | 0.96072 | 16.6 | 2.75 | 94.2 | 99 | 107 | 113.7 | 122.9 | 122.6 | 2.484%
GTS-GLE1 | S | 109.7 | 1 | 0.91847 | 6.9 |  | 120.2 | 126.6 | 136.9 | 139.6 | 139.3 | 143.5 | 15.41% | 19.5288 | 58.6165 | 73.7702 | 71.9589 | 100.3496 | 2.75 | 5.75 | 7 | 6.75 | 8.5
| W | 133.7 | 1 | 0.95943 | 6.9 |  | 106 | 105.1 | 113 | 117.8 | 119.9 | 121.2 | -
GTS-GLE2 | S | 109.7 | 1 | 0.88574 | 6.9 |  | 126.9 | 136.1 | 150.4 | 153.1 | 152.7 | 155.2 | 24.07% | 52.6477 | 153.7588 | 180.4021 | 176.3073 | 202.8433 | 5.5 | 11.5 | 13 | 12.75 | 14
| W | 133.7 | 1 | 0.9375 | 6.9 |  | 110.4 | 109.5 | 117.6 | 125.8 | 125.8 | 127 | -
GLE-DDL1 | S | 74.3 |  | 0.94577 |  |  | 62.7 | 65.9 | 71.1 | 74 | 74 | 75.4 | -
| W | 86.9 |  | 0.98651 |  |  | 51.9 | 51.7 | 55.8 | 58.8 | 59.2 | 59.8 | -
GLE-DDL2 | S | 74.3 |  | 0.94586 |  |  | 62.8 | 66 | 72.4 | 74.2 | 74.1 | 76.9 | -
| W | 86.9 |  | 0.98654 |  |  | 52 | 51.8 | 55.9 | 58.9 | 60.2 | 60.9 | -
HOTS 66kV
HOTS-STL1 | S | 49.2 |  | 0.97287 |  | 16.575 | 25.8 | 25.8 | 26.6 | 26.1 | 25.9 | 25.7 | -
| W | 57.2 |  | 0.97328 |  | 16.575 | 26.2 | 27.1 | 27.8 | 27.7 | 27.4 | 27.5 | -
HOTS-STL2 | S | 25.7 |  | 0.98785 |  | 16.575 | 24.7 | 24.7 | 25.5 | 25 | 24.8 | 24.7 | -
| W | 34.9 |  | 0.992 |  | 16.575 | 25 | 25.9 | 26.6 | 26.7 | 26.2 | 26.3 | -
STL-ART | S | 38.3 |  | 1 |  | 26.25 | 13.1 | 14.2 | 14.9 | 14.3 | 14.1 | 14.2 | -
| W | 43.4 |  | 0.99248 |  | 26.25 | 13.3 | 13.8 | 14.7 | 14.7 | 14.5 | 14.4 | -
HOTS-HSM1 | S | 49.2 |  | 0.98688 |  |  | 38.1 | 44.3 | 45.2 | 47.5 | 47 | 47.3 | -
| W | 52.6 |  | 1 |  |  | 33.8 | 34 | 34.9 | 37.6 | 38 | 38 | -
HOTS-HSM2 | S | 49.2 |  | 0.98947 |  |  | 38 | 44.3 | 45.1 | 47.5 | 47 | 47.3 | -
| W | 52.6 |  | 1 |  |  | 33.8 | 34 | 34.9 | 37.6 | 38 | 37.9 | -
HOTS-KWF | S | 44 |  | 0.83846 |  | 31.05 | 13 | 14.5 | 14.6 | 14.6 | 14.2 | 14.1 | -
| W | 43.4 |  | 0.7931 |  | 31.05 | 11.6 | 10.8 | 11.1 | 11.4 | 11.2 | 11 | -
KWF-NHL | S | 44 |  | 1 |  |  | 10.1 | 10.6 | 10.6 | 10.7 | 10.4 | 10.3 | -
| W | 43.4 |  | 1 |  |  | 8.5 | 8.6 | 8.6 | 8.8 | 8.7 | 8.6 | -
HOTS-CHM | S | 26.2 |  | 0.92593 |  |  | 2.7 | 2.9 | 2.8 | 2.7 | 2.7 | 2.6 | -
| W | 35.4 |  | 1 |  |  | 2.5 | 2.7 | 2.7 | 2.7 | 2.6 | 2.5 | -
KTS 66kV
SBY-GSB1 | S | 51.4 |  | 0.99768 |  | 2.35 | 43.1 | 51.1 | 53.3 | 53.7 | 53.5 | 54.9 | -
| W | 69.7 |  | 0.99617 |  | 2.35 | 52.2 | 53 | 56 | 57.2 | 57.3 | 58.1 | -
SBY-GSB2 | S | 76.6 |  | 0.99535 |  | 2.35 | 43 | 51 | 53.2 | 53.5 | 53.4 | 54.8 | -
| W | 89.2 |  | 0.99415 |  | 2.35 | 51.3 | 52.9 | 55.8 | 57.1 | 57.2 | 58 | -
GSB-WND1 | S | 109.7 |  | 1 |  | 2.35 | 24.7 | 27.2 | 28.1 | 28.5 | 28.4 | 29.1 | -
| W | 114.3 |  | 1 |  | 2.35 | 29.7 | 30.1 | 30.9 | 31.9 | 31.9 | 32.3 | -
GSB-WND2 | S | 46.3 |  | 1 |  | 2.35 | 25.2 | 27.8 | 28.6 | 29 | 29 | 29.7 | -
| W | 49.7 |  | 1 |  | 2.35 | 30.3 | 30.7 | 31.5 | 32.5 | 32.6 | 33 | -
KTS-SA1 | S | 116.6 |  | 0.98605 |  |  | 71.7 | 89.4 | 91.3 | 91.9 | 91.9 | 93.9 | -
| W | 122.3 |  | 0.97703 |  |  | 65.3 | 64.6 | 67.2 | 68.4 | 68.8 | 69.7 | -
KTS-SA2 | S | 108 |  | 0.98466 |  |  | 71.7 | 89.4 | 91.3 | 91.9 | 92.8 | 94.8 | -
| W | 122.3 |  | 0.9755 |  |  | 65.3 | 64.6 | 67.3 | 68.4 | 68.8 | 69.8 | -
KTS-SSE2 | S | 89.4 |  | 0.91371 |  |  | 64.9 | 79 | 81.7 | 81.3 | 80.4 | 81.3 | -
| W | 100.6 |  | 0.93513 |  |  | 63.2 | 66.1 | 69.9 | 72.1 | 70.2 | 70 | -
KTS-SSE1 | S | 89.7 |  | 0.91217 |  |  | 64.9 | 79 | 82.6 | 81.4 | 81.3 | 81.3 | -
| W | 94.3 |  | 0.93354 |  |  | 63.2 | 66.1 | 70.6 | 72.1 | 70.9 | 70 | -
KGTS 66kV
KGTS-CHA | S | 31.4 |  | 0.92357 |  |  | 15.7 | 14.8 | 14.9 | 14.5 | 14.2 | 14.2 | -
| W | 43.4 |  | 0.99275 |  |  | 13.8 | 14.4 | 14.7 | 14.5 | 14.2 | 14 | -
KGTS-SHL | S | 36 | 2 | 0.9568 | 2.5 | 39.4 | 46.3 | 49.5 | 52.9 | 52.3 | 51.3 | 52.1 | 37.5% | 38.8674 | 100.7967 | 86.3368 | 65.9498 | 81.9154 | 12.75 | 30.75 | 27 | 21.75 | 25.75
| W | 36 | 1 | 0.99699 | 2.5 | 39.4 | 33.2 | 33.4 | 35.7 | 36.9 | 35.8 | 35.8 | -
KGTS-GSF | S | 48.6 |  | 0.9697 |  | 25 | 39.6 | 41.8 | 44.4 | 43.4 | 43.1 | 43.7 | -
| W | 52.6 |  | 0.99666 |  | 25 | 29.9 | 30.5 | 32.2 | 32.7 | 32.3 | 32.3 | -
GSF-SHL | S | 76.6 |  | 0.97638 |  | 25 | 38.1 | 40.2 | 42.6 | 41.7 | 41.4 | 42 | -
| W | 89.2 |  | 1 |  | 25 | 29.1 | 29.7 | 31.4 | 31.8 | 31.4 | 31.4 | -
RCTS 66kV
RCTS-MBN | S | 97.2 |  | 0.93843 |  |  | 53.6 | 59.7 | 61.4 | 62 | 62.4 | 62.2 | -
| W | 114.3 |  | 0.97156 |  |  | 42.2 | 40.4 | 43 | 44.4 | 44.3 | 44.3 | -
MBN-DTN | S | 74.3 |  | 0.96479 |  |  | 28.4 | 29.8 | 29.9 | 29.5 | 29.3 | 29.4 | -
| W | 86.9 |  | 0.95971 |  |  | 27.3 | 26.3 | 26.6 | 26.6 | 26.3 | 26.2 | -
MDA-MBN | S | 74.3 |  | 0.97588 |  |  | 53.9 | 58.1 | 60.4 | 62.2 | 62.3 | 62.8 | -
| W | 86.9 |  | 0.98313 |  |  | 41.5 | 39.8 | 42.2 | 44.4 | 45.1 | 45.4 | -
MDA-BNG | S | 104 |  | 0.97111 |  |  | 45 | 47 | 48.5 | 49.1 | 48.9 | 49.3 | -
| W | 114.3 |  | 0.97527 |  |  | 36.4 | 32.5 | 33.6 | 34.7 | 35 | 35.2 | -
RCTS-MDA1 | S | 72 | 1 | 0.92914 | 8.6 |  | 87.5 | 98.2 | 100.7 | 101.2 | 101.6 | 101.1 | 36.39% | 462.5693 | 626.9275 | 663.3046 | 693.3843 | 655.9435 | 70.25 | 85.25 | 88 | 91 | 87.5
| W | 90.9 | 2 | 0.97418 | 8.6 |  | 69.7 | 66.8 | 71.3 | 73.1 | 72.4 | 72.3 | -
RCTS-MDA2 | S | 104 |  | 0.93861 |  |  | 96.1 | 106.7 | 109.8 | 111.4 | 109.4 | 110.8 | 2.596%
| W | 114.3 |  | 0.97917 |  |  | 76.8 | 73.5 | 78.6 | 80.4 | 79.6 | 79.4 | -
RCTS-YSF | S | 84.6 |  | 0.85393 |  | 81 | 8.9 | 9.9 | 9.7 | 9.4 | 9.3 | 9.2 | -
| W | 106.3 |  | 0.84524 |  | 81 | 8.4 | 8.2 | 8.4 | 8.2 | 8 | 7.9 | -
YSF-HTH | S | 17.7 |  | 0.86207 |  |  | 8.7 | 9.5 | 9.5 | 9.2 | 9 | 8.9 | -
| W | 35.4 |  | 0.8625 |  |  | 8 | 7.9 | 8 | 7.9 | 7.7 | 7.6 | -
RCTS-KSF | S | 84.6 |  | 0.95588 |  | 97.5 | 34 | 40.7 | 41.1 | 40.7 | 39.3 | 40 | -
| W | 106.3 |  | 0.98851 |  | 97.5 | 17.4 | 20.8 | 21.3 | 21.6 | 21.5 | 21.2 | -
KSF-RVL | S | 84.6 |  | 0.96667 |  | 7.5 | 33 | 39 | 39.5 | 39 | 37.9 | 38.5 | -
| W | 106.3 |  | 0.9883 |  | 7.5 | 17.1 | 20.5 | 21 | 21.2 | 21.1 | 20.9 | -
RVL-BSP | S | 84.6 |  | 0.99672 |  |  | 30.5 | 34.8 | 35.3 | 35 | 34.1 | 34.8 | -
| W | 106.3 |  | 0.98788 |  |  | 16.5 | 19.8 | 20.1 | 20.5 | 20.4 | 20 | -
BSP-BBD | S | 65.2 |  | 0.96795 |  |  | 31.2 | 33.4 | 35.1 | 36.4 | 35.4 | 35.3 | -
| W | 67.4 |  | 0.9381 |  |  | 21 | 22 | 23.3 | 25.1 | 25.4 | 24.9 | -
SHTS 66kV
SHTS-KYM1 | S | 79.4 |  | 0.98853 |  | 12 | 43.6 | 53.7 | 56.3 | 57 | 55.9 | 56.8 | -
| W | 90.3 |  | 0.99225 |  | 12 | 38.7 | 41.6 | 45 | 46 | 45.7 | 45.3 | -
SHTS-KYM2 | S | 79.4 |  | 0.99093 |  | 12 | 44.1 | 54.4 | 56.9 | 57.7 | 56.3 | 57.5 | -
| W | 90.3 |  | 0.99235 |  | 12 | 39.2 | 42.1 | 45.5 | 46.2 | 46.2 | 45.9 | -
KYM-ECA1 | S | 45.7 |  | 0.99667 |  | 4.8 | 30 | 38.8 | 40.8 | 41.6 | 41.3 | 42 | -
| W | 52.6 |  | 0.96382 |  | 4.8 | 30.4 | 30 | 32.5 | 33.7 | 33.6 | 33.9 | -
KYM-ECA2 | S | 45.7 |  | 0.99672 |  | 4.8 | 30.5 | 38.8 | 41.5 | 42.4 | 42.1 | 42.8 | -
| W | 53.2 |  | 0.96382 |  | 4.8 | 30.4 | 30 | 33.1 | 34.5 | 34.2 | 33.9 | -
SHP-KYM | S | 104 |  | 0.97653 |  | 14.4 | 21.3 | 22.1 | 22.3 | 21.9 | 21.6 | 21.7 | -
| W | 114.3 |  | 1 |  | 14.4 | 18.1 | 21.3 | 19.3 | 19.4 | 19.1 | 18.8 | -
SHTS-SHP | S | 101.7 |  | 0.98795 |  | 14.4 | 33.2 | 39.7 | 41.3 | 41.7 | 40.9 | 41.6 | -
| W | 116 |  | 0.98976 |  | 14.4 | 29.3 | 32 | 33.4 | 34 | 33.7 | 33.5 | -
SHTS-MNA | S | 88 |  | 0.97443 |  | 5.8 | 74.3 | 86.7 | 88 | 88 | 87.4 | 88.9 | -
| W | 114.4 |  | 0.96141 |  | 5.8 | 59.6 | 57.9 | 60.2 | 61.3 | 61 | 60.7 | -
STN-MNA | S | 48.6 |  | 0.98698 |  |  | 38.4 | 42.6 | 43.2 | 42.8 | 42.5 | 43.2 | -
| W | 52.6 |  | 0.97764 |  |  | 31.3 | 30.3 | 31.8 | 31.7 | 31.5 | 31.4 | -
SHTS-STN | S | 91.4 |  | 0.9808 |  | 7.4 | 72.9 | 85.1 | 85.8 | 86.5 | 85.1 | 87.3 | -
| W | 91.4 |  | 0.96752 |  | 7.4 | 58.5 | 57.2 | 59.5 | 60.2 | 60 | 60.5 | -
SHTS-NKA | S | 91.4 |  | 0.9844 |  | 64.425 | 57.7 | 82.8 | 86.2 | 86.5 | 85.8 | 87 | -
| W | 91.4 |  | 0.99801 |  | 64.425 | 50.2 | 53 | 54.2 | 56.5 | 56.5 | 55.7 | -
SHTS-NSF | S | 98.3 |  | 0.98778 |  | 64.425 | 57.3 | 82.1 | 83.6 | 84.8 | 83.7 | 86.3 | -
| W | 114.3 |  | 0.99798 |  | 64.425 | 49.4 | 52.7 | 54.2 | 55.7 | 55.6 | 55.7 | -
NSF-NKA | S | 102.9 |  | 0.99638 |  | 64.425 | 55.2 | 76.2 | 77.2 | 78.3 | 77.3 | 79.3 | -
| W | 114.3 |  | 1 |  | 64.425 | 48.1 | 50.9 | 52.2 | 53.6 | 53.5 | 53.6 | -
NKA-CME | S | 74.3 |  | 0.9835 |  | 7.125 | 30.3 | 46.7 | 47.6 | 47.8 | 47.6 | 48.9 | -
| W | 86.9 |  | 0.9959 |  | 7.125 | 24.4 | 25.3 | 26 | 26.9 | 27.1 | 27.1 | -
SHTS-SHN1 | S | 88 |  | 0.94801 |  | 2.7 | 32.7 | 39.5 | 40.9 | 40.6 | 40.3 | 40.9 | -
| W | 112 |  | 0.97482 |  | 2.7 | 27.8 | 27.7 | 28.7 | 29 | 28.8 | 28.8 | -
SHTS-SHN2 | S | 88 |  | 0.94801 |  | 2.7 | 32.7 | 39.5 | 40.9 | 40.6 | 40.3 | 40.9 | -
| W | 112 |  | 0.97482 |  | 2.7 | 27.8 | 27.7 | 28.7 | 29 | 28.8 | 28.8 | -
TGTS 66kV
TGTS-CDN | S | 76.6 |  | 0.99764 |  | 33 | 42.4 | 42 | 42.3 | 41.3 | 40.8 | 41 | -
| W | 85.7 |  | 0.99531 |  | 33 | 42.6 | 41.9 | 43.3 | 43 | 42.2 | 41.7 | -
COB-CDN | S | 49.2 |  | 1 |  | 33 | 23.8 | 23.4 | 24 | 23.6 | 23.4 | 23.6 | -
| W | 57.2 |  | 1 |  | 33 | 24.6 | 24.1 | 25 | 25.1 | 24.8 | 24.3 | -
CDN-CLC | S | 74.3 |  | 0.9895 |  | 66 | 38.1 | 35.1 | 35.2 | 34.6 | 34 | 34.2 | -
| W | 86.9 |  | 0.99187 |  | 66 | 36.9 | 35.5 | 36.8 | 36.8 | 36.3 | 36.2 | -
TGTS-COB | S | 109.7 |  | 0.98634 |  | 33 | 36.6 | 37 | 37.7 | 36.8 | 36.4 | 36.5 | -
| W | 116 |  | 0.98928 |  | 33 | 37.3 | 37.2 | 38.1 | 38 | 37.4 | 36.7 | -
TGTS-HTN | S | 47.4 |  | 0.94268 |  | 43.35 | 31.4 | 41.3 | 41.2 | 39.2 | 37.9 | 37.8 | -
| W | 48 |  | 0.93472 |  | 43.35 | 33.7 | 34.6 | 35.2 | 34.8 | 33.9 | 33.7 | -
NRB-HTN | S | 27 |  | 0.97211 |  | 43.35 | 31.375 | 37.375 | 37.125 | 36.5 | 35.625 | 35.5 | 38.43% | 265.0847 | 256.5033 | 228.5388 | 191.2642 | 186.3455 | 6 | 6 | 5.75 | 4.75 | 4.75
| W | 27 |  | 0.96578 |  | 43.35 | 32.875 | 33.375 | 33.875 | 33.625 | 32.875 | 32.75 | 23.61%
TGTS-NRB | S | 52.6 |  | 0.93437 |  | 43.35 | 32 | 46.5 | 46.2 | 44.1 | 40.7 | 40.7 | -
| W | 52.6 |  | 0.91908 |  | 43.35 | 34.6 | 35.8 | 36.5 | 36 | 35 | 34.7 | -
TGTS-KRT1 | S | 44 |  | 0.97151 |  | 16.0667 | 35.1 | 32.9 | 33.6 | 33.4 | 32.9 | 33.1 | -
| W | 44.6 |  | 0.97959 |  | 16.0667 | 34.3 | 34.7 | 35.6 | 35.7 | 35.3 | 35.5 | -
TGTS-KRT2 | S | 97.2 |  | 0.8408 |  | 16.0667 | 40.2 | 37.8 | 38.3 | 38.1 | 37.8 | 38.1 | -
| W | 116 |  | 0.86305 |  | 16.0667 | 38.7 | 39.1 | 40.7 | 40.8 | 40.4 | 40.5 | -
KRT-PLD1/CWF | S | 40 |  | 0.99338 |  | 18.2 | 15.1 | 16.4 | 16.5 | 16.2 | 15.9 | 16 | -
| W | 45.7 |  | 1 |  | 18.2 | 17.9 | 18.7 | 19 | 18.8 | 18.5 | 18.4 | -
KRT-PLD2/YWF | S | 29.7 |  | 1 |  | 30 | 15.7 | 17.2 | 17.2 | 17 | 16.8 | 16.8 | -
| W | 29.7 |  | 0.99474 |  | 30 | 19 | 19.8 | 20.2 | 20 | 19.7 | 19.6 | -
KRT-WBL | S | 46.9 |  | 0.77736 |  | 16.0667 | 26.5 | 23.5 | 23.7 | 24 | 23.7 | 24 | -
| W | 47.4 |  | 0.80541 |  | 16.0667 | 18.5 | 21.2 | 22.1 | 22.3 | 22.4 | 22.6 | -
TRG-WBL1 | S | 47.4 |  | 0.92786 |  | 8.0333 | 40.2 | 37.5 | 38.2 | 38 | 37.5 | 37.8 | -
| W | 49.7 |  | 0.94488 |  | 8.0333 | 38.1 | 39 | 40 | 40.2 | 39.8 | 40 | -
TRG-WBL2 | S | 45.7 |  | 0.96919 |  | 8.0333 | 35.7 | 33.2 | 33.7 | 33.6 | 33.3 | 33.6 | -
| W | 46.3 |  | 0.98193 |  | 8.0333 | 33.2 | 33.9 | 35.4 | 35.5 | 35.2 | 35.4 | -
TGTS-TRG1 | S | 91.5 |  | 0.96692 |  | 11.6333 | 66.5 | 65.7 | 67 | 65.9 | 65.3 | 65.7 | -
| W | 91.5 |  | 0.98018 |  | 11.6333 | 65.6 | 68 | 69.8 | 69.8 | 69 | 69.2 | -
TGTS-TRG2 | S | 91.5 |  | 0.96692 |  | 11.6333 | 66.5 | 65.7 | 67 | 65.9 | 65.3 | 65.8 | -
| W | 91.5 |  | 0.98018 |  | 11.6333 | 65.6 | 68 | 69.8 | 69.8 | 69 | 69.2 | -
WETS 66kV
WETS-HTH | S | 17.7 |  | 0.86047 |  |  | 8.6 | 9.4 | 9.4 | 9.1 | 8.8 | 8.8 | -
| W | 35.4 |  | 0.87342 |  |  | 7.9 | 7.8 | 7.9 | 7.8 | 7.6 | 7.5 | -
HTH-OYN | S | 17.7 |  | 0.86905 |  |  | 8.4 | 9.2 | 9.2 | 8.9 | 8.7 | 8.6 | -
| W | 35.4 |  | 0.88312 |  |  | 7.7 | 7.6 | 7.7 | 7.6 | 7.4 | 7.3 | -
WETS-WSF | S | 84.6 |  | 0.96109 |  | 92.05 | 25.7 | 26.6 | 27.3 | 27.6 | 27 | 26.9 | -
| W | 106.3 |  | 0.98817 |  | 92.05 | 16.9 | 19.3 | 19.8 | 20.5 | 20.5 | 20.2 | -
WSF-WMN | S | 31.4 |  | 0.96498 |  | 4.25 | 25.7 | 26.5 | 27.2 | 27.5 | 26.9 | 26.9 | -
| W | 43.4 |  | 0.98817 |  | 4.25 | 16.9 | 19.2 | 19.7 | 20.5 | 20.5 | 20.2 | -
WETS-BSP | S | 84.6 |  | 0.93421 |  | 88 | 68.4 | 77.7 | 80.8 | 82.6 | 79.5 | 80.2 | -
| W | 106.3 |  | 0.94133 |  | 88 | 39.2 | 43.4 | 45.4 | 47.9 | 48 | 47 | -
Note 1: Generation capacity is specified at the location (sub-transmission line/ loop) where the generation is connected to the network.
Note 2: The demand figures are actuals for summer and forecast for winter.
Note 3: Forecast demand worst case N-1 scenario refers to the expected load that the sub-transmission line would supply in the event of the worst case outage of a sub-transmission line within the loop system.
Note 4: Radial lines are studied with the expected load under system normal (or N) conditions and also under N-1 if normally open loop arrangement exists. Where load does not exceed the N rating, the N-1 risk is shown if this is worse case.