## Terminal station minimum demand
Terminal Staation Minimum Demand | On-load Capacity - N Export Rating (MVA) | Hot or Cold Spare Capacity - N Export Rating (MVA) | Total Capacity - N Export Rating (MVA) | Cyclic N-1 Export Rating (MVA) | Hours 95% of Minimum Demand | Station Power Factor at Minimum Demand | Generation Capacity <=1MW (MW) | Generation Capacity >1MW (MW) | Actual Minimum Demand (MVA) | 50% PoE Forecast Minimum Demand (MVA) |  |  |  |  | MW Above N-1 Export Rating (2023) | Energy at Risk (MWh) (N-1 50% PoE) |  |  |  |  | Hours at Risk (N-1 50% PoE)
[9 empty] | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 |  | 2023 | 2024 | 2025 | 2026 | 2027 | 2023 | 2024 | 2025 | 2026 | 2027
ATS 66kV |  |  | -300 | -150 | 3 | 0.98 | 122.2 | 17.1 | -22.5126 | -28.5186 | -34.2517 | -48.8569 | -65.0602 | -75.2536 | 0
ATS/BLTS 66kV |  |  | -450 | -300 | 2 | 0.97 | 46 | 71.5 | 32.4473 | -45.3832 | -60.1813 | -79.6494 | -91.3404 | -97.7568 | 0
BATS 66kV |  |  | -300 | -150 | 32 | -0.99 | 68 | 243 | -115.8399 | -86.0011 | -91.3785 | -102.7779 | -118.6504 | -134.6237 | 0
BETS 66kV |  |  | -150 | -75 | 1 | -0.83 | 77 | 101 | -25.0222 | -18.0311 | -83.89 | -91.2616 | -103.7639 | -115.5406 | 0
DPTS 66kV |  |  | -550 | -225 | 1 | -0.73 | 117 | 8.8 | -17.2595 | -9.1918 | -4.7969 | -3.1797 | -20.3494 | -36.2607 | 0
FBTS 66kV |  |  | -450 | -300 | 5 | 0.99 | 7.7 |  | 28.4637 | 99.5047 | 114.0754 | 137.977 | 138.1784 | 133.8308 | 0
GTS 66kV |  |  | -600 | -450 | 2 | 0.98 | 149 | 170 | 39.0001 | 53.0103 | 49.5608 | 48.9899 | 19.6174 | -16.2251 | 0
HOTS 66kV |  |  | -200 | -100 | 2 | 0.81 | 43 | 38.4 | -37.315 | -27.9666 | -32.407 | -31.8605 | -35.4972 | -39.4373 | 0
KGTS 66kV |  |  | -90 | -60 | 28 | 0.99 | 27.3 | 100.4 | -79.985 | -70.4529 | -70.4218 | -68.583 | -69.3043 | -69.6806 | -9.7484
RCTS 66kV |  |  | -185 | -92 | 31 | 0.95 | 32 | 202 | -167.4277 | -139.5203 | -139.5517 | -137.9951 | -141.6859 | -144.1977 | -40.5443
SHTS 66kV |  |  | -450 | -300 | 34 | 0.9 | 109 | 251 | -170.8169 | -173.0011 | -297.0415 | -306.3699 | -323.6622 | -338.9618 | 0
TGTS 66kV |  |  | -275 | -125 | 3 | 0.7 | 58 | 292 | -133.6713 | -67.1781 | -74.1148 | -77.0434 | -85.8284 | -94.5234 | 0
WETS 66kV |  |  | -140 | -70 | 8 | -0.99 | 9.6 | 197.5 | -138.3003 | -122.1223 | -117.0855 | -114.7266 | -111.3819 | -107.3218 | 0

## Zone substations minimum demand
Zone Substation Minimum Demand |  | On-load Capacity - N Export Rating (MVA) | Cyclic N-1 Export Rating (MVA) | Hours 95% of Minimum Demand | Station Power Factor at Minimum Demand | Generation Capacity <=1MW (MW) | Generation Capacity >1MW (MW) | Actual Minimum Demand (MVA) | 50% PoE Forecast Minimum Demand (MVA) |  |  |  |  | MW Above N-1 Export Rating (2023) | Energy at Risk (MWh) (N-1 50% PoE) |  |  |  |  | Hours at Risk (N-1 50% PoE)
[8 empty] | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 |  | 2023 | 2024 | 2025 | 2026 | 2027 | 2023 | 2024 | 2025 | 2026 | 2027
ATS 66kV
LV | S | -99 | -66 |  | 0.95165 |  | - | -15.595 | -17.5488 | -26.9237 | -37.1769 | -48.0676 | -56.6088 | 0
LV | W | -99 | -66 |  | 0.73146 |  | - | -9.5768 | -8.1529 | -14.0157 | -21.577 | -29.5039 | -33.0471 | 0
WBE | S | -99 | -66 |  | 0.99172 |  | 13.9 | -12.1594 | -14.5845 | -25.6764 | -33.498 | -43.2671 | -50.5782 | 0
WBE | W | -99 | -66 |  | 0.74047 |  | 13.9 | -7.3179 | -10.3468 | -14.4186 | -21.0168 | -27.9955 | -30.5198 | 0
ATS/BLTS 66kV
AC | S | -40 | -20 |  | 0.99999 |  | - | 0.054561 | 1.1069 | 2.0288 | 2.4313 | 2.4313 | 2.4313 | 0
AC | W | -40 | -20 |  | 0.95478 |  | - | 0.31552 | 1.6447 | 2.4409 | 2.5137 | 2.5137 | 2.5137 | 0
AL | S | -30 | 0 |  | 0.6411 |  | - | 2.8196 | 3.9747 | 3.5532 | 3.0647 | 2.3409 | -1.9791 | 0
AL | W | -30 | 0 |  | 0.98787 |  | - | 4.4867 | 5.1956 | 5.0047 | 4.4914 | 3.8485 | 3.5645 | 0
BMH | S | -27 | -13.5 |  | 0.24637 |  | - | 1.6371 | 2.4424 | 2.2992 | -1.2926 | -3.5693 | -5.7909 | 0
BMH | W | -27 | -13.5 |  | 0.71073 |  | - | 2.2934 | 4.1503 | 4.288 | 2.7336 | -1.4919 | -2.4681 | 0
LVN | S | -99 | -66 |  | 0.98106 |  | - | 20.9997 | 29.6924 | 34.3883 | 40.0213 | 39.1649 | 38.1673 | 0
LVN | W | -99 | -66 |  | 0.97151 |  | - | 21.9514 | 32.5847 | 39.9408 | 40.9285 | 40.3744 | 40.0114 | 0
BATS 66kV
ART | S | -20 | -10 |  | 0.97516 |  | 6.9 | -5.2368 | -4.8315 | -5.7062 | -6.6554 | -7.9979 | -9.0682 | 0
ART | W | -20 | -10 |  | 0.93281 |  | 6.9 | -3.552 | -3.5754 | -3.855 | -4.6239 | -5.5085 | -6.0782 | 0
BAN | S | -120 | -80 |  | 0.11874 |  | 6.1 | -1.937 | -1.6996 | -7.4072 | -14.907 | -23.0194 | -28.7197 | 0
BAN | W | -120 | -80 |  | 0.99508 |  | 6.1 | 13.7309 | 10.0253 | 5.8758 | -1.514 | -7.4562 | -10.68 | 0
BAS | S | -99 | -66 |  | 0.95144 |  | 7.15 | -1.0362 | -11.8338 | -18.0393 | -25.3451 | -34.3694 | -42.6238 | 0
BAS | W | -99 | -66 |  | 0.86219 |  | 7.15 | 5.2476 | -4.6888 | -9.2532 | -15.9514 | -23.0667 | -26.7206 | 0
BETS 66kV
BGO | S | -66 | -33 |  | 0.71641 |  | - | 1.4238 | 2.6255 | 0.47434 | -1.5121 | -4.5076 | -7.3586 | 0
BGO | W | -66 | -33 |  | 0.92548 |  | - | 3.7134 | 3.3222 | 3.0871 | 1.0186 | -2.1609 | -3.3944 | 0
CMN | S | -66 | -33 |  | 0.94206 |  | - | -2.6432 | -5.3225 | -7.4247 | -9.2908 | -11.2264 | -12.6944 | 0
CMN | W | -66 | -33 |  | 0.00058479 |  | - | -5.7 | -4.1926 | -5.4948 | -6.927 | -8.4093 | -9.1758 | 0
CTN | S | -39.5 | -26 |  | 0.69782 |  | 7.2 | -5.6052 | -6.9183 | -8.1543 | -9.1701 | -10.3418 | -11.2441 | 0
CTN | W | -39.5 | -26 |  | 0.68758 |  | 7.2 | -5.412 | -6.196 | -6.7799 | -7.4918 | -8.3545 | -8.7342 | 0
EHK | S | -54 | -27 |  | 0.94473 |  |  | 1.3725 | 2.0182 | -4.0188 | -4.5793 | -8.6303 | -10.8351 | 0
EHK | W | -54 | -27 |  | 0.99659 |  | - | 4.6458 | 0.82735 | 0.72945 | -2.0498 | -4.9187 | -6.557 | 0
MRO | S | -27 | -13.5 |  | 0.99193 |  | - | -3.6797 | -4.014 | -8.2987 | -9.5659 | -11.5374 | -13.3601 | 0
MRO | W | -27 | -13.5 |  | 0.98647 |  | - | -1.2604 | -3.7488 | -4.9037 | -6.2236 | -7.8233 | -8.6436 | 0
DPTS 66kV
MLN | S | -99 | -66 |  | 0.78619 |  | - | -8.2635 | 2.728 | -2.401 | -1.6337 | -8.3482 | -14.6396 | 0
MLN | W | -99 | -66 |  | 0.15803 |  | - | -7.0452 | 4.2475 | 8.9075 | 4.3367 | -4.7811 | -6.433 | 0
SU | S | -99 | -66 |  | 0.95009 |  | - | 7.5029 | 16.883 | 12.3924 | 8.8333 | 3.0203 | -2.7285 | 0
SU | W | -99 | -66 |  | 0.99563 |  | - | 16.351 | 22.3302 | 20.7399 | 16.9922 | 12.8092 | 11.2398 | 0
TNA | S | -99 | -66 |  | 0.86247 |  | 8.8 | -18.9147 | -10.9043 | -3.4805 | 11.6126 | 7.1386 | 3.403 | 0
TNA | W | -99 | -66 |  | 0.61137 |  | 8.8 | -10.7791 | 11.8714 | 31.0052 | 31.2221 | 26.7282 | 25.2998 | 0
FBTS 66kV
DLF | S | -66 | -33 |  | 0.67669 |  | - | 3.4776 | 2.5224 | 2.622 | 2.7144 | 2.769 | 2.8157 | 0
DLF | W | -66 | -33 |  | 0.86537 |  | - | 4.2371 | 2.614 | 2.7063 | 2.7772 | 2.8239 | 2.8404 | 0
GTS 66kV
CLC | S | -79 | -46 |  | 0.95141 |  | - | 5.7914 | 8.3286 | 6.4632 | 5.8276 | 3.361 | 0.89677 | 0
CLC | W | -79 | -46 |  | 0.99151 |  | - | 10.1797 | 8.5258 | 8.8167 | 7.3362 | 5.2071 | 4.1159 | 0
CRO | S | -60 | -27 |  | 0.95355 |  | - | 5.2809 | 19.4195 | 14.1245 | 16.2302 | 18.51 | 18.6562 | 0
CRO | W | -60 | -27 |  | 0.99784 |  | - | 8.9375 | 21.355 | 20.3817 | 19.2207 | 17.6421 | 17.4222 | 0
DDL | S | -66 | -33 |  | 0.8848 |  | 1.1 | -6.5148 | -6.6818 | -10.5774 | -14.0314 | -19.7426 | -24.3544 | 0
DDL | W | -66 | -33 |  | 0.37159 |  | 1.1 | -4.7541 | -3.4224 | -4.4135 | -8.351 | -12.9967 | -15.2301 | 0
FNS | S | -99 | -66 |  | 0.85145 |  | 1 | 3.7666 | 8.2514 | 12.6585 | 16.8795 | 14.319 | 11.6759 | 0
FNS | W | -99 | -66 |  | 0.97039 |  | 1 | 6.1225 | 14.4168 | 21.3958 | 20.6678 | 18.0105 | 16.9683 | 0
GB | S | -37.5 | -25 |  | 0.99987 |  | - | 2.3892 | 3.4854 | 8.6487 | 17.4677 | 17.4943 | 17.3253 | 0
GB | W | -37.5 | -25 |  | 0.92963 |  | - | 1.592 | 3.3395 | 14.0018 | 17.0851 | 16.956 | 16.8227 | 0
GCY | S | -66 | -33 |  | 0.96277 |  | 5.5 | 9.2519 | 10.6317 | 12.5131 | 13.1906 | 11.1747 | 8.8776 | 0
GCY | W | -66 | -33 |  | 0.99816 |  | 5.5 | 10.4151 | 10.9669 | 13.7035 | 13.6601 | 12.4384 | 11.6769 | 0
GL | S | -80 | -40 |  | 0.94168 |  | - | 3.7345 | 5.8991 | 3.2294 | 3.6672 | -1.6547 | -3.4 | 0
GL | W | -80 | -40 |  | 0.97636 |  | - | 9.4227 | 5.8238 | 5.3789 | 3.1648 | -2.8898 | -2.8812 | 0
GLE | S | -79.5 | -46.5 |  | 0.73007 |  | - | 1.356 | 3.4321 | -1.1476 | -2.4551 | -5.8948 | -9.4813 | 0
GLE | W | -79.5 | -46.5 |  | 0.99822 |  | - | 4.0773 | 5.3418 | 5.4113 | 3.2104 | -1.7806 | -2.9428 | 0
WIN | S | -20.5 | -7 |  | 0.22561 |  | - | -3.9006 | -3.5096 | -4.2104 | -4.8314 | -5.4661 | -6.1711 | 0
WIN | W | -20.5 | -7 |  | 0.012127 |  | - | -3.7053 | -3.1076 | -3.5339 | -4.0045 | -4.5228 | -4.7303 | 0
WPD | S | -79.5 | -46.5 |  | 0.49426 |  | - | -8.3188 | -7.4842 | -11.1239 | -12.6435 | -15.8737 | -18.6133 | 0
WPD | W | -79.5 | -46.5 |  | 0.41856 |  | - | 7.7822 | 4.9342 | 4.6693 | -3.9036 | -7.4217 | -9.0347 | 0
HOTS 66kV
CHM | S | -33 | 0 |  | 0.15627 |  | - | -0.61965 | -0.67417 | -0.87784 | -1.083 | -1.3503 | -1.6542 | 0.36
CHM | W | -33 | 0 |  | 0.0045532 |  | - | -0.62227 | -0.64008 | -0.77987 | -0.95802 | -1.1687 | -1.3219 | 0.31
HSM | S | -40.5 | -27 |  | 0.091083 |  | - | -2.1958 | -1.3019 | -1.4468 | 1.2502 | -3.7266 | -5.6732 | 0
HSM | W | -40.5 | -27 |  | 0.54479 |  | - | 3.506 | 3.6563 | 5.228 | 3.5656 | 1.5838 | -1.8155 | 0
NHL | S | -20 | -10 |  | 0.57325 |  | - | -1.2566 | -0.9434 | -3.4116 | -3.0995 | -3.7325 | -4.2695 | 0
NHL | W | -20 | -10 |  | 0.44992 |  | - | 1.9979 | -1.1323 | -0.88193 | -1.33 | -1.8602 | -2.2802 | 0
STL | S | -27 | -13.5 |  | 0.90126 |  | - | 4.416 | 4.6429 | -2.9387 | -2.7672 | -3.3668 | -3.9022 | 0
STL | W | -27 | -13.5 |  | 0.9728 |  | - | 5.1227 | 3.4535 | 3.5038 | 3.3039 | 2.8569 | 2.6301 | 0
KGTS 66kV
CHA | S | -27 | -13.5 |  | 0.97654 |  | - | -26.1774 | -3.0742 | -3.3899 | -3.3318 | -3.6864 | -4.0311 | 0
CHA | W | -27 | -13.5 |  | 0.98489 |  | - | -25.9048 | -2.4102 | -2.056 | -2.2006 | -2.4407 | -2.5272 | 0
SHL | S | -40.5 | -27 |  | 0.99991 |  | 14.4 | -13.2646 | -14.1687 | -14.4423 | -12.6237 | -13.8544 | -14.9116 | 0
SHL | W | -40.5 | -27 |  | 0.99581 |  | 14.4 | -11.9266 | -13.0331 | -10.2243 | -10.2467 | -11.2346 | -11.5762 | 0
KTS 66kV
GSB | S | -66 | -33 |  | 0.90935 |  | - | -1.798 | -0.85884 | -1.9925 | -3.523 | -5.6687 | -7.4483 | 0
GSB | W | -66 | -33 |  | 0.68452 |  | - | 1.3094 | 1.337 | 0.97944 | -0.80131 | -2.4891 | -3.2432 | 0
SA | S | -93 | -60 |  | 0.1485 |  | - | -3.0968 | -9.9487 | -13.3289 | -18.3965 | -24.0355 | -29.2614 | 0
SA | W | -93 | -60 |  | 0.74989 |  | - | 5.9861 | 10.2729 | -7.0101 | -10.8438 | -15.5405 | -18.1289 | 0
SSE | S | -99 | -66 |  | 0.82372 |  | - | 6.941 | 13.7059 | 11.0292 | 9.7243 | 5.4935 | -4.5073 | 0
SSE | W | -99 | -66 |  | 0.99476 |  | - | 15.9469 | 18.2553 | 18.0946 | 14.9803 | 11.3448 | 9.1997 | 0
WND | S | -66 | -33 |  | 0.92068 |  | 4.7 | -2.5636 | -3.5989 | -5.0949 | -7.0166 | -9.7442 | -11.7792 | 0
WND | W | -66 | -33 |  | 0.050141 |  | 1.5 | 1.0588 | -1.4904 | -2.0348 | -4.0448 | -6.1751 | -7.314 | 0
RCTS 66kV
BBD | S | -66 | -33 |  | 0.047565 |  | - | -2.1024 | -3.887 | -1.8681 | -1.4849 | -1.3866 | -1.2832 | 0
BBD | W | -66 | -33 |  | 0.73219 |  | - | -0.39152 | 1.2356 | 2.152 | 2.2123 | 2.2366 | 2.2668 | 0
MBN | S | -59 | -27 |  | 0.7548 |  | - | -2.5967 | 0.65513 | 1.5986 | 4.4469 | 2.1474 | 0.55082 | 0
MBN | W | -59 | -27 |  | 0.032805 |  | - | 2.4386 | 2.4924 | 6.8843 | 5.8018 | 4.0115 | 2.9797 | 0
MDA | S | -66 | -33 |  | 0.69936 |  | - | 1.0819 | 4.1401 | -2.7838 | -4.9163 | -8.5618 | -10.8132 | 0
MDA | W | -66 | -33 |  | 0.92667 |  | - | 2.8201 | 2.6816 | 1.8114 | -4.0804 | -6.8564 | -8.5618 | 0
SHTS 66kV
CME | S | -40.5 | -27 |  | 0.98279 |  | 14.25 | -7.5944 | -8.1225 | -9.4225 | -8.0837 | -9.9412 | -11.1339 | 0
CME | W | -40.5 | -27 |  | 0.94296 |  | 14.25 | -6.2866 | -7.4884 | -5.6985 | -6.2847 | -7.7325 | -8.2996 | 0
ECA | S | -40.5 | -27 |  | 0.98519 |  | 9.6 | -9 | -10.1041 | -11.915 | -12.309 | -14.5793 | -16.7468 | 0
ECA | W | -40.5 | -27 |  | 0.90292 |  | 4.8 | -3.234 | -5.2715 | -4.7255 | -6.2029 | -8.2545 | -9.0118 | 0
KYM | S | -40.5 | -27 |  | 0.9892 |  | - | -5.825 | -8.0682 | -8.4031 | -8.674 | -9.9875 | -10.9748 | 0
KYM | W | -40.5 | -27 |  | 0.65668 |  | - | -7.584 | -5.5307 | -5.374 | -6.1006 | -7.1746 | -7.813 | 0
MNA | S | -66 | -33 |  | 0.13546 |  | 5.8 | -0.86127 | 1.3363 | -2.8882 | -5.2142 | -7.4414 | -8.5472 | 0
MNA | W | -66 | -33 |  | 0.82501 |  | 1 | 6.6948 | 5.8327 | 4.3679 | 2.697 | -1.2925 | -2.183 | 0
NKA | S | -39.5 | -26 |  | 0.97712 |  | 14.6 | -9.2394 | -12.1911 | -13.4404 | -13.4404 | -15.2103 | -16.5199 | 0
NKA | W | -39.5 | -26 |  | 0.95679 |  | 9.8 | -11.4257 | -9.47 | -8.1722 | -9.1034 | -10.279 | -10.8804 | 0
SHN | S | -66 | -33 |  | 0.92519 |  | 5.4 | -4.2711 | -5.9141 | -8.6589 | -9.6843 | -12.0906 | -12.9343 | 0
SHN | W | -66 | -33 |  | 0.38309 |  | 5.4 | -1.2816 | -5.304 | -5.394 | -6.8827 | -8.3076 | -9.2889 | 0
SHP | S | -66 | -33 |  | 0.89817 |  | 28.8 | -25.4071 | -22.8064 | -30.1479 | -28.6524 | -29.9367 | -30.5885 | 0
SHP | W | -66 | -33 |  | 0.90786 |  | 19.2 | -19.9628 | -11.8809 | -10.6664 | -10.8565 | -11.6338 | -12.2749 | 0
STN | S | -79 | -46 |  | 0.0036873 |  | 7.4 | 4.52 | -4.3097 | -10.6348 | -12.6746 | -15.6191 | -18.3214 | 0
STN | W | -79 | -46 |  | 0.74323 |  | 3.3 | 2.6954 | 2.122 | -3.0641 | -5.07 | -7.5998 | -8.6453 | 0
TGTS 66kV
CDN | S | -20 | -10 |  | 0.91146 |  | - | 0.77573 | 0.55946 | -4.1336 | -5.338 | -6.8445 | -8.1276 | 0
CDN | W | -20 | -10 |  | 0.99752 |  | - | 1.7699 | -0.82879 | -2.0727 | -3.1277 | -4.3703 | -5.0421 | 0
COB | S | -26 | -10 |  | 0.54246 |  | - | -9.4753 | -6.5099 | -6.3282 | -6.181 | -6.1614 | -6.1378 | 0
COB | W | -26 | -10 |  | 0.49765 |  | - | -8.52 | -6.0678 | -5.8012 | -5.7368 | -5.7174 | -5.705 | 0
HTN | S | -39.5 | -26 |  | 0.82124 |  | - | 1.4665 | 2.4005 | 0.71805 | -1.1302 | -3.0457 | -5.024 | 0
HTN | W | -39.5 | -26 |  | 0.95589 |  | - | 4.3343 | 3.3991 | 3.2723 | 2.215 | -0.60133 | -1.4916 | 0
KRT | S | -40.5 | -27 |  | 0.95333 |  | - | 5.2447 | 5.5869 | 4.3956 | 3.3593 | 1.2996 | -1.3963 | 0
KRT | W | -40.5 | -27 |  | 0.96496 |  | - | 7.3128 | 5.43 | 5.7826 | 5.1552 | 4.0327 | 3.1264 | 0
PLD | S | -32 | -16 |  | 0.15655 |  | - | 2.2783 | 1.5116 | -2.1582 | -3.345 | -5.1505 | -6.8189 | 0
PLD | W | -32 | -16 |  | 1 |  | - | 2.023 | 2.1444 | 1.6193 | -1.458 | -2.9382 | -3.7845 | 0
TRG | S | -46.5 | -13.5 |  | 0.8779 |  | 7.2 | -4.8449 | -5.073 | -6.3561 | -7.5623 | -8.743 | -9.7971 | 0
TRG | W | -46.5 | -13.5 |  | 0.76266 |  | 7.2 | -4.3445 | -3.9641 | -4.6034 | -5.2492 | -6.0336 | -6.3295 | 0
WBL | S | -79.5 | -46.5 |  | 0.9991 |  | - | 15.2003 | 14.7333 | 14.3426 | 14.4125 | 11.5584 | 8.8671 | 0
WBL | W | -79.5 | -46.5 |  | 0.94375 |  | - | 15.4031 | 14.784 | 17.4649 | 17.3562 | 15.5028 | 14.2029 | 0
WETS 66kV
OYN | S | -27 | -13.5 |  | 0.26635 |  | - | -0.60248 | -1.1592 | -1.522 | -1.8699 | -2.213 | -2.4978 | 0
OYN | W | -27 | -13.5 |  | 0.0010017 |  | - | 1.6305 | -1.1245 | -1.3918 | -1.6548 | -1.9138 | -2.1401 | 0
RVL | S | -19.5 | -13 |  | 0.888 |  | 7.5 | -10.8681 | -10.9018 | -10.7804 | -10.35 | -10.22 | -9.97 | 0
RVL | W | -19.5 | -13 |  | 0.94388 |  | 7.5 | -9.8961 | -12.1685 | -11.4488 | -11.2668 | -10.9931 | -10.75 | 0
WMN | S | -46.5 | -13.5 |  | 0.091408 |  | 4.25 | 3.0996 | -4.5265 | -3.7211 | -3.4837 | -3.4363 | -3.3649 | 0
WMN | W | -46.5 | -13.5 |  | 0.23707 |  | 4.25 | -4.8791 | -3.7879 | -3.0663 | -3.0222 | -2.9695 | -2.9296 | 0

## Sub-t lines minimum demand
Subtransmission line Minimum Demand |  | Line Export Rating (MVA) | Hours 95% of Minimum Demand | Power Factor at Minimum Demand | Generation Capacity <=1MW (MW) | Generation Capacity >1MW (MW) | Historical Minimum Demand Worst case N-1 Scenario (MVA) | 50% PoE Forecast Minimum Demand Worst case N-1 Scenario (MVA) |  |  |  |  | MW Above N-1 Export Rating (2023) | Energy at Risk (MWh) (N-1 50% PoE) |  |  |  |  | Hours at Risk (N-1 50% PoE)
[7 empty] | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 |  | 2023 | 2024 | 2025 | 2026 | 2027 | 2023 | 2024 | 2025 | 2026 | 2027
ATS 66kV
ATS-HCP | S | 109.7 |  | 0.87097 |  |  | 12.4 | 13.5 | 24 | 31.3 | 40.4 | 47.6 | 0
| W | 134.9 |  | 0.26316 |  |  | 1.9 | 9.3 | 13.1 | 19.4 | 25.9 | 28.3 | 0
ATS-WBE | S | 109.7 |  | 0.84375 |  |  | 12.8 | 13.9 | 24.3 | 31.5 | 40.5 | 47.6 | 0
| W | 134.9 |  | 0.10714 |  |  | 2.8 | 10.1 | 13.8 | 20 | 26.4 | 28.8 | 0
HCP-WBE | S | 109.7 |  | 0.84375 |  |  | 12.8 | 13.9 | 24.5 | 31.8 | 41 | 48.3 | 0
| W | 134.9 |  | 0.11538 |  |  | 2.6 | 10 | 13.8 | 20.1 | 26.7 | 29 | 0
ATS-LV | S | 135.5 |  | 0.90286 |  |  | 17.5 | 17.5 | 26.7 | 36.7 | 47.8 | 56.1 | 0
| W | 142.3 |  | 0.75926 |  |  | 5.4 | 8.2 | 14 | 21.5 | 29.2 | 32.7 | 0
ATS-AWT | S | 109.7 |  | 0.85616 |  |  | 14.6 | 14.5 | 23.5 | 33.5 | 44.6 | 52.9 | 0
| W | 134.9 |  | 0.77358 |  |  | 5.3 | 6.3 | 11.3 | 18.4 | 26 | 29.5 | 0
AWT-LV | S | 109.7 |  | 0.90286 |  |  | 17.5 | 17.5 | 26.7 | 36.8 | 48 | 56.3 | 0
| W | 134.9 |  | 0.22857 |  |  | 3.5 | 8.2 | 14 | 21.5 | 29.3 | 32.8 | 0
ATS/BLTS 66kV
ATS-AC | S | 102.3 |  | 0.98851 |  |  | 17.4 | 17.5 | 16.8 | 16.5 | 16.3 | 16.7 | 0
| W | 108 |  | 0.99452 |  |  | 36.5 | 36 | 35.4 | 35.1 | 34.3 | 33.6 | 0
AC-CPL | S | 102.9 |  | 0.98883 |  |  | 17.9 | 18.2 | 18.1 | 18.2 | 18 | 18.3 | 0
| W | 108 |  | 0.99464 |  |  | 37.3 | 37.2 | 37.2 | 36.9 | 36.1 | 35.5 | 0
CPL-AL | S | 91.4 |  | 0.99441 |  |  | 17.9 | 18.2 | 18.2 | 18.2 | 18 | 18 | 0
| W | 91.4 |  | 0.99465 |  |  | 37.4 | 37.3 | 37.3 | 37 | 36.2 | 35.6 | 0
AL-BLTS | S | 91.4 |  | 0.95783 |  |  | 16.6 | 16.9 | 17.1 | 17.5 | 17.8 | 18.3 | 0
| W | 91.4 |  | 1 |  |  | 34 | 34.1 | 34.3 | 34.4 | 34.2 | 33.8 | 0
ATS-ATD | S | 102.3 |  | 0.95455 |  |  | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.2 | 0
| W | 130.3 |  | 0.98214 |  |  | 5.6 | 5.6 | 5.6 | 5.6 | 5.5 | 5.5 | 0
BLTS-ATD | S | 97.2 |  | 0.45238 |  |  | 4.2 | 4.2 | 4.2 | 4.3 | 4.3 | 3.1 | 0
| W | 125.7 |  | 0.71111 |  |  | 4.5 | 4.5 | 4.5 | 4.6 | 4.6 | 4.5 | 0
ATS-LVN | S | 109.7 |  | 0.8954 |  |  | 23.9 | 23.9 | 23.9 | 23.8 | 23.8 | 24 | 0
| W | 134.9 |  | 0.96813 |  |  | 25.1 | 25.1 | 24.9 | 24.9 | 24.6 | 24.4 | 0
BLTS-LVN | S | 109.7 |  | 0.93043 |  |  | 23 | 23.1 | 23 | 23 | 23 | 23.2 | 0
| W | 122.3 |  | 0.93013 |  |  | 22.9 | 23.1 | 22.9 | 23.1 | 23 | 23 | 0
ATS-SCI | S | 90.8 |  | 0 |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0
| W | 116 |  | 0 |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0
BLTS-SCI | S | 97.2 |  | 0 |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0
| W | 125.7 |  | 0 |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0
ATS-TYA | S | 102.3 |  | 0.84783 |  |  | 9.2 | 9.3 | 9.3 | 9.4 | 9.4 | 7.8 | 0
| W | 130.3 |  | 0.94828 |  |  | 11.6 | 11.6 | 11.6 | 11.6 | 11.5 | 11.4 | 0
BLTS-TYA | S | 88 |  | 0.83871 |  |  | 9.3 | 9.3 | 9.4 | 9.4 | 9.4 | 7.8 | 0
| W | 112 |  | 0.93966 |  |  | 11.6 | 11.6 | 11.6 | 11.6 | 11.5 | 11.4 | 0
BLTS-BMH | S | 32.6 |  | 0.7766 |  |  | 28.2 | 28.4 | 28.4 | 29.7 | 31.4 | 34.2 | 0
| W | 37.7 |  | 0.76866 |  |  | 26.8 | 26.6 | 26.7 | 28.2 | 29.8 | 30.4 | 0
BATS 66kV
BATS-BAN1 | S | 96 |  | 0.86705 |  |  | 34.6 | 37.2 | 42.6 | 48.8 | 56.8 | 62.6 | 0
| W | 114.3 |  | 0.6549 |  |  | 25.5 | 28.2 | 31.4 | 37.1 | 41.9 | 44.9 | 0
BATS-BAN2 | S | 96 |  | 0.86628 |  |  | 34.4 | 37 | 42.3 | 48.5 | 56.4 | 62.3 | 0
| W | 114.3 |  | 0.78947 |  |  | 24.7 | 28 | 31.2 | 36.9 | 41.7 | 44.6 | 0
BAN-BGR | S | 46.3 |  | 0.73456 |  |  | 59.9 | 60.6 | 61.4 | 61.9 | 63.3 | 64.1 | 0
| W | 49.7 |  | 0.73973 |  |  | 58.4 | 59.3 | 59.6 | 60.4 | 61.1 | 61.5 | 0
BGR-ART | S | 45.7 |  | 0.88851 |  |  | 29.6 | 29.6 | 29.6 | 29.6 | 29.6 | 29.5 | 0
| W | 47.4 |  | 0.89189 |  |  | 29.6 | 29.6 | 29.6 | 29.6 | 29.6 | 29.6 | 0
BATS-YSW/BGL | S | 36.6 |  | 0.83838 |  |  | 29.7 | 29.8 | 30.1 | 30.3 | 32.5 | 34.9 | 0
| W | 37.1 |  | 0.82392 |  |  | 30.1 | 30 | 30.1 | 30.4 | 30.3 | 30.7 | 0
YSW-BMH | S | 36.6 |  | 0.86322 |  |  | 32.9 | 33 | 33 | 33 | 33.4 | 34.6 | 0
| W | 37.2 |  | 0.86061 |  |  | 33 | 32.9 | 33 | 33.1 | 33 | 33.1 | 0
BATS-BAS1 | S | 83.5 |  | 0.89655 |  |  | 8.7 | 11.7 | 17.5 | 24.5 | 33.2 | 41.3 | 0
| W | 102.9 |  | 0.62069 |  |  | 2.9 | 4.7 | 9.2 | 15.5 | 22.3 | 25.8 | 0
BATS-BAS2/BGF | S | 93.2 |  | 0.88636 |  |  | 8.8 | 11.7 | 17.5 | 24.5 | 33.2 | 41.2 | 0
| W | 94.9 |  | 0.62069 |  |  | 2.9 | 4.7 | 9.2 | 15.5 | 22.3 | 25.8 | 0
BETS 66kV
BETS-BGO | S | 109.7 |  | 1 |  |  | 4.7 | 4.3 | 3.7 | 5.6 | 12.6 | 17.5 | 0
| W | 114.3 |  | 1 |  |  | 9.8 | 3.9 | 3.5 | 1.3 | 6.6 | 9.4 | 0
BGO-EHK | S | 48.6 |  | 0.96296 |  |  | 2.7 | 2.6 | 3.9 | 4.5 | 8.6 | 10.7 | 0
| W | 49.2 |  | 1 |  |  | 5.1 | 3.3 | 3 | 2 | 4.8 | 6.5 | 0
BETS-EHK | S | 111.4 |  | 1 |  |  | 4.7 | 4.3 | 3.9 | 5.6 | 12.6 | 17.6 | 0
| W | 111.4 |  | 1 |  |  | 9.8 | 3.9 | 3.6 | 2 | 6.6 | 9.4 | 0
BETS-CMN | S | 64 |  | 0.81818 |  |  | 5.5 | 6.6 | 12.7 | 15.8 | 19.8 | 23 | 0
| W | 65.2 |  | 0.028571 |  |  | 3.5 | 5.1 | 7.5 | 10.3 | 13.3 | 14.9 | 0
CMN-MRO | S | 26.3 |  | 0.5102 |  |  | 4.9 | 5.3 | 8.1 | 9.2 | 11.2 | 12.9 | 0
| W | 35.4 |  | 0.071429 |  |  | 2.8 | 4.1 | 5.5 | 6.9 | 8.3 | 9.1 | 0
BETS-MRO | S | 76.6 |  | 0.80357 |  |  | 5.6 | 6.6 | 12.7 | 16 | 19.8 | 23.3 | 0
| W | 89.2 |  | 0.0625 |  |  | 3.2 | 5.2 | 7.6 | 10.3 | 13.3 | 14.9 | 0
BETS-CTN | S | 26.3 |  | 0.73913 |  |  | 25.3 | 25.6 | 26.7 | 27.5 | 28.6 | 29.3 | 0
| W | 30.3 |  | 0.73251 |  |  | 24.3 | 25 | 25.5 | 26.2 | 26.9 | 27.2 | 0
CTN-CBW | S | 98.9 |  | 0.91429 |  |  | 21 | 21 | 21 | 21 | 21 | 21 | 0
| W | 106.3 |  | 0.90995 |  |  | 21.1 | 21 | 21 | 21.1 | 21 | 21 | 0
DPTS 66kV
DPTS-MLN1 | S | 109.7 |  | 0.67925 |  |  | 5.3 | 3.1 | 2.8 | 2 | 8.5 | 14.6 | 0
| W | 134.9 |  | 0.7069 |  |  | 5.8 | 4.5 | 9.1 | 4.7 | 5.1 | 6.7 | 0
DPTS-MLN2 | S | 109.7 |  | 0.67925 |  |  | 5.3 | 3.1 | 2.7 | 2 | 8.5 | 14.6 | 0
| W | 134.9 |  | 0.7069 |  |  | 5.8 | 4.5 | 9.1 | 4.6 | 5.1 | 6.7 | 0
DPTS-SU1 | S | 109.7 |  | 0.97297 |  |  | 14.8 | 17 | 12.4 | 8.9 | 3.1 | 2.9 | 0
| W | 133.7 |  | 0.99625 |  |  | 26.7 | 22.4 | 20.8 | 17.1 | 12.9 | 11.3 | 0
DPTS-SU2 | S | 109.7 |  | 0.97297 |  |  | 14.8 | 17 | 12.4 | 8.9 | 3.2 | 2.9 | 0
| W | 133.7 |  | 0.99625 |  |  | 26.7 | 22.4 | 20.8 | 17.1 | 12.9 | 11.3 | 0
DPTS-TNA1 | S | 109.7 |  | 0.90683 |  |  | 16.1 | 10.9 | 3.6 | 11.5 | 7.1 | 3.4 | 0
| W | 134.9 |  | 0.5 |  |  | 5 | 11.8 | 30.9 | 31.1 | 26.5 | 25.1 | 0
DPTS-TNA2 | S | 109.7 |  | 0.90683 |  |  | 16.1 | 10.9 | 3.6 | 11.5 | 7.1 | 3.4 | 0
| W | 134.9 |  | 0.5 |  |  | 5 | 11.8 | 30.9 | 31.1 | 26.5 | 25.1 | 0
FBTS 66kV
FBTS-DLF1 | S | 87.5 |  | 0.8 |  |  | 1 | 1.1 | 1.2 | 1.3 | 1.4 | 1.5 | 0
| W | 87.5 |  | 0.84615 |  |  | 1.3 | 1.4 | 1.5 | 1.6 | 1.7 | 1.8 | 0
FBTS-DLF3 | S | 87.5 |  | 0.88889 |  |  | 0.9 | 1 | 1.1 | 1.2 | 1.3 | 1.4 | 0
| W | 87.5 |  | 0.84615 |  |  | 1.3 | 1.4 | 1.5 | 1.6 | 1.6 | 1.7 | 0
GTS 66kV
GTS-BCG | S | 109.7 |  | 0.92208 |  |  | 7.7 | 8.5 | 12 | 13.3 | 16.2 | 18.6 | 0
| W | 134.9 |  | 0.92683 |  |  | 4.1 | 4.1 | 4.1 | 5.2 | 8.7 | 10.1 | 0
BCG-WPD | S | 91.4 |  | 0.63793 |  |  | 5.8 | 6.5 | 9.6 | 10.9 | 13.8 | 16.1 | 0
| W | 91.4 |  | 0.72222 |  |  | 7.2 | 4.3 | 4.2 | 4.1 | 6.4 | 7.8 | 0
GTS-WPD | S | 91.4 |  | 0.91026 |  |  | 7.8 | 8.6 | 12 | 13.4 | 16.3 | 18.7 | 0
| W | 91.4 |  | 0.71622 |  |  | 7.4 | 4.6 | 4.4 | 5.2 | 8.7 | 10.2 | 0
GTS-WIN | S | 74.3 |  | 0.7928 |  |  | 125 | 124.9 | 128 | 130.7 | 132.8 | 136.2 | 0
| W | 87.4 |  | 0.79918 |  |  | 122.5 | 124.3 | 124.6 | 127.1 | 130.9 | 132 | 0
MGW-CLC | S | 74.3 |  | 0.99244 |  |  | 66.1 | 66.1 | 66.2 | 66.1 | 66.2 | 66.1 | 0
| W | 86.9 |  | 0.99244 |  |  | 66.1 | 66.1 | 66.1 | 66.1 | 66.1 | 66.1 | 0
WIN-MGW | S | 98.3 |  | 0.97377 |  |  | 118.2 | 118.3 | 119.9 | 120.9 | 122.3 | 124.3 | 0
| W | 99.5 |  | 0.97521 |  |  | 117 | 118.2 | 118 | 119.4 | 121.4 | 122.2 | 0
GTS-CRO | S | 91.4 |  | 0.84524 |  |  | 8.4 | 19.3 | 14.1 | 16.2 | 18.5 | 18.6 | 0
| W | 91.4 |  | 0.99468 |  |  | 18.8 | 21.2 | 20.6 | 19.2 | 17.6 | 17.3 | 0
FDN-CRO | S | 109.7 |  | 0.85542 |  |  | 8.3 | 19.3 | 14.1 | 16.2 | 18.5 | 18.6 | 0
| W | 134.9 |  | 1 |  |  | 18.7 | 21.2 | 20.5 | 19.2 | 17.5 | 17.3 | 0
GTS-FDN | S | 102.9 |  | 0.84524 |  |  | 8.4 | 19.3 | 14.1 | 16.2 | 18.5 | 18.6 | 0
| W | 134.9 |  | 0.99468 |  |  | 18.8 | 21.2 | 20.6 | 19.2 | 17.6 | 17.3 | 0
GTS-FNS | S | 88 |  | 0.99291 |  |  | 28.2 | 32.2 | 36.8 | 41 | 38.5 | 35.7 | 0
| W | 112 |  | 0.88679 |  |  | 26.5 | 31.7 | 37.6 | 36.7 | 34.6 | 33.7 | 0
FNS-SRC | S | 109.7 |  | 1 |  |  | 25.7 | 25.7 | 25.8 | 25.7 | 25.8 | 25.8 | 0
| W | 125.7 |  | 0.90323 |  |  | 18.6 | 18.6 | 19.5 | 18.7 | 18.6 | 18.5 | 0
GTS-SRC | S | 109.7 |  | 0.99291 |  |  | 28.2 | 32.2 | 36.8 | 41 | 38.5 | 35.7 | 0
| W | 134.9 |  | 0.88679 |  |  | 26.5 | 31.7 | 37.6 | 36.7 | 34.6 | 33.7 | 0
GTS-GB | S | 135.5 |  | 0.91573 |  |  | 17.8 | 18.1 | 22.1 | 31.2 | 26.9 | 23.4 | 0
| W | 142.3 |  | 0.92683 |  |  | 20.5 | 18.1 | 30.2 | 30.8 | 26.6 | 25.7 | 0
GB-GL | S | 89.7 |  | 0.93919 |  |  | 14.8 | 15 | 14 | 16.1 | 16.2 | 16 | 0
| W | 100.6 |  | 0.94972 |  |  | 17.9 | 15.2 | 17.3 | 15.8 | 15.6 | 15.5 | 0
GCY-GL | S | 109.7 |  | 0.98936 |  |  | 9.4 | 9.9 | 11.6 | 19.3 | 16.8 | 15.6 | 0
| W | 134.9 |  | 0.82906 |  |  | 11.7 | 10.2 | 17.9 | 18.5 | 15.6 | 15.4 | 0
GTS-GCY | S | 90.3 |  | 0.90055 |  |  | 18.1 | 18.4 | 22.3 | 31.4 | 27.1 | 23.6 | 0
| W | 96.6 |  | 0.91827 |  |  | 20.8 | 18.4 | 30.5 | 31.1 | 26.8 | 26 | 0
GTS-GLE1 | S | 109.7 |  | 0.88235 |  |  | 1.7 | 3.5 | 10.3 | 14.7 | 23.8 | 31.9 | 0
| W | 133.7 |  | 0.97561 |  |  | 8.2 | 2 | 1 | 5.6 | 13.1 | 16.3 | 0
GTS-GLE2 | S | 109.7 |  | 0.88235 |  |  | 1.7 | 3.5 | 10.4 | 14.7 | 23.8 | 31.9 | 0
| W | 133.7 |  | 0.97561 |  |  | 8.2 | 2 | 1 | 5.6 | 13.1 | 16.3 | 0
GLE-DDL1 | S | 74.3 |  | 0.79245 |  |  | 5.3 | 6.8 | 10.6 | 13.8 | 19.4 | 23.9 | 0
| W | 86.9 |  | 0.3 |  |  | 2 | 3.6 | 4.6 | 8.4 | 12.8 | 14.9 | 0
GLE-DDL2 | S | 74.3 |  | 0.79245 |  |  | 5.3 | 6.8 | 10.6 | 13.8 | 19.4 | 23.9 | 0
| W | 86.9 |  | 0.3 |  |  | 2 | 3.6 | 4.6 | 8.4 | 12.8 | 14.9 | 0
HOTS 66kV
HOTS-STL1 | S | 49.2 |  | 0.90244 |  |  | 16.4 | 16.8 | 18.9 | 19.3 | 20.2 | 21 | 0
| W | 57.2 |  | 0.90566 |  |  | 15.9 | 17.1 | 17.2 | 17.7 | 18.5 | 19 | 0
HOTS-STL2 | S | 25.7 |  | 0.87903 |  |  | 12.4 | 13.1 | 15.2 | 16 | 17 | 17.7 | 0
| W | 34.9 |  | 0.89167 |  |  | 12 | 13.1 | 13.7 | 14.3 | 15.1 | 15.6 | 0
STL-ART | S | 38.3 |  | 0.80606 |  |  | 33 | 33.5 | 34.2 | 34.9 | 35.9 | 36.8 | 0
| W | 43.4 |  | 0.80063 |  |  | 31.6 | 32.3 | 32.7 | 33.3 | 34 | 34.5 | 0
HOTS-HSM1 | S | 49.2 |  | 0.33333 |  |  | 1.8 | 1.4 | 1.5 | 1.4 | 3.7 | 5.7 | 0
| W | 52.6 |  | 0.71795 |  |  | 3.9 | 3.7 | 5.2 | 3.6 | 1.7 | 1.9 | 0
HOTS-HSM2 | S | 49.2 |  | 0.33333 |  |  | 1.8 | 1.4 | 1.5 | 1.3 | 3.7 | 5.7 | 0
| W | 52.6 |  | 0.71795 |  |  | 3.9 | 3.7 | 5.2 | 3.6 | 1.7 | 1.9 | 0
HOTS-KWF | S | 44 |  | 0.68661 |  |  | 35.1 | 35.4 | 37.5 | 37 | 38 | 38.7 | 0
| W | 43.4 |  | 0.69851 |  |  | 33.5 | 35.3 | 35.1 | 35.7 | 36.2 | 36.8 | 0
KWF-NHL | S | 44 |  | 0.33333 |  |  | 0.9 | 1.1 | 3.2 | 3 | 3.5 | 4 | 0
| W | 43.4 |  | 0.6 |  |  | 1.5 | 1.2 | 1 | 1.4 | 1.9 | 2.2 | 0
HOTS-CHM | S | 26.2 |  | 0.11111 |  |  | 1.8 | 1.9 | 1.9 | 2 | 2.1 | 2.3 | 0
| W | 35.4 |  | 0 |  |  | 1.7 | 1.8 | 1.9 | 2 | 2 | 2.1 | 0
KTS 66kV
SBY-GSB1 | S | 51.4 |  | 0.78947 |  |  | 3.8 | 4.9 | 7.3 | 10.6 | 15.3 | 19 | 0
| W | 69.7 |  | 0.7037 |  |  | 2.7 | 2.3 | 2.6 | 5.2 | 8.8 | 10.6 | 0
SBY-GSB2 | S | 76.6 |  | 0.78947 |  |  | 3.8 | 4.8 | 7.3 | 10.6 | 15.3 | 19 | 0
| W | 89.2 |  | 0.7037 |  |  | 2.7 | 2.2 | 2.5 | 5.2 | 8.8 | 10.6 | 0
GSB-WND1 | S | 109.7 |  | 0.9 |  |  | 3 | 3.7 | 5.1 | 7 | 9.7 | 11.7 | 0
| W | 114.3 |  | 0 |  |  | 0.6 | 1.7 | 2.2 | 4.1 | 6.2 | 7.3 | 0
GSB-WND2 | S | 46.3 |  | 0.93103 |  |  | 2.9 | 3.6 | 5.1 | 7 | 9.7 | 11.7 | 0
| W | 49.7 |  | 0 |  |  | 0.5 | 1.6 | 2.1 | 4.1 | 6.2 | 7.3 | 0
KTS-SA1 | S | 116.6 |  | 0.21176 |  |  | 8.5 | 9.8 | 13 | 17.8 | 23.2 | 28.1 | 0
| W | 122.3 |  | 0.51938 |  |  | 12.9 | 10.1 | 6.9 | 10.7 | 15 | 17.5 | 0
KTS-SA2 | S | 108 |  | 0.21176 |  |  | 8.5 | 9.8 | 13 | 17.8 | 23.2 | 28.1 | 0
| W | 122.3 |  | 0.51938 |  |  | 12.9 | 10.1 | 6.9 | 10.6 | 15 | 17.5 | 0
KTS-SSE2 | S | 89.4 |  | 0.79699 |  |  | 13.3 | 13.5 | 10.9 | 9.7 | 5.5 | 4.5 | 0
| W | 100.6 |  | 0.87437 |  |  | 19.9 | 17.9 | 17.8 | 14.8 | 11.2 | 9.2 | 0
KTS-SSE1 | S | 89.7 |  | 0.79699 |  |  | 13.3 | 13.5 | 10.9 | 9.7 | 5.5 | 4.5 | 0
| W | 94.3 |  | 0.87437 |  |  | 19.9 | 17.9 | 17.8 | 14.8 | 11.2 | 9.2 | 0
KGTS 66kV
KGTS-CHA | S | 31.4 |  | 0.92593 |  |  | 2.7 | 2.9 | 3.2 | 3.2 | 3.6 | 3.9 | 0
| W | 43.4 |  | 0.89474 |  |  | 1.9 | 2.2 | 1.8 | 2 | 2.2 | 2.3 | 0
KGTS-SHL | S | 40 |  | 0.90551 |  |  | 12.7 | 13.6 | 13.9 | 12.1 | 13.3 | 14.2 | 0
| W | 49.7 |  | 0.9115 |  |  | 11.3 | 12.5 | 10.1 | 10.1 | 10.6 | 11.1 | 0
KGTS-GSF | S | 48.6 |  | 0.94976 |  |  | 61.7 | 62.7 | 62.8 | 61 | 62.4 | 63.4 | 0
| W | 52.6 |  | 0.95522 |  |  | 60.3 | 61.4 | 58.6 | 58.6 | 59.7 | 60 | 0
GSF-SHL | S | 76.6 |  | 0.92366 |  |  | 13.1 | 14.1 | 14.2 | 12.3 | 13.8 | 14.7 | 0
| W | 89.2 |  | 0.92308 |  |  | 11.7 | 12.8 | 9.9 | 9.9 | 11 | 11.3 | 0
RCTS 66kV
RCTS-MBN | S | 97.2 |  | 1 |  |  | 2.7 | 2.9 | 2.9 | 4.4 | 2.7 | 1.4 | 0
| W | 114.3 |  | 1 |  |  | 3 | 2.8 | 5.2 | 4.4 | 3.1 | 2.3 | 0
MBN-DTN | S | 74.3 |  | 0.94444 |  |  | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 0
| W | 86.9 |  | 0.92593 |  |  | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 0
MDA-MBN | S | 74.3 |  | 0.76923 |  |  | 2.6 | 3 | 3.8 | 6.1 | 5 | 4.2 | 0
| W | 86.9 |  | 0.83333 |  |  | 3 | 3.6 | 7 | 6.2 | 5.4 | 5 | 0
MDA-BNG | S | 104 |  | 0.81818 |  |  | 3.3 | 3.5 | 4.2 | 5.6 | 5 | 4.5 | 0
| W | 114.3 |  | 0.65217 |  |  | 2.3 | 2.7 | 4.5 | 4.3 | 3.9 | 3.6 | 0
RCTS-MDA1 | S | 72 |  | 1 |  |  | 4.8 | 5 | 3.1 | 3.2 | 1.5 | 3.6 | 0
| W | 90.9 |  | 0.98077 |  |  | 5.2 | 3.3 | 5.2 | 2.9 | 1 | 2.2 | 0
RCTS-MDA2 | S | 104 |  | 1 |  |  | 5.4 | 5.6 | 3.5 | 3.6 | 2.4 | 4.2 | 0
| W | 114.3 |  | 0.9661 |  |  | 5.9 | 3.6 | 5.8 | 3.3 | 1.6 | 2.9 | 0
RCTS-YSF | S | 84.6 |  | 0.96163 |  |  | 80.8 | 80.8 | 80.8 | 81 | 81.4 | 81.7 | 0
| W | 106.3 |  | 0.9604 |  |  | 80.8 | 80.9 | 80.8 | 80.8 | 81 | 81.2 | 0
YSF-HTH | S | 17.7 |  | 0.58333 |  |  | 2.4 | 2.4 | 2.5 | 2.8 | 3.1 | 3.3 | 0
| W | 35.4 |  | 0.61538 |  |  | 2.6 | 2.4 | 2.4 | 2.7 | 2.9 | 3 | 0
RCTS-KSF | S | 84.6 |  | 0.94094 |  |  | 98.2 | 98.3 | 97.6 | 97.7 | 96.9 | 97.3 | 0
| W | 106.3 |  | 0.93964 |  |  | 99.4 | 99.3 | 98.7 | 98 | 98.2 | 97.5 | 0
KSF-RVL | S | 84.6 |  | 0.9898 |  |  | 9.8 | 9.8 | 9.7 | 9.3 | 9.2 | 9 | 0
| W | 106.3 |  | 0.99083 |  |  | 10.9 | 10.9 | 10.4 | 10 | 9.9 | 9.6 | 0
RVL-BSP | S | 84.6 |  | 1 |  |  | 9.8 | 9.9 | 9.7 | 9.4 | 9.3 | 9 | 0
| W | 106.3 |  | 0.99091 |  |  | 11 | 11 | 10.5 | 10.2 | 10 | 9.8 | 0
BSP-BBD | S | 65.2 |  | 0.89362 |  |  | 4.7 | 4.1 | 2.2 | 1.8 | 1.7 | 1.6 | 0
| W | 67.4 |  | 0.5 |  |  | 1.6 | 1.6 | 2.4 | 2.5 | 2.5 | 2.5 | 0
SHTS 66kV
SHTS-KYM1 | S | 79.4 |  | 0.92233 |  |  | 20.6 | 20.6 | 24.8 | 24.6 | 27.4 | 29.7 | 0
| W | 90.3 |  | 0.84043 |  |  | 9.4 | 11 | 10 | 11.6 | 13.9 | 15.1 | 0
SHTS-KYM2 | S | 79.4 |  | 0.92308 |  |  | 20.8 | 20.8 | 25.1 | 24.9 | 27.7 | 30.1 | 0
| W | 90.3 |  | 0.84211 |  |  | 9.5 | 11.1 | 10.2 | 11.7 | 14.1 | 15.3 | 0
KYM-ECA1 | S | 45.7 |  | 0.94845 |  |  | 9.7 | 10 | 11.7 | 12.1 | 14.3 | 16.5 | 0
| W | 52.6 |  | 0.84615 |  |  | 3.9 | 5.1 | 4.6 | 6 | 8.1 | 8.9 | 0
KYM-ECA2 | S | 45.7 |  | 0.94845 |  |  | 9.7 | 10 | 11.7 | 12.1 | 14.3 | 16.2 | 0
| W | 53.2 |  | 0.86842 |  |  | 3.8 | 5 | 4.5 | 6 | 8.1 | 8.9 | 0
SHP-KYM | S | 104 |  | 0.96774 |  |  | 21.7 | 22.8 | 29.9 | 28.4 | 29.6 | 30.3 | 0
| W | 114.3 |  | 0.8764 |  |  | 8.9 | 11.8 | 10.6 | 10.8 | 11.6 | 12.2 | 0
SHTS-SHP | S | 101.7 |  | 0.95833 |  |  | 21.6 | 22.7 | 29.7 | 28.2 | 29.4 | 30.1 | 0
| W | 116 |  | 0.88506 |  |  | 8.7 | 11.7 | 10.4 | 10.6 | 11.9 | 12.8 | 0
SHTS-MNA | S | 88 |  | 0.02381 |  |  | 4.2 | 4.8 | 11.6 | 15.5 | 19.9 | 23.1 | 0
| W | 114.4 |  | 0.83193 |  |  | 11.9 | 6.7 | 5.3 | 5.5 | 7.5 | 9.3 | 0
STN-MNA | S | 48.6 |  | 0.4 |  |  | 2.5 | 3.8 | 9.3 | 11.1 | 13.7 | 16.1 | 0
| W | 52.6 |  | 0.8871 |  |  | 6.2 | 5.2 | 3.9 | 4.5 | 6.7 | 7.6 | 0
SHTS-STN | S | 91.4 |  | 0.02439 |  |  | 4.1 | 4.8 | 11.7 | 15.7 | 20.2 | 23.4 | 0
| W | 91.4 |  | 0.83898 |  |  | 11.8 | 6.6 | 5.2 | 5.4 | 7.5 | 9.3 | 0
SHTS-NKA | S | 91.4 |  | 0.95842 |  |  | 50.5 | 52 | 54.5 | 53.2 | 56.8 | 59.4 | 0
| W | 91.4 |  | 0.95949 |  |  | 46.9 | 48.6 | 45.7 | 47 | 49.7 | 50.8 | 0
SHTS-NSF | S | 98.3 |  | 0.90607 |  |  | 120.3 | 121.8 | 124.2 | 123 | 126.8 | 129.6 | 0
| W | 114.3 |  | 0.90566 |  |  | 116.6 | 118.5 | 115.3 | 116.8 | 119.5 | 120.7 | 0
NSF-NKA | S | 102.9 |  | 0.95726 |  |  | 35.1 | 35.1 | 35.1 | 35.1 | 35.1 | 35.1 | 0
| W | 114.3 |  | 0.95726 |  |  | 35.1 | 35.1 | 35.1 | 35.1 | 35 | 35 | 0
NKA-CME | S | 74.3 |  | 0.9726 |  |  | 7.3 | 8.2 | 9.5 | 8.1 | 10.1 | 11.3 | 0
| W | 86.9 |  | 0.97015 |  |  | 6.7 | 7.5 | 5.7 | 6.3 | 7.7 | 8.3 | 0
SHTS-SHN1 | S | 88 |  | 0.76471 |  |  | 5.1 | 6 | 8.9 | 9.9 | 12.4 | 13.3 | 0
| W | 112 |  | 0.625 |  |  | 3.2 | 5.4 | 5.5 | 7 | 8.5 | 9.5 | 0
SHTS-SHN2 | S | 88 |  | 0.76471 |  |  | 5.1 | 6 | 8.9 | 9.9 | 12.4 | 13.3 | 0
| W | 112 |  | 0.625 |  |  | 3.2 | 5.4 | 5.5 | 7 | 8.5 | 9.5 | 0
TGTS 66kV
TGTS-CDN | S | 76.6 |  | 0.82086 |  |  | 44.1 | 45.2 | 48.8 | 49.7 | 52.5 | 55.2 | 0
| W | 85.7 |  | 0.80896 |  |  | 42.4 | 45.1 | 45.3 | 46.9 | 49 | 50.3 | 0
COB-CDN | S | 49.2 |  | 0.93269 |  |  | 31.2 | 31.8 | 35.2 | 36 | 38.1 | 39.9 | 0
| W | 57.2 |  | 0.93023 |  |  | 30.1 | 32.3 | 33.1 | 34.8 | 36.2 | 37.1 | 0
CDN-CLC | S | 74.3 |  | 0.89673 |  |  | 58.1 | 58.8 | 61 | 61.4 | 64 | 66.6 | 0
| W | 86.9 |  | 0.89336 |  |  | 57.2 | 58.6 | 58.4 | 59.9 | 61.8 | 63.1 | 0
TGTS-COB | S | 109.7 |  | 0.88679 |  |  | 37.1 | 37.7 | 40.7 | 41.1 | 43.2 | 45 | 0
| W | 116 |  | 0.86857 |  |  | 35 | 37.2 | 37.2 | 38.7 | 40 | 40.9 | 0
TGTS-HTN | S | 47.4 |  | 0.22814 |  |  | 73.2 | 74 | 76.5 | 77.4 | 79.5 | 82.1 | 0
| W | 48 |  | 0.24579 |  |  | 71.2 | 72.5 | 72.7 | 74.4 | 77 | 77.8 | 0
NRB-HTN | S | 52.6 |  | 1 |  |  | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.9 | 0
| W | 53.2 |  | 1 |  |  | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 0
TGTS-NRB | S | 52.6 |  | 0.59536 |  |  | 77.6 | 77.6 | 78.1 | 78.1 | 80.1 | 81.9 | 0
| W | 52.6 |  | 0.59383 |  |  | 77.8 | 77.6 | 77.6 | 77.9 | 77.9 | 78.5 | 0
TGTS-KRT1 | S | 44 |  | 0.6455 |  |  | 18.9 | 19.4 | 20.6 | 21.4 | 23.1 | 24.7 | 0
| W | 44.6 |  | 0.64324 |  |  | 18.5 | 19.1 | 19.2 | 20 | 20.9 | 21.7 | 0
TGTS-KRT2 | S | 97.2 |  | 0.90456 |  |  | 24.1 | 24.8 | 26.4 | 27.4 | 29.5 | 31.5 | 0
| W | 116 |  | 0.90254 |  |  | 23.6 | 24.4 | 24.6 | 25.5 | 26.8 | 27.8 | 0
KRT-PLD1/CWF | S | 40 |  | 0.85345 |  |  | 23.2 | 23.7 | 24.5 | 25 | 26 | 26.9 | 0
| W | 45.7 |  | 0.85333 |  |  | 22.5 | 23.2 | 23.6 | 24.1 | 24.8 | 25.3 | 0
KRT-PLD2/YWF | S | 29.7 |  | 0.81757 |  |  | 29.6 | 30.4 | 32.4 | 33.4 | 35.5 | 37.1 | 0
| W | 29.7 |  | 0.81469 |  |  | 28.6 | 29.7 | 30.3 | 31.4 | 32.9 | 33.9 | 0
KRT-WBL | S | 46.9 |  | 0.86319 |  |  | 30.7 | 31.2 | 32.9 | 34 | 35.7 | 37.1 | 0
| W | 47.4 |  | 0.85667 |  |  | 30 | 30.9 | 31.7 | 32.7 | 33.6 | 34.4 | 0
TRG-WBL1 | S | 47.4 |  | 0.96629 |  |  | 8.9 | 9.2 | 10.3 | 10.8 | 13.1 | 15.2 | 0
| W | 49.7 |  | 0.7093 |  |  | 8.6 | 9 | 10 | 10 | 10.1 | 11.1 | 0
TRG-WBL2 | S | 45.7 |  | 0.93151 |  |  | 7.3 | 7.4 | 8.2 | 8.7 | 10.5 | 12.3 | 0
| W | 46.3 |  | 0.65217 |  |  | 6.9 | 7.2 | 8.2 | 8.1 | 8.1 | 8.9 | 0
TGTS-TRG1 | S | 91.5 |  | 0.82653 |  |  | 9.8 | 11 | 13.4 | 15.1 | 19.3 | 23.3 | 0
| W | 91.5 |  | 0.78261 |  |  | 9.2 | 10 | 9.1 | 10.3 | 12.8 | 14.5 | 0
TGTS-TRG2 | S | 91.5 |  | 0.82653 |  |  | 9.8 | 11 | 13.4 | 15.1 | 19.3 | 23.3 | 0
| W | 91.5 |  | 0.78261 |  |  | 9.2 | 10 | 9.1 | 10.3 | 12.8 | 14.5 | 0
WETS 66kV
WETS-BPA | S | 31.4 |  | 0.58333 |  |  | 2.4 | 2.4 | 2.5 | 2.5 | 2.6 | 2.7 | 0
| W | 43.4 |  | 0.61538 |  |  | 2.6 | 2.4 | 2.4 | 2.5 | 2.5 | 2.6 | 0
BPA-HTH | S | 17.7 |  | 0.055556 |  |  | 1.8 | 1.9 | 2.2 | 2.5 | 2.8 | 3.1 | 0
| W | 35.4 |  | 0.10526 |  |  | 1.9 | 1.9 | 2.1 | 2.4 | 2.6 | 2.8 | 0
HTH-OYN | S | 17.7 |  | 0.066667 |  |  | 1.5 | 1.7 | 2 | 2.3 | 2.6 | 2.9 | 0
| W | 35.4 |  | 0.0625 |  |  | 1.6 | 1.6 | 1.9 | 2.1 | 2.4 | 2.6 | 0
WETS-WSF | S | 84.6 |  | 0.95936 |  |  | 93.5 | 89.9 | 88.8 | 88.4 | 88.3 | 88.2 | 0
| W | 106.3 |  | 0.99329 |  |  | 89.4 | 88.9 | 87.8 | 87.7 | 87.6 | 87.5 | 0
WSF-WMN | S | 31.4 |  | 0.66667 |  |  | 4.8 | 4.5 | 3.7 | 3.4 | 3.4 | 3.3 | 0
| W | 43.4 |  | 0.54762 |  |  | 4.2 | 3.7 | 3 | 2.9 | 2.9 | 2.8 | 0
WETS-BSP | S | 84.6 |  | 0.95799 |  |  | 97.6 | 97.4 | 94.8 | 94.5 | 93.6 | 94 | 0
| W | 106.3 |  | 0.95525 |  |  | 96.1 | 94.4 | 92.9 | 92 | 92.3 | 91.5 | 0

## Zone substations maximum demand
Zone Substation Maximum Demand |  | On-load Capacity - N Import Rating (MVA) | Hot or Cold Spare Capacity - N Import Rating (MVA) | Total Capacity - N Import Rating (MVA) | Cyclic N-1 Import Rating (MVA) | Hours 95% of Maximum Demand | Station Power Factor at Maximum Demand | Load Transfer Capacity (MVA) | Generation Capacity <1MW (MW) | Generation Capacity >1MW (1MW) | Actual Maximum Demand (MVA) | 50% PoE Forecast Maximum Demand (MVA) |  |  |  |  | % Load Above N-1 Rating (2023) | Energy at Risk (MWh) (N-1 50% PoE) |  |  |  |  | Hours at Risk (N-1 50% PoE)
[11 empty] | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 |  | 2023 | 2024 | 2025 | 2026 | 2027 | 2023 | 2024 | 2025 | 2026 | 2027
ATS 66kV
LV | S | 99 |  | 99 | 79.8 | 456 | 1 |  |  | - | 88.3219 | 100.8944 | 103.9276 | 107.2408 | 107.6901 | 108.2387 | 26.43% | 515.67 | 666.39 | 788.62 | 645.88 | 628.51 | 68 | 80.5 | 84.5 | 66 | 63
LV | W | 99 |  | 99 | 95.4 |  | 1 |  |  | - | 71.5522 | 80.5778 | 85.5272 | 86.5148 | 86.2056 | 86.5647 |  | 515.67 | 666.39 | 788.62 | 645.88 | 628.51 | 68 | 80.5 | 84.5 | 66 | 63
WBE | S | 99 |  | 99 | 82.8 | 386 | 1 |  |  | 13.9 | 100.0175 | 110.9456 | 116.22 | 123.16 | 126.08 | 129.21 | 33.99% | 899.75 | 1231.59 | 1984.39 | 2036.34 | 2256.53 | 94.5 | 111.5 | 159 | 151 | 162
WBE | W | 99 |  | 99 | 92.2 |  | 1 |  |  | 13.9 | 72.5634 | 82.2738 | 88.4215 | 91.4659 | 92.9638 | 95.039 |  | 899.75 | 1231.59 | 1984.39 | 2036.34 | 2256.53 | 94.5 | 111.5 | 159 | 151 | 162
ATS/BLTS 66kV
AC | S | 40 |  | 40 | 30 |  | 0.96 |  |  | - | 2.0525 | 3.3092 | 4.2573 | 4.609 | 4.609 | 4.587
AC | W | 40 |  | 40 | 30 |  | 0.96 |  |  | - | 2.4223 | 4.0292 | 4.6379 | 4.7107 | 4.6914 | 4.6792
AL | S | 30 |  | 30 | 34.2 | 422 | 1 |  |  | - | 21.5149 | 20.4068 | 20.8431 | 21.0992 | 21.0049 | 20.9098
AL | W | 30 |  | 30 | 38.6 |  | 1 |  |  | - | 17.1517 | 17.5417 | 18.1769 | 18.3098 | 18.2716 | 18.3098
BMH | S | 27 |  | 27 | 19.1 |  | 1 |  |  | - | 25.8656 | 28.7163 | 31.8746 | 32.9177 | 33.0979 | 33.2183 | 50.35% | 780.37 | 2942.3201 | 3234.72 | 2454.75 | 2163.79 | 338 | 1054.5 | 1045 | 766.5 | 653
BMH | W | 27 |  | 27 | 20.2 |  | 1 |  |  | - | 21.8679 | 23.883 | 26.7207 | 27.0014 | 27.0014 | 27.1218 | 18.23% | 780.37 | 2942.3201 | 3234.72 | 2454.75 | 2163.79 | 338 | 1054.5 | 1045 | 766.5 | 653
LVN | S | 99 |  | 99 | 79.7 |  | 0.99 |  |  | - | 71.3386 | 75.977 | 83.2622 | 88.1977 | 87.6937 | 86.8173
LVN | W | 99 |  | 99 | 85 |  | 0.99 |  |  | - | 71.7141 | 78.0279 | 86.2822 | 87.5082 | 87.0028 | 86.6942
BATS 66kV
ART | S | 20 |  | 20 | 13.6 |  | 0.99 |  |  | 6.9 | 12.9265 | 13.5446 | 13.9247 | 14.1853 | 13.9655 | 13.8153
ART | W | 20 |  | 20 | 15.2 |  | 0.99 |  |  | 6.9 | 12.9293 | 13.2541 | 13.8849 | 13.8451 | 13.5248 | 13.3238
BAN | S | 120 |  | 120 | 96.4 |  | 0.99 |  |  | 6.1 | 76.1803 | 89.3334 | 92.9315 | 94.7104 | 94.8647 | 95.1552
BAN | W | 120 |  | 120 | 104.4 |  | 0.99 |  |  | 6.1 | 79.5881 | 87.1312 | 89.8187 | 90.4711 | 90.0253 | 90.0564
BAS | S | 99 |  | 99 | 76 |  | 1 |  |  | 7.15 | 67.8002 | 76.3417 | 75.402 | 77.5494 | 77.6383 | 77.8262
BAS | W | 99 |  | 99 | 84.6 |  | 1 |  |  | 7.15 | 61.916 | 67.781 | 70.1266 | 70.5917 | 70.3745 | 70.6415
BETS 66kV
BGO | S | 66 |  | 66 | 38.5 | 351 | 0.98 |  |  | - | 36.9372 | 42.7652 | 43.9398 | 45.6207 | 45.1259 | 44.5543 | 11.08% | 11.67 | 26.64 | 61.77 | 44.65 | 31.47 | 10.5 | 16.5 | 30.5 | 22.5 | 16.5
BGO | W | 66 |  | 66 | 45.4 |  | 0.98 |  |  | - | 34.3095 | 36.1953 | 38.6723 | 39.1252 | 38.5534 | 38.1227 |  | 11.67 | 26.64 | 61.77 | 44.65 | 31.47 | 10.5 | 16.5 | 30.5 | 22.5 | 16.5
CMN | S | 66 |  | 66 | 43 | 471 | 0.99 |  |  | - | 23.1125 | 25.5583 | 25.7747 | 26.031 | 25.8344 | 25.8244
CMN | W | 66 |  | 66 | 49.5 |  | 0.99 |  |  | - | 24.153 | 24.5408 | 24.8673 | 24.7283 | 24.3533 | 24.2552
CTN | S | 39.5 |  | 39.5 | 33.7 |  | 0.98 |  |  | 7.2 | 19.8457 | 18.9389 | 18.8155 | 18.8527 | 18.473 | 18.1976
CTN | W | 39.5 |  | 39.5 | 38.4 |  | 0.98 |  |  | 7.2 | 16.3885 | 18.5786 | 18.5688 | 18.3303 | 17.8371 | 17.3996
EHK | S | 54 |  | 54 | 36.4 | 320 | 0.98 |  |  |  | 48.1202 | 53.103 | 55.3901 | 59.1386 | 59.0778 | 59.3739 | 45.89% | 784.21 | 1100.65 | 2253.3201 | 1835.95 | 1781.37 | 186 | 233.5 | 423 | 327 | 310
EHK | W | 54 |  | 54 | 41 |  | 0.98 |  |  | - | 41.5842 | 43.7017 | 47.4735 | 48.5915 | 48.0424 | 48.1032 | 6.59% | 784.21 | 1100.65 | 2253.3201 | 1835.95 | 1781.37 | 186 | 233.5 | 423 | 327 | 310
MRO | S | 27 |  | 27 | 18.3 | 389 | 1 |  |  | - | 21.048 | 22.7364 | 23.8503 | 24.76 | 24.56 | 24.26 | 24.24% | 90.31 | 147.29 | 216.71 | 179.65 | 131.39 | 62.5 | 83 | 105 | 90.5 | 70.5
MRO | W | 27 |  | 27 | 20.2 |  | 1 |  |  | - | 17.898 | 18.4105 | 19.4147 | 19.634 | 19.2854 | 19.0274 |  | 90.31 | 147.29 | 216.71 | 179.65 | 131.39 | 62.5 | 83 | 105 | 90.5 | 70.5
DPTS 66kV
MLN | S | 99 |  | 99 | 79.8 |  | 1 |  |  | - | 69.1633 | 79.6871 | 87.9547 | 96.3 | 97.3 | 98.42
MLN | W | 99 |  | 99 | 83.4 |  | 1 |  |  | - | 63.0003 | 70.388 | 81.1324 | 83.9831 | 84.2978 | 86.008
SU | S | 99 |  | 99 | 93 |  | 1 |  |  | - | 74.0307 | 92.4823 | 87.7716 | 89.8088 | 89.2424 | 89.2027
SU | W | 99 |  | 99 | 99 |  | 1 |  |  | - | 70.8474 | 74.5242 | 77.3363 | 77.3463 | 76.6906 | 77.0185
TNA | S | 66 |  | 99 | 95.2 |  | 1 |  |  | 8.8 | 78.142 | 82.887 | 105.036 | 118.604 | 119.2015 | 119.3937
TNA | W | 66 |  | 99 | 95.2 |  | 1 |  |  | 8.8 | 61.2502 | 82.735 | 107.7828 | 111.2775 | 111.4398 | 111.7843
FBTS 66kV
DLF | S | 66 |  | 66 | 42 |  | 0.99 |  |  | - | 13.9207 | 17.375 | 18.3214 | 19.041 | 19.4313 | 19.6379
DLF | W | 66 |  | 66 | 49.3 |  | 0.99 |  |  | - | 10.8764 | 15.6692 | 16.3988 | 16.8712 | 17.1181 | 17.1702
GTS 66kV
CLC | S | 79 |  | 79 | 49.2 |  | 1 |  |  | - | 35.3267 | 36.8811 | 37.3704 | 38.4185 | 37.6195 | 36.7013
CLC | W | 79 |  | 79 | 54.8 |  | 1 |  |  | - | 36.9721 | 35.7332 | 37.5002 | 37.4203 | 36.6614 | 36.0228
CRO | S | 60 |  | 60 | 34.3 | 4562 | 0.97 |  |  | - | 29.5365 | 44.8333 | 30.8707 | 31.4461 | 31.1221 | 30.7352 | 30.71% | 8871.4199 | 0 | 0 | 0 | 0 | 3869 | 0 | 0 | 0 | 0
CRO | W | 60 |  | 60 | 38 |  | 0.97 |  |  | - | 26.3427 | 42.6271 | 32.336 | 32.3556 | 31.9805 | 31.7702 | 12.18% | 8871.4199 | 0 | 0 | 0 | 0 | 3869 | 0 | 0 | 0 | 0
DDL | S | 66 |  | 66 | 39.7 | 262 | 0.99 |  |  | 1.1 | 52.9719 | 59.283 | 62.6156 | 65.9183 | 66.2159 | 66.9993 | 49.33% | 887.88 | 1341.65 | 2091.8701 | 1761.97 | 1669.23 | 158.5 | 208 | 309.5 | 241 | 222
DDL | W | 66 |  | 66 | 47.2 |  | 0.99 |  |  | 1.1 | 50.6465 | 50.9524 | 55.0877 | 56.1102 | 55.7628 | 55.872 | 7.95% | 887.88 | 1341.65 | 2091.8701 | 1761.97 | 1669.23 | 158.5 | 208 | 309.5 | 241 | 222
FNS | S | 99 |  | 99 | 87.2 |  | 0.99 |  |  | 1 | 37.1945 | 42.6895 | 51.5171 | 57.7704 | 57.7206 | 57.4412
FNS | W | 99 |  | 99 | 98.6 |  | 0.99 |  |  | 1 | 32.5651 | 41.7922 | 51.0377 | 52.6539 | 52.255 | 51.886
GB | S | 37.5 |  | 37.5 | 37.6 |  | 0.92 |  |  | - | 15.4542 | 14.5623 | 24.7477 | 30.5923 | 30.3768 | 29.9817
GB | W | 37.5 |  | 37.5 | 37.6 |  | 0.92 |  |  | - | 13.4373 | 16.7648 | 28.299 | 29.5285 | 29.2277 | 28.9763
GCY | S | 66 |  | 66 | 37.8 | 1357 | 0.96 |  |  | 5.5 | 41.9598 | 47.8913 | 50.4378 | 52.0256 | 51.1712 | 49.9159 | 26.7% | 504.39 | 1128.51 | 1886.9 | 1405.26 | 852.32 | 170 | 344 | 577 | 429 | 281.5
GCY | W | 66 |  | 66 | 43.9 |  | 0.96 |  |  | 5.5 | 33.6962 | 35.7121 | 38.8968 | 39.1055 | 38.4477 | 38.0083 |  | 504.39 | 1128.51 | 1886.9 | 1405.26 | 852.32 | 170 | 344 | 577 | 429 | 281.5
GL | S | 80 |  | 80 | 47.6 | 302 | 1 |  |  | - | 58.2347 | 59.9182 | 41.5662 | 43.2598 | 43.0805 | 43.1702 | 25.88% | 266.39 | 0 | 0 | 0 | 0 | 66.5 | 0 | 0 | 0 | 0
GL | W | 80 |  | 80 | 47.6 |  | 1 |  |  | - | 53.5871 | 35.8307 | 38.3001 | 38.6493 | 38.2006 | 38.0116 |  | 266.39 | 0 | 0 | 0 | 0 | 66.5 | 0 | 0 | 0 | 0
GLE | S | 79.5 |  | 79.5 | 53.3 |  | 1 |  |  | - | 50.5598 | 55.0077 | 53.4547 | 56.1504 | 56.1903 | 55.6388
GLE | W | 79.5 |  | 79.5 | 59.1 |  | 1 |  |  | - | 48.3012 | 47.8534 | 51.3506 | 52.2215 | 51.8337 | 51.6162
WIN | S | 20.5 |  | 20.5 | 10.5 |  | 0.91 |  |  | - | 8.1043 | 8.3988 | 8.4526 | 8.5649 | 8.6052 | 8.6413
WIN | W | 20.5 |  | 20.5 | 10.5 |  | 0.91 |  |  | - | 9.4423 | 9.1434 | 9.2569 | 9.3026 | 9.2661 | 9.2478
WPD | S | 79.5 |  | 79.5 | 56.8 |  | 1 |  |  | - | 68.1802 | 82.3751 | 58.4457 | 60.8606 | 60.9914 | 61.2131 | 45.03% | 2219.2 | 2.35 | 10.11 | 10.37 | 10.94 | 350.5 | 2.5 | 5 | 5 | 5
WPD | W | 79.5 |  | 79.5 | 62.6 |  | 1 |  |  | - | 70.6367 | 47.2 | 50.1437 | 51.0998 | 50.808 | 50.5765 |  | 2219.2 | 2.35 | 10.11 | 10.37 | 10.94 | 350.5 | 2.5 | 5 | 5 | 5
HOTS 66kV
CHM | S | 33 |  | 33 | 36.9 |  | 0.99 |  |  | - | 2.1634 | 1.9319 | 1.8857 | 1.8578 | 1.8202 | 1.7925
CHM | W | 33 |  | 33 | 44.1 |  | 0.99 |  |  | - | 1.8573 | 1.7573 | 1.7279 | 1.6812 | 1.6445 | 1.5814
HSM | S | 40.5 |  | 40.5 | 39.7 |  | 1 |  |  | - | 38.941 | 40.3394 | 43.6049 | 45.7655 | 45.1582 | 44.6505
HSM | W | 40.5 |  | 40.5 | 40.4 |  | 1 |  |  | - | 33.5384 | 34.0271 | 37.7406 | 37.86 | 37.1531 | 36.6852
NHL | S | 20 |  | 20 | 13 |  | 1 |  |  | - | 9.7478 | 10.9437 | 11.7833 | 12.6429 | 12.3833 | 12.213
NHL | W | 20 |  | 20 | 16.2 |  | 1 |  |  | - | 9.6568 | 9.2635 | 10.7235 | 10.7335 | 10.4834 | 10.1634
STL | S | 27 |  | 27 | 18.5 |  | 0.99 |  |  | - | 20.4468 | 19.1805 | 19.3515 | 20.249 | 19.866 | 19.5027
STL | W | 27 |  | 27 | 18.8 |  | 0.99 |  |  | - | 19.1668 | 18.9997 | 20.2079 | 20.1586 | 19.695 | 19.2216
KGTS 66kV
CHA | S | 27 |  | 27 | 15.2 |  | 0.99 |  |  | - | 14.2512 | 14.7022 | 15.0602 | 15.4083 | 15.0998 | 14.7234
CHA | W | 27 |  | 27 | 15.2 |  | 0.99 |  |  | - | 13.4639 | 14.326 | 15.0701 | 14.9809 | 14.6626 | 14.3458
SHL | S | 40.5 |  | 40.5 | 36.7 |  | 0.99 |  |  | 14.4 | 35.1854 | 36.0498 | 38.6717 | 41.6103 | 41.1639 | 40.5662
SHL | W | 40.5 |  | 40.5 | 40.4 |  | 0.99 |  |  | 14.4 | 27.3591 | 28.7785 | 33.1924 | 33.8278 | 33.3092 | 32.7417
KTS 66kV
GSB | S | 66 |  | 66 | 49.5 |  | 1 |  |  | - | 17.9034 | 21.1376 | 22.6972 | 23.4771 | 23.4563 | 23.507
GSB | W | 66 |  | 66 | 49.5 |  | 1 |  |  | - | 21.786 | 21.7043 | 23.4463 | 23.507 | 23.2744 | 23.0717
SA | S | 93 |  | 93 | 81.2 |  | 0.99 |  |  | - | 73.7608 | 85.4347 | 87.6834 | 89.0658 | 89.0844 | 89.3081 | 5.215% | 6.24 | 15.84 | 24.18 | 22.3 | 20.94 | 2.5 | 5.5 | 7.5 | 7 | 6.5
SA | W | 93 |  | 93 | 89.6 |  | 0.99 |  |  | - | 63.5194 | 65.7674 | 67.0493 | 67.3644 | 67.1792 | 67.439 |  | 6.24 | 15.84 | 24.18 | 22.3 | 20.94 | 2.5 | 5.5 | 7.5 | 7 | 6.5
SSE | S | 99 |  | 99 | 89.7 |  | 0.95 |  |  | - | 62.5045 | 75.3763 | 77.0078 | 79.1712 | 78.1463 | 77.5075
SSE | W | 99 |  | 99 | 99 |  | 0.95 |  |  | - | 57.1616 | 64.8726 | 67.2991 | 67.4694 | 66.5352 | 66.2418
WND | S | 66 |  | 66 | 37.5 |  | 1 |  |  | 4.7 | 22.1804 | 24.7621 | 26.4197 | 27.5213 | 27.4617 | 27.5907
WND | W | 66 |  | 66 | 42.7 |  | 1 |  |  | 1.5 | 31.5112 | 30.05 | 32.14 | 32.29 | 32.01 | 31.88
RCTS 66kV
BBD | S | 66 |  | 66 | 45.2 |  | 0.97 |  |  | - | 29.5898 | 30.2138 | 32.0522 | 31.9892 | 31.197 | 30.2355
BBD | W | 66 |  | 66 | 49.5 |  | 0.97 |  |  | - | 25.7971 | 23.2071 | 24.2753 | 24.0105 | 23.3442 | 22.7
MBN | S | 60 |  | 59 | 37.6 | 206 | 0.99 |  |  | - | 41.4087 | 42.4707 | 48.1558 | 52.3436 | 51.9926 | 51.9517 | 12.95% | 15.56 | 214.9 | 912.22 | 786.03 | 765.64 | 10.5 | 70 | 225 | 192 | 186
MBN | W | 60 |  | 59 | 40.4 |  | 0.99 |  |  | - | 28.407 | 29.7158 | 36.7257 | 37.6393 | 37.1571 | 36.7965 |  | 15.56 | 214.9 | 912.22 | 786.03 | 765.64 | 10.5 | 70 | 225 | 192 | 186
MDA | S | 66 |  | 66 | 39.7 | 434 | 0.99 |  |  | - | 47.2036 | 49.277 | 49.0238 | 49.9694 | 49.1794 | 49.1214 | 24.12% | 224.15 | 183.84 | 267.8 | 183.17 | 172.65 | 78 | 66 | 87 | 64.5 | 62.5
MDA | W | 66 |  | 66 | 44.6 |  | 0.99 |  |  | - | 35.647 | 36.4581 | 38.4565 | 38.6898 | 38.0078 | 37.5496 |  | 224.15 | 183.84 | 267.8 | 183.17 | 172.65 | 78 | 66 | 87 | 64.5 | 62.5
SHTS 66kV
CME | S | 40.5 |  | 40.5 | 32.3 |  | 1 |  |  | 14.25 | 30.4421 | 33.3942 | 35.1751 | 38.7769 | 38.3474 | 38.1432
CME | W | 40.5 |  | 40.5 | 37.3 |  | 1 |  |  | 14.25 | 25.8877 | 28.778 | 32.514 | 33.0664 | 32.6267 | 31.9714
ECA | S | 40.5 |  | 40.5 | 34.6 |  | 0.99 |  |  | 9.6 | 29.6996 | 29.176 | 30.7497 | 32.4349 | 32.1025 | 31.6375
ECA | W | 40.5 |  | 40.5 | 40.4 |  | 0.99 |  |  | 4.8 | 24.5189 | 25.7342 | 28.1965 | 28.53 | 28.0055 | 27.6212
KYM | S | 40.5 |  | 40.5 | 33.8 |  | 1 |  |  | - | 24.726 | 28.73 | 29.72 | 30.82 | 30.43 | 30.16
KYM | W | 40.5 |  | 40.5 | 38.8 |  | 1 |  |  | - | 20.12 | 23.9939 | 25.3638 | 25.6234 | 25.2382 | 24.7847
MNA | S | 66 |  | 66 | 37 | 485 | 0.99 |  |  | 5.8 | 39.6296 | 40.9411 | 42.034 | 42.2832 | 42.0043 | 41.8655 | 10.65% | 20.36 | 40.87 | 41.72 | 31.7 | 27.97 | 17 | 24.5 | 23 | 19 | 18
MNA | W | 66 |  | 66 | 42.5 |  | 0.99 |  |  | 1 | 30.1343 | 30.8495 | 31.3755 | 31.3164 | 30.8495 | 30.6605 |  | 20.36 | 40.87 | 41.72 | 31.7 | 27.97 | 17 | 24.5 | 23 | 19 | 18
NKA | S | 39.5 |  | 39.5 | 30.5 |  | 0.99 |  |  | 14.6 | 25.1905 | 28.95 | 30.2864 | 31.6496 | 31.2044 | 30.8348
NKA | W | 39.5 |  | 39.5 | 30.5 |  | 0.99 |  |  | 9.8 | 24.3559 | 26.27 | 28.856 | 28.8646 | 28.4202 | 27.9846
SHN | S | 66 |  | 66 | 40 |  | 0.99 |  |  | 5.4 | 31.9026 | 33.407 | 34.2693 | 35.8112 | 35.6657 | 35.7821
SHN | W | 66 |  | 66 | 44.1 |  | 0.99 |  |  | 5.4 | 24.7074 | 26.3795 | 28.3764 | 28.6468 | 28.3847 | 28.2298
SHP | S | 66 |  | 66 | 36.6 |  | 0.98 |  |  | 28.8 | 22.2397 | 22.9417 | 24.7233 | 27.4744 | 27.1204 | 27.0426
SHP | W | 66 |  | 66 | 41.9 |  | 0.98 |  |  | 19.2 | 18.6878 | 19.9899 | 24.1389 | 24.3025 | 23.9673 | 23.507
STN | S | 79 |  | 79 | 61.9 |  | 0.99 |  |  | 7.4 | 46.5053 | 46.3994 | 46.7561 | 48.1121 | 47.6946 | 46.9599
STN | W | 79 |  | 79 | 61.9 |  | 0.99 |  |  | 3.3 | 35.5655 | 32.9215 | 34.0006 | 34.3273 | 33.6951 | 33.2171
TGTS 66kV
CDN | S | 20 |  | 20 | 17.2 |  | 0.99 |  |  | - | 11.7251 | 12.7796 | 12.5912 | 12.808 | 12.543 | 12.4439
CDN | W | 20 |  | 20 | 18.2 |  | 0.99 |  |  | - | 13.3165 | 14.1962 | 14.4911 | 14.3337 | 13.9654 | 13.66
COB | S | 26 |  | 26 | 15 |  | 0.94 |  |  | - | 13.1911 | 14.3772 | 14.8856 | 15.5206 | 15.2616 | 14.854
COB | W | 26 |  | 26 | 15 |  | 0.94 |  |  | - | 13.2846 | 14.0234 | 15.0531 | 15.0121 | 14.6583 | 14.3772
HTN | S | 39.5 |  | 39.5 | 34.2 |  | 1 |  |  | - | 24.9237 | 25.3356 | 25.286 | 26.082 | 25.6441 | 25.1365
HTN | W | 39.5 |  | 39.5 | 38.4 |  | 1 |  |  | - | 24.3411 | 24.7286 | 25.6144 | 25.8133 | 25.246 | 24.7586
KRT | S | 40.5 |  | 40.5 | 33.4 |  | 1 |  |  | - | 25.4688 | 25.5377 | 26.0374 | 26.917 | 26.5876 | 26.0474
KRT | W | 40.5 |  | 40.5 | 37.6 |  | 1 |  |  | - | 25.865 | 26.5471 | 27.8871 | 27.7773 | 27.1672 | 26.907
PLD | S | 32 |  | 32 | 22.1 |  | 0.98 |  |  | - | 14.515 | 16.459 | 16.4493 | 16.8533 | 16.6512 | 16.4104
PLD | W | 32 |  | 32 | 24 |  | 0.98 |  |  | - | 16.8889 | 18.5411 | 18.935 | 18.9272 | 18.5411 | 18.2711
TRG | S | 46.5 |  | 46.5 | 19.2 | 38 | 0.99 |  |  | 7.2 | 16.5718 | 19.0878 | 18.9874 | 18.9183 | 18.6006 | 18.2238 |  | 1.81 | 1.78 | 1.56 | 1.09 | 0.71 | 1 | 1 | 1 | 1 | 1
TRG | W | 46.5 |  | 46.5 | 19.4 |  | 0.99 |  |  | 7.2 | 18.44 | 22.1851 | 22.1257 | 21.8965 | 21.3999 | 21.0138 | 14.36% | 1.81 | 1.78 | 1.56 | 1.09 | 0.71 | 1 | 1 | 1 | 1 | 1
WBL | S | 79.5 |  | 79.5 | 49.2 |  | 0.99 |  |  | - | 45.9575 | 48.6046 | 50.5265 | 52.7894 | 51.9786 | 51.0873
WBL | W | 79.5 |  | 79.5 | 54.8 |  | 0.99 |  |  | - | 45.2839 | 47.8336 | 51.2978 | 51.6776 | 50.7765 | 50.076
WETS 66kV
OYN | S | 27 |  | 27 | 15.2 |  | 0.89 |  |  | - | 6.7441 | 7.6117 | 7.5268 | 7.4686 | 7.2899 | 7.1514
OYN | W | 27 |  | 27 | 15.2 |  | 0.89 |  |  | - | 7.1504 | 6.2988 | 6.2365 | 6.1206 | 5.9466 | 5.7774
RVL | S | 19.5 |  | 19.5 | 20.4 | 534 | 0.99 |  |  | 7.5 | 15.8734 | 25.7124 | 26.1478 | 26.2296 | 25.6008 | 24.9224 | 26.04% | 65.21 | 87.98 | 96.93 | 69.04 | 46.29 | 39 | 47 | 48.5 | 42 | 33.5
RVL | W | 19.5 |  | 19.5 | 22.9 |  | 0.99 |  |  | 7.5 | 22.4335 | 23.97 | 24.6595 | 24.4363 | 23.8187 | 23.2 |  | 65.21 | 87.98 | 96.93 | 69.04 | 46.29 | 39 | 47 | 48.5 | 42 | 33.5
WMN | S | 33 | 13.5 | 46.5 | 17.2 | 360 | 0.98 |  |  | 4.25 | 21.4436 | 23.7803 | 24.8133 | 24.8035 | 24.1773 | 23.4263 | 38.26% | 157.87 | 280 | 293.02 | 236.43 | 176.39 | 78 | 122.5 | 127.5 | 114.5 | 95
WMN | W | 33 | 13.5 | 46.5 | 20.2 |  | 0.98 |  |  | 4.25 | 18.4157 | 17.6372 | 18.5968 | 18.4093 | 17.9083 | 17.4173 |  | 157.87 | 280 | 293.02 | 236.43 | 176.39 | 78 | 122.5 | 127.5 | 114.5 | 95

## Sub-t lines maximum demand
Subtransmission line Maximum Demand |  | Line Import Rating (MVA) | Hours 95% of Maximum Demand | Power Factor at Maximum Demand | Load Transfer Capacity (MVA) | Generation Capacity (MW) | Historical Maximum Demand Worst case N-1 Scenario (MVA) | 50% PoE Forecast Maximum Demand Worst case N-1 Scenario (MVA) |  |  |  |  | % Load Above N-1 Import Rating (2023) | Energy at Risk (MWh) (N-1 50% PoE) |  |  |  |  | Hours at Risk (N-1 50% PoE)
[7 empty] | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 |  | 2023 | 2024 | 2025 | 2026 | 2027 | 2023 | 2024 | 2025 | 2026 | 2027
ATS 66kV
ATS-HCP | S | 109.7 | 2 | 0.94327 |  |  | 118.1 | 126.1 | 131.3 | 139.8 | 142.9 | 147.5 | 14.95% | 51 | 100 | 229 | 293 | 403 | 7 | 13 | 21 | 25 | 30
ATS-HCP | W | 134.9 | 4 | 0.94406 |  |  | 87.6 | 92.1 | 99.3 | 102.7 | 104.1 | 106.1
ATS-WBE | S | 109.7 | 2 | 0.94078 |  |  | 118.2 | 126.2 | 131.4 | 139.9 | 144.4 | 147.6 | 15.04% | 52 | 101 | 231 | 325 | 404 | 7 | 13 | 21 | 27 | 30
ATS-WBE | W | 134.9 | 4 | 0.94292 |  |  | 87.6 | 92.1 | 99.4 | 102.7 | 104.2 | 106.2
HCP-WBE | S | 109.7 |  | 0.96756 |  |  | 104.8 | 112 | 116.8 | 124 | 126.7 | 130.7
HCP-WBE | W | 134.9 |  | 0.96031 |  |  | 78.1 | 82.3 | 88.9 | 92.1 | 93.6 | 95.5
ATS-LV | S | 135.5 |  | 0.96886 |  |  | 115.6 | 123.6 | 126.4 | 131 | 131.4 | 131.9
ATS-LV | W | 142.3 |  | 0.9742 |  |  | 96.9 | 100.6 | 105.7 | 106.9 | 106.6 | 106.9
ATS-AWT | S | 109.7 |  | 0.97544 |  |  | 114 | 121.9 | 124.7 | 128.9 | 129.3 | 129.8
ATS-AWT | W | 134.9 |  | 0.98013 |  |  | 95.6 | 99.3 | 104.4 | 105.5 | 105.2 | 105.5
AWT-LV | S | 109.7 |  | 0.97538 |  |  | 97.5 | 105.1 | 107.8 | 111.9 | 112.3 | 112.8
AWT-LV | W | 134.9 |  | 0.97862 |  |  | 79.5 | 83.1 | 88 | 89.2 | 88.9 | 89.2
ATS/BLTS 66kV
ATS-AC | S | 102.3 |  | 0.97143 |  |  | 38.5 | 37.4 | 38.1 | 39.2 | 38.9 | 38.6
ATS-AC | W | 108 |  | 0.96569 |  |  | 40.8 | 41.3 | 42.1 | 42 | 41.7 | 41.4
AC-CPL | S | 102.9 |  | 0.97245 |  |  | 36.3 | 34.9 | 35 | 35.7 | 35.5 | 35.2
AC-CPL | W | 108 |  | 0.96615 |  |  | 38.4 | 38.3 | 38.6 | 38.5 | 38.2 | 37.9
CPL-AL | S | 91.4 |  | 0.9878 |  |  | 24.6 | 25.7 | 25.9 | 26.5 | 26.6 | 26.7
CPL-AL | W | 91.4 |  | 0.98558 |  |  | 20.8 | 20.7 | 21.1 | 21.2 | 21.4 | 21.6
AL-BLTS | S | 91.4 |  | 0.95819 |  |  | 28.7 | 26.7 | 27.5 | 28 | 27.6 | 27.1
AL-BLTS | W | 91.4 |  | 0.94817 |  |  | 32.8 | 33.6 | 34.6 | 34.6 | 33.9 | 33.4
ATS-ATD | S | 102.3 |  | 0.99371 |  |  | 15.9 | 16 | 16 | 16.2 | 16.2 | 16.2
ATS-ATD | W | 130.3 |  | 0.99359 |  |  | 15.6 | 15.6 | 15.5 | 15.6 | 15.6 | 15.6
BLTS-ATD | S | 97.2 |  | 0.99355 |  |  | 15.5 | 15.3 | 15.1 | 15.1 | 15.1 | 15.1
BLTS-ATD | W | 125.7 |  | 0.98765 |  |  | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.1
ATS-LVN | S | 109.7 |  | 0.94393 |  |  | 107 | 106.7 | 106.6 | 106.7 | 106.7 | 106.7
ATS-LVN | W | 134.9 |  | 0.94393 |  |  | 107 | 106.8 | 106.9 | 106.9 | 107 | 106.9
BLTS-LVN | S | 109.7 |  | 0.94161 |  |  | 107.9 | 107.6 | 108.3 | 108.3 | 108.3 | 108.3
BLTS-LVN | W | 122.3 |  | 0.9408 |  |  | 108.1 | 107.9 | 107.8 | 107.9 | 107.9 | 107.9
ATS-SCI | S | 90.8 |  | 0.75488 |  |  | 46.1 | 46 | 45.8 | 45.9 | 45.9 | 45.9
ATS-SCI | W | 116 |  | 0.76674 |  |  | 46.3 | 46.2 | 46.2 | 46.2 | 46.2 | 46.2
BLTS-SCI | S | 97.2 |  | 0.99755 |  |  | 81.6 | 81.5 | 81.2 | 81.2 | 81.2 | 81.2
BLTS-SCI | W | 125.7 |  | 0.99338 |  |  | 75.5 | 75.4 | 75.4 | 75.4 | 75.4 | 75.4
ATS-TYA | S | 102.3 |  | 0.96889 |  |  | 22.5 | 22.8 | 22.9 | 23.6 | 23.7 | 23.7
ATS-TYA | W | 130.3 |  | 0.96279 |  |  | 21.5 | 21.3 | 21.3 | 21.3 | 21.4 | 21.5
BLTS-TYA | S | 88 |  | 0.96875 |  |  | 22.4 | 22.6 | 22.7 | 23.5 | 23.5 | 23.6
BLTS-TYA | W | 112 |  | 0.96729 |  |  | 21.4 | 21.4 | 21.4 | 21.4 | 21.3 | 21.4
BLTS-BMH | S | 32.6 |  | 0.97586 |  |  | 29 | 29.7 | 34 | 35.8 | 36.1 | 36.2
BLTS-BMH | W | 37.7 |  | 0.9823 |  |  | 22.6 | 24.6 | 28 | 28.3 | 28.3 | 28.5
BATS 66kV
BATS-BAN1 | S | 96 |  | 0.9542 |  |  | 91.7 | 98.8 | 104.1 | 106.2 | 106.1 | 106.1
BATS-BAN1 | W | 114.3 |  | 0.9546 |  |  | 85.9 | 95.1 | 99 | 99.6 | 98.7 | 98.3
BATS-BAN2 | S | 96 |  | 0.95109 |  |  | 92 | 99.2 | 103.5 | 106.6 | 106.4 | 106.5
BATS-BAN2 | W | 114.3 |  | 0.95082 |  |  | 85.4 | 94.6 | 99.4 | 100 | 99.1 | 98.7
BAN-BGR | S | 46.3 |  | 0.98621 |  |  | 14.5 | 14.4 | 15 | 15.3 | 15 | 14.9
BAN-BGR | W | 49.7 |  | 0.97887 |  |  | 14.2 | 14.1 | 14.8 | 14.7 | 14.4 | 14.2
BGR-ART | S | 45.7 |  | 0.98561 |  |  | 13.9 | 13.7 | 14.3 | 14.5 | 14.3 | 14.1
BGR-ART | W | 47.4 |  | 0.98519 |  |  | 13.5 | 13.5 | 14.1 | 14 | 13.7 | 13.5
BATS-YSW/BGL | S | 36.6 |  | 1 |  |  | 32.7 | 33.7 | 38.1 | 39.3 | 39.5 | 39.6
BATS-YSW/BGL | W | 37.1 |  | 0.97674 |  |  | 25.8 | 27.3 | 30.7 | 30.9 | 30.9 | 31.1
YSW-BMH | S | 36.6 |  | 0.97407 |  |  | 27 | 27.7 | 31.3 | 32.2 | 32.3 | 32.4
YSW-BMH | W | 37.2 |  | 0.98113 |  |  | 21.2 | 22.6 | 25.7 | 25.9 | 25.9 | 26
BATS-BAS1 | S | 83.5 |  | 0.96927 |  |  | 78.1 | 78.1 | 77 | 79.1 | 79.2 | 79.4
BATS-BAS1 | W | 102.9 |  | 0.96919 |  |  | 71.4 | 69.4 | 71.7 | 72.2 | 72 | 72.3
BATS-BAS2/BGF | S | 93.2 |  | 0.96403 |  |  | 83.4 | 83.3 | 82.3 | 85.5 | 85.6 | 85.8
BATS-BAS2/BGF | W | 94.9 |  | 0.96606 |  |  | 76.6 | 74.6 | 76.9 | 77.4 | 77.2 | 77.5
BETS 66kV
BETS-BGO | S | 109.7 |  | 0.95253 |  |  | 94.8 | 97.9 | 102.2 | 108.2 | 107.9 | 107.9
BETS-BGO | W | 114.3 |  | 0.96556 |  |  | 78.4 | 80.4 | 87.2 | 88.7 | 87.8 | 87.5
BGO-EHK | S | 48.6 | 2 | 0.95489 |  |  | 53.2 | 54.3 | 57.1 | 61.1 | 61.2 | 61.7 | 11.73% | 16 | 41 | 126 | 129 | 142 | 8 | 15 | 34 | 34 | 34
BGO-EHK | W | 49.2 | 1 | 0.96028 |  |  | 42.8 | 43.9 | 48 | 49 | 48.6 | 48.7
BETS-EHK | S | 111.4 |  | 0.94544 |  |  | 95.3 | 99.9 | 102.8 | 109.5 | 110.4 | 110
BETS-EHK | W | 111.4 |  | 0.96046 |  |  | 78.4 | 81 | 88.5 | 90 | 88.4 | 88.1
BETS-CMN | S | 64 |  | 0.98361 |  |  | 54.9 | 55.5 | 57.8 | 59.5 | 59.2 | 58.3
BETS-CMN | W | 65.2 |  | 0.99558 |  |  | 45.2 | 46.4 | 48.2 | 48.7 | 47.6 | 46.8
CMN-MRO | S | 26.3 |  | 0.97255 |  |  | 25.5 | 26 | 27.5 | 28.6 | 28.5 | 28.2
CMN-MRO | W | 35.4 |  | 0.99578 |  |  | 23.7 | 23.9 | 23.9 | 23.7 | 23.6 | 23.6
BETS-MRO | S | 76.6 |  | 0.92401 |  |  | 57.9 | 58.7 | 60 | 62.3 | 60.9 | 61.1
BETS-MRO | W | 89.2 |  | 0.95538 |  |  | 49.3 | 50.6 | 52.7 | 53.1 | 51.9 | 51.5
BETS-CTN | S | 26.3 |  | 0.99541 |  |  | 21.8 | 21.6 | 21.2 | 21.2 | 20.9 | 20.5
BETS-CTN | W | 30.3 |  | 0.99531 |  |  | 21.3 | 21 | 21 | 20.8 | 19.9 | 19.2
CTN-CBW | S | 98.9 |  | 0 |  |  | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
CTN-CBW | W | 106.3 |  | 0 |  |  | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
DPTS 66kV
DPTS-MLN1 | S | 109.7 |  | 0.94798 |  |  | 76.9 | 85.5 | 94.5 | 104.1 | 106.2 | 107.5
DPTS-MLN1 | W | 134.9 |  | 0.94928 |  |  | 69 | 75.4 | 87.5 | 91.1 | 91.5 | 94.1
DPTS-MLN2 | S | 109.7 |  | 0.94928 |  |  | 76.9 | 85.5 | 94.5 | 104 | 105.1 | 106.3
DPTS-MLN2 | W | 134.9 |  | 0.95065 |  |  | 68.9 | 75.3 | 87.1 | 90.1 | 90.5 | 92.2
DPTS-SU1 | S | 109.7 |  | 0.96129 |  |  | 93 | 98.7 | 93 | 94.7 | 94.1 | 94.9
DPTS-SU1 | W | 133.7 |  | 0.96355 |  |  | 82.3 | 77.9 | 81 | 81 | 80.3 | 80.6
DPTS-SU2 | S | 109.7 |  | 0.9543 |  |  | 94.1 | 98.9 | 94.1 | 96.7 | 95.1 | 96
DPTS-SU2 | W | 133.7 |  | 0.95793 |  |  | 83.2 | 79.5 | 81.9 | 81.9 | 81.2 | 81.5
DPTS-TNA1 | S | 109.7 |  | 0.99403 |  |  | 67 | 82.9 | 106.1 | 120.4 | 121 | 121.1
DPTS-TNA1 | W | 134.9 |  | 0.99232 |  |  | 65.1 | 83.4 | 109.8 | 113.3 | 113.5 | 113.7
DPTS-TNA2 | S | 109.7 |  | 0.99403 |  |  | 67 | 82.9 | 106.1 | 120.4 | 122.1 | 122.3
DPTS-TNA2 | W | 134.9 |  | 0.99232 |  |  | 65.1 | 83.4 | 109.8 | 113.3 | 113.5 | 113.7
FBTS 66kV
FBTS-DLF1 | S | 87.5 |  | 0.95154 |  |  | 22.7 | 23.7 | 24.7 | 25.7 | 26 | 25.8
FBTS-DLF1 | W | 87.5 |  | 0.96098 |  |  | 20.5 | 21.4 | 22.1 | 22.6 | 22.7 | 22.7
FBTS-DLF3 | S | 87.5 |  | 0.95154 |  |  | 22.7 | 23.7 | 24.7 | 25.7 | 26 | 25.8
FBTS-DLF3 | W | 87.5 |  | 0.96098 |  |  | 20.5 | 21.4 | 22.1 | 22.6 | 22.8 | 22.7
GTS 66kV
GTS-BCG | S | 109.7 |  | 0.98278 |  |  | 75.5 | 82.6 | 59.8 | 61.8 | 61.8 | 61.9
GTS-BCG | W | 134.9 |  | 0.98417 |  |  | 69.5 | 49.2 | 51.8 | 52.5 | 52.1 | 51.8
BCG-WPD | S | 91.4 |  | 0.99848 |  |  | 66 | 72.6 | 51.4 | 53.3 | 53.4 | 53.6
BCG-WPD | W | 91.4 |  | 1 |  |  | 60.5 | 41.3 | 43.7 | 44.6 | 44.3 | 44.1
GTS-WPD | S | 91.4 |  | 0.98541 |  |  | 75.4 | 81.4 | 59.7 | 61.8 | 61.8 | 61.8
GTS-WPD | W | 91.4 |  | 0.98686 |  |  | 68.5 | 49.2 | 51.7 | 52.5 | 52.1 | 51.7
GTS-WIN | S | 74.3 |  | 0.99549 |  |  | 44.3 | 44.1 | 44.6 | 45.9 | 45.1 | 44.1
GTS-WIN | W | 87.4 |  | 0.99089 |  |  | 43.9 | 43.9 | 45.9 | 45.9 | 45 | 44.3
MGW-CLC | S | 74.3 |  | 0.99708 |  |  | 34.3 | 34.4 | 34.8 | 35.8 | 35.1 | 34.2
MGW-CLC | W | 86.9 |  | 0.99699 |  |  | 33.2 | 33.3 | 35 | 34.9 | 34.2 | 33.6
WIN-MGW | S | 98.3 |  | 0.98034 |  |  | 35.6 | 35.7 | 36.1 | 37.4 | 36.5 | 35.6
WIN-MGW | W | 99.5 |  | 0.96848 |  |  | 34.9 | 35 | 36.9 | 36.8 | 36 | 35.4
GTS-CRO | S | 91.4 |  | 0.95515 |  |  | 37.9 | 47.2 | 32.3 | 33.2 | 32.8 | 32.5
GTS-CRO | W | 91.4 |  | 0.94848 |  |  | 42.7 | 45.2 | 34.4 | 34.4 | 34 | 33.8
FDN-CRO | S | 109.7 |  | 0.95355 |  |  | 36.6 | 46.4 | 31.1 | 31.9 | 31.6 | 31.2
FDN-CRO | W | 134.9 |  | 0.94878 |  |  | 41 | 43.4 | 32.8 | 32.8 | 32.4 | 32.2
GTS-FDN | S | 102.9 |  | 0.95 |  |  | 38 | 47.9 | 32.3 | 33.2 | 32.9 | 32.5
GTS-FDN | W | 134.9 |  | 0.94626 |  |  | 42.8 | 45.2 | 34.4 | 34.4 | 34.1 | 33.9
GTS-FNS | S | 88 |  | 0.97539 |  |  | 77.2 | 83.1 | 91.4 | 97 | 97 | 96.7
GTS-FNS | W | 112 |  | 0.97507 |  |  | 72.2 | 81 | 89.4 | 90.9 | 90.6 | 90.2
FNS-SRC | S | 109.7 |  | 0.96774 |  |  | 43.4 | 43.3 | 47.1 | 52.7 | 52.6 | 52.4
FNS-SRC | W | 125.7 |  | 0.96927 |  |  | 42.3 | 42.3 | 46.2 | 47.7 | 47.3 | 47
GTS-SRC | S | 109.7 |  | 0.9728 |  |  | 77.2 | 83.2 | 91.5 | 97.1 | 97 | 96.8
GTS-SRC | W | 134.9 |  | 0.97249 |  |  | 72.7 | 81.1 | 89.5 | 91 | 90.6 | 90.3
GTS-GB | S | 135.5 |  | 0.9258 |  |  | 118.6 | 122.7 | 117.3 | 128.1 | 126.6 | 124.1
GTS-GB | W | 142.3 |  | 0.94136 |  |  | 97.2 | 85.7 | 104.6 | 106.3 | 104.8 | 104.1
GB-GL | S | 89.7 | 1 | 0.94763 |  |  | 101.2 | 104.8 | 89.8 | 93.7 | 92.7 | 90.8 | 16.83% | 22 | 0 | 3 | 2 | 0 | 3 | 0 | 1 | 1 | 1
GB-GL | W | 100.6 | 2 | 0.9599 |  |  | 82.3 | 68 | 74.5 | 75 | 74 | 73.4
GCY-GL | S | 109.7 |  | 0.96952 |  |  | 68.9 | 69.9 | 61.8 | 68.8 | 68.5 | 68.7
GCY-GL | W | 134.9 |  | 0.97073 |  |  | 61.5 | 49 | 62.6 | 63.6 | 63.4 | 63
GTS-GCY | S | 90.3 | 1 | 0.93333 |  |  | 118.5 | 121.7 | 116.1 | 125.9 | 124.7 | 124.4 | 34.77% | 123 | 84 | 192 | 174 | 168 | 15 | 12 | 23 | 21 | 21
GTS-GCY | W | 96.6 | 2 | 0.94473 |  |  | 97.7 | 85.9 | 105 | 105.7 | 105.3 | 104.5
GTS-GLE1 | S | 109.7 | 1 | 0.93229 |  |  | 121.1 | 125.3 | 129 | 137.3 | 137.7 | 138.2 | 14.22% | 17 | 27 | 62 | 64 | 67 | 3 | 3 | 6 | 6 | 6
GTS-GLE1 | W | 133.7 | 1 | 0.94073 |  |  | 104.6 | 106.2 | 117 | 119 | 118.3 | 118.5
GTS-GLE2 | S | 109.7 | 1 | 0.90063 |  |  | 127.8 | 134.2 | 139.1 | 147.9 | 148.4 | 148.9 | 22.33% | 42 | 63 | 121 | 125 | 129 | 5 | 6 | 10 | 10 | 10
GTS-GLE2 | W | 133.7 | 1 | 0.91462 |  |  | 110.1 | 112.4 | 121.9 | 124.4 | 123.3 | 123.2
GLE-DDL1 | S | 74.3 |  | 0.94488 |  |  | 63.5 | 64.4 | 68.1 | 72.2 | 72.6 | 73.5
GLE-DDL1 | W | 86.9 |  | 0.94877 |  |  | 52.7 | 54.6 | 59.6 | 60.6 | 60.3 | 60.4
GLE-DDL2 | S | 74.3 |  | 0.94497 |  |  | 63.6 | 64.5 | 69.4 | 73.4 | 73.8 | 74.9
GLE-DDL2 | W | 86.9 |  | 0.95066 |  |  | 52.7 | 54.7 | 59.7 | 60.7 | 60.4 | 60.6
HOTS 66kV
HOTS-STL1 | S | 49.2 |  | 0.96296 |  |  | 24.3 | 24.5 | 24.4 | 25 | 24.8 | 24.6
HOTS-STL1 | W | 57.2 |  | 0.97244 |  |  | 25.4 | 25.3 | 26.3 | 26.2 | 25.9 | 25.5
HOTS-STL2 | S | 25.7 |  | 0.98283 |  |  | 23.3 | 23.4 | 23.4 | 24 | 23.8 | 23.6
HOTS-STL2 | W | 34.9 |  | 0.99174 |  |  | 24.2 | 24.2 | 25.1 | 25.1 | 24.8 | 24.5
STL-ART | S | 38.3 |  | 0.97887 |  |  | 14.2 | 13.8 | 14.4 | 14.6 | 14.4 | 14.3
STL-ART | W | 43.4 |  | 0.98529 |  |  | 13.6 | 13.6 | 14.4 | 14.4 | 13.8 | 13.7
HOTS-HSM1 | S | 49.2 |  | 0.98551 |  |  | 41.4 | 41.3 | 44.7 | 46.8 | 46.2 | 45.7
HOTS-HSM1 | W | 52.6 |  | 0.98799 |  |  | 33.3 | 35 | 38.7 | 38.9 | 38.2 | 37.7
HOTS-HSM2 | S | 49.2 |  | 0.98551 |  |  | 41.4 | 41.3 | 44.6 | 46.8 | 46.2 | 45.7
HOTS-HSM2 | W | 52.6 |  | 0.98799 |  |  | 33.3 | 34.9 | 38.7 | 38.8 | 38.1 | 37.7
HOTS-KWF | S | 44 |  | 0.77333 |  |  | 15 | 14.8 | 16.1 | 17.5 | 17.1 | 16.8
HOTS-KWF | W | 43.4 |  | 0.77778 |  |  | 11.7 | 12.1 | 14.3 | 14.3 | 13.9 | 13.4
KWF-NHL | S | 44 |  | 1 |  |  | 10.3 | 10.2 | 11 | 11.8 | 11.6 | 11.4
KWF-NHL | W | 43.4 |  | 1 |  |  | 8.4 | 8.6 | 10 | 10 | 9.8 | 9.5
HOTS-CHM | S | 26.2 |  | 0.8 |  |  | 2.5 | 2.4 | 2.4 | 2.4 | 2.4 | 2.3
HOTS-CHM | W | 35.4 |  | 0.75 |  |  | 2.4 | 2.3 | 2.3 | 2.3 | 2.3 | 2.2
KTS 66kV
SBY-GSB1 | S | 51.4 |  | 0.99351 |  |  | 46.2 | 46.7 | 50.5 | 52.8 | 52.7 | 52.9
SBY-GSB1 | W | 69.7 |  | 0.98844 |  |  | 51.9 | 53.6 | 58 | 58.3 | 57.8 | 57.4
SBY-GSB2 | S | 76.6 |  | 0.99132 |  |  | 46.1 | 46.6 | 50.4 | 52.7 | 52.6 | 52.8
SBY-GSB2 | W | 89.2 |  | 0.98263 |  |  | 51.8 | 53.5 | 57.9 | 58.2 | 57.7 | 57.3
GSB-WND1 | S | 109.7 |  | 1 |  |  | 24.4 | 24.7 | 26.5 | 27.8 | 27.7 | 27.9
GSB-WND1 | W | 114.3 |  | 0.99322 |  |  | 29.5 | 30.3 | 32.8 | 32.9 | 32.7 | 32.1
GSB-WND2 | S | 46.3 |  | 1 |  |  | 24.9 | 25.1 | 27 | 28.4 | 28.3 | 28.4
GSB-WND2 | W | 49.7 |  | 0.99667 |  |  | 30 | 30.9 | 33.5 | 33.6 | 33.4 | 33.2
KTS-SA1 | S | 116.6 |  | 0.9361 |  |  | 89.2 | 90.7 | 93.4 | 94 | 94.1 | 95
KTS-SA1 | W | 122.3 |  | 0.90896 |  |  | 68.1 | 70 | 71.3 | 71.7 | 71.5 | 71.8
KTS-SA2 | S | 108 |  | 0.93498 |  |  | 89.2 | 90.7 | 93.4 | 95 | 95 | 95.3
KTS-SA2 | W | 122.3 |  | 0.90616 |  |  | 68.2 | 70 | 71.3 | 71.7 | 71.6 | 71.8
KTS-SSE2 | S | 89.4 |  | 0.87286 |  |  | 81.8 | 84.6 | 86 | 88.7 | 87.5 | 86.8
KTS-SSE2 | W | 100.6 |  | 0.87642 |  |  | 70.4 | 71.4 | 74.1 | 74.4 | 73.4 | 73.1
KTS-SSE1 | S | 89.7 |  | 0.87042 |  |  | 81.8 | 84.6 | 86.3 | 88.7 | 87.6 | 86.8
KTS-SSE1 | W | 94.3 |  | 0.87358 |  |  | 70.4 | 71.4 | 74.1 | 74.4 | 73.4 | 73.1
KGTS 66kV
KGTS-CHA | S | 31.4 |  | 0.95706 |  |  | 16.3 | 16.2 | 16.6 | 16.9 | 16.7 | 16.1
KGTS-CHA | W | 43.4 |  | 0.96129 |  |  | 15.5 | 15.6 | 16.4 | 16.3 | 15.9 | 15.6
KGTS-SHL | S | 40 | 1 | 0.88842 |  |  | 47.5 | 47.6 | 52.2 | 58.2 | 57.4 | 55.9 | 19% | 14 | 52 | 198 | 170 | 125 | 5 | 19 | 56 | 49 | 38
KGTS-SHL | W | 49.7 | 1 | 0.91281 |  |  | 36.7 | 37 | 43 | 43.9 | 43.2 | 42.4
KGTS-GSF | S | 48.6 |  | 0.89381 |  |  | 45.2 | 45.2 | 48.6 | 52.5 | 52.1 | 51.3
KGTS-GSF | W | 52.6 |  | 0.91768 |  |  | 32.8 | 33.6 | 40 | 41.4 | 40.1 | 39.4
GSF-SHL | S | 76.6 |  | 0.9108 |  |  | 42.6 | 42.5 | 45.5 | 48.8 | 48.4 | 47.9
GSF-SHL | W | 89.2 |  | 0.93016 |  |  | 31.5 | 32.3 | 37.8 | 39.2 | 38 | 37.5
RCTS 66kV
RCTS-MBN | S | 97.2 |  | 0.92403 |  |  | 56.6 | 57.9 | 60.8 | 63.2 | 62.8 | 63.4
RCTS-MBN | W | 114.3 |  | 0.93953 |  |  | 43 | 43.7 | 48.3 | 48.8 | 48.5 | 47.9
MBN-DTN | S | 74.3 |  | 0.92784 |  |  | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1
MBN-DTN | W | 86.9 |  | 0.94245 |  |  | 27.8 | 27.9 | 27.8 | 27.8 | 27.8 | 27.8
MDA-MBN | S | 74.3 |  | 0.9484 |  |  | 56.2 | 57.9 | 62.3 | 66.3 | 65.6 | 65.6
MDA-MBN | W | 86.9 |  | 0.95804 |  |  | 42.9 | 44.6 | 50.6 | 51.7 | 51 | 50.2
MDA-BNG | S | 104 |  | 0.93987 |  |  | 44.9 | 45.9 | 48.5 | 50.3 | 50.3 | 50.3
MDA-BNG | W | 114.3 |  | 0.96078 |  |  | 35.7 | 36.6 | 39.7 | 40.2 | 39.8 | 39.7
RCTS-MDA1 | S | 72 | 1 | 0.92374 |  |  | 93.1 | 94.9 | 98.6 | 101.9 | 101.2 | 102 | 31.81% | 261 | 444 | 659 | 609 | 666 | 49 | 71 | 92 | 87 | 92
RCTS-MDA1 | W | 90.9 | 2 | 0.93785 |  |  | 70.8 | 71.5 | 78 | 78.7 | 78.3 | 77.3
RCTS-MDA2 | S | 104 |  | 0.93514 |  |  | 103.3 | 104.3 | 107.5 | 111.6 | 110.3 | 110.4
RCTS-MDA2 | W | 114.3 |  | 0.94622 |  |  | 78.1 | 78.5 | 85.3 | 86.1 | 85.3 | 84.7
RCTS-YSF | S | 84.6 |  | 0.99329 |  |  | 14.9 | 14.7 | 14.6 | 14.6 | 14.4 | 14.2
RCTS-YSF | W | 106.3 |  | 1 |  |  | 13.4 | 13.3 | 13.3 | 13.1 | 13 | 12.8
YSF-HTH | S | 17.7 |  | 0.9932 |  |  | 14.7 | 14.5 | 14.5 | 14.4 | 14.2 | 14.1
YSF-HTH | W | 35.4 |  | 1 |  |  | 13.2 | 13.2 | 13.1 | 12.9 | 12.8 | 12.6
RCTS-KSF | S | 84.6 |  | 0.94361 |  |  | 26.6 | 26.6 | 27 | 27.1 | 26.4 | 25.5
RCTS-KSF | W | 106.3 |  | 0.95102 |  |  | 24.5 | 24.4 | 25.2 | 24.9 | 24.1 | 23.4
KSF-RVL | S | 84.6 |  | 0.95367 |  |  | 25.9 | 25.9 | 26.3 | 26.4 | 25.8 | 24.9
KSF-RVL | W | 106.3 |  | 0.95816 |  |  | 23.9 | 23.8 | 24.5 | 24.3 | 23.6 | 22.8
RVL-BSP | S | 84.6 |  | 0.97826 |  |  | 23 | 22.9 | 23.1 | 23.3 | 22.7 | 22.4
RVL-BSP | W | 106.3 |  | 0.97788 |  |  | 22.6 | 22.4 | 23 | 22.8 | 22.1 | 21.7
BSP-BBD | S | 65.2 |  | 0.94375 |  |  | 32 | 32.6 | 34.6 | 34.8 | 33.6 | 32.7
BSP-BBD | W | 67.4 |  | 0.96552 |  |  | 23.2 | 24.3 | 25.5 | 25.3 | 24.6 | 23.8
SHTS 66kV
SHTS-KYM1 | S | 79.4 |  | 0.97495 |  |  | 47.9 | 49.1 | 52.5 | 56.1 | 55.5 | 54.7
SHTS-KYM1 | W | 90.3 |  | 0.9797 |  |  | 39.4 | 41.8 | 46.6 | 47 | 46.3 | 45.6
SHTS-KYM2 | S | 79.4 |  | 0.97727 |  |  | 48.4 | 49.7 | 52.4 | 56.7 | 56.2 | 55
SHTS-KYM2 | W | 90.3 |  | 0.97995 |  |  | 39.9 | 42.3 | 47.2 | 47.6 | 46.9 | 46.2
KYM-ECA1 | S | 45.7 |  | 0.99687 |  |  | 31.9 | 32 | 34.5 | 37.2 | 36.3 | 35.8
KYM-ECA1 | W | 52.6 |  | 0.99634 |  |  | 27.3 | 27.5 | 30.8 | 31.1 | 30.6 | 30.2
KYM-ECA2 | S | 45.7 |  | 0.99692 |  |  | 32.5 | 32.5 | 34.6 | 37.3 | 37 | 35.9
KYM-ECA2 | W | 53.2 |  | 1 |  |  | 27.3 | 28 | 31.4 | 31.7 | 30.6 | 30.3
SHP-KYM | S | 104 |  | 0.96916 |  |  | 22.7 | 22.6 | 24.3 | 26.9 | 26.6 | 26.7
SHP-KYM | W | 114.3 |  | 0.9641 |  |  | 19.5 | 19.5 | 23.8 | 23.9 | 23.6 | 22.9
SHTS-SHP | S | 101.7 |  | 0.9697 |  |  | 36.3 | 37 | 39.8 | 42.8 | 42.4 | 41.9
SHTS-SHP | W | 116 |  | 0.97342 |  |  | 30.1 | 31.6 | 35.9 | 36.2 | 35.7 | 35.1
SHTS-MNA | S | 88 |  | 0.99241 |  |  | 79 | 78.8 | 80.1 | 81.8 | 81.4 | 80.7
SHTS-MNA | W | 114.4 |  | 0.99467 |  |  | 56.3 | 56.7 | 58.4 | 58.5 | 57.6 | 57.1
STN-MNA | S | 48.6 |  | 0.99511 |  |  | 40.9 | 40.5 | 41 | 42.2 | 41.9 | 41.4
STN-MNA | W | 52.6 |  | 0.99659 |  |  | 29.3 | 29 | 30 | 30.2 | 29.8 | 29.4
SHTS-STN | S | 91.4 |  | 0.99615 |  |  | 78 | 77.8 | 79.1 | 80.7 | 79.7 | 79.1
SHTS-STN | W | 91.4 |  | 0.99643 |  |  | 56.1 | 56.5 | 58.1 | 58.2 | 57.4 | 56.9
SHTS-NKA | S | 91.4 |  | 0.90336 |  |  | 74.5 | 76 | 81.8 | 91.8 | 90.1 | 89
SHTS-NKA | W | 91.4 |  | 0.94536 |  |  | 60.4 | 62.1 | 72.8 | 73.3 | 72.5 | 70.3
SHTS-NSF | S | 98.3 |  | 0.91896 |  |  | 72.8 | 72.9 | 78.8 | 85.8 | 84 | 83.3
SHTS-NSF | W | 114.3 |  | 0.94746 |  |  | 59 | 61.7 | 70.6 | 72 | 70.3 | 69.3
NSF-NKA | S | 102.9 |  | 0.95407 |  |  | 67.5 | 67.4 | 72.1 | 76.9 | 75.9 | 75.5
NSF-NKA | W | 114.3 |  | 0.97138 |  |  | 55.9 | 58.2 | 65.9 | 66.9 | 65.6 | 64.5
NKA-CME | S | 74.3 |  | 0.95845 |  |  | 36.1 | 36.4 | 38.5 | 43.1 | 42.3 | 41.9
NKA-CME | W | 86.9 |  | 0.98973 |  |  | 29.2 | 30.3 | 35.2 | 35.7 | 35.3 | 34.3
SHTS-SHN1 | S | 88 |  | 1 |  |  | 32.9 | 33.5 | 34.6 | 35.7 | 35.6 | 35.8
SHTS-SHN1 | W | 112 |  | 1 |  |  | 26 | 26.2 | 28.4 | 28.6 | 28.4 | 28.3
SHTS-SHN2 | S | 88 |  | 1 |  |  | 32.9 | 33.5 | 34.6 | 35.7 | 35.6 | 35.8
SHTS-SHN2 | W | 112 |  | 1 |  |  | 26 | 26.2 | 28.4 | 28.6 | 28.4 | 28.3
TGTS 66kV
TGTS-CDN | S | 76.6 |  | 0.99754 |  |  | 40.7 | 40.6 | 40.9 | 42.1 | 41.3 | 40.2
TGTS-CDN | W | 85.7 |  | 0.99752 |  |  | 40.4 | 40.4 | 42.6 | 42.3 | 41.5 | 40.6
COB-CDN | S | 49.2 |  | 1 |  |  | 22.1 | 22.3 | 21.6 | 22.1 | 21.6 | 21.4
COB-CDN | W | 57.2 |  | 1 |  |  | 22.6 | 22.1 | 22.6 | 22.8 | 22.4 | 22.1
CDN-CLC | S | 74.3 |  | 0.98588 |  |  | 35.4 | 35.5 | 36 | 37 | 36.2 | 35.4
CDN-CLC | W | 86.9 |  | 0.97965 |  |  | 34.4 | 34.5 | 36.2 | 36.1 | 35.3 | 34.8
TGTS-COB | S | 109.7 |  | 0.9831 |  |  | 35.5 | 35.6 | 35.2 | 36.5 | 35.5 | 35
TGTS-COB | W | 116 |  | 0.98592 |  |  | 35.5 | 35 | 36.3 | 36.7 | 35.7 | 35.3
TGTS-HTN | S | 47.4 |  | 0.91268 |  |  | 35.5 | 34.9 | 34.9 | 36.4 | 35.5 | 34.6
TGTS-HTN | W | 48 |  | 0.92082 |  |  | 34.1 | 33.9 | 35.5 | 35.8 | 34.8 | 33.9
NRB-HTN | S | 52.6 |  | 0.95185 |  |  | 27 | 26.8 | 26.7 | 27.5 | 27.1 | 26.5
NRB-HTN | W | 53.2 |  | 0.95437 |  |  | 26.3 | 26.1 | 27 | 27.2 | 26.7 | 26.1
TGTS-NRB | S | 52.6 |  | 0.89516 |  |  | 37.2 | 36.4 | 36.4 | 38.5 | 37.2 | 36
TGTS-NRB | W | 52.6 |  | 0.90368 |  |  | 35.3 | 35 | 37.2 | 37.8 | 36.2 | 35.1
TGTS-KRT1 | S | 44 |  | 0.9881 |  |  | 33.6 | 33.6 | 34.4 | 36.1 | 35.4 | 34.6
TGTS-KRT1 | W | 44.6 |  | 0.98841 |  |  | 34.5 | 34.8 | 37 | 37.2 | 36.4 | 36
TGTS-KRT2 | S | 97.2 |  | 0.8971 |  |  | 37.9 | 37.9 | 39.5 | 41.2 | 40.6 | 39.7
TGTS-KRT2 | W | 116 |  | 0.88325 |  |  | 39.4 | 39.8 | 42.8 | 43 | 41.9 | 41
KRT-PLD1/CWF | S | 40 |  | 0.99432 |  |  | 17.6 | 17.5 | 17.5 | 17.9 | 17.5 | 17.4
KRT-PLD1/CWF | W | 45.7 |  | 1 |  |  | 19.9 | 19.9 | 20 | 20.3 | 19.8 | 19.6
KRT-PLD2/YWF | S | 29.7 |  | 1 |  |  | 18.4 | 18.2 | 18.2 | 18.7 | 18.5 | 18.2
KRT-PLD2/YWF | W | 29.7 |  | 1 |  |  | 20.9 | 20.8 | 21.7 | 21.7 | 20.9 | 20.5
KRT-WBL | S | 46.9 |  | 0.83117 |  |  | 23.1 | 23.3 | 24.6 | 25.6 | 25.3 | 25
KRT-WBL | W | 47.4 |  | 0.8216 |  |  | 21.3 | 21.7 | 23.9 | 24.2 | 24 | 23.2
TRG-WBL1 | S | 47.4 |  | 0.96053 |  |  | 38 | 38.1 | 39.2 | 41 | 40.3 | 39.4
TRG-WBL1 | W | 49.7 |  | 0.95855 |  |  | 38.6 | 39 | 41.6 | 41.8 | 41 | 40.5
TRG-WBL2 | S | 45.7 |  | 0.99396 |  |  | 33.1 | 33.2 | 34.7 | 36.3 | 35.8 | 35
TRG-WBL2 | W | 46.3 |  | 0.98827 |  |  | 34.1 | 34.5 | 37.3 | 37.4 | 36.6 | 35.7
TGTS-TRG1 | S | 91.5 |  | 0.9862 |  |  | 65.2 | 65.1 | 67 | 69.5 | 68.1 | 66.7
TGTS-TRG1 | W | 91.5 |  | 0.98551 |  |  | 69 | 69.5 | 72.6 | 73.1 | 70.9 | 69.9
TGTS-TRG2 | S | 91.5 |  | 0.9862 |  |  | 65.2 | 65.2 | 67 | 69.5 | 68.1 | 66.7
TGTS-TRG2 | W | 91.5 |  | 0.98551 |  |  | 69 | 69.5 | 72.7 | 73.1 | 70.9 | 69.9
WETS 66kV
WETS-BPA | S | 31.4 |  | 0.98592 |  |  | 14.2 | 14.1 | 14.1 | 14 | 13.8 | 13.7
WETS-BPA | W | 43.4 |  | 0.99219 |  |  | 12.8 | 12.7 | 12.7 | 12.6 | 12.4 | 12.2
BPA-HTH | S | 17.7 |  | 0.90123 |  |  | 8.1 | 8 | 7.9 | 7.9 | 7.7 | 7.6
BPA-HTH | W | 35.4 |  | 0.95775 |  |  | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1
HTH-OYN | S | 17.7 |  | 0.89873 |  |  | 7.9 | 7.8 | 7.8 | 7.7 | 7.5 | 7.4
HTH-OYN | W | 35.4 |  | 0.87879 |  |  | 6.6 | 6.6 | 6.5 | 6.4 | 6.2 | 6
WETS-WSF | S | 84.6 |  | 0.99588 |  |  | 24.3 | 24.5 | 25.6 | 25.7 | 25 | 24
WETS-WSF | W | 106.3 |  | 1 |  |  | 17.6 | 18.1 | 19 | 18.8 | 18.3 | 17.8
WSF-WMN | S | 31.4 |  | 1 |  |  | 24.2 | 24.5 | 25.6 | 25.6 | 25 | 24
WSF-WMN | W | 43.4 |  | 1 |  |  | 17.5 | 18.1 | 18.9 | 18.8 | 18.3 | 17.8
WETS-BSP | S | 84.6 |  | 0.87781 |  |  | 62.2 | 62.6 | 65.5 | 65.8 | 63.7 | 61.9
WETS-BSP | W | 106.3 |  | 0.93 |  |  | 50 | 51.2 | 53.8 | 53.2 | 51.4 | 49.7