## BAS031
Distribution Feeder load limitation - Ballarat South 033 (BAS033)
Year
Field Name | Data | 2024 | 2025 | 2026 | 2027 | 2028
Asset Description | BAS033
Asset Code | BAS033
Constraint primary driver | Capacity
Location of constraint (start) | -37.574900, 143.827767
Location of constraint (end) | -37.574900, 143.827767
Asset ID | 177751170
Network Element | Feeder
Residential customers affected (No.) | 5953
Residential customers affected (% of total Customers) | 86.09%
Asset Rating (MVA) | Summer N-1 Rating | 11.3 | 11.3 | 11.3 | 11.3 | 11.3
Asset Rating (MW) | Summer N-1 Rating | N/A | N/A | N/A | N/A | N/A
Forecast Demand (MVA) | 10% POE Summer | 12.9422 | 13.1828 | 13.3529 | 13.764 | 14.0146
| 50% POE Summer | 11.2201 | 11.4302 | 11.6103 | 11.9807 | 12.3012
Forecast Demand (MW) | 10% POE Summer | 12.94 | 13.18 | 13.35 | 13.76 | 14.01
| 50% POE Summer | 11.22 | 11.43 | 11.61 | 11.98 | 12.3
Voltage level (kV) | 22
Maximum Load at risk (MVA) N-1 50% PoE |  | -0.079888 | 0.13021 | 0.31035 | 0.6807 | 1.0012
Energy at risk (MWh) N-1 50% PoE |  | 0 | 1 | 1 | 1 | 1
Preferred network investment | Construction of new BAS031 feeder
Preferred network investment capital cost ($) | 1890000
Preferred annual network investment operating cost ($) | 189000
Preferred network investment cost accuracy | +20%
Preferred network investment cost accuracy | -20%
Proposed timing | 2024
Demand reduction required to defer investment by 1 year (MVA) | 12.3012
Demand reduction required to defer investment by 1 year (MW) | 12.3
Annual Deferral Value | 68607
Load transfer capability (MVA) | -
Load transfer capability (MW) | -
Emergency generation (MVA) | 0
Emergency generation (MW) | 0
Date : Time | Historic load trace (MVA) | Historic asset rating (MVA) | Historic asset rating (MW) | Historic use of existing emergency response (MVA) | Historic use of existing emergency response (MW)
2020-07-08 12:00 | 0 | 0 | N/A | 0 | 0
2020-07-08 12:30 | 0 | 0 | N/A | 0 | 0
2020-07-08 13:00 | 0 | 0 | N/A | 0 | 0
2020-07-08 13:30 | 0 | 0 | N/A | 0 | 0
2020-07-08 14:00 | 0 | 0 | N/A | 0 | 0
2020-07-08 14:30 | 0.76 | 0 | N/A | 0 | 0
2020-07-08 15:00 | 0 | 0 | N/A | 0 | 0
2020-07-08 15:30 | 0 | 0 | N/A | 0 | 0
2020-07-08 16:00 | 0 | 0 | N/A | 0 | 0
2020-07-08 16:30 | 0 | 0 | N/A | 0 | 0
2020-07-08 17:00 | 0 | 0 | N/A | 0 | 0
2020-07-08 17:30 | 0 | 0 | N/A | 0 | 0
2020-07-08 18:00 | 0 | 0 | N/A | 0 | 0
2020-07-08 18:30 | 0 | 0 | N/A | 0 | 0
2020-07-08 19:00 | 0 | 0 | N/A | 0 | 0
2020-07-08 19:30 | 0 | 0 | N/A | 0 | 0
2020-07-08 20:00 | 0 | 0 | N/A | 0 | 0
2020-07-08 20:30 | 0 | 0 | N/A | 0 | 0
2020-07-08 21:00 | 0 | 0 | N/A | 0 | 0
2020-07-08 21:30 | 0 | 0 | N/A | 0 | 0
2020-07-08 22:00 | 0 | 0 | N/A | 0 | 0
2020-07-08 22:30 | 0 | 0 | N/A | 0 | 0
2020-07-08 23:00 | 0 | 0 | N/A | 0 | 0
2020-07-08 23:30 | 0 | 0 | N/A | 0 | 0
2020-07-09 | 0 | 0 | N/A | 0 | 0
2020-07-09 00:30 | 0 | 0 | N/A | 0 | 0
2020-07-09 01:00 | 0 | 0 | N/A | 0 | 0
2020-07-09 01:30 | 0 | 0 | N/A | 0 | 0
2020-07-09 02:00 | 0 | 0 | N/A | 0 | 0
2020-07-09 02:30 | 0 | 0 | N/A | 0 | 0
2020-07-09 03:00 | 0 | 0 | N/A | 0 | 0
2020-07-09 03:30 | 0 | 0 | N/A | 0 | 0
2020-07-09 04:00 | 0 | 0 | N/A | 0 | 0
2020-07-09 04:30 | 0 | 0 | N/A | 0 | 0
2020-07-09 05:00 | 0 | 0 | N/A | 0 | 0
2020-07-09 05:30 | 0 | 0 | N/A | 0 | 0
2020-07-09 06:00 | 0 | 0 | N/A | 0 | 0
2020-07-09 06:30 | 0 | 0 | N/A | 0 | 0
2020-07-09 07:00 | 0 | 0 | N/A | 0 | 0
2020-07-09 07:30 | 0 | 0 | N/A | 0 | 0
2020-07-09 08:00 | 0 | 0 | N/A | 0 | 0
2020-07-09 08:30 | 0 | 0 | N/A | 0 | 0
2020-07-09 09:00 | 0 | 0 | N/A | 0 | 0
2020-07-09 09:30 | 0 | 0 | N/A | 0 | 0
2020-07-09 10:00 | 0 | 0 | N/A | 0 | 0
2020-07-09 10:30 | 0 | 0 | N/A | 0 | 0
2020-07-09 11:00 | 0 | 0 | N/A | 0 | 0
2020-07-09 11:30 | 0 | 0 | N/A | 0 | 0
2020-07-09 12:00 | 0 | 0 | N/A | 0 | 0
2020-07-09 12:30 | 0 | 0 | N/A | 0 | 0
2020-07-09 13:00 | 0 | 0 | N/A | 0 | 0
2020-07-09 13:30 | 0 | 0 | N/A | 0 | 0
2020-07-09 14:00 | 0 | 0 | N/A | 0 | 0
2020-07-09 14:30 | 0 | 0 | N/A | 0 | 0
2020-07-09 15:00 | 0 | 0 | N/A | 0 | 0
2020-07-09 15:30 | 0 | 0 | N/A | 0 | 0
2020-07-09 16:00 | 0 | 0 | N/A | 0 | 0
2020-07-09 16:30 | 0 | 0 | N/A | 0 | 0
2020-07-09 17:00 | 0 | 0 | N/A | 0 | 0
2020-07-09 17:30 | 0 | 0 | N/A | 0 | 0
2020-07-09 18:00 | 0 | 0 | N/A | 0 | 0
2020-07-09 18:30 | 0 | 0 | N/A | 0 | 0
2020-07-09 19:00 | 0 | 0 | N/A | 0 | 0
2020-07-09 19:30 | 0 | 0 | N/A | 0 | 0
2020-07-09 20:00 | 0 | 0 | N/A | 0 | 0
2020-07-09 20:30 | 0 | 0 | N/A | 0 | 0
2020-07-09 21:00 | 0 | 0 | N/A | 0 | 0
2020-07-09 21:30 | 0 | 0 | N/A | 0 | 0
2020-07-09 22:00 | 0 | 0 | N/A | 0 | 0
2020-07-09 22:30 | 0 | 0 | N/A | 0 | 0
2020-07-09 23:00 | 0 | 0 | N/A | 0 | 0
2020-07-09 23:30 | 0 | 0 | N/A | 0 | 0
2020-07-10 | 0 | 0 | N/A | 0 | 0
2020-07-10 00:30 | 0 | 0 | N/A | 0 | 0
2020-07-10 01:00 | 0 | 0 | N/A | 0 | 0
2020-07-10 01:30 | 0 | 0 | N/A | 0 | 0
2020-07-10 02:00 | 0 | 0 | N/A | 0 | 0
2020-07-10 02:30 | 0 | 0 | N/A | 0 | 0
2020-07-10 03:00 | 0 | 0 | N/A | 0 | 0
2020-07-10 03:30 | 0 | 0 | N/A | 0 | 0
2020-07-10 04:00 | 0 | 0 | N/A | 0 | 0
2020-07-10 04:30 | 0 | 0 | N/A | 0 | 0
2020-07-10 05:00 | 0 | 0 | N/A | 0 | 0
2020-07-10 05:30 | 0 | 0 | N/A | 0 | 0
2020-07-10 06:00 | 0 | 0 | N/A | 0 | 0
2020-07-10 06:30 | 0 | 0 | N/A | 0 | 0
2020-07-10 07:00 | 0 | 0 | N/A | 0 | 0
2020-07-10 07:30 | 0 | 0 | N/A | 0 | 0
2020-07-10 08:00 | 0 | 0 | N/A | 0 | 0
2020-07-10 08:30 | 0 | 0 | N/A | 0 | 0
2020-07-10 09:00 | 0 | 0 | N/A | 0 | 0
2020-07-10 09:30 | 0 | 0 | N/A | 0 | 0
2020-07-10 10:00 | 0 | 0 | N/A | 0 | 0
2020-07-10 10:30 | 0 | 0 | N/A | 0 | 0
2020-07-10 11:00 | 0 | 0 | N/A | 0 | 0
2020-07-10 11:30 | 0 | 0 | N/A | 0 | 0
2020-07-10 12:00 | 0 | 0 | N/A | 0 | 0
2020-07-10 12:30 | 0 | 0 | N/A | 0 | 0
2020-07-10 13:00 | 0 | 0 | N/A | 0 | 0
2020-07-10 13:30 | 0 | 0 | N/A | 0 | 0
2020-07-10 14:00 | 0 | 0 | N/A | 0 | 0
2020-07-10 14:30 | 0 | 0 | N/A | 0 | 0
2020-07-10 15:00 | 0 | 0 | N/A | 0 | 0
2020-07-10 15:30 | 0 | 0 | N/A | 0 | 0
2020-07-10 16:00 | 0 | 0 | N/A | 0 | 0
2020-07-10 16:30 | 0 | 0 | N/A | 0 | 0
2020-07-10 17:00 | 0 | 0 | N/A | 0 | 0
2020-07-10 17:30 | 0 | 0 | N/A | 0 | 0
2020-07-10 18:00 | 0 | 0 | N/A | 0 | 0
2020-07-10 18:30 | 0 | 0 | N/A | 0 | 0
2020-07-10 19:00 | 0 | 0 | N/A | 0 | 0
2020-07-10 19:30 | 0 | 0 | N/A | 0 | 0
2020-07-10 20:00 | 0 | 0 | N/A | 0 | 0
2020-07-10 20:30 | 0 | 0 | N/A | 0 | 0
2020-07-10 21:00 | 0 | 0 | N/A | 0 | 0
2020-07-10 21:30 | 0 | 0 | N/A | 0 | 0
2020-07-10 22:00 | 0 | 0 | N/A | 0 | 0
2020-07-10 22:30 | 0 | 0 | N/A | 0 | 0
2020-07-10 23:00 | 0 | 0 | N/A | 0 | 0
2020-07-10 23:30 | 0 | 0 | N/A | 0 | 0
2020-07-11 | 0 | 0 | N/A | 0 | 0
2020-07-11 00:30 | 0 | 0 | N/A | 0 | 0
2020-07-11 01:00 | 0 | 0 | N/A | 0 | 0
2020-07-11 01:30 | 0 | 0 | N/A | 0 | 0
2020-07-11 02:00 | 0 | 0 | N/A | 0 | 0
2020-07-11 02:30 | 0 | 0 | N/A | 0 | 0
2020-07-11 03:00 | 0 | 0 | N/A | 0 | 0
2020-07-11 03:30 | 0 | 0 | N/A | 0 | 0
2020-07-11 04:00 | 0 | 0 | N/A | 0 | 0
2020-07-11 04:30 | 0 | 0 | N/A | 0 | 0
2020-07-11 05:00 | 0 | 0 | N/A | 0 | 0
2020-07-11 05:30 | 0 | 0 | N/A | 0 | 0
2020-07-11 06:00 | 0 | 0 | N/A | 0 | 0
2020-07-11 06:30 | 0 | 0 | N/A | 0 | 0
2020-07-11 07:00 | 0 | 0 | N/A | 0 | 0
2020-07-11 07:30 | 0 | 0 | N/A | 0 | 0
2020-07-11 08:00 | 0 | 0 | N/A | 0 | 0
2020-07-11 08:30 | 0 | 0 | N/A | 0 | 0
2020-07-11 09:00 | 0 | 0 | N/A | 0 | 0
2020-07-11 09:30 | 0 | 0 | N/A | 0 | 0
2020-07-11 10:00 | 0 | 0 | N/A | 0 | 0
2020-07-11 10:30 | 0 | 0 | N/A | 0 | 0
2020-07-11 11:00 | 0 | 0 | N/A | 0 | 0
2020-07-11 11:30 | 0 | 0 | N/A | 0 | 0
2020-07-11 12:00 | 0 | 0 | N/A | 0 | 0
2020-07-11 12:30 | 0 | 0 | N/A | 0 | 0
2020-07-11 13:00 | 0 | 0 | N/A | 0 | 0
2020-07-11 13:30 | 0 | 0 | N/A | 0 | 0
2020-07-11 14:00 | 0 | 0 | N/A | 0 | 0
2020-07-11 14:30 | 0 | 0 | N/A | 0 | 0
2020-07-11 15:00 | 0 | 0 | N/A | 0 | 0
2020-07-11 15:30 | 0 | 0 | N/A | 0 | 0
2020-07-11 16:00 | 0 | 0 | N/A | 0 | 0
2020-07-11 16:30 | 0 | 0 | N/A | 0 | 0
2020-07-11 17:00 | 0 | 0 | N/A | 0 | 0
2020-07-11 17:30 | 0 | 0 | N/A | 0 | 0
2020-07-11 18:00 | 0 | 0 | N/A | 0 | 0
2020-07-11 18:30 | 0 | 0 | N/A | 0 | 0
2020-07-11 19:00 | 0 | 0 | N/A | 0 | 0
2020-07-11 19:30 | 0 | 0 | N/A | 0 | 0
2020-07-11 20:00 | 0 | 0 | N/A | 0 | 0
2020-07-11 20:30 | 0 | 0 | N/A | 0 | 0
2020-07-11 21:00 | 0 | 0 | N/A | 0 | 0
2020-07-11 21:30 | 0 | 0 | N/A | 0 | 0
2020-07-11 22:00 | 0 | 0 | N/A | 0 | 0
2020-07-11 22:30 | 0 | 0 | N/A | 0 | 0
2020-07-11 23:00 | 0 | 0 | N/A | 0 | 0
2020-07-11 23:30 | 0 | 0 | N/A | 0 | 0
2020-07-12 | 0 | 0 | N/A | 0 | 0
2020-07-12 00:30 | 0 | 0 | N/A | 0 | 0
2020-07-12 01:00 | 0 | 0 | N/A | 0 | 0
2020-07-12 01:30 | 0 | 0 | N/A | 0 | 0
2020-07-12 02:00 | 0 | 0 | N/A | 0 | 0
2020-07-12 02:30 | 0 | 0 | N/A | 0 | 0
2020-07-12 03:00 | 0 | 0 | N/A | 0 | 0
2020-07-12 03:30 | 0 | 0 | N/A | 0 | 0
2020-07-12 04:00 | 0 | 0 | N/A | 0 | 0
2020-07-12 04:30 | 0 | 0 | N/A | 0 | 0
2020-07-12 05:00 | 0 | 0 | N/A | 0 | 0
2020-07-12 05:30 | 0 | 0 | N/A | 0 | 0
2020-07-12 06:00 | 0 | 0 | N/A | 0 | 0
2020-07-12 06:30 | 0 | 0 | N/A | 0 | 0
2020-07-12 07:00 | 0 | 0 | N/A | 0 | 0
2020-07-12 07:30 | 0 | 0 | N/A | 0 | 0
2020-07-12 08:00 | 0 | 0 | N/A | 0 | 0
2020-07-12 08:30 | 0 | 0 | N/A | 0 | 0
2020-07-12 09:00 | 0 | 0 | N/A | 0 | 0
2020-07-12 09:30 | 0 | 0 | N/A | 0 | 0
2020-07-12 10:00 | 0 | 0 | N/A | 0 | 0
2020-07-12 10:30 | 0 | 0 | N/A | 0 | 0
2020-07-12 11:00 | 0 | 0 | N/A | 0 | 0
2020-07-12 11:30 | 0 | 0 | N/A | 0 | 0
2020-07-12 12:00 | 0 | 0 | N/A | 0 | 0
2020-07-12 12:30 | 0 | 0 | N/A | 0 | 0
2020-07-12 13:00 | 0 | 0 | N/A | 0 | 0
2020-07-12 13:30 | 0 | 0 | N/A | 0 | 0
2020-07-12 14:00 | 0 | 0 | N/A | 0 | 0
2020-07-12 14:30 | 0 | 0 | N/A | 0 | 0
2020-07-12 15:00 | 0 | 0 | N/A | 0 | 0
2020-07-12 15:30 | 0 | 0 | N/A | 0 | 0
2020-07-12 16:00 | 0 | 0 | N/A | 0 | 0
2020-07-12 16:30 | 0 | 0 | N/A | 0 | 0
2020-07-12 17:00 | 0 | 0 | N/A | 0 | 0
2020-07-12 17:30 | 0 | 0 | N/A | 0 | 0
2020-07-12 18:00 | 0 | 0 | N/A | 0 | 0
2020-07-12 18:30 | 0 | 0 | N/A | 0 | 0
2020-07-12 19:00 | 0 | 0 | N/A | 0 | 0
2020-07-12 19:30 | 0 | 0 | N/A | 0 | 0
2020-07-12 20:00 | 0 | 0 | N/A | 0 | 0
2020-07-12 20:30 | 0 | 0 | N/A | 0 | 0
2020-07-12 21:00 | 0 | 0 | N/A | 0 | 0
2020-07-12 21:30 | 0 | 0 | N/A | 0 | 0
2020-07-12 22:00 | 0 | 0 | N/A | 0 | 0
2020-07-12 22:30 | 0 | 0 | N/A | 0 | 0
2020-07-12 23:00 | 0 | 0 | N/A | 0 | 0
2020-07-12 23:30 | 0 | 0 | N/A | 0 | 0
2020-07-13 | 0 | 0 | N/A | 0 | 0
2020-07-13 00:30 | 0 | 0 | N/A | 0 | 0
2020-07-13 01:00 | 0 | 0 | N/A | 0 | 0
2020-07-13 01:30 | 0 | 0 | N/A | 0 | 0
2020-07-13 02:00 | 0 | 0 | N/A | 0 | 0
2020-07-13 02:30 | 0 | 0 | N/A | 0 | 0
2020-07-13 03:00 | 0 | 0 | N/A | 0 | 0
2020-07-13 03:30 | 0 | 0 | N/A | 0 | 0
2020-07-13 04:00 | 0 | 0 | N/A | 0 | 0
2020-07-13 04:30 | 0 | 0 | N/A | 0 | 0
2020-07-13 05:00 | 0 | 0 | N/A | 0 | 0
2020-07-13 05:30 | 0 | 0 | N/A | 0 | 0
2020-07-13 06:00 | 0 | 0 | N/A | 0 | 0
2020-07-13 06:30 | 0 | 0 | N/A | 0 | 0
2020-07-13 07:00 | 0 | 0 | N/A | 0 | 0
2020-07-13 07:30 | 0 | 0 | N/A | 0 | 0
2020-07-13 08:00 | 0 | 0 | N/A | 0 | 0
2020-07-13 08:30 | 0 | 0 | N/A | 0 | 0
2020-07-13 09:00 | 0 | 0 | N/A | 0 | 0
2020-07-13 09:30 | 0 | 0 | N/A | 0 | 0
2020-07-13 10:00 | 0 | 0 | N/A | 0 | 0
2020-07-13 10:30 | 0 | 0 | N/A | 0 | 0
2020-07-13 11:00 | 0 | 0 | N/A | 0 | 0
2020-07-13 11:30 | 0 | 0 | N/A | 0 | 0
2020-07-13 12:00 | 0 | 0 | N/A | 0 | 0
2020-07-13 12:30 | 0 | 0 | N/A | 0 | 0
2020-07-13 13:00 | 0 | 0 | N/A | 0 | 0
2020-07-13 13:30 | 0 | 0 | N/A | 0 | 0
2020-07-13 14:00 | 0 | 0 | N/A | 0 | 0
2020-07-13 14:30 | 0 | 0 | N/A | 0 | 0
2020-07-13 15:00 | 0 | 0 | N/A | 0 | 0
2020-07-13 15:30 | 0 | 0 | N/A | 0 | 0
2020-07-13 16:00 | 0 | 0 | N/A | 0 | 0
2020-07-13 16:30 | 0 | 0 | N/A | 0 | 0
2020-07-13 17:00 | 0 | 0 | N/A | 0 | 0
2020-07-13 17:30 | 0 | 0 | N/A | 0 | 0
2020-07-13 18:00 | 0 | 0 | N/A | 0 | 0
2020-07-13 18:30 | 0 | 0 | N/A | 0 | 0
2020-07-13 19:00 | 0 | 0 | N/A | 0 | 0
2020-07-13 19:30 | 0 | 0 | N/A | 0 | 0
2020-07-13 20:00 | 0 | 0 | N/A | 0 | 0
2020-07-13 20:30 | 0 | 0 | N/A | 0 | 0
2020-07-13 21:00 | 0 | 0 | N/A | 0 | 0
2020-07-13 21:30 | 0 | 0 | N/A | 0 | 0
2020-07-13 22:00 | 0 | 0 | N/A | 0 | 0
2020-07-13 22:30 | 0 | 0 | N/A | 0 | 0
2020-07-13 23:00 | 0 | 0 | N/A | 0 | 0
2020-07-13 23:30 | 0 | 0 | N/A | 0 | 0
2020-07-14 | 0 | 0 | N/A | 0 | 0
2020-07-14 00:30 | 0 | 0 | N/A | 0 | 0
2020-07-14 01:00 | 0 | 0 | N/A | 0 | 0
2020-07-14 01:30 | 0 | 0 | N/A | 0 | 0
2020-07-14 02:00 | 0 | 0 | N/A | 0 | 0
2020-07-14 02:30 | 0 | 0 | N/A | 0 | 0
2020-07-14 03:00 | 0 | 0 | N/A | 0 | 0
2020-07-14 03:30 | 0 | 0 | N/A | 0 | 0
2020-07-14 04:00 | 0 | 0 | N/A | 0 | 0
2020-07-14 04:30 | 0 | 0 | N/A | 0 | 0
2020-07-14 05:00 | 0 | 0 | N/A | 0 | 0
2020-07-14 05:30 | 0 | 0 | N/A | 0 | 0
2020-07-14 06:00 | 0 | 0 | N/A | 0 | 0
2020-07-14 06:30 | 0 | 0 | N/A | 0 | 0
2020-07-14 07:00 | 0 | 0 | N/A | 0 | 0
2020-07-14 07:30 | 0 | 0 | N/A | 0 | 0
2020-07-14 08:00 | 0 | 0 | N/A | 0 | 0
2020-07-14 08:30 | 0 | 0 | N/A | 0 | 0
2020-07-14 09:00 | 0 | 0 | N/A | 0 | 0
2020-07-14 09:30 | 0 | 0 | N/A | 0 | 0
2020-07-14 10:00 | 0 | 0 | N/A | 0 | 0
2020-07-14 10:30 | 0 | 0 | N/A | 0 | 0
2020-07-14 11:00 | 0 | 0 | N/A | 0 | 0
2020-07-14 11:30 | 0 | 0 | N/A | 0 | 0
2020-07-14 12:00 | 0 | 0 | N/A | 0 | 0
2020-07-14 12:30 | 0 | 0 | N/A | 0 | 0
2020-07-14 13:00 | 0 | 0 | N/A | 0 | 0
2020-07-14 13:30 | 0 | 0 | N/A | 0 | 0
2020-07-14 14:00 | 0 | 0 | N/A | 0 | 0
2020-07-14 14:30 | 0 | 0 | N/A | 0 | 0
2020-07-14 15:00 | 0 | 0 | N/A | 0 | 0
2020-07-14 15:30 | 0 | 0 | N/A | 0 | 0
2020-07-14 16:00 | 0 | 0 | N/A | 0 | 0
2020-07-14 16:30 | 0 | 0 | N/A | 0 | 0
2020-07-14 17:00 | 0 | 0 | N/A | 0 | 0
2020-07-14 17:30 | 0 | 0 | N/A | 0 | 0
2020-07-14 18:00 | 0 | 0 | N/A | 0 | 0
2020-07-14 18:30 | 0 | 0 | N/A | 0 | 0
2020-07-14 19:00 | 0 | 0 | N/A | 0 | 0
2020-07-14 19:30 | 0 | 0 | N/A | 0 | 0
2020-07-14 20:00 | 0 | 0 | N/A | 0 | 0
2020-07-14 20:30 | 0 | 0 | N/A | 0 | 0
2020-07-14 21:00 | 0 | 0 | N/A | 0 | 0
2020-07-14 21:30 | 0 | 0 | N/A | 0 | 0
2020-07-14 22:00 | 0 | 0 | N/A | 0 | 0
2020-07-14 22:30 | 0 | 0 | N/A | 0 | 0
2020-07-14 23:00 | 0 | 0 | N/A | 0 | 0
2020-07-14 23:30 | 0 | 0 | N/A | 0 | 0
2020-07-15 | 0 | 0 | N/A | 0 | 0
2020-07-15 00:30 | 0 | 0 | N/A | 0 | 0
2020-07-15 01:00 | 0 | 0 | N/A | 0 | 0
2020-07-15 01:30 | 0 | 0 | N/A | 0 | 0
2020-07-15 02:00 | 0 | 0 | N/A | 0 | 0
2020-07-15 02:30 | 0 | 0 | N/A | 0 | 0
2020-07-15 03:00 | 0 | 0 | N/A | 0 | 0
2020-07-15 03:30 | 0 | 0 | N/A | 0 | 0
2020-07-15 04:00 | 0 | 0 | N/A | 0 | 0
2020-07-15 04:30 | 0 | 0 | N/A | 0 | 0
2020-07-15 05:00 | 0 | 0 | N/A | 0 | 0
2020-07-15 05:30 | 0 | 0 | N/A | 0 | 0
2020-07-15 06:00 | 0 | 0 | N/A | 0 | 0
2020-07-15 06:30 | 0 | 0 | N/A | 0 | 0
2020-07-15 07:00 | 0 | 0 | N/A | 0 | 0
2020-07-15 07:30 | 0 | 0 | N/A | 0 | 0
2020-07-15 08:00 | 0 | 0 | N/A | 0 | 0
2020-07-15 08:30 | 0 | 0 | N/A | 0 | 0
2020-07-15 09:00 | 0 | 0 | N/A | 0 | 0
2020-07-15 09:30 | 0 | 0 | N/A | 0 | 0
2020-07-15 10:00 | 0 | 0 | N/A | 0 | 0
2020-07-15 10:30 | 0 | 0 | N/A | 0 | 0
2020-07-15 11:00 | 0 | 0 | N/A | 0 | 0
2020-07-15 11:30 | 0 | 0 | N/A | 0 | 0
2020-07-15 12:00 | 0 | 0 | N/A | 0 | 0
2020-07-15 12:30 | 0 | 0 | N/A | 0 | 0
2020-07-15 13:00 | 0 | 0 | N/A | 0 | 0
2020-07-15 13:30 | 0 | 0 | N/A | 0 | 0
2020-07-15 14:00 | 0 | 0 | N/A | 0 | 0
2020-07-15 14:30 | 0 | 0 | N/A | 0 | 0
2020-07-15 15:00 | 0 | 0 | N/A | 0 | 0
2020-07-15 15:30 | 0 | 0 | N/A | 0 | 0
2020-07-15 16:00 | 0 | 0 | N/A | 0 | 0
2020-07-15 16:30 | 0 | 0 | N/A | 0 | 0
2020-07-15 17:00 | 0 | 0 | N/A | 0 | 0
2020-07-15 17:30 | 0 | 0 | N/A | 0 | 0
2020-07-15 18:00 | 0 | 0 | N/A | 0 | 0
2020-07-15 18:30 | 0 | 0 | N/A | 0 | 0
2020-07-15 19:00 | 0 | 0 | N/A | 0 | 0
2020-07-15 19:30 | 0 | 0 | N/A | 0 | 0
2020-07-15 20:00 | 0 | 0 | N/A | 0 | 0
2020-07-15 20:30 | 0 | 0 | N/A | 0 | 0
2020-07-15 21:00 | 0 | 0 | N/A | 0 | 0
2020-07-15 21:30 | 0 | 0 | N/A | 0 | 0
2020-07-15 22:00 | 0 | 0 | N/A | 0 | 0
2020-07-15 22:30 | 0 | 0 | N/A | 0 | 0
2020-07-15 23:00 | 0 | 0 | N/A | 0 | 0
2020-07-15 23:30 | 0 | 0 | N/A | 0 | 0
2020-07-16 | 0 | 0 | N/A | 0 | 0
2020-07-16 00:30 | 0 | 0 | N/A | 0 | 0
2020-07-16 01:00 | 0 | 0 | N/A | 0 | 0
2020-07-16 01:30 | 0 | 0 | N/A | 0 | 0
2020-07-16 02:00 | 0 | 0 | N/A | 0 | 0
2020-07-16 02:30 | 0 | 0 | N/A | 0 | 0
2020-07-16 03:00 | 0 | 0 | N/A | 0 | 0
2020-07-16 03:30 | 0 | 0 | N/A | 0 | 0
2020-07-16 04:00 | 0 | 0 | N/A | 0 | 0
2020-07-16 04:30 | 0 | 0 | N/A | 0 | 0
2020-07-16 05:00 | 0 | 0 | N/A | 0 | 0
2020-07-16 05:30 | 0 | 0 | N/A | 0 | 0
2020-07-16 06:00 | 0 | 0 | N/A | 0 | 0
2020-07-16 06:30 | 0 | 0 | N/A | 0 | 0
2020-07-16 07:00 | 0 | 0 | N/A | 0 | 0
2020-07-16 07:30 | 0 | 0 | N/A | 0 | 0
2020-07-16 08:00 | 0 | 0 | N/A | 0 | 0
2020-07-16 08:30 | 0 | 0 | N/A | 0 | 0
2020-07-16 09:00 | 0 | 0 | N/A | 0 | 0
2020-07-16 09:30 | 0 | 0 | N/A | 0 | 0
2020-07-16 10:00 | 0 | 0 | N/A | 0 | 0
2020-07-16 10:30 | 0 | 0 | N/A | 0 | 0
2020-07-16 11:00 | 0 | 0 | N/A | 0 | 0
2020-07-16 11:30 | 0 | 0 | N/A | 0 | 0
2020-07-16 12:00 | 0 | 0 | N/A | 0 | 0
2020-07-16 12:30 | 0 | 0 | N/A | 0 | 0
2020-07-16 13:00 | 0 | 0 | N/A | 0 | 0
2020-07-16 13:30 | 0 | 0 | N/A | 0 | 0
2020-07-16 14:00 | 0 | 0 | N/A | 0 | 0
2020-07-16 14:30 | 0 | 0 | N/A | 0 | 0
2020-07-16 15:00 | 0 | 0 | N/A | 0 | 0
2020-07-16 15:30 | 0 | 0 | N/A | 0 | 0
2020-07-16 16:00 | 0 | 0 | N/A | 0 | 0
2020-07-16 16:30 | 0 | 0 | N/A | 0 | 0
2020-07-16 17:00 | 0 | 0 | N/A | 0 | 0
2020-07-16 17:30 | 0 | 0 | N/A | 0 | 0
2020-07-16 18:00 | 0 | 0 | N/A | 0 | 0
2020-07-16 18:30 | 0 | 0 | N/A | 0 | 0
2020-07-16 19:00 | 0 | 0 | N/A | 0 | 0
2020-07-16 19:30 | 0 | 0 | N/A | 0 | 0
2020-07-16 20:00 | 0 | 0 | N/A | 0 | 0
2020-07-16 20:30 | 0 | 0 | N/A | 0 | 0
2020-07-16 21:00 | 0 | 0 | N/A | 0 | 0
2020-07-16 21:30 | 0 | 0 | N/A | 0 | 0
2020-07-16 22:00 | 0 | 0 | N/A | 0 | 0
2020-07-16 22:30 | 0 | 0 | N/A | 0 | 0
2020-07-16 23:00 | 0 | 0 | N/A | 0 | 0
2020-07-16 23:30 | 0 | 0 | N/A | 0 | 0
2020-07-17 | 0 | 0 | N/A | 0 | 0
2020-07-17 00:30 | 0 | 0 | N/A | 0 | 0
2020-07-17 01:00 | 0 | 0 | N/A | 0 | 0
2020-07-17 01:30 | 0 | 0 | N/A | 0 | 0
2020-07-17 02:00 | 0 | 0 | N/A | 0 | 0
2020-07-17 02:30 | 0 | 0 | N/A | 0 | 0
2020-07-17 03:00 | 0 | 0 | N/A | 0 | 0
2020-07-17 03:30 | 0 | 0 | N/A | 0 | 0
2020-07-17 04:00 | 0 | 0 | N/A | 0 | 0
2020-07-17 04:30 | 0 | 0 | N/A | 0 | 0
2020-07-17 05:00 | 0 | 0 | N/A | 0 | 0
2020-07-17 05:30 | 0 | 0 | N/A | 0 | 0
2020-07-17 06:00 | 0 | 0 | N/A | 0 | 0
2020-07-17 06:30 | 0 | 0 | N/A | 0 | 0
2020-07-17 07:00 | 0 | 0 | N/A | 0 | 0
2020-07-17 07:30 | 0 | 0 | N/A | 0 | 0
2020-07-17 08:00 | 0 | 0 | N/A | 0 | 0
2020-07-17 08:30 | 0 | 0 | N/A | 0 | 0
2020-07-17 09:00 | 0 | 0 | N/A | 0 | 0
2020-07-17 09:30 | 0 | 0 | N/A | 0 | 0
2020-07-17 10:00 | 0 | 0 | N/A | 0 | 0
2020-07-17 10:30 | 0 | 0 | N/A | 0 | 0
2020-07-17 11:00 | 0 | 0 | N/A | 0 | 0
2020-07-17 11:30 | 0 | 0 | N/A | 0 | 0
2020-07-17 12:00 | 0 | 0 | N/A | 0 | 0
2020-07-17 12:30 | 0 | 0 | N/A | 0 | 0
2020-07-17 13:00 | 0 | 0 | N/A | 0 | 0
2020-07-17 13:30 | 0 | 0 | N/A | 0 | 0
2020-07-17 14:00 | 0 | 0 | N/A | 0 | 0
2020-07-17 14:30 | 0 | 0 | N/A | 0 | 0
2020-07-17 15:00 | 0.025386 | 0 | N/A | 0 | 0
2020-07-17 15:30 | 0 | 0 | N/A | 0 | 0
2020-07-17 16:00 | 0 | 0 | N/A | 0 | 0
2020-07-17 16:30 | 0 | 0 | N/A | 0 | 0
2020-07-17 17:00 | 0 | 0 | N/A | 0 | 0
2020-07-17 17:30 | 0 | 0 | N/A | 0 | 0
2020-07-17 18:00 | 0 | 0 | N/A | 0 | 0
2020-07-17 18:30 | 0 | 0 | N/A | 0 | 0
2020-07-17 19:00 | 0 | 0 | N/A | 0 | 0
2020-07-17 19:30 | 0 | 0 | N/A | 0 | 0
2020-07-17 20:00 | 0 | 0 | N/A | 0 | 0
2020-07-17 20:30 | 0 | 0 | N/A | 0 | 0
2020-07-17 21:00 | 0 | 0 | N/A | 0 | 0
2020-07-17 21:30 | 0 | 0 | N/A | 0 | 0
2020-07-17 22:00 | 0 | 0 | N/A | 0 | 0
2020-07-17 22:30 | 0 | 0 | N/A | 0 | 0
2020-07-17 23:00 | 0 | 0 | N/A | 0 | 0
2020-07-17 23:30 | 0 | 0 | N/A | 0 | 0
2020-07-18 | 0 | 0 | N/A | 0 | 0
2020-07-18 00:30 | 0 | 0 | N/A | 0 | 0
2020-07-18 01:00 | 0 | 0 | N/A | 0 | 0
2020-07-18 01:30 | 0 | 0 | N/A | 0 | 0
2020-07-18 02:00 | 0 | 0 | N/A | 0 | 0
2020-07-18 02:30 | 0 | 0 | N/A | 0 | 0
2020-07-18 03:00 | 0 | 0 | N/A | 0 | 0
2020-07-18 03:30 | 0 | 0 | N/A | 0 | 0
2020-07-18 04:00 | 0 | 0 | N/A | 0 | 0
2020-07-18 04:30 | 0 | 0 | N/A | 0 | 0
2020-07-18 05:00 | 0 | 0 | N/A | 0 | 0
2020-07-18 05:30 | 0 | 0 | N/A | 0 | 0
2020-07-18 06:00 | 0 | 0 | N/A | 0 | 0
2020-07-18 06:30 | 0 | 0 | N/A | 0 | 0
2020-07-18 07:00 | 0 | 0 | N/A | 0 | 0
2020-07-18 07:30 | 0 | 0 | N/A | 0 | 0
2020-07-18 08:00 | 0 | 0 | N/A | 0 | 0
2020-07-18 08:30 | 0 | 0 | N/A | 0 | 0
2020-07-18 09:00 | 0 | 0 | N/A | 0 | 0
2020-07-18 09:30 | 0 | 0 | N/A | 0 | 0
2020-07-18 10:00 | 0 | 0 | N/A | 0 | 0
2020-07-18 10:30 | 0 | 0 | N/A | 0 | 0
2020-07-18 11:00 | 0 | 0 | N/A | 0 | 0
2020-07-18 11:30 | 0 | 0 | N/A | 0 | 0
2020-07-18 12:00 | 0 | 0 | N/A | 0 | 0
2020-07-18 12:30 | 0 | 0 | N/A | 0 | 0
2020-07-18 13:00 | 0 | 0 | N/A | 0 | 0
2020-07-18 13:30 | 0 | 0 | N/A | 0 | 0
2020-07-18 14:00 | 0 | 0 | N/A | 0 | 0
2020-07-18 14:30 | 0 | 0 | N/A | 0 | 0
2020-07-18 15:00 | 0 | 0 | N/A | 0 | 0
2020-07-18 15:30 | 0 | 0 | N/A | 0 | 0
2020-07-18 16:00 | 0 | 0 | N/A | 0 | 0
2020-07-18 16:30 | 0 | 0 | N/A | 0 | 0
2020-07-18 17:00 | 0 | 0 | N/A | 0 | 0
2020-07-18 17:30 | 0 | 0 | N/A | 0 | 0
2020-07-18 18:00 | 0 | 0 | N/A | 0 | 0
2020-07-18 18:30 | 0 | 0 | N/A | 0 | 0
2020-07-18 19:00 | 0 | 0 | N/A | 0 | 0
2020-07-18 19:30 | 0 | 0 | N/A | 0 | 0
2020-07-18 20:00 | 0 | 0 | N/A | 0 | 0
2020-07-18 20:30 | 0 | 0 | N/A | 0 | 0
2020-07-18 21:00 | 0 | 0 | N/A | 0 | 0
2020-07-18 21:30 | 0 | 0 | N/A | 0 | 0
2020-07-18 22:00 | 0 | 0 | N/A | 0 | 0
2020-07-18 22:30 | 0 | 0 | N/A | 0 | 0
2020-07-18 23:00 | 0 | 0 | N/A | 0 | 0
2020-07-18 23:30 | 0 | 0 | N/A | 0 | 0
2020-07-19 | 0 | 0 | N/A | 0 | 0
2020-07-19 00:30 | 0 | 0 | N/A | 0 | 0
2020-07-19 01:00 | 0 | 0 | N/A | 0 | 0
2020-07-19 01:30 | 0 | 0 | N/A | 0 | 0
2020-07-19 02:00 | 0 | 0 | N/A | 0 | 0
2020-07-19 02:30 | 0 | 0 | N/A | 0 | 0
2020-07-19 03:00 | 0 | 0 | N/A | 0 | 0
2020-07-19 03:30 | 0 | 0 | N/A | 0 | 0
2020-07-19 04:00 | 0 | 0 | N/A | 0 | 0
2020-07-19 04:30 | 0 | 0 | N/A | 0 | 0
2020-07-19 05:00 | 0 | 0 | N/A | 0 | 0
2020-07-19 05:30 | 0 | 0 | N/A | 0 | 0
2020-07-19 06:00 | 0 | 0 | N/A | 0 | 0
2020-07-19 06:30 | 0 | 0 | N/A | 0 | 0
2020-07-19 07:00 | 0 | 0 | N/A | 0 | 0
2020-07-19 07:30 | 0 | 0 | N/A | 0 | 0
2020-07-19 08:00 | 0 | 0 | N/A | 0 | 0
2020-07-19 08:30 | 0 | 0 | N/A | 0 | 0
2020-07-19 09:00 | 0 | 0 | N/A | 0 | 0
2020-07-19 09:30 | 0 | 0 | N/A | 0 | 0
2020-07-19 10:00 | 0 | 0 | N/A | 0 | 0
2020-07-19 10:30 | 0 | 0 | N/A | 0 | 0
2020-07-19 11:00 | 0 | 0 | N/A | 0 | 0
2020-07-19 11:30 | 0 | 0 | N/A | 0 | 0
2020-07-19 12:00 | 0 | 0 | N/A | 0 | 0
2020-07-19 12:30 | 0 | 0 | N/A | 0 | 0
2020-07-19 13:00 | 0 | 0 | N/A | 0 | 0
2020-07-19 13:30 | 0 | 0 | N/A | 0 | 0
2020-07-19 14:00 | 0 | 0 | N/A | 0 | 0
2020-07-19 14:30 | 0 | 0 | N/A | 0 | 0
2020-07-19 15:00 | 0 | 0 | N/A | 0 | 0
2020-07-19 15:30 | 0 | 0 | N/A | 0 | 0
2020-07-19 16:00 | 0 | 0 | N/A | 0 | 0
2020-07-19 16:30 | 0 | 0 | N/A | 0 | 0
2020-07-19 17:00 | 0 | 0 | N/A | 0 | 0
2020-07-19 17:30 | 0 | 0 | N/A | 0 | 0
2020-07-19 18:00 | 0 | 0 | N/A | 0 | 0
2020-07-19 18:30 | 0 | 0 | N/A | 0 | 0
2020-07-19 19:00 | 0 | 0 | N/A | 0 | 0
2020-07-19 19:30 | 0 | 0 | N/A | 0 | 0
2020-07-19 20:00 | 0 | 0 | N/A | 0 | 0
2020-07-19 20:30 | 0 | 0 | N/A | 0 | 0
2020-07-19 21:00 | 0 | 0 | N/A | 0 | 0
2020-07-19 21:30 | 0 | 0 | N/A | 0 | 0
2020-07-19 22:00 | 0 | 0 | N/A | 0 | 0
2020-07-19 22:30 | 0 | 0 | N/A | 0 | 0
2020-07-19 23:00 | 0 | 0 | N/A | 0 | 0
2020-07-19 23:30 | 0 | 0 | N/A | 0 | 0
2020-07-20 | 0 | 0 | N/A | 0 | 0
2020-07-20 00:30 | 0 | 0 | N/A | 0 | 0
2020-07-20 01:00 | 0 | 0 | N/A | 0 | 0
2020-07-20 01:30 | 0 | 0 | N/A | 0 | 0
2020-07-20 02:00 | 0 | 0 | N/A | 0 | 0
2020-07-20 02:30 | 0 | 0 | N/A | 0 | 0
2020-07-20 03:00 | 0 | 0 | N/A | 0 | 0
2020-07-20 03:30 | 0 | 0 | N/A | 0 | 0
2020-07-20 04:00 | 0 | 0 | N/A | 0 | 0
2020-07-20 04:30 | 0 | 0 | N/A | 0 | 0
2020-07-20 05:00 | 0 | 0 | N/A | 0 | 0
2020-07-20 05:30 | 0 | 0 | N/A | 0 | 0
2020-07-20 06:00 | 0 | 0 | N/A | 0 | 0
2020-07-20 06:30 | 0 | 0 | N/A | 0 | 0
2020-07-20 07:00 | 0 | 0 | N/A | 0 | 0
2020-07-20 07:30 | 0 | 0 | N/A | 0 | 0
2020-07-20 08:00 | 0 | 0 | N/A | 0 | 0
2020-07-20 08:30 | 0 | 0 | N/A | 0 | 0
2020-07-20 09:00 | 0 | 0 | N/A | 0 | 0
2020-07-20 09:30 | 0 | 0 | N/A | 0 | 0
2020-07-20 10:00 | 0 | 0 | N/A | 0 | 0
2020-07-20 10:30 | 0 | 0 | N/A | 0 | 0
2020-07-20 11:00 | 0 | 0 | N/A | 0 | 0
2020-07-20 11:30 | 0 | 0 | N/A | 0 | 0
2020-07-20 12:00 | 0 | 0 | N/A | 0 | 0
2020-07-20 12:30 | 0 | 0 | N/A | 0 | 0
2020-07-20 13:00 | 0 | 0 | N/A | 0 | 0
2020-07-20 13:30 | 0 | 0 | N/A | 0 | 0
2020-07-20 14:00 | 0 | 0 | N/A | 0 | 0
2020-07-20 14:30 | 0 | 0 | N/A | 0 | 0
2020-07-20 15:00 | 0 | 0 | N/A | 0 | 0
2020-07-20 15:30 | 0 | 0 | N/A | 0 | 0
2020-07-20 16:00 | 0 | 0 | N/A | 0 | 0
2020-07-20 16:30 | 0 | 0 | N/A | 0 | 0
2020-07-20 17:00 | 0 | 0 | N/A | 0 | 0
2020-07-20 17:30 | 0 | 0 | N/A | 0 | 0
2020-07-20 18:00 | 0 | 0 | N/A | 0 | 0
2020-07-20 18:30 | 0 | 0 | N/A | 0 | 0
2020-07-20 19:00 | 0 | 0 | N/A | 0 | 0
2020-07-20 19:30 | 0 | 0 | N/A | 0 | 0
2020-07-20 20:00 | 0 | 0 | N/A | 0 | 0
2020-07-20 20:30 | 0 | 0 | N/A | 0 | 0
2020-07-20 21:00 | 0 | 0 | N/A | 0 | 0
2020-07-20 21:30 | 0 | 0 | N/A | 0 | 0
2020-07-20 22:00 | 0 | 0 | N/A | 0 | 0
2020-07-20 22:30 | 0 | 0 | N/A | 0 | 0
2020-07-20 23:00 | 0 | 0 | N/A | 0 | 0
2020-07-20 23:30 | 0 | 0 | N/A | 0 | 0
2020-07-21 | 0 | 0 | N/A | 0 | 0
2020-07-21 00:30 | 0 | 0 | N/A | 0 | 0
2020-07-21 01:00 | 0 | 0 | N/A | 0 | 0
2020-07-21 01:30 | 0 | 0 | N/A | 0 | 0
2020-07-21 02:00 | 0 | 0 | N/A | 0 | 0
2020-07-21 02:30 | 0 | 0 | N/A | 0 | 0
2020-07-21 03:00 | 0 | 0 | N/A | 0 | 0
2020-07-21 03:30 | 0 | 0 | N/A | 0 | 0
2020-07-21 04:00 | 0 | 0 | N/A | 0 | 0
2020-07-21 04:30 | 0 | 0 | N/A | 0 | 0
2020-07-21 05:00 | 0 | 0 | N/A | 0 | 0
2020-07-21 05:30 | 0 | 0 | N/A | 0 | 0
2020-07-21 06:00 | 0 | 0 | N/A | 0 | 0
2020-07-21 06:30 | 0 | 0 | N/A | 0 | 0
2020-07-21 07:00 | 0 | 0 | N/A | 0 | 0
2020-07-21 07:30 | 0 | 0 | N/A | 0 | 0
2020-07-21 08:00 | 0 | 0 | N/A | 0 | 0
2020-07-21 08:30 | 0 | 0 | N/A | 0 | 0
2020-07-21 09:00 | 0 | 0 | N/A | 0 | 0
2020-07-21 09:30 | 0 | 0 | N/A | 0 | 0
2020-07-21 10:00 | 0 | 0 | N/A | 0 | 0
2020-07-21 10:30 | 0 | 0 | N/A | 0 | 0
2020-07-21 11:00 | 0 | 0 | N/A | 0 | 0
2020-07-21 11:30 | 0 | 0 | N/A | 0 | 0
2020-07-21 12:00 | 0 | 0 | N/A | 0 | 0
2020-07-21 12:30 | 0 | 0 | N/A | 0 | 0
2020-07-21 13:00 | 0 | 0 | N/A | 0 | 0
2020-07-21 13:30 | 0 | 0 | N/A | 0 | 0
2020-07-21 14:00 | 0 | 0 | N/A | 0 | 0
2020-07-21 14:30 | 0 | 0 | N/A | 0 | 0
2020-07-21 15:00 | 0 | 0 | N/A | 0 | 0
2020-07-21 15:30 | 0 | 0 | N/A | 0 | 0
2020-07-21 16:00 | 0 | 0 | N/A | 0 | 0
2020-07-21 16:30 | 0 | 0 | N/A | 0 | 0
2020-07-21 17:00 | 0 | 0 | N/A | 0 | 0
2020-07-21 17:30 | 0 | 0 | N/A | 0 | 0
2020-07-21 18:00 | 0 | 0 | N/A | 0 | 0
2020-07-21 18:30 | 0 | 0 | N/A | 0 | 0
2020-07-21 19:00 | 0 | 0 | N/A | 0 | 0
2020-07-21 19:30 | 0 | 0 | N/A | 0 | 0
2020-07-21 20:00 | 0 | 0 | N/A | 0 | 0
2020-07-21 20:30 | 0 | 0 | N/A | 0 | 0
2020-07-21 21:00 | 0 | 0 | N/A | 0 | 0
2020-07-21 21:30 | 0 | 0 | N/A | 0 | 0
2020-07-21 22:00 | 0 | 0 | N/A | 0 | 0
2020-07-21 22:30 | 0 | 0 | N/A | 0 | 0
2020-07-21 23:00 | 0 | 0 | N/A | 0 | 0
2020-07-21 23:30 | 0 | 0 | N/A | 0 | 0
2020-07-22 | 0 | 0 | N/A | 0 | 0
2020-07-22 00:30 | 0 | 0 | N/A | 0 | 0
2020-07-22 01:00 | 0 | 0 | N/A | 0 | 0
2020-07-22 01:30 | 0 | 0 | N/A | 0 | 0
2020-07-22 02:00 | 0 | 0 | N/A | 0 | 0
2020-07-22 02:30 | 0 | 0 | N/A | 0 | 0
2020-07-22 03:00 | 0 | 0 | N/A | 0 | 0
2020-07-22 03:30 | 0 | 0 | N/A | 0 | 0
2020-07-22 04:00 | 0 | 0 | N/A | 0 | 0
2020-07-22 04:30 | 0 | 0 | N/A | 0 | 0
2020-07-22 05:00 | 0 | 0 | N/A | 0 | 0
2020-07-22 05:30 | 0 | 0 | N/A | 0 | 0
2020-07-22 06:00 | 0 | 0 | N/A | 0 | 0
2020-07-22 06:30 | 0 | 0 | N/A | 0 | 0
2020-07-22 07:00 | 0 | 0 | N/A | 0 | 0
2020-07-22 07:30 | 0 | 0 | N/A | 0 | 0
2020-07-22 08:00 | 0 | 0 | N/A | 0 | 0
2020-07-22 08:30 | 0 | 0 | N/A | 0 | 0
2020-07-22 09:00 | 0 | 0 | N/A | 0 | 0
2020-07-22 09:30 | 0 | 0 | N/A | 0 | 0
2020-07-22 10:00 | 0 | 0 | N/A | 0 | 0
2020-07-22 10:30 | 0 | 0 | N/A | 0 | 0
2020-07-22 11:00 | 0 | 0 | N/A | 0 | 0
2020-07-22 11:30 | 0 | 0 | N/A | 0 | 0
2020-07-22 12:00 | 0 | 0 | N/A | 0 | 0
2020-07-22 12:30 | 0 | 0 | N/A | 0 | 0
2020-07-22 13:00 | 0 | 0 | N/A | 0 | 0
2020-07-22 13:30 | 0 | 0 | N/A | 0 | 0
2020-07-22 14:00 | 0 | 0 | N/A | 0 | 0
2020-07-22 14:30 | 0 | 0 | N/A | 0 | 0
2020-07-22 15:00 | 0 | 0 | N/A | 0 | 0
2020-07-22 15:30 | 0 | 0 | N/A | 0 | 0
2020-07-22 16:00 | 0 | 0 | N/A | 0 | 0
2020-07-22 16:30 | 0 | 0 | N/A | 0 | 0
2020-07-22 17:00 | 0 | 0 | N/A | 0 | 0
2020-07-22 17:30 | 0 | 0 | N/A | 0 | 0
2020-07-22 18:00 | 0 | 0 | N/A | 0 | 0
2020-07-22 18:30 | 0 | 0 | N/A | 0 | 0
2020-07-22 19:00 | 0 | 0 | N/A | 0 | 0
2020-07-22 19:30 | 0 | 0 | N/A | 0 | 0
2020-07-22 20:00 | 0 | 0 | N/A | 0 | 0
2020-07-22 20:30 | 0 | 0 | N/A | 0 | 0
2020-07-22 21:00 | 0 | 0 | N/A | 0 | 0
2020-07-22 21:30 | 0 | 0 | N/A | 0 | 0
2020-07-22 22:00 | 0 | 0 | N/A | 0 | 0
2020-07-22 22:30 | 0 | 0 | N/A | 0 | 0
2020-07-22 23:00 | 0 | 0 | N/A | 0 | 0
2020-07-22 23:30 | 0 | 0 | N/A | 0 | 0
2020-07-23 | 0 | 0 | N/A | 0 | 0
2020-07-23 00:30 | 0 | 0 | N/A | 0 | 0
2020-07-23 01:00 | 0 | 0 | N/A | 0 | 0
2020-07-23 01:30 | 0 | 0 | N/A | 0 | 0
2020-07-23 02:00 | 0 | 0 | N/A | 0 | 0
2020-07-23 02:30 | 0 | 0 | N/A | 0 | 0
2020-07-23 03:00 | 0 | 0 | N/A | 0 | 0
2020-07-23 03:30 | 0 | 0 | N/A | 0 | 0
2020-07-23 04:00 | 0 | 0 | N/A | 0 | 0
2020-07-23 04:30 | 0 | 0 | N/A | 0 | 0
2020-07-23 05:00 | 0 | 0 | N/A | 0 | 0
2020-07-23 05:30 | 0 | 0 | N/A | 0 | 0
2020-07-23 06:00 | 0 | 0 | N/A | 0 | 0
2020-07-23 06:30 | 0 | 0 | N/A | 0 | 0
2020-07-23 07:00 | 0 | 0 | N/A | 0 | 0
2020-07-23 07:30 | 0 | 0 | N/A | 0 | 0
2020-07-23 08:00 | 0 | 0 | N/A | 0 | 0
2020-07-23 08:30 | 0 | 0 | N/A | 0 | 0
2020-07-23 09:00 | 0 | 0 | N/A | 0 | 0
2020-07-23 09:30 | 0 | 0 | N/A | 0 | 0
2020-07-23 10:00 | 0 | 0 | N/A | 0 | 0
2020-07-23 10:30 | 0 | 0 | N/A | 0 | 0
2020-07-23 11:00 | 0 | 0 | N/A | 0 | 0
2020-07-23 11:30 | 0 | 0 | N/A | 0 | 0
2020-07-23 12:00 | 0 | 0 | N/A | 0 | 0
2020-07-23 12:30 | 0 | 0 | N/A | 0 | 0
2020-07-23 13:00 | 0 | 0 | N/A | 0 | 0
2020-07-23 13:30 | 0 | 0 | N/A | 0 | 0
2020-07-23 14:00 | 0 | 0 | N/A | 0 | 0
2020-07-23 14:30 | 0 | 0 | N/A | 0 | 0
2020-07-23 15:00 | 0 | 0 | N/A | 0 | 0
2020-07-23 15:30 | 0 | 0 | N/A | 0 | 0
2020-07-23 16:00 | 0 | 0 | N/A | 0 | 0
2020-07-23 16:30 | 0 | 0 | N/A | 0 | 0
2020-07-23 17:00 | 0 | 0 | N/A | 0 | 0
2020-07-23 17:30 | 0 | 0 | N/A | 0 | 0
2020-07-23 18:00 | 0 | 0 | N/A | 0 | 0
2020-07-23 18:30 | 0 | 0 | N/A | 0 | 0
2020-07-23 19:00 | 0 | 0 | N/A | 0 | 0
2020-07-23 19:30 | 0 | 0 | N/A | 0 | 0
2020-07-23 20:00 | 0 | 0 | N/A | 0 | 0
2020-07-23 20:30 | 0 | 0 | N/A | 0 | 0
2020-07-23 21:00 | 0 | 0 | N/A | 0 | 0
2020-07-23 21:30 | 0 | 0 | N/A | 0 | 0
2020-07-23 22:00 | 0 | 0 | N/A | 0 | 0
2020-07-23 22:30 | 0 | 0 | N/A | 0 | 0
2020-07-23 23:00 | 0 | 0 | N/A | 0 | 0
2020-07-23 23:30 | 0 | 0 | N/A | 0 | 0
2020-07-24 | 0 | 0 | N/A | 0 | 0
2020-07-24 00:30 | 0 | 0 | N/A | 0 | 0
2020-07-24 01:00 | 0 | 0 | N/A | 0 | 0
2020-07-24 01:30 | 0 | 0 | N/A | 0 | 0
2020-07-24 02:00 | 0 | 0 | N/A | 0 | 0
2020-07-24 02:30 | 0 | 0 | N/A | 0 | 0
2020-07-24 03:00 | 0 | 0 | N/A | 0 | 0
2020-07-24 03:30 | 0 | 0 | N/A | 0 | 0
2020-07-24 04:00 | 0 | 0 | N/A | 0 | 0
2020-07-24 04:30 | 0 | 0 | N/A | 0 | 0
2020-07-24 05:00 | 0 | 0 | N/A | 0 | 0
2020-07-24 05:30 | 0 | 0 | N/A | 0 | 0
2020-07-24 06:00 | 0 | 0 | N/A | 0 | 0
2020-07-24 06:30 | 0 | 0 | N/A | 0 | 0
2020-07-24 07:00 | 0 | 0 | N/A | 0 | 0
2020-07-24 07:30 | 0 | 0 | N/A | 0 | 0
2020-07-24 08:00 | 0 | 0 | N/A | 0 | 0
2020-07-24 08:30 | 0 | 0 | N/A | 0 | 0
2020-07-24 09:00 | 0 | 0 | N/A | 0 | 0
2020-07-24 09:30 | 0 | 0 | N/A | 0 | 0
2020-07-24 10:00 | 0 | 0 | N/A | 0 | 0
2020-07-24 10:30 | 0 | 0 | N/A | 0 | 0
2020-07-24 11:00 | 0 | 0 | N/A | 0 | 0
2020-07-24 11:30 | 0 | 0 | N/A | 0 | 0
2020-07-24 12:00 | 0 | 0 | N/A | 0 | 0
2020-07-24 12:30 | 0 | 0 | N/A | 0 | 0
2020-07-24 13:00 | 0 | 0 | N/A | 0 | 0
2020-07-24 13:30 | 0 | 0 | N/A | 0 | 0
2020-07-24 14:00 | 0 | 0 | N/A | 0 | 0
2020-07-24 14:30 | 0 | 0 | N/A | 0 | 0
2020-07-24 15:00 | 0 | 0 | N/A | 0 | 0
2020-07-24 15:30 | 0 | 0 | N/A | 0 | 0
2020-07-24 16:00 | 0 | 0 | N/A | 0 | 0
2020-07-24 16:30 | 0 | 0 | N/A | 0 | 0
2020-07-24 17:00 | 0 | 0 | N/A | 0 | 0
2020-07-24 17:30 | 0 | 0 | N/A | 0 | 0
2020-07-24 18:00 | 0 | 0 | N/A | 0 | 0
2020-07-24 18:30 | 0 | 0 | N/A | 0 | 0
2020-07-24 19:00 | 0 | 0 | N/A | 0 | 0
2020-07-24 19:30 | 0 | 0 | N/A | 0 | 0
2020-07-24 20:00 | 0 | 0 | N/A | 0 | 0
2020-07-24 20:30 | 0 | 0 | N/A | 0 | 0
2020-07-24 21:00 | 0 | 0 | N/A | 0 | 0
2020-07-24 21:30 | 0 | 0 | N/A | 0 | 0
2020-07-24 22:00 | 0 | 0 | N/A | 0 | 0
2020-07-24 22:30 | 0 | 0 | N/A | 0 | 0
2020-07-24 23:00 | 0 | 0 | N/A | 0 | 0
2020-07-24 23:30 | 0 | 0 | N/A | 0 | 0
2020-07-25 | 0 | 0 | N/A | 0 | 0
2020-07-25 00:30 | 0 | 0 | N/A | 0 | 0
2020-07-25 01:00 | 0 | 0 | N/A | 0 | 0
2020-07-25 01:30 | 0 | 0 | N/A | 0 | 0
2020-07-25 02:00 | 0 | 0 | N/A | 0 | 0
2020-07-25 02:30 | 0 | 0 | N/A | 0 | 0
2020-07-25 03:00 | 0 | 0 | N/A | 0 | 0
2020-07-25 03:30 | 0 | 0 | N/A | 0 | 0
2020-07-25 04:00 | 0 | 0 | N/A | 0 | 0
2020-07-25 04:30 | 0 | 0 | N/A | 0 | 0
2020-07-25 05:00 | 0 | 0 | N/A | 0 | 0
2020-07-25 05:30 | 0 | 0 | N/A | 0 | 0
2020-07-25 06:00 | 0 | 0 | N/A | 0 | 0
2020-07-25 06:30 | 0 | 0 | N/A | 0 | 0
2020-07-25 07:00 | 0 | 0 | N/A | 0 | 0
2020-07-25 07:30 | 0 | 0 | N/A | 0 | 0
2020-07-25 08:00 | 0 | 0 | N/A | 0 | 0
2020-07-25 08:30 | 0 | 0 | N/A | 0 | 0
2020-07-25 09:00 | 0 | 0 | N/A | 0 | 0
2020-07-25 09:30 | 0 | 0 | N/A | 0 | 0
2020-07-25 10:00 | 0 | 0 | N/A | 0 | 0
2020-07-25 10:30 | 0 | 0 | N/A | 0 | 0
2020-07-25 11:00 | 0 | 0 | N/A | 0 | 0
2020-07-25 11:30 | 0 | 0 | N/A | 0 | 0
2020-07-25 12:00 | 0 | 0 | N/A | 0 | 0
2020-07-25 12:30 | 0 | 0 | N/A | 0 | 0
2020-07-25 13:00 | 0 | 0 | N/A | 0 | 0
2020-07-25 13:30 | 0 | 0 | N/A | 0 | 0
2020-07-25 14:00 | 0 | 0 | N/A | 0 | 0
2020-07-25 14:30 | 0 | 0 | N/A | 0 | 0
2020-07-25 15:00 | 0 | 0 | N/A | 0 | 0
2020-07-25 15:30 | 0 | 0 | N/A | 0 | 0
2020-07-25 16:00 | 0 | 0 | N/A | 0 | 0
2020-07-25 16:30 | 0 | 0 | N/A | 0 | 0
2020-07-25 17:00 | 0 | 0 | N/A | 0 | 0
2020-07-25 17:30 | 0 | 0 | N/A | 0 | 0
2020-07-25 18:00 | 0 | 0 | N/A | 0 | 0
2020-07-25 18:30 | 0 | 0 | N/A | 0 | 0
2020-07-25 19:00 | 0 | 0 | N/A | 0 | 0
2020-07-25 19:30 | 0 | 0 | N/A | 0 | 0
2020-07-25 20:00 | 0 | 0 | N/A | 0 | 0
2020-07-25 20:30 | 0 | 0 | N/A | 0 | 0
2020-07-25 21:00 | 0 | 0 | N/A | 0 | 0
2020-07-25 21:30 | 0 | 0 | N/A | 0 | 0
2020-07-25 22:00 | 0 | 0 | N/A | 0 | 0
2020-07-25 22:30 | 0 | 0 | N/A | 0 | 0
2020-07-25 23:00 | 0 | 0 | N/A | 0 | 0
2020-07-25 23:30 | 0 | 0 | N/A | 0 | 0
2020-07-26 | 0 | 0 | N/A | 0 | 0
2020-07-26 00:30 | 0 | 0 | N/A | 0 | 0
2020-07-26 01:00 | 0 | 0 | N/A | 0 | 0
2020-07-26 01:30 | 0 | 0 | N/A | 0 | 0
2020-07-26 02:00 | 0 | 0 | N/A | 0 | 0
2020-07-26 02:30 | 0 | 0 | N/A | 0 | 0
2020-07-26 03:00 | 0 | 0 | N/A | 0 | 0
2020-07-26 03:30 | 0 | 0 | N/A | 0 | 0
2020-07-26 04:00 | 0 | 0 | N/A | 0 | 0
2020-07-26 04:30 | 0 | 0 | N/A | 0 | 0
2020-07-26 05:00 | 0 | 0 | N/A | 0 | 0
2020-07-26 05:30 | 0 | 0 | N/A | 0 | 0
2020-07-26 06:00 | 0 | 0 | N/A | 0 | 0
2020-07-26 06:30 | 0 | 0 | N/A | 0 | 0
2020-07-26 07:00 | 0 | 0 | N/A | 0 | 0
2020-07-26 07:30 | 0 | 0 | N/A | 0 | 0
2020-07-26 08:00 | 0 | 0 | N/A | 0 | 0
2020-07-26 08:30 | 0 | 0 | N/A | 0 | 0
2020-07-26 09:00 | 0 | 0 | N/A | 0 | 0
2020-07-26 09:30 | 0 | 0 | N/A | 0 | 0
2020-07-26 10:00 | 0 | 0 | N/A | 0 | 0
2020-07-26 10:30 | 0 | 0 | N/A | 0 | 0
2020-07-26 11:00 | 0 | 0 | N/A | 0 | 0
2020-07-26 11:30 | 0 | 0 | N/A | 0 | 0
2020-07-26 12:00 | 0 | 0 | N/A | 0 | 0
2020-07-26 12:30 | 0 | 0 | N/A | 0 | 0
2020-07-26 13:00 | 0 | 0 | N/A | 0 | 0
2020-07-26 13:30 | 0 | 0 | N/A | 0 | 0
2020-07-26 14:00 | 0 | 0 | N/A | 0 | 0
2020-07-26 14:30 | 0 | 0 | N/A | 0 | 0
2020-07-26 15:00 | 0 | 0 | N/A | 0 | 0
2020-07-26 15:30 | 0 | 0 | N/A | 0 | 0
2020-07-26 16:00 | 0 | 0 | N/A | 0 | 0
2020-07-26 16:30 | 0 | 0 | N/A | 0 | 0
2020-07-26 17:00 | 0 | 0 | N/A | 0 | 0
2020-07-26 17:30 | 0 | 0 | N/A | 0 | 0
2020-07-26 18:00 | 0 | 0 | N/A | 0 | 0
2020-07-26 18:30 | 0 | 0 | N/A | 0 | 0
2020-07-26 19:00 | 0 | 0 | N/A | 0 | 0
2020-07-26 19:30 | 0 | 0 | N/A | 0 | 0
2020-07-26 20:00 | 0 | 0 | N/A | 0 | 0
2020-07-26 20:30 | 0 | 0 | N/A | 0 | 0
2020-07-26 21:00 | 0 | 0 | N/A | 0 | 0
2020-07-26 21:30 | 0 | 0 | N/A | 0 | 0
2020-07-26 22:00 | 0 | 0 | N/A | 0 | 0
2020-07-26 22:30 | 0 | 0 | N/A | 0 | 0
2020-07-26 23:00 | 0 | 0 | N/A | 0 | 0
2020-07-26 23:30 | 0 | 0 | N/A | 0 | 0
2020-07-27 | 0 | 0 | N/A | 0 | 0
2020-07-27 00:30 | 0 | 0 | N/A | 0 | 0
2020-07-27 01:00 | 0 | 0 | N/A | 0 | 0
2020-07-27 01:30 | 0 | 0 | N/A | 0 | 0
2020-07-27 02:00 | 0 | 0 | N/A | 0 | 0
2020-07-27 02:30 | 0 | 0 | N/A | 0 | 0
2020-07-27 03:00 | 0 | 0 | N/A | 0 | 0
2020-07-27 03:30 | 0 | 0 | N/A | 0 | 0
2020-07-27 04:00 | 0 | 0 | N/A | 0 | 0
2020-07-27 04:30 | 0 | 0 | N/A | 0 | 0
2020-07-27 05:00 | 0 | 0 | N/A | 0 | 0
2020-07-27 05:30 | 0 | 0 | N/A | 0 | 0
2020-07-27 06:00 | 0 | 0 | N/A | 0 | 0
2020-07-27 06:30 | 0 | 0 | N/A | 0 | 0
2020-07-27 07:00 | 0 | 0 | N/A | 0 | 0
2020-07-27 07:30 | 0 | 0 | N/A | 0 | 0
2020-07-27 08:00 | 0 | 0 | N/A | 0 | 0
2020-07-27 08:30 | 0 | 0 | N/A | 0 | 0
2020-07-27 09:00 | 0 | 0 | N/A | 0 | 0
2020-07-27 09:30 | 0 | 0 | N/A | 0 | 0
2020-07-27 10:00 | 0 | 0 | N/A | 0 | 0
2020-07-27 10:30 | 0 | 0 | N/A | 0 | 0
2020-07-27 11:00 | 0 | 0 | N/A | 0 | 0
2020-07-27 11:30 | 0 | 0 | N/A | 0 | 0
2020-07-27 12:00 | 0 | 0 | N/A | 0 | 0
2020-07-27 12:30 | 0 | 0 | N/A | 0 | 0
2020-07-27 13:00 | 0 | 0 | N/A | 0 | 0
2020-07-27 13:30 | 0 | 0 | N/A | 0 | 0
2020-07-27 14:00 | 0 | 0 | N/A | 0 | 0
2020-07-27 14:30 | 0 | 0 | N/A | 0 | 0
2020-07-27 15:00 | 0 | 0 | N/A | 0 | 0
2020-07-27 15:30 | 0 | 0 | N/A | 0 | 0
2020-07-27 16:00 | 0 | 0 | N/A | 0 | 0
2020-07-27 16:30 | 0 | 0 | N/A | 0 | 0
2020-07-27 17:00 | 0 | 0 | N/A | 0 | 0
2020-07-27 17:30 | 0 | 0 | N/A | 0 | 0
2020-07-27 18:00 | 0 | 0 | N/A | 0 | 0
2020-07-27 18:30 | 0 | 0 | N/A | 0 | 0
2020-07-27 19:00 | 0 | 0 | N/A | 0 | 0
2020-07-27 19:30 | 0 | 0 | N/A | 0 | 0
2020-07-27 20:00 | 0 | 0 | N/A | 0 | 0
2020-07-27 20:30 | 0 | 0 | N/A | 0 | 0
2020-07-27 21:00 | 0 | 0 | N/A | 0 | 0
2020-07-27 21:30 | 0 | 0 | N/A | 0 | 0
2020-07-27 22:00 | 0 | 0 | N/A | 0 | 0
2020-07-27 22:30 | 0 | 0 | N/A | 0 | 0
2020-07-27 23:00 | 0 | 0 | N/A | 0 | 0
2020-07-27 23:30 | 0 | 0 | N/A | 0 | 0
2020-07-28 | 0 | 0 | N/A | 0 | 0
2020-07-28 00:30 | 0 | 0 | N/A | 0 | 0
2020-07-28 01:00 | 0 | 0 | N/A | 0 | 0
2020-07-28 01:30 | 0 | 0 | N/A | 0 | 0
2020-07-28 02:00 | 0 | 0 | N/A | 0 | 0
2020-07-28 02:30 | 0 | 0 | N/A | 0 | 0
2020-07-28 03:00 | 0 | 0 | N/A | 0 | 0
2020-07-28 03:30 | 0 | 0 | N/A | 0 | 0
2020-07-28 04:00 | 0 | 0 | N/A | 0 | 0
2020-07-28 04:30 | 0 | 0 | N/A | 0 | 0
2020-07-28 05:00 | 0 | 0 | N/A | 0 | 0
2020-07-28 05:30 | 0 | 0 | N/A | 0 | 0
2020-07-28 06:00 | 0 | 0 | N/A | 0 | 0
2020-07-28 06:30 | 0 | 0 | N/A | 0 | 0
2020-07-28 07:00 | 0 | 0 | N/A | 0 | 0
2020-07-28 07:30 | 0 | 0 | N/A | 0 | 0
2020-07-28 08:00 | 0 | 0 | N/A | 0 | 0
2020-07-28 08:30 | 0 | 0 | N/A | 0 | 0
2020-07-28 09:00 | 0 | 0 | N/A | 0 | 0
2020-07-28 09:30 | 0 | 0 | N/A | 0 | 0
2020-07-28 10:00 | 0 | 0 | N/A | 0 | 0
2020-07-28 10:30 | 0 | 0 | N/A | 0 | 0
2020-07-28 11:00 | 0 | 0 | N/A | 0 | 0
2020-07-28 11:30 | 0 | 0 | N/A | 0 | 0
2020-07-28 12:00 | 0 | 0 | N/A | 0 | 0
2020-07-28 12:30 | 0 | 0 | N/A | 0 | 0
2020-07-28 13:00 | 0 | 0 | N/A | 0 | 0
2020-07-28 13:30 | 0 | 0 | N/A | 0 | 0
2020-07-28 14:00 | 0 | 0 | N/A | 0 | 0
2020-07-28 14:30 | 0 | 0 | N/A | 0 | 0
2020-07-28 15:00 | 0 | 0 | N/A | 0 | 0
2020-07-28 15:30 | 0 | 0 | N/A | 0 | 0
2020-07-28 16:00 | 0 | 0 | N/A | 0 | 0
2020-07-28 16:30 | 0 | 0 | N/A | 0 | 0
2020-07-28 17:00 | 0 | 0 | N/A | 0 | 0
2020-07-28 17:30 | 0 | 0 | N/A | 0 | 0
2020-07-28 18:00 | 0 | 0 | N/A | 0 | 0
2020-07-28 18:30 | 0 | 0 | N/A | 0 | 0
2020-07-28 19:00 | 0 | 0 | N/A | 0 | 0
2020-07-28 19:30 | 0 | 0 | N/A | 0 | 0
2020-07-28 20:00 | 0 | 0 | N/A | 0 | 0
2020-07-28 20:30 | 0 | 0 | N/A | 0 | 0
2020-07-28 21:00 | 0 | 0 | N/A | 0 | 0
2020-07-28 21:30 | 0 | 0 | N/A | 0 | 0
2020-07-28 22:00 | 0 | 0 | N/A | 0 | 0
2020-07-28 22:30 | 0 | 0 | N/A | 0 | 0
2020-07-28 23:00 | 0 | 0 | N/A | 0 | 0
2020-07-28 23:30 | 0 | 0 | N/A | 0 | 0
2020-07-29 | 0 | 0 | N/A | 0 | 0
2020-07-29 00:30 | 0 | 0 | N/A | 0 | 0
2020-07-29 01:00 | 0 | 0 | N/A | 0 | 0
2020-07-29 01:30 | 0 | 0 | N/A | 0 | 0
2020-07-29 02:00 | 0 | 0 | N/A | 0 | 0
2020-07-29 02:30 | 0 | 0 | N/A | 0 | 0
2020-07-29 03:00 | 0 | 0 | N/A | 0 | 0
2020-07-29 03:30 | 0 | 0 | N/A | 0 | 0
2020-07-29 04:00 | 0 | 0 | N/A | 0 | 0
2020-07-29 04:30 | 0 | 0 | N/A | 0 | 0
2020-07-29 05:00 | 0 | 0 | N/A | 0 | 0
2020-07-29 05:30 | 0 | 0 | N/A | 0 | 0
2020-07-29 06:00 | 0 | 0 | N/A | 0 | 0
2020-07-29 06:30 | 0 | 0 | N/A | 0 | 0
2020-07-29 07:00 | 0 | 0 | N/A | 0 | 0
2020-07-29 07:30 | 0 | 0 | N/A | 0 | 0
2020-07-29 08:00 | 0 | 0 | N/A | 0 | 0
2020-07-29 08:30 | 0 | 0 | N/A | 0 | 0
2020-07-29 09:00 | 0 | 0 | N/A | 0 | 0
2020-07-29 09:30 | 0 | 0 | N/A | 0 | 0
2020-07-29 10:00 | 0 | 0 | N/A | 0 | 0
2020-07-29 10:30 | 1.1311 | 0 | N/A | 0 | 0
2020-07-29 11:00 | 4.5049 | 0 | N/A | 0 | 0
2020-07-29 11:30 | 4.0837 | 0 | N/A | 0 | 0
2020-07-29 12:00 | 4.0339 | 0 | N/A | 0 | 0
2020-07-29 12:30 | 4.408 | 0 | N/A | 0 | 0
2020-07-29 13:00 | 2.8039 | 0 | N/A | 0 | 0
2020-07-29 13:30 | 3.0574 | 0 | N/A | 0 | 0
2020-07-29 14:00 | 3.1572 | 0 | N/A | 0 | 0
2020-07-29 14:30 | 3.4363 | 0 | N/A | 0 | 0
2020-07-29 15:00 | 3.8027 | 0 | N/A | 0 | 0
2020-07-29 15:30 | 3.7365 | 0 | N/A | 0 | 0
2020-07-29 16:00 | 4.0385 | 0 | N/A | 0 | 0
2020-07-29 16:30 | 5.0465 | 0 | N/A | 0 | 0
2020-07-29 17:00 | 6.4329 | 0 | N/A | 0 | 0
2020-07-29 17:30 | 7.6428 | 0 | N/A | 0 | 0
2020-07-29 18:00 | 8.5441 | 0 | N/A | 0 | 0
2020-07-29 18:30 | 9.0437 | 0 | N/A | 0 | 0
2020-07-29 19:00 | 8.7422 | 0 | N/A | 0 | 0
2020-07-29 19:30 | 8.3877 | 0 | N/A | 0 | 0
2020-07-29 20:00 | 8.1262 | 0 | N/A | 0 | 0
2020-07-29 20:30 | 7.7841 | 0 | N/A | 0 | 0
2020-07-29 21:00 | 7.2574 | 0 | N/A | 0 | 0
2020-07-29 21:30 | 7.5729 | 0 | N/A | 0 | 0
2020-07-29 22:00 | 7.5998 | 0 | N/A | 0 | 0
2020-07-29 22:30 | 7.195 | 0 | N/A | 0 | 0
2020-07-29 23:00 | 6.8996 | 0 | N/A | 0 | 0
2020-07-29 23:30 | 6.9724 | 0 | N/A | 0 | 0
2020-07-30 | 7.2767 | 0 | N/A | 0 | 0
2020-07-30 00:30 | 6.4501 | 0 | N/A | 0 | 0
2020-07-30 01:00 | 5.639 | 0 | N/A | 0 | 0
2020-07-30 01:30 | 5.5959 | 0 | N/A | 0 | 0
2020-07-30 02:00 | 5.245 | 0 | N/A | 0 | 0
2020-07-30 02:30 | 4.6485 | 0 | N/A | 0 | 0
2020-07-30 03:00 | 4.2607 | 0 | N/A | 0 | 0
2020-07-30 03:30 | 4.0248 | 0 | N/A | 0 | 0
2020-07-30 04:00 | 3.9065 | 0 | N/A | 0 | 0
2020-07-30 04:30 | 3.9487 | 0 | N/A | 0 | 0
2020-07-30 05:00 | 4.104 | 0 | N/A | 0 | 0
2020-07-30 05:30 | 4.4683 | 0 | N/A | 0 | 0
2020-07-30 06:00 | 4.8704 | 0 | N/A | 0 | 0
2020-07-30 06:30 | 5.7989 | 0 | N/A | 0 | 0
2020-07-30 07:00 | 6.6285 | 0 | N/A | 0 | 0
2020-07-30 07:30 | 7.0873 | 0 | N/A | 0 | 0
2020-07-30 08:00 | 7.9578 | 0 | N/A | 0 | 0
2020-07-30 08:30 | 8.1837 | 0 | N/A | 0 | 0
2020-07-30 09:00 | 7.8467 | 0 | N/A | 0 | 0
2020-07-30 09:30 | 7.4702 | 0 | N/A | 0 | 0
2020-07-30 10:00 | 6.3402 | 0 | N/A | 0 | 0
2020-07-30 10:30 | 5.3067 | 0 | N/A | 0 | 0
2020-07-30 11:00 | 4.7938 | 0 | N/A | 0 | 0
2020-07-30 11:30 | 4.2345 | 0 | N/A | 0 | 0
2020-07-30 12:00 | 4.1876 | 0 | N/A | 0 | 0
2020-07-30 12:30 | 4.3894 | 0 | N/A | 0 | 0
2020-07-30 13:00 | 4.1046 | 0 | N/A | 0 | 0
2020-07-30 13:30 | 3.9817 | 0 | N/A | 0 | 0
2020-07-30 14:00 | 4.3822 | 0 | N/A | 0 | 0
2020-07-30 14:30 | 4.7706 | 0 | N/A | 0 | 0
2020-07-30 15:00 | 4.721 | 0 | N/A | 0 | 0
2020-07-30 15:30 | 4.4404 | 0 | N/A | 0 | 0
2020-07-30 16:00 | 4.2611 | 0 | N/A | 0 | 0
2020-07-30 16:30 | 4.5576 | 0 | N/A | 0 | 0
2020-07-30 17:00 | 5.0139 | 0 | N/A | 0 | 0
2020-07-30 17:30 | 6.1762 | 0 | N/A | 0 | 0
2020-07-30 18:00 | 7.3943 | 0 | N/A | 0 | 0
2020-07-30 18:30 | 8.3785 | 0 | N/A | 0 | 0
2020-07-30 19:00 | 8.4516 | 0 | N/A | 0 | 0
2020-07-30 19:30 | 8.1471 | 0 | N/A | 0 | 0
2020-07-30 20:00 | 7.9474 | 0 | N/A | 0 | 0
2020-07-30 20:30 | 7.6061 | 0 | N/A | 0 | 0
2020-07-30 21:00 | 7.2929 | 0 | N/A | 0 | 0
2020-07-30 21:30 | 7.4536 | 0 | N/A | 0 | 0
2020-07-30 22:00 | 7.6094 | 0 | N/A | 0 | 0
2020-07-30 22:30 | 7.1016 | 0 | N/A | 0 | 0
2020-07-30 23:00 | 7.0482 | 0 | N/A | 0 | 0
2020-07-30 23:30 | 7.0158 | 0 | N/A | 0 | 0
2020-07-31 | 7.3019 | 0 | N/A | 0 | 0
2020-07-31 00:30 | 6.5466 | 0 | N/A | 0 | 0
2020-07-31 01:00 | 5.8707 | 0 | N/A | 0 | 0
2020-07-31 01:30 | 5.8264 | 0 | N/A | 0 | 0
2020-07-31 02:00 | 5.3994 | 0 | N/A | 0 | 0
2020-07-31 02:30 | 4.7877 | 0 | N/A | 0 | 0
2020-07-31 03:00 | 4.4361 | 0 | N/A | 0 | 0
2020-07-31 03:30 | 4.3142 | 0 | N/A | 0 | 0
2020-07-31 04:00 | 4.1242 | 0 | N/A | 0 | 0
2020-07-31 04:30 | 4.0682 | 0 | N/A | 0 | 0
2020-07-31 05:00 | 4.2392 | 0 | N/A | 0 | 0
2020-07-31 05:30 | 4.53 | 0 | N/A | 0 | 0
2020-07-31 06:00 | 4.9017 | 0 | N/A | 0 | 0
2020-07-31 06:30 | 5.7912 | 0 | N/A | 0 | 0
2020-07-31 07:00 | 6.6704 | 0 | N/A | 0 | 0
2020-07-31 07:30 | 6.9269 | 0 | N/A | 0 | 0
2020-07-31 08:00 | 7.7949 | 0 | N/A | 0 | 0
2020-07-31 08:30 | 8.2869 | 0 | N/A | 0 | 0
2020-07-31 09:00 | 7.5867 | 0 | N/A | 0 | 0
2020-07-31 09:30 | 6.888 | 0 | N/A | 0 | 0
2020-07-31 10:00 | 5.83 | 0 | N/A | 0 | 0
2020-07-31 10:30 | 4.4313 | 0 | N/A | 0 | 0
2020-07-31 11:00 | 4.057 | 0 | N/A | 0 | 0
2020-07-31 11:30 | 3.6168 | 0 | N/A | 0 | 0
2020-07-31 12:00 | 2.7017 | 0 | N/A | 0 | 0
2020-07-31 12:30 | 2.579 | 0 | N/A | 0 | 0
2020-07-31 13:00 | 2.5358 | 0 | N/A | 0 | 0
2020-07-31 13:30 | 2.5614 | 0 | N/A | 0 | 0
2020-07-31 14:00 | 2.4979 | 0 | N/A | 0 | 0
2020-07-31 14:30 | 2.7012 | 0 | N/A | 0 | 0
2020-07-31 15:00 | 2.9148 | 0 | N/A | 0 | 0
2020-07-31 15:30 | 3.1263 | 0 | N/A | 0 | 0
2020-07-31 16:00 | 3.6349 | 0 | N/A | 0 | 0
2020-07-31 16:30 | 4.3497 | 0 | N/A | 0 | 0
2020-07-31 17:00 | 5.181 | 0 | N/A | 0 | 0
2020-07-31 17:30 | 6.2672 | 0 | N/A | 0 | 0
2020-07-31 18:00 | 7.3545 | 0 | N/A | 0 | 0
2020-07-31 18:30 | 7.8588 | 0 | N/A | 0 | 0
2020-07-31 19:00 | 7.9304 | 0 | N/A | 0 | 0
2020-07-31 19:30 | 7.7145 | 0 | N/A | 0 | 0
2020-07-31 20:00 | 7.3674 | 0 | N/A | 0 | 0
2020-07-31 20:30 | 7.0529 | 0 | N/A | 0 | 0
2020-07-31 21:00 | 6.755 | 0 | N/A | 0 | 0
2020-07-31 21:30 | 7.1116 | 0 | N/A | 0 | 0
2020-07-31 22:00 | 7.3211 | 0 | N/A | 0 | 0
2020-07-31 22:30 | 6.9148 | 0 | N/A | 0 | 0
2020-07-31 23:00 | 6.7122 | 0 | N/A | 0 | 0
2020-07-31 23:30 | 6.8502 | 0 | N/A | 0 | 0
2020-08-01 | 7.1142 | 0 | N/A | 0 | 0
2020-08-01 00:30 | 6.3143 | 0 | N/A | 0 | 0
2020-08-01 01:00 | 5.4735 | 0 | N/A | 0 | 0
2020-08-01 01:30 | 5.3612 | 0 | N/A | 0 | 0
2020-08-01 02:00 | 4.8931 | 0 | N/A | 0 | 0
2020-08-01 02:30 | 4.3164 | 0 | N/A | 0 | 0
2020-08-01 03:00 | 3.8965 | 0 | N/A | 0 | 0
2020-08-01 03:30 | 3.6486 | 0 | N/A | 0 | 0
2020-08-01 04:00 | 3.4807 | 0 | N/A | 0 | 0
2020-08-01 04:30 | 3.4454 | 0 | N/A | 0 | 0
2020-08-01 05:00 | 3.4659 | 0 | N/A | 0 | 0
2020-08-01 05:30 | 3.6105 | 0 | N/A | 0 | 0
2020-08-01 06:00 | 3.6869 | 0 | N/A | 0 | 0
2020-08-01 06:30 | 4.1727 | 0 | N/A | 0 | 0
2020-08-01 07:00 | 4.4627 | 0 | N/A | 0 | 0
2020-08-01 07:30 | 4.4283 | 0 | N/A | 0 | 0
2020-08-01 08:00 | 5.1315 | 0 | N/A | 0 | 0
2020-08-01 08:30 | 5.7337 | 0 | N/A | 0 | 0
2020-08-01 09:00 | 5.3133 | 0 | N/A | 0 | 0
2020-08-01 09:30 | 4.824 | 0 | N/A | 0 | 0
2020-08-01 10:00 | 4.4058 | 0 | N/A | 0 | 0
2020-08-01 10:30 | 3.5781 | 0 | N/A | 0 | 0
2020-08-01 11:00 | 2.8693 | 0 | N/A | 0 | 0
2020-08-01 11:30 | 2.4774 | 0 | N/A | 0 | 0
2020-08-01 12:00 | 2.2076 | 0 | N/A | 0 | 0
2020-08-01 12:30 | 2.1221 | 0 | N/A | 0 | 0
2020-08-01 13:00 | 1.939 | 0 | N/A | 0 | 0
2020-08-01 13:30 | 2.0351 | 0 | N/A | 0 | 0
2020-08-01 14:00 | 1.9828 | 0 | N/A | 0 | 0
2020-08-01 14:30 | 2.0081 | 0 | N/A | 0 | 0
2020-08-01 15:00 | 2.2095 | 0 | N/A | 0 | 0
2020-08-01 15:30 | 2.6973 | 0 | N/A | 0 | 0
2020-08-01 16:00 | 3.1958 | 0 | N/A | 0 | 0
2020-08-01 16:30 | 3.8062 | 0 | N/A | 0 | 0
2020-08-01 17:00 | 4.6115 | 0 | N/A | 0 | 0
2020-08-01 17:30 | 5.7362 | 0 | N/A | 0 | 0
2020-08-01 18:00 | 6.8063 | 0 | N/A | 0 | 0
2020-08-01 18:30 | 7.541 | 0 | N/A | 0 | 0
2020-08-01 19:00 | 7.574 | 0 | N/A | 0 | 0
2020-08-01 19:30 | 7.1412 | 0 | N/A | 0 | 0
2020-08-01 20:00 | 6.8331 | 0 | N/A | 0 | 0
2020-08-01 20:30 | 6.4842 | 0 | N/A | 0 | 0
2020-08-01 21:00 | 6.1434 | 0 | N/A | 0 | 0
2020-08-01 21:30 | 6.5292 | 0 | N/A | 0 | 0
2020-08-01 22:00 | 6.7573 | 0 | N/A | 0 | 0
2020-08-01 22:30 | 6.5939 | 0 | N/A | 0 | 0
2020-08-01 23:00 | 6.5622 | 0 | N/A | 0 | 0
2020-08-01 23:30 | 6.5959 | 0 | N/A | 0 | 0
2020-08-02 | 7.0005 | 0 | N/A | 0 | 0
2020-08-02 00:30 | 6.3609 | 0 | N/A | 0 | 0
2020-08-02 01:00 | 5.4708 | 0 | N/A | 0 | 0
2020-08-02 01:30 | 5.349 | 0 | N/A | 0 | 0
2020-08-02 02:00 | 4.9488 | 0 | N/A | 0 | 0
2020-08-02 02:30 | 4.339 | 0 | N/A | 0 | 0
2020-08-02 03:00 | 3.9675 | 0 | N/A | 0 | 0
2020-08-02 03:30 | 3.7484 | 0 | N/A | 0 | 0
2020-08-02 04:00 | 3.5471 | 0 | N/A | 0 | 0
2020-08-02 04:30 | 3.4848 | 0 | N/A | 0 | 0
2020-08-02 05:00 | 3.4595 | 0 | N/A | 0 | 0
2020-08-02 05:30 | 3.5639 | 0 | N/A | 0 | 0
2020-08-02 06:00 | 3.619 | 0 | N/A | 0 | 0
2020-08-02 06:30 | 3.8531 | 0 | N/A | 0 | 0
2020-08-02 07:00 | 4.0305 | 0 | N/A | 0 | 0
2020-08-02 07:30 | 4.0189 | 0 | N/A | 0 | 0
2020-08-02 08:00 | 4.6 | 0 | N/A | 0 | 0
2020-08-02 08:30 | 4.8892 | 0 | N/A | 0 | 0
2020-08-02 09:00 | 4.7039 | 0 | N/A | 0 | 0
2020-08-02 09:30 | 4.31 | 0 | N/A | 0 | 0
2020-08-02 10:00 | 3.82 | 0 | N/A | 0 | 0
2020-08-02 10:30 | 3.4783 | 0 | N/A | 0 | 0
2020-08-02 11:00 | 2.7739 | 0 | N/A | 0 | 0
2020-08-02 11:30 | 2.4834 | 0 | N/A | 0 | 0
2020-08-02 12:00 | 2.175 | 0 | N/A | 0 | 0
2020-08-02 12:30 | 2.0823 | 0 | N/A | 0 | 0
2020-08-02 13:00 | 2.0139 | 0 | N/A | 0 | 0
2020-08-02 13:30 | 2.0703 | 0 | N/A | 0 | 0
2020-08-02 14:00 | 2.0659 | 0 | N/A | 0 | 0
2020-08-02 14:30 | 2.5689 | 0 | N/A | 0 | 0
2020-08-02 15:00 | 2.3381 | 0 | N/A | 0 | 0
2020-08-02 15:30 | 2.5618 | 0 | N/A | 0 | 0
2020-08-02 16:00 | 3.1133 | 0 | N/A | 0 | 0
2020-08-02 16:30 | 3.8176 | 0 | N/A | 0 | 0
2020-08-02 17:00 | 4.7983 | 0 | N/A | 0 | 0
2020-08-02 17:30 | 5.9967 | 0 | N/A | 0 | 0
2020-08-02 18:00 | 7.1206 | 0 | N/A | 0 | 0
2020-08-02 18:30 | 7.8137 | 0 | N/A | 0 | 0
2020-08-02 19:00 | 7.8738 | 0 | N/A | 0 | 0
2020-08-02 19:30 | 7.3668 | 0 | N/A | 0 | 0
2020-08-02 20:00 | 7.0167 | 0 | N/A | 0 | 0
2020-08-02 20:30 | 6.6574 | 0 | N/A | 0 | 0
2020-08-02 21:00 | 6.423 | 0 | N/A | 0 | 0
2020-08-02 21:30 | 6.7242 | 0 | N/A | 0 | 0
2020-08-02 22:00 | 6.917 | 0 | N/A | 0 | 0
2020-08-02 22:30 | 6.358 | 0 | N/A | 0 | 0
2020-08-02 23:00 | 6.3276 | 0 | N/A | 0 | 0
2020-08-02 23:30 | 6.3027 | 0 | N/A | 0 | 0
2020-08-03 | 6.8625 | 0 | N/A | 0 | 0
2020-08-03 00:30 | 6.0896 | 0 | N/A | 0 | 0
2020-08-03 01:00 | 5.321 | 0 | N/A | 0 | 0
2020-08-03 01:30 | 5.2797 | 0 | N/A | 0 | 0
2020-08-03 02:00 | 5.0085 | 0 | N/A | 0 | 0
2020-08-03 02:30 | 4.3481 | 0 | N/A | 0 | 0
2020-08-03 03:00 | 4.0251 | 0 | N/A | 0 | 0
2020-08-03 03:30 | 3.7717 | 0 | N/A | 0 | 0
2020-08-03 04:00 | 3.5703 | 0 | N/A | 0 | 0
2020-08-03 04:30 | 3.5779 | 0 | N/A | 0 | 0
2020-08-03 05:00 | 3.585 | 0 | N/A | 0 | 0
2020-08-03 05:30 | 3.8856 | 0 | N/A | 0 | 0
2020-08-03 06:00 | 4.2762 | 0 | N/A | 0 | 0
2020-08-03 06:30 | 5.1597 | 0 | N/A | 0 | 0
2020-08-03 07:00 | 6.0146 | 0 | N/A | 0 | 0
2020-08-03 07:30 | 6.2946 | 0 | N/A | 0 | 0
2020-08-03 08:00 | 6.9367 | 0 | N/A | 0 | 0
2020-08-03 08:30 | 7.2633 | 0 | N/A | 0 | 0
2020-08-03 09:00 | 6.3505 | 0 | N/A | 0 | 0
2020-08-03 09:30 | 5.8067 | 0 | N/A | 0 | 0
2020-08-03 10:00 | 5.0502 | 0 | N/A | 0 | 0
2020-08-03 10:30 | 4.2063 | 0 | N/A | 0 | 0
2020-08-03 11:00 | 4.5273 | 0 | N/A | 0 | 0
2020-08-03 11:30 | 4.5249 | 0 | N/A | 0 | 0
2020-08-03 12:00 | 4.081 | 0 | N/A | 0 | 0
2020-08-03 12:30 | 4.7552 | 0 | N/A | 0 | 0
2020-08-03 13:00 | 5.2599 | 0 | N/A | 0 | 0
2020-08-03 13:30 | 5.5622 | 0 | N/A | 0 | 0
2020-08-03 14:00 | 5.4151 | 0 | N/A | 0 | 0
2020-08-03 14:30 | 5.4994 | 0 | N/A | 0 | 0
2020-08-03 15:00 | 5.3402 | 0 | N/A | 0 | 0
2020-08-03 15:30 | 5.2842 | 0 | N/A | 0 | 0
2020-08-03 16:00 | 5.7426 | 0 | N/A | 0 | 0
2020-08-03 16:30 | 5.8279 | 0 | N/A | 0 | 0
2020-08-03 17:00 | 6.3292 | 0 | N/A | 0 | 0
2020-08-03 17:30 | 7.4639 | 0 | N/A | 0 | 0
2020-08-03 18:00 | 8.501 | 0 | N/A | 0 | 0
2020-08-03 18:30 | 8.8517 | 0 | N/A | 0 | 0
2020-08-03 19:00 | 8.5887 | 0 | N/A | 0 | 0
2020-08-03 19:30 | 8.1217 | 0 | N/A | 0 | 0
2020-08-03 20:00 | 7.6773 | 0 | N/A | 0 | 0
2020-08-03 20:30 | 7.3124 | 0 | N/A | 0 | 0
2020-08-03 21:00 | 6.9702 | 0 | N/A | 0 | 0
2020-08-03 21:30 | 7.3133 | 0 | N/A | 0 | 0
2020-08-03 22:00 | 7.4964 | 0 | N/A | 0 | 0
2020-08-03 22:30 | 6.8475 | 0 | N/A | 0 | 0
2020-08-03 23:00 | 6.6805 | 0 | N/A | 0 | 0
2020-08-03 23:30 | 6.7974 | 0 | N/A | 0 | 0
2020-08-04 | 7.3931 | 0 | N/A | 0 | 0
2020-08-04 00:30 | 6.6379 | 0 | N/A | 0 | 0
2020-08-04 01:00 | 5.7935 | 0 | N/A | 0 | 0
2020-08-04 01:30 | 5.8429 | 0 | N/A | 0 | 0
2020-08-04 02:00 | 5.4545 | 0 | N/A | 0 | 0
2020-08-04 02:30 | 4.7929 | 0 | N/A | 0 | 0
2020-08-04 03:00 | 4.4523 | 0 | N/A | 0 | 0
2020-08-04 03:30 | 4.1585 | 0 | N/A | 0 | 0
2020-08-04 04:00 | 3.8926 | 0 | N/A | 0 | 0
2020-08-04 04:30 | 3.9373 | 0 | N/A | 0 | 0
2020-08-04 05:00 | 4.1242 | 0 | N/A | 0 | 0
2020-08-04 05:30 | 4.5015 | 0 | N/A | 0 | 0
2020-08-04 06:00 | 4.8052 | 0 | N/A | 0 | 0
2020-08-04 06:30 | 5.7139 | 0 | N/A | 0 | 0
2020-08-04 07:00 | 6.2791 | 0 | N/A | 0 | 0
2020-08-04 07:30 | 6.5471 | 0 | N/A | 0 | 0
2020-08-04 08:00 | 7.604 | 0 | N/A | 0 | 0
2020-08-04 08:30 | 8.3306 | 0 | N/A | 0 | 0
2020-08-04 09:00 | 8.8214 | 0 | N/A | 0 | 0
2020-08-04 09:30 | 8.6482 | 0 | N/A | 0 | 0
2020-08-04 10:00 | 7.6851 | 0 | N/A | 0 | 0
2020-08-04 10:30 | 7.5171 | 0 | N/A | 0 | 0
2020-08-04 11:00 | 7.9014 | 0 | N/A | 0 | 0
2020-08-04 11:30 | 6.3952 | 0 | N/A | 0 | 0
2020-08-04 12:00 | 6.0268 | 0 | N/A | 0 | 0
2020-08-04 12:30 | 6.2 | 0 | N/A | 0 | 0
2020-08-04 13:00 | 6.9401 | 0 | N/A | 0 | 0
2020-08-04 13:30 | 6.7333 | 0 | N/A | 0 | 0
2020-08-04 14:00 | 6.6867 | 0 | N/A | 0 | 0
2020-08-04 14:30 | 7.5705 | 0 | N/A | 0 | 0
2020-08-04 15:00 | 6.3681 | 0 | N/A | 0 | 0
2020-08-04 15:30 | 6.6827 | 0 | N/A | 0 | 0
2020-08-04 16:00 | 7.3806 | 0 | N/A | 0 | 0
2020-08-04 16:30 | 7.1965 | 0 | N/A | 0 | 0
2020-08-04 17:00 | 8.1903 | 0 | N/A | 0 | 0
2020-08-04 17:30 | 8.9248 | 0 | N/A | 0 | 0
2020-08-04 18:00 | 9.5402 | 0 | N/A | 0 | 0
2020-08-04 18:30 | 9.86 | 0 | N/A | 0 | 0
2020-08-04 19:00 | 9.7533 | 0 | N/A | 0 | 0
2020-08-04 19:30 | 9.1274 | 0 | N/A | 0 | 0
2020-08-04 20:00 | 8.8911 | 0 | N/A | 0 | 0
2020-08-04 20:30 | 8.5298 | 0 | N/A | 0 | 0
2020-08-04 21:00 | 8.2365 | 0 | N/A | 0 | 0
2020-08-04 21:30 | 8.5067 | 0 | N/A | 0 | 0
2020-08-04 22:00 | 8.4875 | 0 | N/A | 0 | 0
2020-08-04 22:30 | 7.77 | 0 | N/A | 0 | 0
2020-08-04 23:00 | 7.5306 | 0 | N/A | 0 | 0
2020-08-04 23:30 | 7.628 | 0 | N/A | 0 | 0
2020-08-05 | 8.0381 | 0 | N/A | 0 | 0
2020-08-05 00:30 | 7.4071 | 0 | N/A | 0 | 0
2020-08-05 01:00 | 6.5635 | 0 | N/A | 0 | 0
2020-08-05 01:30 | 6.4726 | 0 | N/A | 0 | 0
2020-08-05 02:00 | 6.0152 | 0 | N/A | 0 | 0
2020-08-05 02:30 | 5.3485 | 0 | N/A | 0 | 0
2020-08-05 03:00 | 4.9018 | 0 | N/A | 0 | 0
2020-08-05 03:30 | 4.6279 | 0 | N/A | 0 | 0
2020-08-05 04:00 | 4.3899 | 0 | N/A | 0 | 0
2020-08-05 04:30 | 4.3197 | 0 | N/A | 0 | 0
2020-08-05 05:00 | 4.5237 | 0 | N/A | 0 | 0
2020-08-05 05:30 | 4.7722 | 0 | N/A | 0 | 0
2020-08-05 06:00 | 5.0912 | 0 | N/A | 0 | 0
2020-08-05 06:30 | 5.9039 | 0 | N/A | 0 | 0
2020-08-05 07:00 | 6.4648 | 0 | N/A | 0 | 0
2020-08-05 07:30 | 6.7451 | 0 | N/A | 0 | 0
2020-08-05 08:00 | 7.8467 | 0 | N/A | 0 | 0
2020-08-05 08:30 | 8.4171 | 0 | N/A | 0 | 0
2020-08-05 09:00 | 8.4682 | 0 | N/A | 0 | 0
2020-08-05 09:30 | 8.2437 | 0 | N/A | 0 | 0
2020-08-05 10:00 | 7.1967 | 0 | N/A | 0 | 0
2020-08-05 10:30 | 6.5809 | 0 | N/A | 0 | 0
2020-08-05 11:00 | 7.2967 | 0 | N/A | 0 | 0
2020-08-05 11:30 | 6.2934 | 0 | N/A | 0 | 0
2020-08-05 12:00 | 6.1106 | 0 | N/A | 0 | 0
2020-08-05 12:30 | 5.8934 | 0 | N/A | 0 | 0
2020-08-05 13:00 | 6.3367 | 0 | N/A | 0 | 0
2020-08-05 13:30 | 6.63 | 0 | N/A | 0 | 0
2020-08-05 14:00 | 6.2871 | 0 | N/A | 0 | 0
2020-08-05 14:30 | 5.4568 | 0 | N/A | 0 | 0
2020-08-05 15:00 | 5.6633 | 0 | N/A | 0 | 0
2020-08-05 15:30 | 5.6867 | 0 | N/A | 0 | 0
2020-08-05 16:00 | 5.7342 | 0 | N/A | 0 | 0
2020-08-05 16:30 | 6.1938 | 0 | N/A | 0 | 0
2020-08-05 17:00 | 6.7063 | 0 | N/A | 0 | 0
2020-08-05 17:30 | 7.6288 | 0 | N/A | 0 | 0
2020-08-05 18:00 | 8.5775 | 0 | N/A | 0 | 0
2020-08-05 18:30 | 9.0681 | 0 | N/A | 0 | 0
2020-08-05 19:00 | 9.1149 | 0 | N/A | 0 | 0
2020-08-05 19:30 | 8.6964 | 0 | N/A | 0 | 0
2020-08-05 20:00 | 8.4017 | 0 | N/A | 0 | 0
2020-08-05 20:30 | 7.9854 | 0 | N/A | 0 | 0
2020-08-05 21:00 | 7.4479 | 0 | N/A | 0 | 0
2020-08-05 21:30 | 7.6631 | 0 | N/A | 0 | 0
2020-08-05 22:00 | 7.808 | 0 | N/A | 0 | 0
2020-08-05 22:30 | 7.3126 | 0 | N/A | 0 | 0
2020-08-05 23:00 | 6.9996 | 0 | N/A | 0 | 0
2020-08-05 23:30 | 6.9252 | 0 | N/A | 0 | 0
2020-08-06 | 7.4794 | 0 | N/A | 0 | 0
2020-08-06 00:30 | 6.836 | 0 | N/A | 0 | 0
2020-08-06 01:00 | 5.9571 | 0 | N/A | 0 | 0
2020-08-06 01:30 | 5.8966 | 0 | N/A | 0 | 0
2020-08-06 02:00 | 5.6554 | 0 | N/A | 0 | 0
2020-08-06 02:30 | 5.0213 | 0 | N/A | 0 | 0
2020-08-06 03:00 | 4.5548 | 0 | N/A | 0 | 0
2020-08-06 03:30 | 4.245 | 0 | N/A | 0 | 0
2020-08-06 04:00 | 4.0769 | 0 | N/A | 0 | 0
2020-08-06 04:30 | 3.9488 | 0 | N/A | 0 | 0
2020-08-06 05:00 | 4.0169 | 0 | N/A | 0 | 0
2020-08-06 05:30 | 4.3206 | 0 | N/A | 0 | 0
2020-08-06 06:00 | 4.6364 | 0 | N/A | 0 | 0
2020-08-06 06:30 | 5.3688 | 0 | N/A | 0 | 0
2020-08-06 07:00 | 6.0142 | 0 | N/A | 0 | 0
2020-08-06 07:30 | 6.2559 | 0 | N/A | 0 | 0
2020-08-06 08:00 | 7.0594 | 0 | N/A | 0 | 0
2020-08-06 08:30 | 7.3038 | 0 | N/A | 0 | 0
2020-08-06 09:00 | 7.3069 | 0 | N/A | 0 | 0
2020-08-06 09:30 | 6.6913 | 0 | N/A | 0 | 0
2020-08-06 10:00 | 5.9221 | 0 | N/A | 0 | 0
2020-08-06 10:30 | 5.8831 | 0 | N/A | 0 | 0
2020-08-06 11:00 | 5.7767 | 0 | N/A | 0 | 0
2020-08-06 11:30 | 5.6469 | 0 | N/A | 0 | 0
2020-08-06 12:00 | 5.3204 | 0 | N/A | 0 | 0
2020-08-06 12:30 | 5.2805 | 0 | N/A | 0 | 0
2020-08-06 13:00 | 5.131 | 0 | N/A | 0 | 0
2020-08-06 13:30 | 5.3573 | 0 | N/A | 0 | 0
2020-08-06 14:00 | 5.8305 | 0 | N/A | 0 | 0
2020-08-06 14:30 | 5.6803 | 0 | N/A | 0 | 0
2020-08-06 15:00 | 5.4541 | 0 | N/A | 0 | 0
2020-08-06 15:30 | 5.8803 | 0 | N/A | 0 | 0
2020-08-06 16:00 | 6.4288 | 0 | N/A | 0 | 0
2020-08-06 16:30 | 6.5187 | 0 | N/A | 0 | 0
2020-08-06 17:00 | 6.3222 | 0 | N/A | 0 | 0
2020-08-06 17:30 | 7.2967 | 0 | N/A | 0 | 0
2020-08-06 18:00 | 8.4965 | 0 | N/A | 0 | 0
2020-08-06 18:30 | 9.0359 | 0 | N/A | 0 | 0
2020-08-06 19:00 | 8.9828 | 0 | N/A | 0 | 0
2020-08-06 19:30 | 8.5018 | 0 | N/A | 0 | 0
2020-08-06 20:00 | 8.0865 | 0 | N/A | 0 | 0
2020-08-06 20:30 | 7.7039 | 0 | N/A | 0 | 0
2020-08-06 21:00 | 7.238 | 0 | N/A | 0 | 0
2020-08-06 21:30 | 7.4145 | 0 | N/A | 0 | 0
2020-08-06 22:00 | 7.5555 | 0 | N/A | 0 | 0
2020-08-06 22:30 | 6.9832 | 0 | N/A | 0 | 0
2020-08-06 23:00 | 6.87 | 0 | N/A | 0 | 0
2020-08-06 23:30 | 6.8641 | 0 | N/A | 0 | 0
2020-08-07 | 7.3185 | 0 | N/A | 0 | 0
2020-08-07 00:30 | 6.6454 | 0 | N/A | 0 | 0
2020-08-07 01:00 | 5.941 | 0 | N/A | 0 | 0
2020-08-07 01:30 | 5.8987 | 0 | N/A | 0 | 0
2020-08-07 02:00 | 5.5231 | 0 | N/A | 0 | 0
2020-08-07 02:30 | 4.8318 | 0 | N/A | 0 | 0
2020-08-07 03:00 | 4.4053 | 0 | N/A | 0 | 0
2020-08-07 03:30 | 4.1307 | 0 | N/A | 0 | 0
2020-08-07 04:00 | 3.9871 | 0 | N/A | 0 | 0
2020-08-07 04:30 | 3.9753 | 0 | N/A | 0 | 0
2020-08-07 05:00 | 4.0402 | 0 | N/A | 0 | 0
2020-08-07 05:30 | 4.2909 | 0 | N/A | 0 | 0
2020-08-07 06:00 | 4.5975 | 0 | N/A | 0 | 0
2020-08-07 06:30 | 5.3731 | 0 | N/A | 0 | 0
2020-08-07 07:00 | 5.9484 | 0 | N/A | 0 | 0
2020-08-07 07:30 | 6.0511 | 0 | N/A | 0 | 0
2020-08-07 08:00 | 6.9999 | 0 | N/A | 0 | 0
2020-08-07 08:30 | 7.75 | 0 | N/A | 0 | 0
2020-08-07 09:00 | 7.9033 | 0 | N/A | 0 | 0
2020-08-07 09:30 | 7.9869 | 0 | N/A | 0 | 0
2020-08-07 10:00 | 7.8368 | 0 | N/A | 0 | 0
2020-08-07 10:30 | 7.77 | 0 | N/A | 0 | 0
2020-08-07 11:00 | 7.9573 | 0 | N/A | 0 | 0
2020-08-07 11:30 | 7.6937 | 0 | N/A | 0 | 0
2020-08-07 12:00 | 7.8903 | 0 | N/A | 0 | 0
2020-08-07 12:30 | 7.9735 | 0 | N/A | 0 | 0
2020-08-07 13:00 | 7.59 | 0 | N/A | 0 | 0
2020-08-07 13:30 | 7.8067 | 0 | N/A | 0 | 0
2020-08-07 14:00 | 8.2767 | 0 | N/A | 0 | 0
2020-08-07 14:30 | 8.5634 | 0 | N/A | 0 | 0
2020-08-07 15:00 | 7.9267 | 0 | N/A | 0 | 0
2020-08-07 15:30 | 7.92 | 0 | N/A | 0 | 0
2020-08-07 16:00 | 7.7209 | 0 | N/A | 0 | 0
2020-08-07 16:30 | 7.4863 | 0 | N/A | 0 | 0
2020-08-07 17:00 | 7.886 | 0 | N/A | 0 | 0
2020-08-07 17:30 | 8.2718 | 0 | N/A | 0 | 0
2020-08-07 18:00 | 8.8354 | 0 | N/A | 0 | 0
2020-08-07 18:30 | 9.1515 | 0 | N/A | 0 | 0
2020-08-07 19:00 | 8.9883 | 0 | N/A | 0 | 0
2020-08-07 19:30 | 8.6632 | 0 | N/A | 0 | 0
2020-08-07 20:00 | 8.213 | 0 | N/A | 0 | 0
2020-08-07 20:30 | 7.8371 | 0 | N/A | 0 | 0
2020-08-07 21:00 | 7.5517 | 0 | N/A | 0 | 0
2020-08-07 21:30 | 7.9276 | 0 | N/A | 0 | 0
2020-08-07 22:00 | 7.9878 | 0 | N/A | 0 | 0
2020-08-07 22:30 | 7.417 | 0 | N/A | 0 | 0
2020-08-07 23:00 | 7.159 | 0 | N/A | 0 | 0
2020-08-07 23:30 | 7.2585 | 0 | N/A | 0 | 0
2020-08-08 | 7.7843 | 0 | N/A | 0 | 0
2020-08-08 00:30 | 7.1615 | 0 | N/A | 0 | 0
2020-08-08 01:00 | 6.3381 | 0 | N/A | 0 | 0
2020-08-08 01:30 | 6.059 | 0 | N/A | 0 | 0
2020-08-08 02:00 | 5.6089 | 0 | N/A | 0 | 0
2020-08-08 02:30 | 4.8983 | 0 | N/A | 0 | 0
2020-08-08 03:00 | 4.4424 | 0 | N/A | 0 | 0
2020-08-08 03:30 | 4.1757 | 0 | N/A | 0 | 0
2020-08-08 04:00 | 3.8763 | 0 | N/A | 0 | 0
2020-08-08 04:30 | 3.7235 | 0 | N/A | 0 | 0
2020-08-08 05:00 | 3.6909 | 0 | N/A | 0 | 0
2020-08-08 05:30 | 3.794 | 0 | N/A | 0 | 0
2020-08-08 06:00 | 3.8757 | 0 | N/A | 0 | 0
2020-08-08 06:30 | 4.2173 | 0 | N/A | 0 | 0
2020-08-08 07:00 | 4.4094 | 0 | N/A | 0 | 0
2020-08-08 07:30 | 4.4048 | 0 | N/A | 0 | 0
2020-08-08 08:00 | 4.9653 | 0 | N/A | 0 | 0
2020-08-08 08:30 | 5.614 | 0 | N/A | 0 | 0
2020-08-08 09:00 | 6.0907 | 0 | N/A | 0 | 0
2020-08-08 09:30 | 6.4549 | 0 | N/A | 0 | 0
2020-08-08 10:00 | 6.243 | 0 | N/A | 0 | 0
2020-08-08 10:30 | 6.3231 | 0 | N/A | 0 | 0
2020-08-08 11:00 | 6.1718 | 0 | N/A | 0 | 0
2020-08-08 11:30 | 5.6606 | 0 | N/A | 0 | 0
2020-08-08 12:00 | 6.0817 | 0 | N/A | 0 | 0
2020-08-08 12:30 | 5.8207 | 0 | N/A | 0 | 0
2020-08-08 13:00 | 5.3997 | 0 | N/A | 0 | 0
2020-08-08 13:30 | 5.1041 | 0 | N/A | 0 | 0
2020-08-08 14:00 | 5.1938 | 0 | N/A | 0 | 0
2020-08-08 14:30 | 4.6568 | 0 | N/A | 0 | 0
2020-08-08 15:00 | 4.8456 | 0 | N/A | 0 | 0
2020-08-08 15:30 | 4.6477 | 0 | N/A | 0 | 0
2020-08-08 16:00 | 5.2332 | 0 | N/A | 0 | 0
2020-08-08 16:30 | 5.6225 | 0 | N/A | 0 | 0
2020-08-08 17:00 | 6.4051 | 0 | N/A | 0 | 0
2020-08-08 17:30 | 7.2307 | 0 | N/A | 0 | 0
2020-08-08 18:00 | 7.9982 | 0 | N/A | 0 | 0
2020-08-08 18:30 | 8.2751 | 0 | N/A | 0 | 0
2020-08-08 19:00 | 8.0258 | 0 | N/A | 0 | 0
2020-08-08 19:30 | 7.6016 | 0 | N/A | 0 | 0
2020-08-08 20:00 | 7.2606 | 0 | N/A | 0 | 0
2020-08-08 20:30 | 6.7959 | 0 | N/A | 0 | 0
2020-08-08 21:00 | 6.4748 | 0 | N/A | 0 | 0
2020-08-08 21:30 | 6.7706 | 0 | N/A | 0 | 0
2020-08-08 22:00 | 7.0573 | 0 | N/A | 0 | 0
2020-08-08 22:30 | 6.6715 | 0 | N/A | 0 | 0
2020-08-08 23:00 | 6.6707 | 0 | N/A | 0 | 0
2020-08-08 23:30 | 6.7577 | 0 | N/A | 0 | 0
2020-08-09 | 7.2568 | 0 | N/A | 0 | 0
2020-08-09 00:30 | 6.5607 | 0 | N/A | 0 | 0
2020-08-09 01:00 | 5.7523 | 0 | N/A | 0 | 0
2020-08-09 01:30 | 5.6592 | 0 | N/A | 0 | 0
2020-08-09 02:00 | 5.1442 | 0 | N/A | 0 | 0
2020-08-09 02:30 | 4.4772 | 0 | N/A | 0 | 0
2020-08-09 03:00 | 4.0522 | 0 | N/A | 0 | 0
2020-08-09 03:30 | 3.8278 | 0 | N/A | 0 | 0
2020-08-09 04:00 | 3.5976 | 0 | N/A | 0 | 0
2020-08-09 04:30 | 3.4977 | 0 | N/A | 0 | 0
2020-08-09 05:00 | 3.4385 | 0 | N/A | 0 | 0
2020-08-09 05:30 | 3.5011 | 0 | N/A | 0 | 0
2020-08-09 06:00 | 3.5871 | 0 | N/A | 0 | 0
2020-08-09 06:30 | 3.8153 | 0 | N/A | 0 | 0
2020-08-09 07:00 | 3.9491 | 0 | N/A | 0 | 0
2020-08-09 07:30 | 3.9377 | 0 | N/A | 0 | 0
2020-08-09 08:00 | 4.4548 | 0 | N/A | 0 | 0
2020-08-09 08:30 | 5.0711 | 0 | N/A | 0 | 0
2020-08-09 09:00 | 5.5749 | 0 | N/A | 0 | 0
2020-08-09 09:30 | 5.6913 | 0 | N/A | 0 | 0
2020-08-09 10:00 | 5.6485 | 0 | N/A | 0 | 0
2020-08-09 10:30 | 5.5762 | 0 | N/A | 0 | 0
2020-08-09 11:00 | 5.8065 | 0 | N/A | 0 | 0
2020-08-09 11:30 | 6.0811 | 0 | N/A | 0 | 0
2020-08-09 12:00 | 6.101 | 0 | N/A | 0 | 0
2020-08-09 12:30 | 6.2774 | 0 | N/A | 0 | 0
2020-08-09 13:00 | 6.352 | 0 | N/A | 0 | 0
2020-08-09 13:30 | 6.4877 | 0 | N/A | 0 | 0
2020-08-09 14:00 | 6.4807 | 0 | N/A | 0 | 0
2020-08-09 14:30 | 6.0529 | 0 | N/A | 0 | 0
2020-08-09 15:00 | 5.4323 | 0 | N/A | 0 | 0
2020-08-09 15:30 | 5.2007 | 0 | N/A | 0 | 0
2020-08-09 16:00 | 5.304 | 0 | N/A | 0 | 0
2020-08-09 16:30 | 5.3548 | 0 | N/A | 0 | 0
2020-08-09 17:00 | 6.0485 | 0 | N/A | 0 | 0
2020-08-09 17:30 | 7.0489 | 0 | N/A | 0 | 0
2020-08-09 18:00 | 8.1191 | 0 | N/A | 0 | 0
2020-08-09 18:30 | 8.7056 | 0 | N/A | 0 | 0
2020-08-09 19:00 | 8.6186 | 0 | N/A | 0 | 0
2020-08-09 19:30 | 8.0167 | 0 | N/A | 0 | 0
2020-08-09 20:00 | 7.408 | 0 | N/A | 0 | 0
2020-08-09 20:30 | 7.0688 | 0 | N/A | 0 | 0
2020-08-09 21:00 | 6.6804 | 0 | N/A | 0 | 0
2020-08-09 21:30 | 7.0872 | 0 | N/A | 0 | 0
2020-08-09 22:00 | 7.229 | 0 | N/A | 0 | 0
2020-08-09 22:30 | 6.7747 | 0 | N/A | 0 | 0
2020-08-09 23:00 | 6.6938 | 0 | N/A | 0 | 0
2020-08-09 23:30 | 6.683 | 0 | N/A | 0 | 0
2020-08-10 | 7.0944 | 0 | N/A | 0 | 0
2020-08-10 00:30 | 6.5395 | 0 | N/A | 0 | 0
2020-08-10 01:00 | 5.7392 | 0 | N/A | 0 | 0
2020-08-10 01:30 | 5.674 | 0 | N/A | 0 | 0
2020-08-10 02:00 | 5.3162 | 0 | N/A | 0 | 0
2020-08-10 02:30 | 4.6261 | 0 | N/A | 0 | 0
2020-08-10 03:00 | 4.2035 | 0 | N/A | 0 | 0
2020-08-10 03:30 | 3.9712 | 0 | N/A | 0 | 0
2020-08-10 04:00 | 3.7938 | 0 | N/A | 0 | 0
2020-08-10 04:30 | 3.6725 | 0 | N/A | 0 | 0
2020-08-10 05:00 | 3.6695 | 0 | N/A | 0 | 0
2020-08-10 05:30 | 3.9887 | 0 | N/A | 0 | 0
2020-08-10 06:00 | 4.2567 | 0 | N/A | 0 | 0
2020-08-10 06:30 | 5.1044 | 0 | N/A | 0 | 0
2020-08-10 07:00 | 5.6913 | 0 | N/A | 0 | 0
2020-08-10 07:30 | 5.6875 | 0 | N/A | 0 | 0
2020-08-10 08:00 | 6.1245 | 0 | N/A | 0 | 0
2020-08-10 08:30 | 6.3301 | 0 | N/A | 0 | 0
2020-08-10 09:00 | 6.4502 | 0 | N/A | 0 | 0
2020-08-10 09:30 | 6.2264 | 0 | N/A | 0 | 0
2020-08-10 10:00 | 5.2604 | 0 | N/A | 0 | 0
2020-08-10 10:30 | 4.4369 | 0 | N/A | 0 | 0
2020-08-10 11:00 | 3.6242 | 0 | N/A | 0 | 0
2020-08-10 11:30 | 3.1588 | 0 | N/A | 0 | 0
2020-08-10 12:00 | 2.9171 | 0 | N/A | 0 | 0
2020-08-10 12:30 | 2.8578 | 0 | N/A | 0 | 0
2020-08-10 13:00 | 2.6778 | 0 | N/A | 0 | 0
2020-08-10 13:30 | 2.7431 | 0 | N/A | 0 | 0
2020-08-10 14:00 | 2.6419 | 0 | N/A | 0 | 0
2020-08-10 14:30 | 2.6431 | 0 | N/A | 0 | 0
2020-08-10 15:00 | 2.7319 | 0 | N/A | 0 | 0
2020-08-10 15:30 | 3.0924 | 0 | N/A | 0 | 0
2020-08-10 16:00 | 3.4528 | 0 | N/A | 0 | 0
2020-08-10 16:30 | 4.193 | 0 | N/A | 0 | 0
2020-08-10 17:00 | 5.1755 | 0 | N/A | 0 | 0
2020-08-10 17:30 | 6.4822 | 0 | N/A | 0 | 0
2020-08-10 18:00 | 8.0908 | 0 | N/A | 0 | 0
2020-08-10 18:30 | 9.0204 | 0 | N/A | 0 | 0
2020-08-10 19:00 | 9.0522 | 0 | N/A | 0 | 0
2020-08-10 19:30 | 8.6289 | 0 | N/A | 0 | 0
2020-08-10 20:00 | 8.3421 | 0 | N/A | 0 | 0
2020-08-10 20:30 | 7.9026 | 0 | N/A | 0 | 0
2020-08-10 21:00 | 7.6651 | 0 | N/A | 0 | 0
2020-08-10 21:30 | 7.9549 | 0 | N/A | 0 | 0
2020-08-10 22:00 | 8.0787 | 0 | N/A | 0 | 0
2020-08-10 22:30 | 7.6151 | 0 | N/A | 0 | 0
2020-08-10 23:00 | 7.3827 | 0 | N/A | 0 | 0
2020-08-10 23:30 | 7.4864 | 0 | N/A | 0 | 0
2020-08-11 | 7.7074 | 0 | N/A | 0 | 0
2020-08-11 00:30 | 7.0664 | 0 | N/A | 0 | 0
2020-08-11 01:00 | 6.3085 | 0 | N/A | 0 | 0
2020-08-11 01:30 | 6.2888 | 0 | N/A | 0 | 0
2020-08-11 02:00 | 5.8606 | 0 | N/A | 0 | 0
2020-08-11 02:30 | 5.1633 | 0 | N/A | 0 | 0
2020-08-11 03:00 | 4.7969 | 0 | N/A | 0 | 0
2020-08-11 03:30 | 4.4697 | 0 | N/A | 0 | 0
2020-08-11 04:00 | 4.2302 | 0 | N/A | 0 | 0
2020-08-11 04:30 | 4.2065 | 0 | N/A | 0 | 0
2020-08-11 05:00 | 4.3236 | 0 | N/A | 0 | 0
2020-08-11 05:30 | 4.6476 | 0 | N/A | 0 | 0
2020-08-11 06:00 | 5.0029 | 0 | N/A | 0 | 0
2020-08-11 06:30 | 5.7938 | 0 | N/A | 0 | 0
2020-08-11 07:00 | 6.3562 | 0 | N/A | 0 | 0
2020-08-11 07:30 | 6.3268 | 0 | N/A | 0 | 0
2020-08-11 08:00 | 7.2468 | 0 | N/A | 0 | 0
2020-08-11 08:30 | 7.8535 | 0 | N/A | 0 | 0
2020-08-11 09:00 | 7.7074 | 0 | N/A | 0 | 0
2020-08-11 09:30 | 6.4083 | 0 | N/A | 0 | 0
2020-08-11 10:00 | 6.535 | 0 | N/A | 0 | 0
2020-08-11 10:30 | 6.8844 | 0 | N/A | 0 | 0
2020-08-11 11:00 | 6.6265 | 0 | N/A | 0 | 0
2020-08-11 11:30 | 6.8989 | 0 | N/A | 0 | 0
2020-08-11 12:00 | 6.9802 | 0 | N/A | 0 | 0
2020-08-11 12:30 | 7.35 | 0 | N/A | 0 | 0
2020-08-11 13:00 | 6.8249 | 0 | N/A | 0 | 0
2020-08-11 13:30 | 6.6839 | 0 | N/A | 0 | 0
2020-08-11 14:00 | 7.5639 | 0 | N/A | 0 | 0
2020-08-11 14:30 | 7.812 | 0 | N/A | 0 | 0
2020-08-11 15:00 | 8.0203 | 0 | N/A | 0 | 0
2020-08-11 15:30 | 7.7584 | 0 | N/A | 0 | 0
2020-08-11 16:00 | 8.0154 | 0 | N/A | 0 | 0
2020-08-11 16:30 | 8.0953 | 0 | N/A | 0 | 0
2020-08-11 17:00 | 8.4673 | 0 | N/A | 0 | 0
2020-08-11 17:30 | 9.2957 | 0 | N/A | 0 | 0
2020-08-11 18:00 | 9.9596 | 0 | N/A | 0 | 0
2020-08-11 18:30 | 9.0407 | 0 | N/A | 0 | 0
2020-08-11 19:00 | 8.7388 | 0 | N/A | 0 | 0
2020-08-11 19:30 | 8.1215 | 0 | N/A | 0 | 0
2020-08-11 20:00 | 7.8283 | 0 | N/A | 0 | 0
2020-08-11 20:30 | 7.4522 | 0 | N/A | 0 | 0
2020-08-11 21:00 | 6.9768 | 0 | N/A | 0 | 0
2020-08-11 21:30 | 7.1425 | 0 | N/A | 0 | 0
2020-08-11 22:00 | 7.2148 | 0 | N/A | 0 | 0
2020-08-11 22:30 | 6.641 | 0 | N/A | 0 | 0
2020-08-11 23:00 | 6.4834 | 0 | N/A | 0 | 0
2020-08-11 23:30 | 6.6045 | 0 | N/A | 0 | 0
2020-08-12 | 6.9535 | 0 | N/A | 0 | 0
2020-08-12 00:30 | 6.3419 | 0 | N/A | 0 | 0
2020-08-12 01:00 | 5.5383 | 0 | N/A | 0 | 0
2020-08-12 01:30 | 5.4447 | 0 | N/A | 0 | 0
2020-08-12 02:00 | 4.9652 | 0 | N/A | 0 | 0
2020-08-12 02:30 | 4.2779 | 0 | N/A | 0 | 0
2020-08-12 03:00 | 3.8546 | 0 | N/A | 0 | 0
2020-08-12 03:30 | 3.6061 | 0 | N/A | 0 | 0
2020-08-12 04:00 | 3.4495 | 0 | N/A | 0 | 0
2020-08-12 04:30 | 3.3767 | 0 | N/A | 0 | 0
2020-08-12 05:00 | 3.4198 | 0 | N/A | 0 | 0
2020-08-12 05:30 | 3.6653 | 0 | N/A | 0 | 0
2020-08-12 06:00 | 3.984 | 0 | N/A | 0 | 0
2020-08-12 06:30 | 4.7186 | 0 | N/A | 0 | 0
2020-08-12 07:00 | 5.1525 | 0 | N/A | 0 | 0
2020-08-12 07:30 | 5.4284 | 0 | N/A | 0 | 0
2020-08-12 08:00 | 6.2232 | 0 | N/A | 0 | 0
2020-08-12 08:30 | 6.8802 | 0 | N/A | 0 | 0
2020-08-12 09:00 | 7.12 | 0 | N/A | 0 | 0
2020-08-12 09:30 | 6.9634 | 0 | N/A | 0 | 0
2020-08-12 10:00 | 6.5968 | 0 | N/A | 0 | 0
2020-08-12 10:30 | 6.5311 | 0 | N/A | 0 | 0
2020-08-12 11:00 | 6.7257 | 0 | N/A | 0 | 0
2020-08-12 11:30 | 6.7235 | 0 | N/A | 0 | 0
2020-08-12 12:00 | 6.5904 | 0 | N/A | 0 | 0
2020-08-12 12:30 | 6.9372 | 0 | N/A | 0 | 0
2020-08-12 13:00 | 7.017 | 0 | N/A | 0 | 0
2020-08-12 13:30 | 7.1272 | 0 | N/A | 0 | 0
2020-08-12 14:00 | 6.5974 | 0 | N/A | 0 | 0
2020-08-12 14:30 | 6.7202 | 0 | N/A | 0 | 0
2020-08-12 15:00 | 6.6002 | 0 | N/A | 0 | 0
2020-08-12 15:30 | 6.044 | 0 | N/A | 0 | 0
2020-08-12 16:00 | 5.162 | 0 | N/A | 0 | 0
2020-08-12 16:30 | 5.4896 | 0 | N/A | 0 | 0
2020-08-12 17:00 | 6.0508 | 0 | N/A | 0 | 0
2020-08-12 17:30 | 6.9417 | 0 | N/A | 0 | 0
2020-08-12 18:00 | 7.7705 | 0 | N/A | 0 | 0
2020-08-12 18:30 | 8.0615 | 0 | N/A | 0 | 0
2020-08-12 19:00 | 7.8726 | 0 | N/A | 0 | 0
2020-08-12 19:30 | 7.3984 | 0 | N/A | 0 | 0
2020-08-12 20:00 | 7.0031 | 0 | N/A | 0 | 0
2020-08-12 20:30 | 6.6453 | 0 | N/A | 0 | 0
2020-08-12 21:00 | 6.3361 | 0 | N/A | 0 | 0
2020-08-12 21:30 | 6.5008 | 0 | N/A | 0 | 0
2020-08-12 22:00 | 6.7133 | 0 | N/A | 0 | 0
2020-08-12 22:30 | 6.3154 | 0 | N/A | 0 | 0
2020-08-12 23:00 | 6.1135 | 0 | N/A | 0 | 0
2020-08-12 23:30 | 6.1822 | 0 | N/A | 0 | 0
2020-08-13 | 6.6169 | 0 | N/A | 0 | 0
2020-08-13 00:30 | 6.0355 | 0 | N/A | 0 | 0
2020-08-13 01:00 | 5.1797 | 0 | N/A | 0 | 0
2020-08-13 01:30 | 5.0755 | 0 | N/A | 0 | 0
2020-08-13 02:00 | 4.6423 | 0 | N/A | 0 | 0
2020-08-13 02:30 | 4.0754 | 0 | N/A | 0 | 0
2020-08-13 03:00 | 3.6646 | 0 | N/A | 0 | 0
2020-08-13 03:30 | 3.4648 | 0 | N/A | 0 | 0
2020-08-13 04:00 | 3.2571 | 0 | N/A | 0 | 0
2020-08-13 04:30 | 3.1789 | 0 | N/A | 0 | 0
2020-08-13 05:00 | 3.2905 | 0 | N/A | 0 | 0
2020-08-13 05:30 | 3.5745 | 0 | N/A | 0 | 0
2020-08-13 06:00 | 3.8319 | 0 | N/A | 0 | 0
2020-08-13 06:30 | 4.5322 | 0 | N/A | 0 | 0
2020-08-13 07:00 | 4.9394 | 0 | N/A | 0 | 0
2020-08-13 07:30 | 5.2609 | 0 | N/A | 0 | 0
2020-08-13 08:00 | 5.8591 | 0 | N/A | 0 | 0
2020-08-13 08:30 | 6.6234 | 0 | N/A | 0 | 0
2020-08-13 09:00 | 6.5704 | 0 | N/A | 0 | 0
2020-08-13 09:30 | 6.387 | 0 | N/A | 0 | 0
2020-08-13 10:00 | 5.9503 | 0 | N/A | 0 | 0
2020-08-13 10:30 | 4.9716 | 0 | N/A | 0 | 0
2020-08-13 11:00 | 4.6839 | 0 | N/A | 0 | 0
2020-08-13 11:30 | 4.2537 | 0 | N/A | 0 | 0
2020-08-13 12:00 | 4.4434 | 0 | N/A | 0 | 0
2020-08-13 12:30 | 4.6983 | 0 | N/A | 0 | 0
2020-08-13 13:00 | 5.2538 | 0 | N/A | 0 | 0
2020-08-13 13:30 | 5.0469 | 0 | N/A | 0 | 0
2020-08-13 14:00 | 4.4034 | 0 | N/A | 0 | 0
2020-08-13 14:30 | 3.827 | 0 | N/A | 0 | 0
2020-08-13 15:00 | 3.7214 | 0 | N/A | 0 | 0
2020-08-13 15:30 | 4.208 | 0 | N/A | 0 | 0
2020-08-13 16:00 | 4.3993 | 0 | N/A | 0 | 0
2020-08-13 16:30 | 4.8511 | 0 | N/A | 0 | 0
2020-08-13 17:00 | 5.2864 | 0 | N/A | 0 | 0
2020-08-13 17:30 | 5.9559 | 0 | N/A | 0 | 0
2020-08-13 18:00 | 6.8807 | 0 | N/A | 0 | 0
2020-08-13 18:30 | 7.5319 | 0 | N/A | 0 | 0
2020-08-13 19:00 | 7.5678 | 0 | N/A | 0 | 0
2020-08-13 19:30 | 7.2685 | 0 | N/A | 0 | 0
2020-08-13 20:00 | 6.86 | 0 | N/A | 0 | 0
2020-08-13 20:30 | 6.4945 | 0 | N/A | 0 | 0
2020-08-13 21:00 | 6.2369 | 0 | N/A | 0 | 0
2020-08-13 21:30 | 6.543 | 0 | N/A | 0 | 0
2020-08-13 22:00 | 6.7093 | 0 | N/A | 0 | 0
2020-08-13 22:30 | 6.1782 | 0 | N/A | 0 | 0
2020-08-13 23:00 | 5.9788 | 0 | N/A | 0 | 0
2020-08-13 23:30 | 6.1509 | 0 | N/A | 0 | 0
2020-08-14 | 6.6495 | 0 | N/A | 0 | 0
2020-08-14 00:30 | 6.0002 | 0 | N/A | 0 | 0
2020-08-14 01:00 | 5.1476 | 0 | N/A | 0 | 0
2020-08-14 01:30 | 4.9305 | 0 | N/A | 0 | 0
2020-08-14 02:00 | 4.6161 | 0 | N/A | 0 | 0
2020-08-14 02:30 | 3.9772 | 0 | N/A | 0 | 0
2020-08-14 03:00 | 3.6779 | 0 | N/A | 0 | 0
2020-08-14 03:30 | 3.4711 | 0 | N/A | 0 | 0
2020-08-14 04:00 | 3.393 | 0 | N/A | 0 | 0
2020-08-14 04:30 | 3.3614 | 0 | N/A | 0 | 0
2020-08-14 05:00 | 3.3789 | 0 | N/A | 0 | 0
2020-08-14 05:30 | 3.6579 | 0 | N/A | 0 | 0
2020-08-14 06:00 | 3.9088 | 0 | N/A | 0 | 0
2020-08-14 06:30 | 4.6382 | 0 | N/A | 0 | 0
2020-08-14 07:00 | 5.0822 | 0 | N/A | 0 | 0
2020-08-14 07:30 | 5.0492 | 0 | N/A | 0 | 0
2020-08-14 08:00 | 5.7934 | 0 | N/A | 0 | 0
2020-08-14 08:30 | 6.7158 | 0 | N/A | 0 | 0
2020-08-14 09:00 | 6.7848 | 0 | N/A | 0 | 0
2020-08-14 09:30 | 6.961 | 0 | N/A | 0 | 0
2020-08-14 10:00 | 6.4438 | 0 | N/A | 0 | 0
2020-08-14 10:30 | 4.6017 | 0 | N/A | 0 | 0
2020-08-14 11:00 | 3.635 | 0 | N/A | 0 | 0
2020-08-14 11:30 | 3.3102 | 0 | N/A | 0 | 0
2020-08-14 12:00 | 3.8451 | 0 | N/A | 0 | 0
2020-08-14 12:30 | 4.0706 | 0 | N/A | 0 | 0
2020-08-14 13:00 | 4.3552 | 0 | N/A | 0 | 0
2020-08-14 13:30 | 3.9156 | 0 | N/A | 0 | 0
2020-08-14 14:00 | 4.2721 | 0 | N/A | 0 | 0
2020-08-14 14:30 | 5.1156 | 0 | N/A | 0 | 0
2020-08-14 15:00 | 4.5164 | 0 | N/A | 0 | 0
2020-08-14 15:30 | 4.2208 | 0 | N/A | 0 | 0
2020-08-14 16:00 | 4.18 | 0 | N/A | 0 | 0
2020-08-14 16:30 | 4.4983 | 0 | N/A | 0 | 0
2020-08-14 17:00 | 5.2186 | 0 | N/A | 0 | 0
2020-08-14 17:30 | 6.382 | 0 | N/A | 0 | 0
2020-08-14 18:00 | 6.2978 | 0 | N/A | 0 | 0
2020-08-14 18:30 | 7.2058 | 0 | N/A | 0 | 0
2020-08-14 19:00 | 7.3297 | 0 | N/A | 0 | 0
2020-08-14 19:30 | 7.0679 | 0 | N/A | 0 | 0
2020-08-14 20:00 | 6.7323 | 0 | N/A | 0 | 0
2020-08-14 20:30 | 6.4148 | 0 | N/A | 0 | 0
2020-08-14 21:00 | 6.1378 | 0 | N/A | 0 | 0
2020-08-14 21:30 | 6.5505 | 0 | N/A | 0 | 0
2020-08-14 22:00 | 6.8711 | 0 | N/A | 0 | 0
2020-08-14 22:30 | 6.3932 | 0 | N/A | 0 | 0
2020-08-14 23:00 | 6.2402 | 0 | N/A | 0 | 0
2020-08-14 23:30 | 6.5536 | 0 | N/A | 0 | 0
2020-08-15 | 6.9285 | 0 | N/A | 0 | 0
2020-08-15 00:30 | 6.1632 | 0 | N/A | 0 | 0
2020-08-15 01:00 | 5.2102 | 0 | N/A | 0 | 0
2020-08-15 01:30 | 5.1611 | 0 | N/A | 0 | 0
2020-08-15 02:00 | 4.7653 | 0 | N/A | 0 | 0
2020-08-15 02:30 | 4.1508 | 0 | N/A | 0 | 0
2020-08-15 03:00 | 3.7784 | 0 | N/A | 0 | 0
2020-08-15 03:30 | 3.5502 | 0 | N/A | 0 | 0
2020-08-15 04:00 | 3.3548 | 0 | N/A | 0 | 0
2020-08-15 04:30 | 3.287 | 0 | N/A | 0 | 0
2020-08-15 05:00 | 3.3105 | 0 | N/A | 0 | 0
2020-08-15 05:30 | 3.3121 | 0 | N/A | 0 | 0
2020-08-15 06:00 | 3.5302 | 0 | N/A | 0 | 0
2020-08-15 06:30 | 3.8693 | 0 | N/A | 0 | 0
2020-08-15 07:00 | 3.9991 | 0 | N/A | 0 | 0
2020-08-15 07:30 | 3.9012 | 0 | N/A | 0 | 0
2020-08-15 08:00 | 4.3107 | 0 | N/A | 0 | 0
2020-08-15 08:30 | 5.267 | 0 | N/A | 0 | 0
2020-08-15 09:00 | 5.4861 | 0 | N/A | 0 | 0
2020-08-15 09:30 | 5.2271 | 0 | N/A | 0 | 0
2020-08-15 10:00 | 5.3506 | 0 | N/A | 0 | 0
2020-08-15 10:30 | 5.4899 | 0 | N/A | 0 | 0
2020-08-15 11:00 | 5.1572 | 0 | N/A | 0 | 0
2020-08-15 11:30 | 4.9852 | 0 | N/A | 0 | 0
2020-08-15 12:00 | 4.5637 | 0 | N/A | 0 | 0
2020-08-15 12:30 | 4.6468 | 0 | N/A | 0 | 0
2020-08-15 13:00 | 4.4858 | 0 | N/A | 0 | 0
2020-08-15 13:30 | 5.1153 | 0 | N/A | 0 | 0
2020-08-15 14:00 | 4.6404 | 0 | N/A | 0 | 0
2020-08-15 14:30 | 4.5368 | 0 | N/A | 0 | 0
2020-08-15 15:00 | 4.7377 | 0 | N/A | 0 | 0
2020-08-15 15:30 | 4.168 | 0 | N/A | 0 | 0
2020-08-15 16:00 | 4.1325 | 0 | N/A | 0 | 0
2020-08-15 16:30 | 4.5702 | 0 | N/A | 0 | 0
2020-08-15 17:00 | 5.6261 | 0 | N/A | 0 | 0
2020-08-15 17:30 | 6.287 | 0 | N/A | 0 | 0
2020-08-15 18:00 | 7.1822 | 0 | N/A | 0 | 0
2020-08-15 18:30 | 8.0178 | 0 | N/A | 0 | 0
2020-08-15 19:00 | 8.2041 | 0 | N/A | 0 | 0
2020-08-15 19:30 | 7.7218 | 0 | N/A | 0 | 0
2020-08-15 20:00 | 7.3238 | 0 | N/A | 0 | 0
2020-08-15 20:30 | 6.9079 | 0 | N/A | 0 | 0
2020-08-15 21:00 | 6.5376 | 0 | N/A | 0 | 0
2020-08-15 21:30 | 6.9649 | 0 | N/A | 0 | 0
2020-08-15 22:00 | 7.0412 | 0 | N/A | 0 | 0
2020-08-15 22:30 | 6.0985 | 0 | N/A | 0 | 0
2020-08-15 23:00 | 6.1514 | 0 | N/A | 0 | 0
2020-08-15 23:30 | 6.2064 | 0 | N/A | 0 | 0
2020-08-16 | 6.5529 | 0 | N/A | 0 | 0
2020-08-16 00:30 | 5.8469 | 0 | N/A | 0 | 0
2020-08-16 01:00 | 4.9572 | 0 | N/A | 0 | 0
2020-08-16 01:30 | 4.8835 | 0 | N/A | 0 | 0
2020-08-16 02:00 | 4.4799 | 0 | N/A | 0 | 0
2020-08-16 02:30 | 3.8623 | 0 | N/A | 0 | 0
2020-08-16 03:00 | 3.5312 | 0 | N/A | 0 | 0
2020-08-16 03:30 | 3.277 | 0 | N/A | 0 | 0
2020-08-16 04:00 | 3.0547 | 0 | N/A | 0 | 0
2020-08-16 04:30 | 3.0052 | 0 | N/A | 0 | 0
2020-08-16 05:00 | 2.9309 | 0 | N/A | 0 | 0
2020-08-16 05:30 | 2.8195 | 0 | N/A | 0 | 0
2020-08-16 06:00 | 2.865 | 0 | N/A | 0 | 0
2020-08-16 06:30 | 3.1693 | 0 | N/A | 0 | 0
2020-08-16 07:00 | 3.2486 | 0 | N/A | 0 | 0
2020-08-16 07:30 | 3.3176 | 0 | N/A | 0 | 0
2020-08-16 08:00 | 3.6058 | 0 | N/A | 0 | 0
2020-08-16 08:30 | 4.2201 | 0 | N/A | 0 | 0
2020-08-16 09:00 | 4.4846 | 0 | N/A | 0 | 0
2020-08-16 09:30 | 4.7188 | 0 | N/A | 0 | 0
2020-08-16 10:00 | 4.9845 | 0 | N/A | 0 | 0
2020-08-16 10:30 | 4.9949 | 0 | N/A | 0 | 0
2020-08-16 11:00 | 4.6417 | 0 | N/A | 0 | 0
2020-08-16 11:30 | 4.1418 | 0 | N/A | 0 | 0
2020-08-16 12:00 | 4.2344 | 0 | N/A | 0 | 0
2020-08-16 12:30 | 4.2615 | 0 | N/A | 0 | 0
2020-08-16 13:00 | 3.5304 | 0 | N/A | 0 | 0
2020-08-16 13:30 | 2.9345 | 0 | N/A | 0 | 0
2020-08-16 14:00 | 2.9285 | 0 | N/A | 0 | 0
2020-08-16 14:30 | 3.179 | 0 | N/A | 0 | 0
2020-08-16 15:00 | 3.6239 | 0 | N/A | 0 | 0
2020-08-16 15:30 | 3.5729 | 0 | N/A | 0 | 0
2020-08-16 16:00 | 4.1897 | 0 | N/A | 0 | 0
2020-08-16 16:30 | 4.793 | 0 | N/A | 0 | 0
2020-08-16 17:00 | 5.6733 | 0 | N/A | 0 | 0
2020-08-16 17:30 | 6.6663 | 0 | N/A | 0 | 0
2020-08-16 18:00 | 7.4571 | 0 | N/A | 0 | 0
2020-08-16 18:30 | 7.88 | 0 | N/A | 0 | 0
2020-08-16 19:00 | 7.7267 | 0 | N/A | 0 | 0
2020-08-16 19:30 | 7.3133 | 0 | N/A | 0 | 0
2020-08-16 20:00 | 6.8435 | 0 | N/A | 0 | 0
2020-08-16 20:30 | 6.2631 | 0 | N/A | 0 | 0
2020-08-16 21:00 | 5.9643 | 0 | N/A | 0 | 0
2020-08-16 21:30 | 6.4452 | 0 | N/A | 0 | 0
2020-08-16 22:00 | 6.6903 | 0 | N/A | 0 | 0
2020-08-16 22:30 | 6.2647 | 0 | N/A | 0 | 0
2020-08-16 23:00 | 6.2181 | 0 | N/A | 0 | 0
2020-08-16 23:30 | 6.2582 | 0 | N/A | 0 | 0
2020-08-17 | 6.7181 | 0 | N/A | 0 | 0
2020-08-17 00:30 | 6.004 | 0 | N/A | 0 | 0
2020-08-17 01:00 | 5.2197 | 0 | N/A | 0 | 0
2020-08-17 01:30 | 5.1082 | 0 | N/A | 0 | 0
2020-08-17 02:00 | 4.7331 | 0 | N/A | 0 | 0
2020-08-17 02:30 | 4.0509 | 0 | N/A | 0 | 0
2020-08-17 03:00 | 3.6535 | 0 | N/A | 0 | 0
2020-08-17 03:30 | 3.3702 | 0 | N/A | 0 | 0
2020-08-17 04:00 | 3.1784 | 0 | N/A | 0 | 0
2020-08-17 04:30 | 3.1206 | 0 | N/A | 0 | 0
2020-08-17 05:00 | 3.1733 | 0 | N/A | 0 | 0
2020-08-17 05:30 | 3.4671 | 0 | N/A | 0 | 0
2020-08-17 06:00 | 3.7814 | 0 | N/A | 0 | 0
2020-08-17 06:30 | 4.48 | 0 | N/A | 0 | 0
2020-08-17 07:00 | 5.0182 | 0 | N/A | 0 | 0
2020-08-17 07:30 | 5.0902 | 0 | N/A | 0 | 0
2020-08-17 08:00 | 5.6807 | 0 | N/A | 0 | 0
2020-08-17 08:30 | 6.6274 | 0 | N/A | 0 | 0
2020-08-17 09:00 | 6.7243 | 0 | N/A | 0 | 0
2020-08-17 09:30 | 6.4878 | 0 | N/A | 0 | 0
2020-08-17 10:00 | 6.0213 | 0 | N/A | 0 | 0
2020-08-17 10:30 | 5.3752 | 0 | N/A | 0 | 0
2020-08-17 11:00 | 4.605 | 0 | N/A | 0 | 0
2020-08-17 11:30 | 4.1404 | 0 | N/A | 0 | 0
2020-08-17 12:00 | 3.8431 | 0 | N/A | 0 | 0
2020-08-17 12:30 | 3.1499 | 0 | N/A | 0 | 0
2020-08-17 13:00 | 2.768 | 0 | N/A | 0 | 0
2020-08-17 13:30 | 2.8173 | 0 | N/A | 0 | 0
2020-08-17 14:00 | 2.8797 | 0 | N/A | 0 | 0
2020-08-17 14:30 | 3.2719 | 0 | N/A | 0 | 0
2020-08-17 15:00 | 4.6674 | 0 | N/A | 0 | 0
2020-08-17 15:30 | 4.8049 | 0 | N/A | 0 | 0
2020-08-17 16:00 | 5.6265 | 0 | N/A | 0 | 0
2020-08-17 16:30 | 6.019 | 0 | N/A | 0 | 0
2020-08-17 17:00 | 6.2334 | 0 | N/A | 0 | 0
2020-08-17 17:30 | 6.8367 | 0 | N/A | 0 | 0
2020-08-17 18:00 | 7.5 | 0 | N/A | 0 | 0
2020-08-17 18:30 | 7.9401 | 0 | N/A | 0 | 0
2020-08-17 19:00 | 7.7734 | 0 | N/A | 0 | 0
2020-08-17 19:30 | 7.45 | 0 | N/A | 0 | 0
2020-08-17 20:00 | 7.0967 | 0 | N/A | 0 | 0
2020-08-17 20:30 | 6.6467 | 0 | N/A | 0 | 0
2020-08-17 21:00 | 6.344 | 0 | N/A | 0 | 0
2020-08-17 21:30 | 6.5577 | 0 | N/A | 0 | 0
2020-08-17 22:00 | 6.7078 | 0 | N/A | 0 | 0
2020-08-17 22:30 | 6.1305 | 0 | N/A | 0 | 0
2020-08-17 23:00 | 6.0774 | 0 | N/A | 0 | 0
2020-08-17 23:30 | 6.155 | 0 | N/A | 0 | 0
2020-08-18 | 6.4257 | 0 | N/A | 0 | 0
2020-08-18 00:30 | 5.7931 | 0 | N/A | 0 | 0
2020-08-18 01:00 | 5.0157 | 0 | N/A | 0 | 0
2020-08-18 01:30 | 4.952 | 0 | N/A | 0 | 0
2020-08-18 02:00 | 4.5329 | 0 | N/A | 0 | 0
2020-08-18 02:30 | 3.8341 | 0 | N/A | 0 | 0
2020-08-18 03:00 | 3.4045 | 0 | N/A | 0 | 0
2020-08-18 03:30 | 3.1255 | 0 | N/A | 0 | 0
2020-08-18 04:00 | 3.0287 | 0 | N/A | 0 | 0
2020-08-18 04:30 | 3.01 | 0 | N/A | 0 | 0
2020-08-18 05:00 | 3.0823 | 0 | N/A | 0 | 0
2020-08-18 05:30 | 3.3827 | 0 | N/A | 0 | 0
2020-08-18 06:00 | 3.7743 | 0 | N/A | 0 | 0
2020-08-18 06:30 | 4.5573 | 0 | N/A | 0 | 0
2020-08-18 07:00 | 5.129 | 0 | N/A | 0 | 0
2020-08-18 07:30 | 5.2922 | 0 | N/A | 0 | 0
2020-08-18 08:00 | 5.8805 | 0 | N/A | 0 | 0
2020-08-18 08:30 | 6.093 | 0 | N/A | 0 | 0
2020-08-18 09:00 | 6.4618 | 0 | N/A | 0 | 0
2020-08-18 09:30 | 5.6501 | 0 | N/A | 0 | 0
2020-08-18 10:00 | 4.6932 | 0 | N/A | 0 | 0
2020-08-18 10:30 | 4.3633 | 0 | N/A | 0 | 0
2020-08-18 11:00 | 4.0734 | 0 | N/A | 0 | 0
2020-08-18 11:30 | 3.6764 | 0 | N/A | 0 | 0
2020-08-18 12:00 | 3.7962 | 0 | N/A | 0 | 0
2020-08-18 12:30 | 3.9075 | 0 | N/A | 0 | 0
2020-08-18 13:00 | 3.6629 | 0 | N/A | 0 | 0
2020-08-18 13:30 | 4.0862 | 0 | N/A | 0 | 0
2020-08-18 14:00 | 4.0684 | 0 | N/A | 0 | 0
2020-08-18 14:30 | 3.4802 | 0 | N/A | 0 | 0
2020-08-18 15:00 | 4.2058 | 0 | N/A | 0 | 0
2020-08-18 15:30 | 5.3473 | 0 | N/A | 0 | 0
2020-08-18 16:00 | 6.1269 | 0 | N/A | 0 | 0
2020-08-18 16:30 | 6.7206 | 0 | N/A | 0 | 0
2020-08-18 17:00 | 7.4767 | 0 | N/A | 0 | 0
2020-08-18 17:30 | 6.7035 | 0 | N/A | 0 | 0
2020-08-18 18:00 | 8.0136 | 0 | N/A | 0 | 0
2020-08-18 18:30 | 8.3172 | 0 | N/A | 0 | 0
2020-08-18 19:00 | 8.054 | 0 | N/A | 0 | 0
2020-08-18 19:30 | 7.5534 | 0 | N/A | 0 | 0
2020-08-18 20:00 | 7.2067 | 0 | N/A | 0 | 0
2020-08-18 20:30 | 6.9067 | 0 | N/A | 0 | 0
2020-08-18 21:00 | 6.4972 | 0 | N/A | 0 | 0
2020-08-18 21:30 | 6.7974 | 0 | N/A | 0 | 0
2020-08-18 22:00 | 6.8408 | 0 | N/A | 0 | 0
2020-08-18 22:30 | 6.2489 | 0 | N/A | 0 | 0
2020-08-18 23:00 | 6.0772 | 0 | N/A | 0 | 0
2020-08-18 23:30 | 6.2387 | 0 | N/A | 0 | 0
2020-08-19 | 6.6666 | 0 | N/A | 0 | 0
2020-08-19 00:30 | 5.9734 | 0 | N/A | 0 | 0
2020-08-19 01:00 | 5.2161 | 0 | N/A | 0 | 0
2020-08-19 01:30 | 5.2112 | 0 | N/A | 0 | 0
2020-08-19 02:00 | 4.7679 | 0 | N/A | 0 | 0
2020-08-19 02:30 | 4.1099 | 0 | N/A | 0 | 0
2020-08-19 03:00 | 3.5412 | 0 | N/A | 0 | 0
2020-08-19 03:30 | 3.3303 | 0 | N/A | 0 | 0
2020-08-19 04:00 | 3.268 | 0 | N/A | 0 | 0
2020-08-19 04:30 | 3.0759 | 0 | N/A | 0 | 0
2020-08-19 05:00 | 3.1883 | 0 | N/A | 0 | 0
2020-08-19 05:30 | 3.5204 | 0 | N/A | 0 | 0
2020-08-19 06:00 | 3.8676 | 0 | N/A | 0 | 0
2020-08-19 06:30 | 4.6755 | 0 | N/A | 0 | 0
2020-08-19 07:00 | 5.1856 | 0 | N/A | 0 | 0
2020-08-19 07:30 | 5.4933 | 0 | N/A | 0 | 0
2020-08-19 08:00 | 6.3451 | 0 | N/A | 0 | 0
2020-08-19 08:30 | 6.9816 | 0 | N/A | 0 | 0
2020-08-19 09:00 | 7.3426 | 0 | N/A | 0 | 0
2020-08-19 09:30 | 7.446 | 0 | N/A | 0 | 0
2020-08-19 10:00 | 7.1337 | 0 | N/A | 0 | 0
2020-08-19 10:30 | 6.8695 | 0 | N/A | 0 | 0
2020-08-19 11:00 | 6.9556 | 0 | N/A | 0 | 0
2020-08-19 11:30 | 7.1699 | 0 | N/A | 0 | 0
2020-08-19 12:00 | 7.2897 | 0 | N/A | 0 | 0
2020-08-19 13:00 | 6.934 | 0 | N/A | 0 | 0
2020-08-19 13:30 | 7.1747 | 0 | N/A | 0 | 0
2020-08-19 14:00 | 7.0965 | 0 | N/A | 0 | 0
2020-08-19 14:30 | 6.7487 | 0 | N/A | 0 | 0
2020-08-19 15:00 | 5.7838 | 0 | N/A | 0 | 0
2020-08-19 15:30 | 5.5515 | 0 | N/A | 0 | 0
2020-08-19 16:00 | 5.7659 | 0 | N/A | 0 | 0
2020-08-19 16:30 | 5.8229 | 0 | N/A | 0 | 0
2020-08-19 17:00 | 6.71 | 0 | N/A | 0 | 0
2020-08-19 17:30 | 7.46 | 0 | N/A | 0 | 0
2020-08-19 18:00 | 8.29 | 0 | N/A | 0 | 0
2020-08-19 18:30 | 8.584 | 0 | N/A | 0 | 0
2020-08-19 19:00 | 8.5914 | 0 | N/A | 0 | 0
2020-08-19 19:30 | 8.2071 | 0 | N/A | 0 | 0
2020-08-19 20:00 | 7.8633 | 0 | N/A | 0 | 0
2020-08-19 20:30 | 7.4334 | 0 | N/A | 0 | 0
2020-08-19 21:00 | 7.0003 | 0 | N/A | 0 | 0
2020-08-19 21:30 | 7.1839 | 0 | N/A | 0 | 0
2020-08-19 22:00 | 7.4038 | 0 | N/A | 0 | 0
2020-08-19 22:30 | 6.8986 | 0 | N/A | 0 | 0
2020-08-19 23:00 | 6.6668 | 0 | N/A | 0 | 0
2020-08-19 23:30 | 6.7037 | 0 | N/A | 0 | 0
2020-08-20 | 7.0901 | 0 | N/A | 0 | 0
2020-08-20 00:30 | 6.4456 | 0 | N/A | 0 | 0
2020-08-20 01:00 | 5.6812 | 0 | N/A | 0 | 0
2020-08-20 01:30 | 5.625 | 0 | N/A | 0 | 0
2020-08-20 02:00 | 5.1735 | 0 | N/A | 0 | 0
2020-08-20 02:30 | 4.546 | 0 | N/A | 0 | 0
2020-08-20 03:00 | 4.1145 | 0 | N/A | 0 | 0
2020-08-20 03:30 | 3.8053 | 0 | N/A | 0 | 0
2020-08-20 04:00 | 3.6113 | 0 | N/A | 0 | 0
2020-08-20 04:30 | 3.5416 | 0 | N/A | 0 | 0
2020-08-20 05:00 | 3.6124 | 0 | N/A | 0 | 0
2020-08-20 05:30 | 3.8367 | 0 | N/A | 0 | 0
2020-08-20 06:00 | 4.1702 | 0 | N/A | 0 | 0
2020-08-20 06:30 | 5.0121 | 0 | N/A | 0 | 0
2020-08-20 07:00 | 5.5374 | 0 | N/A | 0 | 0
2020-08-20 07:30 | 5.9334 | 0 | N/A | 0 | 0
2020-08-20 08:00 | 6.9218 | 0 | N/A | 0 | 0
2020-08-20 08:30 | 7.4985 | 0 | N/A | 0 | 0
2020-08-20 09:00 | 7.6498 | 0 | N/A | 0 | 0
2020-08-20 09:30 | 7.1796 | 0 | N/A | 0 | 0
2020-08-20 10:00 | 6.294 | 0 | N/A | 0 | 0
2020-08-20 10:30 | 5.2103 | 0 | N/A | 0 | 0
2020-08-20 11:00 | 4.5109 | 0 | N/A | 0 | 0
2020-08-20 11:30 | 4.3896 | 0 | N/A | 0 | 0
2020-08-20 12:00 | 4.4118 | 0 | N/A | 0 | 0
2020-08-20 12:30 | 5.3386 | 0 | N/A | 0 | 0
2020-08-20 13:00 | 5.4152 | 0 | N/A | 0 | 0
2020-08-20 13:30 | 5.2228 | 0 | N/A | 0 | 0
2020-08-20 14:00 | 4.7198 | 0 | N/A | 0 | 0
2020-08-20 14:30 | 4.3004 | 0 | N/A | 0 | 0
2020-08-20 15:00 | 4.6535 | 0 | N/A | 0 | 0
2020-08-20 15:30 | 5.42 | 0 | N/A | 0 | 0
2020-08-20 16:00 | 5.1968 | 0 | N/A | 0 | 0
2020-08-20 16:30 | 5.3628 | 0 | N/A | 0 | 0
2020-08-20 17:00 | 5.7984 | 0 | N/A | 0 | 0
2020-08-20 17:30 | 6.8935 | 0 | N/A | 0 | 0
2020-08-20 18:00 | 7.9433 | 0 | N/A | 0 | 0
2020-08-20 18:30 | 8.5575 | 0 | N/A | 0 | 0
2020-08-20 19:00 | 8.3944 | 0 | N/A | 0 | 0
2020-08-20 19:30 | 7.9903 | 0 | N/A | 0 | 0
2020-08-20 20:00 | 7.5833 | 0 | N/A | 0 | 0
2020-08-20 20:30 | 7.2567 | 0 | N/A | 0 | 0
2020-08-20 21:00 | 6.9403 | 0 | N/A | 0 | 0
2020-08-20 21:30 | 7.2173 | 0 | N/A | 0 | 0
2020-08-20 22:00 | 7.3439 | 0 | N/A | 0 | 0
2020-08-20 22:30 | 6.652 | 0 | N/A | 0 | 0
2020-08-20 23:00 | 6.3506 | 0 | N/A | 0 | 0
2020-08-20 23:30 | 6.579 | 0 | N/A | 0 | 0
2020-08-21 | 7.0539 | 0 | N/A | 0 | 0
2020-08-21 00:30 | 6.3524 | 0 | N/A | 0 | 0
2020-08-21 01:00 | 5.5613 | 0 | N/A | 0 | 0
2020-08-21 01:30 | 5.5061 | 0 | N/A | 0 | 0
2020-08-21 02:00 | 4.9584 | 0 | N/A | 0 | 0
2020-08-21 02:30 | 4.328 | 0 | N/A | 0 | 0
2020-08-21 03:00 | 3.8362 | 0 | N/A | 0 | 0
2020-08-21 03:30 | 3.572 | 0 | N/A | 0 | 0
2020-08-21 04:00 | 3.4602 | 0 | N/A | 0 | 0
2020-08-21 04:30 | 3.4328 | 0 | N/A | 0 | 0
2020-08-21 05:00 | 3.5232 | 0 | N/A | 0 | 0
2020-08-21 05:30 | 3.8034 | 0 | N/A | 0 | 0
2020-08-21 06:00 | 4.2059 | 0 | N/A | 0 | 0
2020-08-21 06:30 | 5.1129 | 0 | N/A | 0 | 0
2020-08-21 07:00 | 5.6107 | 0 | N/A | 0 | 0
2020-08-21 07:30 | 5.5741 | 0 | N/A | 0 | 0
2020-08-21 08:00 | 5.9615 | 0 | N/A | 0 | 0
2020-08-21 08:30 | 6.3602 | 0 | N/A | 0 | 0
2020-08-21 09:00 | 6.5746 | 0 | N/A | 0 | 0
2020-08-21 09:30 | 5.3172 | 0 | N/A | 0 | 0
2020-08-21 10:00 | 4.7501 | 0 | N/A | 0 | 0
2020-08-21 10:30 | 4.3634 | 0 | N/A | 0 | 0
2020-08-21 11:00 | 4.5837 | 0 | N/A | 0 | 0
2020-08-21 11:30 | 4.5437 | 0 | N/A | 0 | 0
2020-08-21 12:00 | 4.6267 | 0 | N/A | 0 | 0
2020-08-21 12:30 | 4.87 | 0 | N/A | 0 | 0
2020-08-21 13:00 | 6.1933 | 0 | N/A | 0 | 0
2020-08-21 13:30 | 6.758 | 0 | N/A | 0 | 0
2020-08-21 14:00 | 4.7028 | 0 | N/A | 0 | 0
2020-08-21 14:30 | 5.1636 | 0 | N/A | 0 | 0
2020-08-21 15:00 | 5.3835 | 0 | N/A | 0 | 0
2020-08-21 15:30 | 4.8737 | 0 | N/A | 0 | 0
2020-08-21 16:00 | 5.4168 | 0 | N/A | 0 | 0
2020-08-21 16:30 | 5.7534 | 0 | N/A | 0 | 0
2020-08-21 17:00 | 6.2968 | 0 | N/A | 0 | 0
2020-08-21 17:30 | 7.2967 | 0 | N/A | 0 | 0
2020-08-21 18:00 | 8.3072 | 0 | N/A | 0 | 0
2020-08-21 18:30 | 8.9489 | 0 | N/A | 0 | 0
2020-08-21 19:00 | 9.2026 | 0 | N/A | 0 | 0
2020-08-21 19:30 | 8.8546 | 0 | N/A | 0 | 0
2020-08-21 20:00 | 8.5444 | 0 | N/A | 0 | 0
2020-08-21 20:30 | 7.9968 | 0 | N/A | 0 | 0
2020-08-21 21:00 | 7.5733 | 0 | N/A | 0 | 0
2020-08-21 21:30 | 7.8667 | 0 | N/A | 0 | 0
2020-08-21 22:00 | 8.2033 | 0 | N/A | 0 | 0
2020-08-21 22:30 | 7.6146 | 0 | N/A | 0 | 0
2020-08-21 23:00 | 7.3404 | 0 | N/A | 0 | 0
2020-08-21 23:30 | 7.3094 | 0 | N/A | 0 | 0
2020-08-22 | 7.7294 | 0 | N/A | 0 | 0
2020-08-22 00:30 | 7.0542 | 0 | N/A | 0 | 0
2020-08-22 01:00 | 6.2375 | 0 | N/A | 0 | 0
2020-08-22 01:30 | 6.1 | 0 | N/A | 0 | 0
2020-08-22 02:00 | 5.7349 | 0 | N/A | 0 | 0
2020-08-22 02:30 | 5.0121 | 0 | N/A | 0 | 0
2020-08-22 03:00 | 4.5621 | 0 | N/A | 0 | 0
2020-08-22 03:30 | 4.3557 | 0 | N/A | 0 | 0
2020-08-22 04:00 | 4.0904 | 0 | N/A | 0 | 0
2020-08-22 04:30 | 4.0792 | 0 | N/A | 0 | 0
2020-08-22 05:00 | 4.0739 | 0 | N/A | 0 | 0
2020-08-22 05:30 | 4.1154 | 0 | N/A | 0 | 0
2020-08-22 06:00 | 4.2801 | 0 | N/A | 0 | 0
2020-08-22 06:30 | 4.6124 | 0 | N/A | 0 | 0
2020-08-22 07:00 | 4.9125 | 0 | N/A | 0 | 0
2020-08-22 07:30 | 4.8723 | 0 | N/A | 0 | 0
2020-08-22 08:00 | 5.7025 | 0 | N/A | 0 | 0
2020-08-22 08:30 | 6.4667 | 0 | N/A | 0 | 0
2020-08-22 09:00 | 7.2435 | 0 | N/A | 0 | 0
2020-08-22 09:30 | 7.17 | 0 | N/A | 0 | 0
2020-08-22 10:00 | 7.28 | 0 | N/A | 0 | 0
2020-08-22 10:30 | 7.3935 | 0 | N/A | 0 | 0
2020-08-22 11:00 | 7.0567 | 0 | N/A | 0 | 0
2020-08-22 11:30 | 7.7474 | 0 | N/A | 0 | 0
2020-08-22 12:00 | 7.3903 | 0 | N/A | 0 | 0
2020-08-22 12:30 | 6.1701 | 0 | N/A | 0 | 0
2020-08-22 13:00 | 5.3034 | 0 | N/A | 0 | 0
2020-08-22 13:30 | 6.7134 | 0 | N/A | 0 | 0
2020-08-22 14:00 | 7.52 | 0 | N/A | 0 | 0
2020-08-22 14:30 | 7.9068 | 0 | N/A | 0 | 0
2020-08-22 15:00 | 8.4272 | 0 | N/A | 0 | 0
2020-08-22 15:30 | 8.634 | 0 | N/A | 0 | 0
2020-08-22 16:00 | 8.8282 | 0 | N/A | 0 | 0
2020-08-22 16:30 | 8.4679 | 0 | N/A | 0 | 0
2020-08-22 17:00 | 8.9061 | 0 | N/A | 0 | 0
2020-08-22 17:30 | 9.5938 | 0 | N/A | 0 | 0
2020-08-22 18:00 | 10.1087 | 0 | N/A | 0 | 0
2020-08-22 18:30 | 10.0257 | 0 | N/A | 0 | 0
2020-08-22 19:00 | 9.7615 | 0 | N/A | 0 | 0
2020-08-22 19:30 | 9.2937 | 0 | N/A | 0 | 0
2020-08-22 20:00 | 8.6886 | 0 | N/A | 0 | 0
2020-08-22 20:30 | 8.1501 | 0 | N/A | 0 | 0
2020-08-22 21:00 | 7.8333 | 0 | N/A | 0 | 0
2020-08-22 21:30 | 8.12 | 0 | N/A | 0 | 0
2020-08-22 22:00 | 8.2933 | 0 | N/A | 0 | 0
2020-08-22 22:30 | 7.8106 | 0 | N/A | 0 | 0
2020-08-22 23:00 | 7.6749 | 0 | N/A | 0 | 0
2020-08-22 23:30 | 7.7987 | 0 | N/A | 0 | 0
2020-08-23 | 8.1778 | 0 | N/A | 0 | 0
2020-08-23 00:30 | 7.4775 | 0 | N/A | 0 | 0
2020-08-23 01:00 | 6.5323 | 0 | N/A | 0 | 0
2020-08-23 01:30 | 6.4092 | 0 | N/A | 0 | 0
2020-08-23 02:00 | 6.0665 | 0 | N/A | 0 | 0
2020-08-23 02:30 | 5.3785 | 0 | N/A | 0 | 0
2020-08-23 03:00 | 4.8072 | 0 | N/A | 0 | 0
2020-08-23 03:30 | 4.5765 | 0 | N/A | 0 | 0
2020-08-23 04:00 | 4.278 | 0 | N/A | 0 | 0
2020-08-23 04:30 | 4.2036 | 0 | N/A | 0 | 0
2020-08-23 05:00 | 4.1069 | 0 | N/A | 0 | 0
2020-08-23 05:30 | 4.1097 | 0 | N/A | 0 | 0
2020-08-23 06:00 | 4.1645 | 0 | N/A | 0 | 0
2020-08-23 06:30 | 4.4821 | 0 | N/A | 0 | 0
2020-08-23 07:00 | 4.565 | 0 | N/A | 0 | 0
2020-08-23 07:30 | 4.4458 | 0 | N/A | 0 | 0
2020-08-23 08:00 | 4.9268 | 0 | N/A | 0 | 0
2020-08-23 08:30 | 5.3578 | 0 | N/A | 0 | 0
2020-08-23 09:00 | 5.7016 | 0 | N/A | 0 | 0
2020-08-23 09:30 | 5.865 | 0 | N/A | 0 | 0
2020-08-23 10:00 | 5.8294 | 0 | N/A | 0 | 0
2020-08-23 10:30 | 5.9616 | 0 | N/A | 0 | 0
2020-08-23 11:00 | 5.468 | 0 | N/A | 0 | 0
2020-08-23 11:30 | 5.0314 | 0 | N/A | 0 | 0
2020-08-23 12:00 | 4.7452 | 0 | N/A | 0 | 0
2020-08-23 12:30 | 4.8893 | 0 | N/A | 0 | 0
2020-08-23 13:00 | 5.1321 | 0 | N/A | 0 | 0
2020-08-23 13:30 | 4.9257 | 0 | N/A | 0 | 0
2020-08-23 14:00 | 4.82 | 0 | N/A | 0 | 0
2020-08-23 14:30 | 5.1494 | 0 | N/A | 0 | 0
2020-08-23 15:00 | 4.9564 | 0 | N/A | 0 | 0
2020-08-23 15:30 | 5.4258 | 0 | N/A | 0 | 0
2020-08-23 16:00 | 5.8383 | 0 | N/A | 0 | 0
2020-08-23 16:30 | 6.0481 | 0 | N/A | 0 | 0
2020-08-23 17:00 | 6.7743 | 0 | N/A | 0 | 0
2020-08-23 17:30 | 7.6767 | 0 | N/A | 0 | 0
2020-08-23 18:00 | 8.6401 | 0 | N/A | 0 | 0
2020-08-23 18:30 | 9.1743 | 0 | N/A | 0 | 0
2020-08-23 19:00 | 9.1179 | 0 | N/A | 0 | 0
2020-08-23 19:30 | 8.6068 | 0 | N/A | 0 | 0
2020-08-23 20:00 | 8.15 | 0 | N/A | 0 | 0
2020-08-23 20:30 | 7.5135 | 0 | N/A | 0 | 0
2020-08-23 21:00 | 7.0982 | 0 | N/A | 0 | 0
2020-08-23 21:30 | 7.5577 | 0 | N/A | 0 | 0
2020-08-23 22:00 | 7.7407 | 0 | N/A | 0 | 0
2020-08-23 22:30 | 7.2022 | 0 | N/A | 0 | 0
2020-08-23 23:00 | 7.1458 | 0 | N/A | 0 | 0
2020-08-23 23:30 | 7.0164 | 0 | N/A | 0 | 0
2020-08-24 | 7.3341 | 0 | N/A | 0 | 0
2020-08-24 00:30 | 6.7088 | 0 | N/A | 0 | 0
2020-08-24 01:00 | 5.9749 | 0 | N/A | 0 | 0
2020-08-24 01:30 | 6.0418 | 0 | N/A | 0 | 0
2020-08-24 02:00 | 5.72 | 0 | N/A | 0 | 0
2020-08-24 02:30 | 5.0259 | 0 | N/A | 0 | 0
2020-08-24 03:00 | 4.5891 | 0 | N/A | 0 | 0
2020-08-24 03:30 | 4.2878 | 0 | N/A | 0 | 0
2020-08-24 04:00 | 4.0311 | 0 | N/A | 0 | 0
2020-08-24 04:30 | 3.9009 | 0 | N/A | 0 | 0
2020-08-24 05:00 | 3.8488 | 0 | N/A | 0 | 0
2020-08-24 05:30 | 4.1476 | 0 | N/A | 0 | 0
2020-08-24 06:00 | 4.612 | 0 | N/A | 0 | 0
2020-08-24 06:30 | 5.4789 | 0 | N/A | 0 | 0
2020-08-24 07:00 | 6.0302 | 0 | N/A | 0 | 0
2020-08-24 07:30 | 6.0653 | 0 | N/A | 0 | 0
2020-08-24 08:00 | 6.55 | 0 | N/A | 0 | 0
2020-08-24 08:30 | 6.9167 | 0 | N/A | 0 | 0
2020-08-24 09:00 | 7.1172 | 0 | N/A | 0 | 0
2020-08-24 09:30 | 7.1514 | 0 | N/A | 0 | 0
2020-08-24 10:00 | 6.4508 | 0 | N/A | 0 | 0
2020-08-24 10:30 | 6.2402 | 0 | N/A | 0 | 0
2020-08-24 11:00 | 5.9003 | 0 | N/A | 0 | 0
2020-08-24 11:30 | 5.2085 | 0 | N/A | 0 | 0
2020-08-24 12:00 | 5.1943 | 0 | N/A | 0 | 0
2020-08-24 12:30 | 4.841 | 0 | N/A | 0 | 0
2020-08-24 13:00 | 4.4243 | 0 | N/A | 0 | 0
2020-08-24 13:30 | 4.3709 | 0 | N/A | 0 | 0
2020-08-24 14:00 | 4.8777 | 0 | N/A | 0 | 0
2020-08-24 14:30 | 5.0237 | 0 | N/A | 0 | 0
2020-08-24 15:00 | 5.2637 | 0 | N/A | 0 | 0
2020-08-24 15:30 | 5.3233 | 0 | N/A | 0 | 0
2020-08-24 16:00 | 5.3667 | 0 | N/A | 0 | 0
2020-08-24 16:30 | 6.3667 | 0 | N/A | 0 | 0
2020-08-24 17:00 | 6.85 | 0 | N/A | 0 | 0
2020-08-24 17:30 | 7.66 | 0 | N/A | 0 | 0
2020-08-24 18:00 | 8.5836 | 0 | N/A | 0 | 0
2020-08-24 18:30 | 9.0379 | 0 | N/A | 0 | 0
2020-08-24 19:00 | 8.9717 | 0 | N/A | 0 | 0
2020-08-24 19:30 | 8.5373 | 0 | N/A | 0 | 0
2020-08-24 20:00 | 8.0401 | 0 | N/A | 0 | 0
2020-08-24 20:30 | 7.6067 | 0 | N/A | 0 | 0
2020-08-24 21:00 | 7.37 | 0 | N/A | 0 | 0
2020-08-24 21:30 | 7.7201 | 0 | N/A | 0 | 0
2020-08-24 22:00 | 7.8802 | 0 | N/A | 0 | 0
2020-08-24 22:30 | 7.3792 | 0 | N/A | 0 | 0
2020-08-24 23:00 | 7.2707 | 0 | N/A | 0 | 0
2020-08-24 23:30 | 7.1311 | 0 | N/A | 0 | 0
2020-08-25 | 7.5911 | 0 | N/A | 0 | 0
2020-08-25 00:30 | 7.0048 | 0 | N/A | 0 | 0
2020-08-25 01:00 | 6.2237 | 0 | N/A | 0 | 0
2020-08-25 01:30 | 6.2363 | 0 | N/A | 0 | 0
2020-08-25 02:00 | 5.8553 | 0 | N/A | 0 | 0
2020-08-25 02:30 | 5.166 | 0 | N/A | 0 | 0
2020-08-25 03:00 | 4.7522 | 0 | N/A | 0 | 0
2020-08-25 03:30 | 4.4458 | 0 | N/A | 0 | 0
2020-08-25 04:00 | 4.2262 | 0 | N/A | 0 | 0
2020-08-25 04:30 | 4.1775 | 0 | N/A | 0 | 0
2020-08-25 05:00 | 4.3006 | 0 | N/A | 0 | 0
2020-08-25 05:30 | 4.6086 | 0 | N/A | 0 | 0
2020-08-25 06:00 | 5.1357 | 0 | N/A | 0 | 0
2020-08-25 06:30 | 5.985 | 0 | N/A | 0 | 0
2020-08-25 07:00 | 6.46 | 0 | N/A | 0 | 0
2020-08-25 07:30 | 6.6805 | 0 | N/A | 0 | 0
2020-08-25 08:00 | 7.1767 | 0 | N/A | 0 | 0
2020-08-25 08:30 | 7.1214 | 0 | N/A | 0 | 0
2020-08-25 09:00 | 6.6248 | 0 | N/A | 0 | 0
2020-08-25 09:30 | 5.849 | 0 | N/A | 0 | 0
2020-08-25 10:00 | 4.9494 | 0 | N/A | 0 | 0
2020-08-25 10:30 | 4.2793 | 0 | N/A | 0 | 0
2020-08-25 11:00 | 3.7971 | 0 | N/A | 0 | 0
2020-08-25 11:30 | 3.7702 | 0 | N/A | 0 | 0
2020-08-25 12:00 | 4.6334 | 0 | N/A | 0 | 0
2020-08-25 12:30 | 5.1967 | 0 | N/A | 0 | 0
2020-08-25 13:00 | 5.48 | 0 | N/A | 0 | 0
2020-08-25 13:30 | 5.6401 | 0 | N/A | 0 | 0
2020-08-25 14:00 | 5.4134 | 0 | N/A | 0 | 0
2020-08-25 14:30 | 5.1633 | 0 | N/A | 0 | 0
2020-08-25 15:00 | 5.4533 | 0 | N/A | 0 | 0
2020-08-25 15:30 | 5.3933 | 0 | N/A | 0 | 0
2020-08-25 16:00 | 5.6967 | 0 | N/A | 0 | 0
2020-08-25 16:30 | 6.0538 | 0 | N/A | 0 | 0
2020-08-25 17:00 | 6.6369 | 0 | N/A | 0 | 0
2020-08-25 17:30 | 7.5801 | 0 | N/A | 0 | 0
2020-08-25 18:00 | 8.3301 | 0 | N/A | 0 | 0
2020-08-25 18:30 | 8.8843 | 0 | N/A | 0 | 0
2020-08-25 19:00 | 8.8816 | 0 | N/A | 0 | 0
2020-08-25 19:30 | 8.3637 | 0 | N/A | 0 | 0
2020-08-25 20:00 | 7.91 | 0 | N/A | 0 | 0
2020-08-25 20:30 | 7.3934 | 0 | N/A | 0 | 0
2020-08-25 21:00 | 7.1203 | 0 | N/A | 0 | 0
2020-08-25 21:30 | 7.4077 | 0 | N/A | 0 | 0
2020-08-25 22:00 | 7.4646 | 0 | N/A | 0 | 0
2020-08-25 22:30 | 6.9151 | 0 | N/A | 0 | 0
2020-08-25 23:00 | 6.7313 | 0 | N/A | 0 | 0
2020-08-25 23:30 | 6.7759 | 0 | N/A | 0 | 0
2020-08-26 | 7.1829 | 0 | N/A | 0 | 0
2020-08-26 00:30 | 6.6061 | 0 | N/A | 0 | 0
2020-08-26 01:00 | 5.7446 | 0 | N/A | 0 | 0
2020-08-26 01:30 | 5.6926 | 0 | N/A | 0 | 0
2020-08-26 02:00 | 5.2227 | 0 | N/A | 0 | 0
2020-08-26 02:30 | 4.6059 | 0 | N/A | 0 | 0
2020-08-26 03:00 | 4.2885 | 0 | N/A | 0 | 0
2020-08-26 03:30 | 3.9023 | 0 | N/A | 0 | 0
2020-08-26 04:00 | 3.7781 | 0 | N/A | 0 | 0
2020-08-26 04:30 | 3.7745 | 0 | N/A | 0 | 0
2020-08-26 05:00 | 3.8234 | 0 | N/A | 0 | 0
2020-08-26 05:30 | 4.236 | 0 | N/A | 0 | 0
2020-08-26 06:00 | 4.7044 | 0 | N/A | 0 | 0
2020-08-26 06:30 | 5.5874 | 0 | N/A | 0 | 0
2020-08-26 07:00 | 6.0717 | 0 | N/A | 0 | 0
2020-08-26 07:30 | 6.1337 | 0 | N/A | 0 | 0
2020-08-26 08:00 | 6.6448 | 0 | N/A | 0 | 0
2020-08-26 08:30 | 6.5027 | 0 | N/A | 0 | 0
2020-08-26 09:00 | 6.4765 | 0 | N/A | 0 | 0
2020-08-26 09:30 | 5.5906 | 0 | N/A | 0 | 0
2020-08-26 10:00 | 4.662 | 0 | N/A | 0 | 0
2020-08-26 10:30 | 4.2276 | 0 | N/A | 0 | 0
2020-08-26 11:00 | 5.4933 | 0 | N/A | 0 | 0
2020-08-26 11:30 | 5.4426 | 0 | N/A | 0 | 0
2020-08-26 12:00 | 5.4168 | 0 | N/A | 0 | 0
2020-08-26 12:30 | 4.5055 | 0 | N/A | 0 | 0
2020-08-26 13:00 | 4.1702 | 0 | N/A | 0 | 0
2020-08-26 13:30 | 3.8978 | 0 | N/A | 0 | 0
2020-08-26 14:00 | 3.52 | 0 | N/A | 0 | 0
2020-08-26 14:30 | 3.9714 | 0 | N/A | 0 | 0
2020-08-26 15:00 | 4.1583 | 0 | N/A | 0 | 0
2020-08-26 15:30 | 4.3417 | 0 | N/A | 0 | 0
2020-08-26 16:00 | 4.3768 | 0 | N/A | 0 | 0
2020-08-26 16:30 | 4.9066 | 0 | N/A | 0 | 0
2020-08-26 17:00 | 5.29 | 0 | N/A | 0 | 0
2020-08-26 17:30 | 5.9028 | 0 | N/A | 0 | 0
2020-08-26 18:00 | 7.1602 | 0 | N/A | 0 | 0
2020-08-26 18:30 | 7.92 | 0 | N/A | 0 | 0
2020-08-26 19:00 | 8.0767 | 0 | N/A | 0 | 0
2020-08-26 19:30 | 7.6933 | 0 | N/A | 0 | 0
2020-08-26 20:00 | 7.4267 | 0 | N/A | 0 | 0
2020-08-26 20:30 | 7.08 | 0 | N/A | 0 | 0
2020-08-26 21:00 | 6.7106 | 0 | N/A | 0 | 0
2020-08-26 21:30 | 7.0219 | 0 | N/A | 0 | 0
2020-08-26 22:00 | 7.2676 | 0 | N/A | 0 | 0
2020-08-26 22:30 | 6.8671 | 0 | N/A | 0 | 0
2020-08-26 23:00 | 6.5993 | 0 | N/A | 0 | 0
2020-08-26 23:30 | 6.5986 | 0 | N/A | 0 | 0
2020-08-27 | 7.0031 | 0 | N/A | 0 | 0
2020-08-27 00:30 | 6.2291 | 0 | N/A | 0 | 0
2020-08-27 01:00 | 5.3461 | 0 | N/A | 0 | 0
2020-08-27 01:30 | 5.3199 | 0 | N/A | 0 | 0
2020-08-27 02:00 | 5.0163 | 0 | N/A | 0 | 0
2020-08-27 02:30 | 4.379 | 0 | N/A | 0 | 0
2020-08-27 03:00 | 3.9256 | 0 | N/A | 0 | 0
2020-08-27 03:30 | 3.6403 | 0 | N/A | 0 | 0
2020-08-27 04:00 | 3.4784 | 0 | N/A | 0 | 0
2020-08-27 04:30 | 3.4583 | 0 | N/A | 0 | 0
2020-08-27 05:00 | 3.5208 | 0 | N/A | 0 | 0
2020-08-27 05:30 | 3.7999 | 0 | N/A | 0 | 0
2020-08-27 06:00 | 4.2978 | 0 | N/A | 0 | 0
2020-08-27 06:30 | 5.1098 | 0 | N/A | 0 | 0
2020-08-27 07:00 | 5.7035 | 0 | N/A | 0 | 0
2020-08-27 07:30 | 5.7944 | 0 | N/A | 0 | 0
2020-08-27 08:00 | 6.02 | 0 | N/A | 0 | 0
2020-08-27 08:30 | 5.2542 | 0 | N/A | 0 | 0
2020-08-27 09:00 | 0.11671 | 0 | N/A | 0 | 0
2020-08-27 09:30 | 0 | 0 | N/A | 0 | 0
2020-08-27 10:00 | 0 | 0 | N/A | 0 | 0
2020-08-27 10:30 | 0 | 0 | N/A | 0 | 0
2020-08-27 11:00 | 0 | 0 | N/A | 0 | 0
2020-08-27 12:00 | 0 | 0 | N/A | 0 | 0
2020-08-27 12:30 | 0 | 0 | N/A | 0 | 0
2020-08-27 13:00 | 0 | 0 | N/A | 0 | 0
2020-08-27 13:30 | 0 | 0 | N/A | 0 | 0
2020-08-27 14:00 | 0 | 0 | N/A | 0 | 0
2020-08-27 14:30 | 0 | 0 | N/A | 0 | 0
2020-08-27 15:00 | 0 | 0 | N/A | 0 | 0
2020-08-27 15:30 | 0 | 0 | N/A | 0 | 0
2020-08-27 16:00 | 0 | 0 | N/A | 0 | 0
2020-08-27 16:30 | 0 | 0 | N/A | 0 | 0
2020-08-27 17:00 | 4.9537 | 0 | N/A | 0 | 0
2020-08-27 17:30 | 6.1792 | 0 | N/A | 0 | 0
2020-08-27 18:00 | 7.4401 | 0 | N/A | 0 | 0
2020-08-27 18:30 | 8.3834 | 0 | N/A | 0 | 0
2020-08-27 19:00 | 8.2502 | 0 | N/A | 0 | 0
2020-08-27 19:30 | 7.9267 | 0 | N/A | 0 | 0
2020-08-27 20:00 | 7.6267 | 0 | N/A | 0 | 0
2020-08-27 20:30 | 7.36 | 0 | N/A | 0 | 0
2020-08-27 21:00 | 6.9735 | 0 | N/A | 0 | 0
2020-08-27 21:30 | 7.086 | 0 | N/A | 0 | 0
2020-08-27 22:00 | 7.2755 | 0 | N/A | 0 | 0
2020-08-27 22:30 | 6.8168 | 0 | N/A | 0 | 0
2020-08-27 23:00 | 6.6705 | 0 | N/A | 0 | 0
2020-08-27 23:30 | 6.6722 | 0 | N/A | 0 | 0
2020-08-28 | 7.2188 | 0 | N/A | 0 | 0
2020-08-28 00:30 | 6.3688 | 0 | N/A | 0 | 0
2020-08-28 01:00 | 5.6256 | 0 | N/A | 0 | 0
2020-08-28 01:30 | 5.631 | 0 | N/A | 0 | 0
2020-08-28 02:00 | 5.2519 | 0 | N/A | 0 | 0
2020-08-28 02:30 | 4.6352 | 0 | N/A | 0 | 0
2020-08-28 03:00 | 4.2328 | 0 | N/A | 0 | 0
2020-08-28 03:30 | 3.9215 | 0 | N/A | 0 | 0
2020-08-28 04:00 | 3.79 | 0 | N/A | 0 | 0
2020-08-28 04:30 | 3.7533 | 0 | N/A | 0 | 0
2020-08-28 05:00 | 3.7578 | 0 | N/A | 0 | 0
2020-08-28 05:30 | 4.1005 | 0 | N/A | 0 | 0
2020-08-28 06:00 | 4.5091 | 0 | N/A | 0 | 0
2020-08-28 06:30 | 5.3856 | 0 | N/A | 0 | 0
2020-08-28 07:00 | 5.9433 | 0 | N/A | 0 | 0
2020-08-28 07:30 | 5.9263 | 0 | N/A | 0 | 0
2020-08-28 08:00 | 6.4802 | 0 | N/A | 0 | 0
2020-08-28 08:30 | 6.6939 | 0 | N/A | 0 | 0
2020-08-28 09:00 | 6.3985 | 0 | N/A | 0 | 0
2020-08-28 09:30 | 5.8374 | 0 | N/A | 0 | 0
2020-08-28 10:00 | 4.9447 | 0 | N/A | 0 | 0
2020-08-28 10:30 | 4.1048 | 0 | N/A | 0 | 0
2020-08-28 11:00 | 3.1667 | 0 | N/A | 0 | 0
2020-08-28 11:30 | 2.6103 | 0 | N/A | 0 | 0
2020-08-28 12:00 | 2.2971 | 0 | N/A | 0 | 0
2020-08-28 12:30 | 1.9769 | 0 | N/A | 0 | 0
2020-08-28 13:00 | 1.4868 | 0 | N/A | 0 | 0
2020-08-28 13:30 | 1.4533 | 0 | N/A | 0 | 0
2020-08-28 14:00 | 1.31 | 0 | N/A | 0 | 0
2020-08-28 14:30 | 1.3469 | 0 | N/A | 0 | 0
2020-08-28 15:00 | 1.5437 | 0 | N/A | 0 | 0
2020-08-28 15:30 | 1.7221 | 0 | N/A | 0 | 0
2020-08-28 16:00 | 2.1879 | 0 | N/A | 0 | 0
2020-08-28 16:30 | 2.7125 | 0 | N/A | 0 | 0
2020-08-28 17:00 | 3.5902 | 0 | N/A | 0 | 0
2020-08-28 17:30 | 4.7012 | 0 | N/A | 0 | 0
2020-08-28 18:00 | 5.9487 | 0 | N/A | 0 | 0
2020-08-28 18:30 | 6.9469 | 0 | N/A | 0 | 0
2020-08-28 19:00 | 7.4867 | 0 | N/A | 0 | 0
2020-08-28 19:30 | 7.19 | 0 | N/A | 0 | 0
2020-08-28 20:00 | 6.9601 | 0 | N/A | 0 | 0
2020-08-28 20:30 | 6.6542 | 0 | N/A | 0 | 0
2020-08-28 21:00 | 6.5573 | 0 | N/A | 0 | 0
2020-08-28 21:30 | 6.8922 | 0 | N/A | 0 | 0
2020-08-28 22:00 | 7.1988 | 0 | N/A | 0 | 0
2020-08-28 22:30 | 6.7489 | 0 | N/A | 0 | 0
2020-08-28 23:00 | 6.6235 | 0 | N/A | 0 | 0
2020-08-28 23:30 | 6.7676 | 0 | N/A | 0 | 0
2020-08-29 | 7.0274 | 0 | N/A | 0 | 0
2020-08-29 00:30 | 6.0741 | 0 | N/A | 0 | 0
2020-08-29 01:00 | 5.3656 | 0 | N/A | 0 | 0
2020-08-29 01:30 | 5.3473 | 0 | N/A | 0 | 0
2020-08-29 02:00 | 4.8756 | 0 | N/A | 0 | 0
2020-08-29 02:30 | 4.1783 | 0 | N/A | 0 | 0
2020-08-29 03:00 | 3.8177 | 0 | N/A | 0 | 0
2020-08-29 03:30 | 3.6606 | 0 | N/A | 0 | 0
2020-08-29 04:00 | 3.4752 | 0 | N/A | 0 | 0
2020-08-29 04:30 | 3.376 | 0 | N/A | 0 | 0
2020-08-29 05:00 | 3.3904 | 0 | N/A | 0 | 0
2020-08-29 05:30 | 3.4857 | 0 | N/A | 0 | 0
2020-08-29 06:00 | 3.665 | 0 | N/A | 0 | 0
2020-08-29 06:30 | 4.0815 | 0 | N/A | 0 | 0
2020-08-29 07:00 | 4.3148 | 0 | N/A | 0 | 0
2020-08-29 07:30 | 4.2228 | 0 | N/A | 0 | 0
2020-08-29 08:00 | 4.3187 | 0 | N/A | 0 | 0
2020-08-29 08:30 | 4.2816 | 0 | N/A | 0 | 0
2020-08-29 09:00 | 3.8644 | 0 | N/A | 0 | 0
2020-08-29 09:30 | 3.2324 | 0 | N/A | 0 | 0
2020-08-29 10:00 | 2.5279 | 0 | N/A | 0 | 0
2020-08-29 10:30 | 1.9299 | 0 | N/A | 0 | 0
2020-08-29 11:00 | 1.429 | 0 | N/A | 0 | 0
2020-08-29 11:30 | 1.0187 | 0 | N/A | 0 | 0
2020-08-29 12:00 | 0.72946 | 0 | N/A | 0 | 0
2020-08-29 12:30 | 0.68898 | 0 | N/A | 0 | 0
2020-08-29 13:00 | 0.56652 | 0 | N/A | 0 | 0
2020-08-29 13:30 | 0.56436 | 0 | N/A | 0 | 0
2020-08-29 14:00 | 0.57144 | 0 | N/A | 0 | 0
2020-08-29 14:30 | 0.6738 | 0 | N/A | 0 | 0
2020-08-29 15:00 | 0.80145 | 0 | N/A | 0 | 0
2020-08-29 15:30 | 1.1495 | 0 | N/A | 0 | 0
2020-08-29 16:00 | 1.6887 | 0 | N/A | 0 | 0
2020-08-29 16:30 | 2.4404 | 0 | N/A | 0 | 0
2020-08-29 17:00 | 3.4785 | 0 | N/A | 0 | 0
2020-08-29 17:30 | 4.5911 | 0 | N/A | 0 | 0
2020-08-29 18:00 | 5.8278 | 0 | N/A | 0 | 0
2020-08-29 18:30 | 6.8979 | 0 | N/A | 0 | 0
2020-08-29 19:00 | 7.27 | 0 | N/A | 0 | 0
2020-08-29 19:30 | 7.0034 | 0 | N/A | 0 | 0
2020-08-29 20:00 | 6.6838 | 0 | N/A | 0 | 0
2020-08-29 20:30 | 6.1857 | 0 | N/A | 0 | 0
2020-08-29 21:00 | 5.8643 | 0 | N/A | 0 | 0
2020-08-29 21:30 | 6.2811 | 0 | N/A | 0 | 0
2020-08-29 22:00 | 6.6139 | 0 | N/A | 0 | 0
2020-08-29 22:30 | 6.2189 | 0 | N/A | 0 | 0
2020-08-29 23:00 | 6.2981 | 0 | N/A | 0 | 0
2020-08-29 23:30 | 6.4194 | 0 | N/A | 0 | 0
2020-08-30 | 6.6815 | 0 | N/A | 0 | 0
2020-08-30 00:30 | 6.0218 | 0 | N/A | 0 | 0
2020-08-30 01:00 | 5.1974 | 0 | N/A | 0 | 0
2020-08-30 01:30 | 5.0986 | 0 | N/A | 0 | 0
2020-08-30 02:00 | 4.6463 | 0 | N/A | 0 | 0
2020-08-30 02:30 | 4.0369 | 0 | N/A | 0 | 0
2020-08-30 03:00 | 3.68 | 0 | N/A | 0 | 0
2020-08-30 03:30 | 3.4314 | 0 | N/A | 0 | 0
2020-08-30 04:00 | 3.2078 | 0 | N/A | 0 | 0
2020-08-30 04:30 | 3.0885 | 0 | N/A | 0 | 0
2020-08-30 05:00 | 3.0298 | 0 | N/A | 0 | 0
2020-08-30 05:30 | 3.1255 | 0 | N/A | 0 | 0
2020-08-30 06:00 | 3.2531 | 0 | N/A | 0 | 0
2020-08-30 06:30 | 3.5636 | 0 | N/A | 0 | 0
2020-08-30 07:00 | 3.6551 | 0 | N/A | 0 | 0
2020-08-30 07:30 | 3.4272 | 0 | N/A | 0 | 0
2020-08-30 08:00 | 3.3174 | 0 | N/A | 0 | 0
2020-08-30 08:30 | 3.6832 | 0 | N/A | 0 | 0
2020-08-30 09:00 | 3.6905 | 0 | N/A | 0 | 0
2020-08-30 09:30 | 2.8917 | 0 | N/A | 0 | 0
2020-08-30 10:00 | 3.5022 | 0 | N/A | 0 | 0
2020-08-30 10:30 | 3.417 | 0 | N/A | 0 | 0
2020-08-30 11:00 | 4.595 | 0 | N/A | 0 | 0
2020-08-30 11:30 | 4.8129 | 0 | N/A | 0 | 0
2020-08-30 12:00 | 4.6324 | 0 | N/A | 0 | 0
2020-08-30 12:30 | 4.9822 | 0 | N/A | 0 | 0
2020-08-30 13:00 | 4.7475 | 0 | N/A | 0 | 0
2020-08-30 13:30 | 4.9832 | 0 | N/A | 0 | 0
2020-08-30 14:00 | 5.6075 | 0 | N/A | 0 | 0
2020-08-30 14:30 | 6.0091 | 0 | N/A | 0 | 0
2020-08-30 15:00 | 6.1166 | 0 | N/A | 0 | 0
2020-08-30 15:30 | 6.2915 | 0 | N/A | 0 | 0
2020-08-30 16:00 | 6.2455 | 0 | N/A | 0 | 0
2020-08-30 16:30 | 6.3284 | 0 | N/A | 0 | 0
2020-08-30 17:00 | 6.8744 | 0 | N/A | 0 | 0
2020-08-30 17:30 | 7.3771 | 0 | N/A | 0 | 0
2020-08-30 18:00 | 7.8568 | 0 | N/A | 0 | 0
2020-08-30 18:30 | 8.19 | 0 | N/A | 0 | 0
2020-08-30 19:00 | 8.1733 | 0 | N/A | 0 | 0
2020-08-30 19:30 | 7.8433 | 0 | N/A | 0 | 0
2020-08-30 20:00 | 7.2004 | 0 | N/A | 0 | 0
2020-08-30 20:30 | 6.7694 | 0 | N/A | 0 | 0
2020-08-30 21:00 | 6.4405 | 0 | N/A | 0 | 0
2020-08-30 21:30 | 6.7444 | 0 | N/A | 0 | 0
2020-08-30 22:00 | 6.9262 | 0 | N/A | 0 | 0
2020-08-30 22:30 | 6.441 | 0 | N/A | 0 | 0
2020-08-30 23:00 | 6.4772 | 0 | N/A | 0 | 0
2020-08-30 23:30 | 6.5123 | 0 | N/A | 0 | 0
2020-08-31 | 6.8635 | 0 | N/A | 0 | 0
2020-08-31 00:30 | 6.2736 | 0 | N/A | 0 | 0
2020-08-31 01:00 | 5.5797 | 0 | N/A | 0 | 0
2020-08-31 01:30 | 5.5492 | 0 | N/A | 0 | 0
2020-08-31 02:00 | 5.1554 | 0 | N/A | 0 | 0
2020-08-31 02:30 | 4.52 | 0 | N/A | 0 | 0
2020-08-31 03:00 | 4.0064 | 0 | N/A | 0 | 0
2020-08-31 03:30 | 3.7802 | 0 | N/A | 0 | 0
2020-08-31 04:00 | 3.6164 | 0 | N/A | 0 | 0
2020-08-31 04:30 | 3.5236 | 0 | N/A | 0 | 0
2020-08-31 05:00 | 3.4968 | 0 | N/A | 0 | 0
2020-08-31 05:30 | 3.9348 | 0 | N/A | 0 | 0
2020-08-31 06:00 | 4.3872 | 0 | N/A | 0 | 0
2020-08-31 06:30 | 5.2353 | 0 | N/A | 0 | 0
2020-08-31 07:00 | 6.041 | 0 | N/A | 0 | 0
2020-08-31 07:30 | 5.9468 | 0 | N/A | 0 | 0
2020-08-31 08:00 | 6.7467 | 0 | N/A | 0 | 0
2020-08-31 08:30 | 6.2037 | 0 | N/A | 0 | 0
2020-08-31 09:00 | 5.8309 | 0 | N/A | 0 | 0
2020-08-31 09:30 | 5.0139 | 0 | N/A | 0 | 0
2020-08-31 10:00 | 4.4549 | 0 | N/A | 0 | 0
2020-08-31 10:30 | 3.9308 | 0 | N/A | 0 | 0
2020-08-31 11:00 | 3.7181 | 0 | N/A | 0 | 0
2020-08-31 11:30 | 3.8625 | 0 | N/A | 0 | 0
2020-08-31 12:00 | 4.3309 | 0 | N/A | 0 | 0
2020-08-31 12:30 | 4.52 | 0 | N/A | 0 | 0
2020-08-31 13:00 | 4.7635 | 0 | N/A | 0 | 0
2020-08-31 13:30 | 5.0562 | 0 | N/A | 0 | 0
2020-08-31 14:00 | 4.6396 | 0 | N/A | 0 | 0
2020-08-31 14:30 | 4.8266 | 0 | N/A | 0 | 0
2020-08-31 15:00 | 5.1482 | 0 | N/A | 0 | 0
2020-08-31 15:30 | 5.5903 | 0 | N/A | 0 | 0
2020-08-31 16:00 | 6.0388 | 0 | N/A | 0 | 0
2020-08-31 16:30 | 6.0447 | 0 | N/A | 0 | 0
2020-08-31 17:00 | 5.8281 | 0 | N/A | 0 | 0
2020-08-31 17:30 | 6.8501 | 0 | N/A | 0 | 0
2020-08-31 18:00 | 7.86 | 0 | N/A | 0 | 0
2020-08-31 18:30 | 8.3768 | 0 | N/A | 0 | 0
2020-08-31 19:00 | 8.4276 | 0 | N/A | 0 | 0
2020-08-31 19:30 | 8.0037 | 0 | N/A | 0 | 0
2020-08-31 20:00 | 7.6502 | 0 | N/A | 0 | 0
2020-08-31 20:30 | 7.1034 | 0 | N/A | 0 | 0
2020-08-31 21:00 | 6.7205 | 0 | N/A | 0 | 0
2020-08-31 21:30 | 7.0179 | 0 | N/A | 0 | 0
2020-08-31 22:00 | 7.0845 | 0 | N/A | 0 | 0
2020-08-31 22:30 | 6.4013 | 0 | N/A | 0 | 0
2020-08-31 23:00 | 6.089 | 0 | N/A | 0 | 0
2020-08-31 23:30 | 6.322 | 0 | N/A | 0 | 0
2020-09-01 | 6.6705 | 0 | N/A | 0 | 0
2020-09-01 00:30 | 6.1178 | 0 | N/A | 0 | 0
2020-09-01 01:00 | 5.3815 | 0 | N/A | 0 | 0
2020-09-01 01:30 | 5.3736 | 0 | N/A | 0 | 0
2020-09-01 02:00 | 4.8711 | 0 | N/A | 0 | 0
2020-09-01 02:30 | 4.2543 | 0 | N/A | 0 | 0
2020-09-01 03:00 | 3.9233 | 0 | N/A | 0 | 0
2020-09-01 03:30 | 3.6891 | 0 | N/A | 0 | 0
2020-09-01 04:00 | 3.5301 | 0 | N/A | 0 | 0
2020-09-01 04:30 | 3.5596 | 0 | N/A | 0 | 0
2020-09-01 05:00 | 3.5982 | 0 | N/A | 0 | 0
2020-09-01 05:30 | 3.949 | 0 | N/A | 0 | 0
2020-09-01 06:00 | 4.5527 | 0 | N/A | 0 | 0
2020-09-01 06:30 | 5.424 | 0 | N/A | 0 | 0
2020-09-01 07:00 | 6.1667 | 0 | N/A | 0 | 0
2020-09-01 07:30 | 6.0134 | 0 | N/A | 0 | 0
2020-09-01 08:00 | 6.6742 | 0 | N/A | 0 | 0
2020-09-01 08:30 | 7.0843 | 0 | N/A | 0 | 0
2020-09-01 09:00 | 6.5579 | 0 | N/A | 0 | 0
2020-09-01 09:30 | 5.3232 | 0 | N/A | 0 | 0
2020-09-01 10:00 | 4.5888 | 0 | N/A | 0 | 0
2020-09-01 10:30 | 3.912 | 0 | N/A | 0 | 0
2020-09-01 11:00 | 3.9419 | 0 | N/A | 0 | 0
2020-09-01 11:30 | 3.0651 | 0 | N/A | 0 | 0
2020-09-01 12:00 | 2.7117 | 0 | N/A | 0 | 0
2020-09-01 12:30 | 2.9069 | 0 | N/A | 0 | 0
2020-09-01 13:00 | 2.3122 | 0 | N/A | 0 | 0
2020-09-01 13:30 | 2.0136 | 0 | N/A | 0 | 0
2020-09-01 14:00 | 2.2797 | 0 | N/A | 0 | 0
2020-09-01 14:30 | 2.6435 | 0 | N/A | 0 | 0
2020-09-01 15:00 | 2.7527 | 0 | N/A | 0 | 0
2020-09-01 15:30 | 3.1167 | 0 | N/A | 0 | 0
2020-09-01 16:00 | 3.327 | 0 | N/A | 0 | 0
2020-09-01 16:30 | 4.1101 | 0 | N/A | 0 | 0
2020-09-01 17:00 | 4.6519 | 0 | N/A | 0 | 0
2020-09-01 17:30 | 5.9842 | 0 | N/A | 0 | 0
2020-09-01 18:00 | 7.3367 | 0 | N/A | 0 | 0
2020-09-01 18:30 | 8.1906 | 0 | N/A | 0 | 0
2020-09-01 19:00 | 8.4759 | 0 | N/A | 0 | 0
2020-09-01 19:30 | 8.0719 | 0 | N/A | 0 | 0
2020-09-01 20:00 | 7.6672 | 0 | N/A | 0 | 0
2020-09-01 20:30 | 7.3134 | 0 | N/A | 0 | 0
2020-09-01 21:00 | 6.9467 | 0 | N/A | 0 | 0
2020-09-01 21:30 | 7.1736 | 0 | N/A | 0 | 0
2020-09-01 22:00 | 7.277 | 0 | N/A | 0 | 0
2020-09-01 22:30 | 6.6054 | 0 | N/A | 0 | 0
2020-09-01 23:00 | 6.3533 | 0 | N/A | 0 | 0
2020-09-01 23:30 | 6.4716 | 0 | N/A | 0 | 0
2020-09-02 | 6.8831 | 0 | N/A | 0 | 0
2020-09-02 00:30 | 6.2193 | 0 | N/A | 0 | 0
2020-09-02 01:00 | 5.3522 | 0 | N/A | 0 | 0
2020-09-02 01:30 | 5.2339 | 0 | N/A | 0 | 0
2020-09-02 02:00 | 4.8513 | 0 | N/A | 0 | 0
2020-09-02 02:30 | 4.3457 | 0 | N/A | 0 | 0
2020-09-02 03:00 | 3.848 | 0 | N/A | 0 | 0
2020-09-02 03:30 | 3.5811 | 0 | N/A | 0 | 0
2020-09-02 04:00 | 3.3124 | 0 | N/A | 0 | 0
2020-09-02 04:30 | 3.2967 | 0 | N/A | 0 | 0
2020-09-02 05:00 | 3.3956 | 0 | N/A | 0 | 0
2020-09-02 05:30 | 3.6749 | 0 | N/A | 0 | 0
2020-09-02 06:00 | 4.0737 | 0 | N/A | 0 | 0
2020-09-02 06:30 | 5.0032 | 0 | N/A | 0 | 0
2020-09-02 07:00 | 5.3908 | 0 | N/A | 0 | 0
2020-09-02 07:30 | 5.3753 | 0 | N/A | 0 | 0
2020-09-02 08:00 | 5.6333 | 0 | N/A | 0 | 0
2020-09-02 08:30 | 5.5077 | 0 | N/A | 0 | 0
2020-09-02 09:00 | 5.846 | 0 | N/A | 0 | 0
2020-09-02 09:30 | 5.914 | 0 | N/A | 0 | 0
2020-09-02 10:00 | 5.1658 | 0 | N/A | 0 | 0
2020-09-02 10:30 | 3.2495 | 0 | N/A | 0 | 0
2020-09-02 11:00 | 2.5914 | 0 | N/A | 0 | 0
2020-09-02 11:30 | 2.4648 | 0 | N/A | 0 | 0
2020-09-02 12:00 | 1.8443 | 0 | N/A | 0 | 0
2020-09-02 12:30 | 1.76 | 0 | N/A | 0 | 0
2020-09-02 13:00 | 1.6569 | 0 | N/A | 0 | 0
2020-09-02 13:30 | 1.84 | 0 | N/A | 0 | 0
2020-09-02 14:00 | 3.2067 | 0 | N/A | 0 | 0
2020-09-02 14:30 | 2.53 | 0 | N/A | 0 | 0
2020-09-02 15:00 | 2.7633 | 0 | N/A | 0 | 0
2020-09-02 15:30 | 3.3435 | 0 | N/A | 0 | 0
2020-09-02 16:00 | 4.0414 | 0 | N/A | 0 | 0
2020-09-02 16:30 | 4.0705 | 0 | N/A | 0 | 0
2020-09-02 17:00 | 4.3899 | 0 | N/A | 0 | 0
2020-09-02 17:30 | 5.2478 | 0 | N/A | 0 | 0
2020-09-02 18:00 | 6.3493 | 0 | N/A | 0 | 0
2020-09-02 18:30 | 7.0334 | 0 | N/A | 0 | 0
2020-09-02 19:00 | 7.0604 | 0 | N/A | 0 | 0
2020-09-02 19:30 | 6.6812 | 0 | N/A | 0 | 0
2020-09-02 20:00 | 6.4123 | 0 | N/A | 0 | 0
2020-09-02 20:30 | 6.0153 | 0 | N/A | 0 | 0
2020-09-02 21:00 | 5.7075 | 0 | N/A | 0 | 0
2020-09-02 21:30 | 6.0622 | 0 | N/A | 0 | 0
2020-09-02 22:00 | 6.2489 | 0 | N/A | 0 | 0
2020-09-02 22:30 | 5.8031 | 0 | N/A | 0 | 0
2020-09-02 23:00 | 5.6167 | 0 | N/A | 0 | 0
2020-09-02 23:30 | 5.8043 | 0 | N/A | 0 | 0
2020-09-03 | 6.2896 | 0 | N/A | 0 | 0
2020-09-03 00:30 | 5.5863 | 0 | N/A | 0 | 0
2020-09-03 01:00 | 4.728 | 0 | N/A | 0 | 0
2020-09-03 01:30 | 4.55 | 0 | N/A | 0 | 0
2020-09-03 02:00 | 4.0673 | 0 | N/A | 0 | 0
2020-09-03 02:30 | 3.4969 | 0 | N/A | 0 | 0
2020-09-03 03:00 | 3.2687 | 0 | N/A | 0 | 0
2020-09-03 03:30 | 3.0067 | 0 | N/A | 0 | 0
2020-09-03 04:00 | 2.9557 | 0 | N/A | 0 | 0
2020-09-03 04:30 | 2.8684 | 0 | N/A | 0 | 0
2020-09-03 05:00 | 3.0374 | 0 | N/A | 0 | 0
2020-09-03 05:30 | 3.2754 | 0 | N/A | 0 | 0
2020-09-03 06:00 | 3.7097 | 0 | N/A | 0 | 0
2020-09-03 06:30 | 4.4882 | 0 | N/A | 0 | 0
2020-09-03 07:00 | 5.0421 | 0 | N/A | 0 | 0
2020-09-03 07:30 | 5.3703 | 0 | N/A | 0 | 0
2020-09-03 08:00 | 5.4835 | 0 | N/A | 0 | 0
2020-09-03 08:30 | 5.4319 | 0 | N/A | 0 | 0
2020-09-03 09:00 | 4.5799 | 0 | N/A | 0 | 0
2020-09-03 09:30 | 3.8758 | 0 | N/A | 0 | 0
2020-09-03 10:00 | 3.375 | 0 | N/A | 0 | 0
2020-09-03 10:30 | 2.6809 | 0 | N/A | 0 | 0
2020-09-03 11:00 | 2.2874 | 0 | N/A | 0 | 0
2020-09-03 11:30 | 2.15 | 0 | N/A | 0 | 0
2020-09-03 12:00 | 2.5628 | 0 | N/A | 0 | 0
2020-09-03 12:30 | 2.2798 | 0 | N/A | 0 | 0
2020-09-03 13:00 | 2.1991 | 0 | N/A | 0 | 0
2020-09-03 13:30 | 3.4029 | 0 | N/A | 0 | 0
2020-09-03 14:00 | 2.5656 | 0 | N/A | 0 | 0
2020-09-03 14:30 | 3.1919 | 0 | N/A | 0 | 0
2020-09-03 15:00 | 4.0234 | 0 | N/A | 0 | 0
2020-09-03 15:30 | 3.9833 | 0 | N/A | 0 | 0
2020-09-03 16:00 | 4.85 | 0 | N/A | 0 | 0
2020-09-03 16:30 | 5.0414 | 0 | N/A | 0 | 0
2020-09-03 17:00 | 5.5953 | 0 | N/A | 0 | 0
2020-09-03 17:30 | 6.3602 | 0 | N/A | 0 | 0
2020-09-03 18:00 | 7.26 | 0 | N/A | 0 | 0
2020-09-03 18:30 | 7.5567 | 0 | N/A | 0 | 0
2020-09-03 19:00 | 7.5867 | 0 | N/A | 0 | 0
2020-09-03 19:30 | 7.2433 | 0 | N/A | 0 | 0
2020-09-03 20:00 | 6.8567 | 0 | N/A | 0 | 0
2020-09-03 20:30 | 6.4669 | 0 | N/A | 0 | 0
2020-09-03 21:00 | 6.1274 | 0 | N/A | 0 | 0
2020-09-03 21:30 | 6.4782 | 0 | N/A | 0 | 0
2020-09-03 22:00 | 6.6218 | 0 | N/A | 0 | 0
2020-09-03 22:30 | 6.0385 | 0 | N/A | 0 | 0
2020-09-03 23:00 | 5.8305 | 0 | N/A | 0 | 0
2020-09-03 23:30 | 6.0187 | 0 | N/A | 0 | 0
2020-09-04 | 6.4055 | 0 | N/A | 0 | 0
2020-09-04 00:30 | 5.7937 | 0 | N/A | 0 | 0
2020-09-04 01:00 | 4.9961 | 0 | N/A | 0 | 0
2020-09-04 01:30 | 4.9832 | 0 | N/A | 0 | 0
2020-09-04 02:00 | 4.6437 | 0 | N/A | 0 | 0
2020-09-04 02:30 | 3.9637 | 0 | N/A | 0 | 0
2020-09-04 03:00 | 3.5974 | 0 | N/A | 0 | 0
2020-09-04 03:30 | 3.4687 | 0 | N/A | 0 | 0
2020-09-04 04:00 | 3.2801 | 0 | N/A | 0 | 0
2020-09-04 04:30 | 3.2649 | 0 | N/A | 0 | 0
2020-09-04 05:00 | 3.3036 | 0 | N/A | 0 | 0
2020-09-04 05:30 | 3.6316 | 0 | N/A | 0 | 0
2020-09-04 06:00 | 4.0776 | 0 | N/A | 0 | 0
2020-09-04 06:30 | 4.8663 | 0 | N/A | 0 | 0
2020-09-04 07:00 | 5.4018 | 0 | N/A | 0 | 0
2020-09-04 07:30 | 5.097 | 0 | N/A | 0 | 0
2020-09-04 08:00 | 5.4523 | 0 | N/A | 0 | 0
2020-09-04 08:30 | 6.15 | 0 | N/A | 0 | 0
2020-09-04 09:00 | 5.91 | 0 | N/A | 0 | 0
2020-09-04 09:30 | 5.2367 | 0 | N/A | 0 | 0
2020-09-04 10:00 | 4.0902 | 0 | N/A | 0 | 0
2020-09-04 10:30 | 3.9178 | 0 | N/A | 0 | 0
2020-09-04 11:00 | 4.5168 | 0 | N/A | 0 | 0
2020-09-04 11:30 | 4.4334 | 0 | N/A | 0 | 0
2020-09-04 12:00 | 4.8067 | 0 | N/A | 0 | 0
2020-09-04 12:30 | 4.4467 | 0 | N/A | 0 | 0
2020-09-04 13:00 | 4.7908 | 0 | N/A | 0 | 0
2020-09-04 13:30 | 4.5236 | 0 | N/A | 0 | 0
2020-09-04 14:00 | 3.7567 | 0 | N/A | 0 | 0
2020-09-04 14:30 | 3.1729 | 0 | N/A | 0 | 0
2020-09-04 15:00 | 3.2322 | 0 | N/A | 0 | 0
2020-09-04 15:30 | 3.0712 | 0 | N/A | 0 | 0
2020-09-04 16:00 | 3.1242 | 0 | N/A | 0 | 0
2020-09-04 16:30 | 3.5624 | 0 | N/A | 0 | 0
2020-09-04 17:00 | 4.4297 | 0 | N/A | 0 | 0
2020-09-04 17:30 | 5.2131 | 0 | N/A | 0 | 0
2020-09-04 18:00 | 6.1983 | 0 | N/A | 0 | 0
2020-09-04 18:30 | 7.0434 | 0 | N/A | 0 | 0
2020-09-04 19:00 | 7.4867 | 0 | N/A | 0 | 0
2020-09-04 19:30 | 7.3867 | 0 | N/A | 0 | 0
2020-09-04 20:00 | 7.0867 | 0 | N/A | 0 | 0
2020-09-04 20:30 | 6.7367 | 0 | N/A | 0 | 0
2020-09-04 21:00 | 6.4039 | 0 | N/A | 0 | 0
2020-09-04 21:30 | 6.9046 | 0 | N/A | 0 | 0
2020-09-04 22:00 | 6.965 | 0 | N/A | 0 | 0
2020-09-04 22:30 | 6.3975 | 0 | N/A | 0 | 0
2020-09-04 23:00 | 6.314 | 0 | N/A | 0 | 0
2020-09-04 23:30 | 6.6 | 0 | N/A | 0 | 0
2020-09-05 | 6.8776 | 0 | N/A | 0 | 0
2020-09-05 00:30 | 6.1331 | 0 | N/A | 0 | 0
2020-09-05 01:00 | 5.102 | 0 | N/A | 0 | 0
2020-09-05 01:30 | 4.975 | 0 | N/A | 0 | 0
2020-09-05 02:00 | 4.5973 | 0 | N/A | 0 | 0
2020-09-05 02:30 | 3.899 | 0 | N/A | 0 | 0
2020-09-05 03:00 | 3.5453 | 0 | N/A | 0 | 0
2020-09-05 03:30 | 3.3041 | 0 | N/A | 0 | 0
2020-09-05 04:00 | 3.1386 | 0 | N/A | 0 | 0
2020-09-05 04:30 | 3.0443 | 0 | N/A | 0 | 0
2020-09-05 05:00 | 3.0624 | 0 | N/A | 0 | 0
2020-09-05 05:30 | 3.179 | 0 | N/A | 0 | 0
2020-09-05 06:00 | 3.3565 | 0 | N/A | 0 | 0
2020-09-05 06:30 | 3.8268 | 0 | N/A | 0 | 0
2020-09-05 07:00 | 4.0541 | 0 | N/A | 0 | 0
2020-09-05 07:30 | 3.9325 | 0 | N/A | 0 | 0
2020-09-05 08:00 | 3.8462 | 0 | N/A | 0 | 0
2020-09-05 08:30 | 3.9567 | 0 | N/A | 0 | 0
2020-09-05 09:00 | 4.2585 | 0 | N/A | 0 | 0
2020-09-05 09:30 | 4.541 | 0 | N/A | 0 | 0
2020-09-05 10:00 | 3.8794 | 0 | N/A | 0 | 0
2020-09-05 10:30 | 3.5229 | 0 | N/A | 0 | 0
2020-09-05 11:00 | 2.8751 | 0 | N/A | 0 | 0
2020-09-05 11:30 | 1.9838 | 0 | N/A | 0 | 0
2020-09-05 12:00 | 1.7614 | 0 | N/A | 0 | 0
2020-09-05 12:30 | 1.237 | 0 | N/A | 0 | 0
2020-09-05 13:00 | 0.93408 | 0 | N/A | 0 | 0
2020-09-05 13:30 | 0.95548 | 0 | N/A | 0 | 0
2020-09-05 14:00 | 1.0628 | 0 | N/A | 0 | 0
2020-09-05 14:30 | 1.7568 | 0 | N/A | 0 | 0
2020-09-05 15:00 | 2.4668 | 0 | N/A | 0 | 0
2020-09-05 15:30 | 2.6892 | 0 | N/A | 0 | 0
2020-09-05 16:00 | 2.8513 | 0 | N/A | 0 | 0
2020-09-05 16:30 | 3.4003 | 0 | N/A | 0 | 0
2020-09-05 17:00 | 4.263 | 0 | N/A | 0 | 0
2020-09-05 17:30 | 5.0359 | 0 | N/A | 0 | 0
2020-09-05 18:00 | 6.0252 | 0 | N/A | 0 | 0
2020-09-05 18:30 | 6.7395 | 0 | N/A | 0 | 0
2020-09-05 19:00 | 7.3234 | 0 | N/A | 0 | 0
2020-09-05 19:30 | 7.1002 | 0 | N/A | 0 | 0
2020-09-05 20:00 | 6.6414 | 0 | N/A | 0 | 0
2020-09-05 20:30 | 6.2043 | 0 | N/A | 0 | 0
2020-09-05 21:00 | 5.7745 | 0 | N/A | 0 | 0
2020-09-05 21:30 | 6.2838 | 0 | N/A | 0 | 0
2020-09-05 22:00 | 6.642 | 0 | N/A | 0 | 0
2020-09-05 22:30 | 6.3169 | 0 | N/A | 0 | 0
2020-09-05 23:00 | 6.4142 | 0 | N/A | 0 | 0
2020-09-05 23:30 | 6.4316 | 0 | N/A | 0 | 0
2020-09-06 | 6.9047 | 0 | N/A | 0 | 0
2020-09-06 00:30 | 6.128 | 0 | N/A | 0 | 0
2020-09-06 01:00 | 5.3052 | 0 | N/A | 0 | 0
2020-09-06 01:30 | 5.2369 | 0 | N/A | 0 | 0
2020-09-06 02:00 | 4.9136 | 0 | N/A | 0 | 0
2020-09-06 02:30 | 4.2462 | 0 | N/A | 0 | 0
2020-09-06 03:00 | 3.889 | 0 | N/A | 0 | 0
2020-09-06 03:30 | 3.6153 | 0 | N/A | 0 | 0
2020-09-06 04:00 | 3.4191 | 0 | N/A | 0 | 0
2020-09-06 04:30 | 3.3762 | 0 | N/A | 0 | 0
2020-09-06 05:00 | 3.3141 | 0 | N/A | 0 | 0
2020-09-06 05:30 | 3.3197 | 0 | N/A | 0 | 0
2020-09-06 06:00 | 3.5171 | 0 | N/A | 0 | 0
2020-09-06 06:30 | 3.8778 | 0 | N/A | 0 | 0
2020-09-06 07:00 | 4.0843 | 0 | N/A | 0 | 0
2020-09-06 07:30 | 3.8913 | 0 | N/A | 0 | 0
2020-09-06 08:00 | 3.8582 | 0 | N/A | 0 | 0
2020-09-06 08:30 | 3.7822 | 0 | N/A | 0 | 0
2020-09-06 09:00 | 3.3616 | 0 | N/A | 0 | 0
2020-09-06 09:30 | 2.7586 | 0 | N/A | 0 | 0
2020-09-06 10:00 | 2.1973 | 0 | N/A | 0 | 0
2020-09-06 10:30 | 1.668 | 0 | N/A | 0 | 0
2020-09-06 11:00 | 1.1057 | 0 | N/A | 0 | 0
2020-09-06 11:30 | 0.74839 | 0 | N/A | 0 | 0
2020-09-06 12:00 | 0.52566 | 0 | N/A | 0 | 0
2020-09-06 12:30 | 0.42605 | 0 | N/A | 0 | 0
2020-09-06 13:00 | 0.46001 | 0 | N/A | 0 | 0
2020-09-06 13:30 | 0.46934 | 0 | N/A | 0 | 0
2020-09-06 14:00 | 0.55479 | 0 | N/A | 0 | 0
2020-09-06 14:30 | 0.87273 | 0 | N/A | 0 | 0
2020-09-06 15:00 | 1.2391 | 0 | N/A | 0 | 0
2020-09-06 15:30 | 1.497 | 0 | N/A | 0 | 0
2020-09-06 16:00 | 2.1064 | 0 | N/A | 0 | 0
2020-09-06 16:30 | 2.9856 | 0 | N/A | 0 | 0
2020-09-06 17:00 | 3.8207 | 0 | N/A | 0 | 0
2020-09-06 17:30 | 4.809 | 0 | N/A | 0 | 0
2020-09-06 18:00 | 5.8482 | 0 | N/A | 0 | 0
2020-09-06 18:30 | 6.5944 | 0 | N/A | 0 | 0
2020-09-06 19:00 | 6.848 | 0 | N/A | 0 | 0
2020-09-06 19:30 | 6.6615 | 0 | N/A | 0 | 0
2020-09-06 20:00 | 6.3099 | 0 | N/A | 0 | 0
2020-09-06 20:30 | 6.0265 | 0 | N/A | 0 | 0
2020-09-06 21:00 | 5.7084 | 0 | N/A | 0 | 0
2020-09-06 21:30 | 6.118 | 0 | N/A | 0 | 0
2020-09-06 22:00 | 6.4169 | 0 | N/A | 0 | 0
2020-09-06 22:30 | 6.0185 | 0 | N/A | 0 | 0
2020-09-06 23:00 | 6.0297 | 0 | N/A | 0 | 0
2020-09-06 23:30 | 5.9744 | 0 | N/A | 0 | 0
2020-09-07 | 6.3859 | 0 | N/A | 0 | 0
2020-09-07 00:30 | 5.6981 | 0 | N/A | 0 | 0
2020-09-07 01:00 | 4.8564 | 0 | N/A | 0 | 0
2020-09-07 01:30 | 4.8696 | 0 | N/A | 0 | 0
2020-09-07 02:00 | 4.5295 | 0 | N/A | 0 | 0
2020-09-07 02:30 | 3.8478 | 0 | N/A | 0 | 0
2020-09-07 03:00 | 3.4654 | 0 | N/A | 0 | 0
2020-09-07 03:30 | 3.2033 | 0 | N/A | 0 | 0
2020-09-07 04:00 | 3.0926 | 0 | N/A | 0 | 0
2020-09-07 04:30 | 3.0471 | 0 | N/A | 0 | 0
2020-09-07 05:00 | 3.0903 | 0 | N/A | 0 | 0
2020-09-07 05:30 | 3.3628 | 0 | N/A | 0 | 0
2020-09-07 06:00 | 3.8225 | 0 | N/A | 0 | 0
2020-09-07 06:30 | 4.404 | 0 | N/A | 0 | 0
2020-09-07 07:00 | 5.3373 | 0 | N/A | 0 | 0
2020-09-07 07:30 | 5.0867 | 0 | N/A | 0 | 0
2020-09-07 08:00 | 5.0948 | 0 | N/A | 0 | 0
2020-09-07 08:30 | 5.0803 | 0 | N/A | 0 | 0
2020-09-07 09:00 | 4.4055 | 0 | N/A | 0 | 0
2020-09-07 09:30 | 3.5947 | 0 | N/A | 0 | 0
2020-09-07 10:00 | 2.9806 | 0 | N/A | 0 | 0
2020-09-07 10:30 | 2.2628 | 0 | N/A | 0 | 0
2020-09-07 11:00 | 1.8732 | 0 | N/A | 0 | 0
2020-09-07 11:30 | 1.4979 | 0 | N/A | 0 | 0
2020-09-07 12:00 | 1.1241 | 0 | N/A | 0 | 0
2020-09-07 12:30 | 0.98814 | 0 | N/A | 0 | 0
2020-09-07 13:00 | 0.84241 | 0 | N/A | 0 | 0
2020-09-07 13:30 | 0.90139 | 0 | N/A | 0 | 0
2020-09-07 14:00 | 0.79163 | 0 | N/A | 0 | 0
2020-09-07 14:30 | 0.88255 | 0 | N/A | 0 | 0
2020-09-07 15:00 | 1.1 | 0 | N/A | 0 | 0
2020-09-07 15:30 | 1.4506 | 0 | N/A | 0 | 0
2020-09-07 16:00 | 1.873 | 0 | N/A | 0 | 0
2020-09-07 16:30 | 2.2925 | 0 | N/A | 0 | 0
2020-09-07 17:00 | 3.2839 | 0 | N/A | 0 | 0
2020-09-07 17:30 | 4.5419 | 0 | N/A | 0 | 0
2020-09-07 18:00 | 5.6386 | 0 | N/A | 0 | 0
2020-09-07 18:30 | 6.4128 | 0 | N/A | 0 | 0
2020-09-07 19:00 | 6.5253 | 0 | N/A | 0 | 0
2020-09-07 19:30 | 6.2161 | 0 | N/A | 0 | 0
2020-09-07 20:00 | 5.8359 | 0 | N/A | 0 | 0
2020-09-07 20:30 | 5.5047 | 0 | N/A | 0 | 0
2020-09-07 21:00 | 5.2029 | 0 | N/A | 0 | 0
2020-09-07 21:30 | 5.6053 | 0 | N/A | 0 | 0
2020-09-07 22:00 | 5.8464 | 0 | N/A | 0 | 0
2020-09-07 22:30 | 5.3734 | 0 | N/A | 0 | 0
2020-09-07 23:00 | 5.2184 | 0 | N/A | 0 | 0
2020-09-07 23:30 | 5.2954 | 0 | N/A | 0 | 0
2020-09-08 | 5.8442 | 0 | N/A | 0 | 0
2020-09-08 00:30 | 5.0432 | 0 | N/A | 0 | 0
2020-09-08 01:00 | 4.1913 | 0 | N/A | 0 | 0
2020-09-08 01:30 | 4.0866 | 0 | N/A | 0 | 0
2020-09-08 02:00 | 3.7708 | 0 | N/A | 0 | 0
2020-09-08 02:30 | 3.1856 | 0 | N/A | 0 | 0
2020-09-08 03:00 | 2.7708 | 0 | N/A | 0 | 0
2020-09-08 03:30 | 2.6098 | 0 | N/A | 0 | 0
2020-09-08 04:00 | 2.4789 | 0 | N/A | 0 | 0
2020-09-08 04:30 | 2.4393 | 0 | N/A | 0 | 0
2020-09-08 05:00 | 2.516 | 0 | N/A | 0 | 0
2020-09-08 05:30 | 2.6179 | 0 | N/A | 0 | 0
2020-09-08 06:00 | 2.9333 | 0 | N/A | 0 | 0
2020-09-08 06:30 | 3.654 | 0 | N/A | 0 | 0
2020-09-08 07:00 | 3.9917 | 0 | N/A | 0 | 0
2020-09-08 07:30 | 3.9576 | 0 | N/A | 0 | 0
2020-09-08 08:00 | 4.397 | 0 | N/A | 0 | 0
2020-09-08 08:30 | 4.9003 | 0 | N/A | 0 | 0
2020-09-08 09:00 | 5.1776 | 0 | N/A | 0 | 0
2020-09-08 09:30 | 5.3636 | 0 | N/A | 0 | 0
2020-09-08 10:00 | 5.5077 | 0 | N/A | 0 | 0
2020-09-08 10:30 | 5.5767 | 0 | N/A | 0 | 0
2020-09-08 11:00 | 6.1735 | 0 | N/A | 0 | 0
2020-09-08 11:30 | 6.1552 | 0 | N/A | 0 | 0
2020-09-08 12:00 | 5.8142 | 0 | N/A | 0 | 0
2020-09-08 12:30 | 5.5509 | 0 | N/A | 0 | 0
2020-09-08 13:00 | 5.518 | 0 | N/A | 0 | 0
2020-09-08 13:30 | 5.0656 | 0 | N/A | 0 | 0
2020-09-08 14:00 | 4.7948 | 0 | N/A | 0 | 0
2020-09-08 14:30 | 4.6768 | 0 | N/A | 0 | 0
2020-09-08 15:00 | 4.1767 | 0 | N/A | 0 | 0
2020-09-08 15:30 | 3.9802 | 0 | N/A | 0 | 0
2020-09-08 16:00 | 3.8333 | 0 | N/A | 0 | 0
2020-09-08 16:30 | 3.954 | 0 | N/A | 0 | 0
2020-09-08 17:00 | 4.7195 | 0 | N/A | 0 | 0
2020-09-08 17:30 | 5.4672 | 0 | N/A | 0 | 0
2020-09-08 18:00 | 6.3834 | 0 | N/A | 0 | 0
2020-09-08 18:30 | 6.9878 | 0 | N/A | 0 | 0
2020-09-08 19:00 | 7.127 | 0 | N/A | 0 | 0
2020-09-08 19:30 | 6.8568 | 0 | N/A | 0 | 0
2020-09-08 20:00 | 6.5975 | 0 | N/A | 0 | 0
2020-09-08 20:30 | 6.2859 | 0 | N/A | 0 | 0
2020-09-08 21:00 | 5.9512 | 0 | N/A | 0 | 0
2020-09-08 21:30 | 6.3711 | 0 | N/A | 0 | 0
2020-09-08 22:00 | 6.496 | 0 | N/A | 0 | 0
2020-09-08 22:30 | 5.9382 | 0 | N/A | 0 | 0
2020-09-08 23:00 | 5.8313 | 0 | N/A | 0 | 0
2020-09-08 23:30 | 6.0049 | 0 | N/A | 0 | 0
2020-09-09 | 6.3395 | 0 | N/A | 0 | 0
2020-09-09 00:30 | 5.7147 | 0 | N/A | 0 | 0
2020-09-09 01:00 | 4.9408 | 0 | N/A | 0 | 0
2020-09-09 01:30 | 4.7931 | 0 | N/A | 0 | 0
2020-09-09 02:00 | 4.4322 | 0 | N/A | 0 | 0
2020-09-09 02:30 | 3.7796 | 0 | N/A | 0 | 0
2020-09-09 03:00 | 3.4978 | 0 | N/A | 0 | 0
2020-09-09 03:30 | 3.2962 | 0 | N/A | 0 | 0
2020-09-09 04:00 | 3.159 | 0 | N/A | 0 | 0
2020-09-09 04:30 | 3.2366 | 0 | N/A | 0 | 0
2020-09-09 05:00 | 3.3178 | 0 | N/A | 0 | 0
2020-09-09 05:30 | 3.6053 | 0 | N/A | 0 | 0
2020-09-09 06:00 | 4.0112 | 0 | N/A | 0 | 0
2020-09-09 06:30 | 4.905 | 0 | N/A | 0 | 0
2020-09-09 07:00 | 5.2586 | 0 | N/A | 0 | 0
2020-09-09 07:30 | 5.2923 | 0 | N/A | 0 | 0
2020-09-09 08:00 | 5.7567 | 0 | N/A | 0 | 0
2020-09-09 08:30 | 6.0985 | 0 | N/A | 0 | 0
2020-09-09 09:00 | 5.1878 | 0 | N/A | 0 | 0
2020-09-09 09:30 | 4.4528 | 0 | N/A | 0 | 0
2020-09-09 10:00 | 3.8077 | 0 | N/A | 0 | 0
2020-09-09 10:30 | 2.9639 | 0 | N/A | 0 | 0
2020-09-09 11:00 | 2.4667 | 0 | N/A | 0 | 0
2020-09-09 11:30 | 2.19 | 0 | N/A | 0 | 0
2020-09-09 12:00 | 1.847 | 0 | N/A | 0 | 0
2020-09-09 12:30 | 1.6429 | 0 | N/A | 0 | 0
2020-09-09 13:00 | 1.4962 | 0 | N/A | 0 | 0
2020-09-09 13:30 | 1.4954 | 0 | N/A | 0 | 0
2020-09-09 14:00 | 1.3252 | 0 | N/A | 0 | 0
2020-09-09 14:30 | 1.5604 | 0 | N/A | 0 | 0
2020-09-09 15:00 | 1.9147 | 0 | N/A | 0 | 0
2020-09-09 15:30 | 2.4876 | 0 | N/A | 0 | 0
2020-09-09 16:00 | 2.7767 | 0 | N/A | 0 | 0
2020-09-09 16:30 | 3.567 | 0 | N/A | 0 | 0
2020-09-09 17:00 | 4.3633 | 0 | N/A | 0 | 0
2020-09-09 17:30 | 5.0677 | 0 | N/A | 0 | 0
2020-09-09 18:00 | 6.1252 | 0 | N/A | 0 | 0
2020-09-09 18:30 | 7.2673 | 0 | N/A | 0 | 0
2020-09-09 19:00 | 8.1395 | 0 | N/A | 0 | 0
2020-09-09 19:30 | 7.7704 | 0 | N/A | 0 | 0
2020-09-09 20:00 | 7.4734 | 0 | N/A | 0 | 0
2020-09-09 20:30 | 7.081 | 0 | N/A | 0 | 0
2020-09-09 21:00 | 6.7388 | 0 | N/A | 0 | 0
2020-09-09 21:30 | 7.0926 | 0 | N/A | 0 | 0
2020-09-09 22:00 | 7.2316 | 0 | N/A | 0 | 0
2020-09-09 22:30 | 6.6038 | 0 | N/A | 0 | 0
2020-09-09 23:00 | 6.284 | 0 | N/A | 0 | 0
2020-09-09 23:30 | 6.3237 | 0 | N/A | 0 | 0
2020-09-10 | 6.689 | 0 | N/A | 0 | 0
2020-09-10 00:30 | 5.9882 | 0 | N/A | 0 | 0
2020-09-10 01:00 | 5.2463 | 0 | N/A | 0 | 0
2020-09-10 01:30 | 5.0961 | 0 | N/A | 0 | 0
2020-09-10 02:00 | 4.7237 | 0 | N/A | 0 | 0
2020-09-10 02:30 | 4.2172 | 0 | N/A | 0 | 0
2020-09-10 03:00 | 3.8332 | 0 | N/A | 0 | 0
2020-09-10 03:30 | 3.581 | 0 | N/A | 0 | 0
2020-09-10 04:00 | 3.3719 | 0 | N/A | 0 | 0
2020-09-10 04:30 | 3.3583 | 0 | N/A | 0 | 0
2020-09-10 05:00 | 3.3942 | 0 | N/A | 0 | 0
2020-09-10 05:30 | 3.7587 | 0 | N/A | 0 | 0
2020-09-10 06:00 | 4.1458 | 0 | N/A | 0 | 0
2020-09-10 06:30 | 4.9237 | 0 | N/A | 0 | 0
2020-09-10 07:00 | 5.4851 | 0 | N/A | 0 | 0
2020-09-10 07:30 | 5.3233 | 0 | N/A | 0 | 0
2020-09-10 08:00 | 5.26 | 0 | N/A | 0 | 0
2020-09-10 08:30 | 5.292 | 0 | N/A | 0 | 0
2020-09-10 09:00 | 4.4788 | 0 | N/A | 0 | 0
2020-09-10 09:30 | 3.4436 | 0 | N/A | 0 | 0
2020-09-10 10:00 | 2.6746 | 0 | N/A | 0 | 0
2020-09-10 10:30 | 1.9183 | 0 | N/A | 0 | 0
2020-09-10 11:00 | 1.2914 | 0 | N/A | 0 | 0
2020-09-10 11:30 | 1.0329 | 0 | N/A | 0 | 0
2020-09-10 12:00 | 0.74765 | 0 | N/A | 0 | 0
2020-09-10 12:30 | 0.45353 | 0 | N/A | 0 | 0
2020-09-10 13:00 | 0.39474 | 0 | N/A | 0 | 0
2020-09-10 13:30 | 0.69871 | 0 | N/A | 0 | 0
2020-09-10 14:00 | 0.49546 | 0 | N/A | 0 | 0
2020-09-10 14:30 | 0.74396 | 0 | N/A | 0 | 0
2020-09-10 15:00 | 1.2172 | 0 | N/A | 0 | 0
2020-09-10 15:30 | 1.5072 | 0 | N/A | 0 | 0
2020-09-10 16:00 | 1.8467 | 0 | N/A | 0 | 0
2020-09-10 16:30 | 2.7435 | 0 | N/A | 0 | 0
2020-09-10 17:00 | 3.3284 | 0 | N/A | 0 | 0
2020-09-10 17:30 | 4.0375 | 0 | N/A | 0 | 0
2020-09-10 18:00 | 5.1559 | 0 | N/A | 0 | 0
2020-09-10 18:30 | 6.0498 | 0 | N/A | 0 | 0
2020-09-10 19:00 | 6.4333 | 0 | N/A | 0 | 0
2020-09-10 19:30 | 6.1992 | 0 | N/A | 0 | 0
2020-09-10 20:00 | 6.0408 | 0 | N/A | 0 | 0
2020-09-10 20:30 | 5.7926 | 0 | N/A | 0 | 0
2020-09-10 21:00 | 5.5369 | 0 | N/A | 0 | 0
2020-09-10 21:30 | 5.8193 | 0 | N/A | 0 | 0
2020-09-10 22:00 | 6.0172 | 0 | N/A | 0 | 0
2020-09-10 22:30 | 5.6221 | 0 | N/A | 0 | 0
2020-09-10 23:00 | 5.3836 | 0 | N/A | 0 | 0
2020-09-10 23:30 | 5.348 | 0 | N/A | 0 | 0
2020-09-11 | 5.4107 | 0 | N/A | 0 | 0
2020-09-11 00:30 | 4.8113 | 0 | N/A | 0 | 0
2020-09-11 01:00 | 4.0528 | 0 | N/A | 0 | 0
2020-09-11 01:30 | 3.9986 | 0 | N/A | 0 | 0
2020-09-11 02:00 | 3.8511 | 0 | N/A | 0 | 0
2020-09-11 02:30 | 3.6743 | 0 | N/A | 0 | 0
2020-09-11 03:00 | 3.3995 | 0 | N/A | 0 | 0
2020-09-11 03:30 | 3.1666 | 0 | N/A | 0 | 0
2020-09-11 04:00 | 2.8628 | 0 | N/A | 0 | 0
2020-09-11 04:30 | 2.8086 | 0 | N/A | 0 | 0
2020-09-11 05:00 | 2.9056 | 0 | N/A | 0 | 0
2020-09-11 05:30 | 3.0891 | 0 | N/A | 0 | 0
2020-09-11 06:00 | 3.579 | 0 | N/A | 0 | 0
2020-09-11 06:30 | 4.4076 | 0 | N/A | 0 | 0
2020-09-11 07:00 | 4.9853 | 0 | N/A | 0 | 0
2020-09-11 07:30 | 4.6043 | 0 | N/A | 0 | 0
2020-09-11 08:00 | 4.5333 | 0 | N/A | 0 | 0
2020-09-11 08:30 | 4.3267 | 0 | N/A | 0 | 0
2020-09-11 09:00 | 3.4806 | 0 | N/A | 0 | 0
2020-09-11 09:30 | 2.7881 | 0 | N/A | 0 | 0
2020-09-11 10:00 | 2.1985 | 0 | N/A | 0 | 0
2020-09-11 10:30 | 1.9909 | 0 | N/A | 0 | 0
2020-09-11 11:00 | 2.0904 | 0 | N/A | 0 | 0
2020-09-11 11:30 | 2.9411 | 0 | N/A | 0 | 0
2020-09-11 12:00 | 3.4733 | 0 | N/A | 0 | 0
2020-09-11 12:30 | 4.1301 | 0 | N/A | 0 | 0
2020-09-11 13:00 | 3.8501 | 0 | N/A | 0 | 0
2020-09-11 13:30 | 3.52 | 0 | N/A | 0 | 0
2020-09-11 14:00 | 4.3169 | 0 | N/A | 0 | 0
2020-09-11 14:30 | 4.3903 | 0 | N/A | 0 | 0
2020-09-11 15:00 | 4.4333 | 0 | N/A | 0 | 0
2020-09-11 15:30 | 4.4567 | 0 | N/A | 0 | 0
2020-09-11 16:00 | 3.6982 | 0 | N/A | 0 | 0
2020-09-11 16:30 | 3.4651 | 0 | N/A | 0 | 0
2020-09-11 17:00 | 4.9823 | 0 | N/A | 0 | 0
2020-09-11 17:30 | 5.2333 | 0 | N/A | 0 | 0
2020-09-11 18:00 | 5.8399 | 0 | N/A | 0 | 0
2020-09-11 18:30 | 6.367 | 0 | N/A | 0 | 0
2020-09-11 19:00 | 6.7141 | 0 | N/A | 0 | 0
2020-09-11 19:30 | 6.5974 | 0 | N/A | 0 | 0
2020-09-11 20:00 | 6.2883 | 0 | N/A | 0 | 0
2020-09-11 20:30 | 6.003 | 0 | N/A | 0 | 0
2020-09-11 21:00 | 5.6729 | 0 | N/A | 0 | 0
2020-09-11 21:30 | 6.1272 | 0 | N/A | 0 | 0
2020-09-11 22:00 | 6.2881 | 0 | N/A | 0 | 0
2020-09-11 22:30 | 5.8461 | 0 | N/A | 0 | 0
2020-09-11 23:00 | 5.74 | 0 | N/A | 0 | 0
2020-09-11 23:30 | 5.9397 | 0 | N/A | 0 | 0
2020-09-12 | 6.2389 | 0 | N/A | 0 | 0
2020-09-12 00:30 | 5.4863 | 0 | N/A | 0 | 0
2020-09-12 01:00 | 4.6563 | 0 | N/A | 0 | 0
2020-09-12 01:30 | 4.5293 | 0 | N/A | 0 | 0
2020-09-12 02:00 | 4.0326 | 0 | N/A | 0 | 0
2020-09-12 02:30 | 3.4407 | 0 | N/A | 0 | 0
2020-09-12 03:00 | 3.0569 | 0 | N/A | 0 | 0
2020-09-12 03:30 | 2.7755 | 0 | N/A | 0 | 0
2020-09-12 04:00 | 2.6595 | 0 | N/A | 0 | 0
2020-09-12 04:30 | 2.5357 | 0 | N/A | 0 | 0
2020-09-12 05:00 | 2.5835 | 0 | N/A | 0 | 0
2020-09-12 05:30 | 2.6958 | 0 | N/A | 0 | 0
2020-09-12 06:00 | 2.7175 | 0 | N/A | 0 | 0
2020-09-12 06:30 | 3.1902 | 0 | N/A | 0 | 0
2020-09-12 07:00 | 3.3479 | 0 | N/A | 0 | 0
2020-09-12 07:30 | 3.5768 | 0 | N/A | 0 | 0
2020-09-12 08:00 | 4.0107 | 0 | N/A | 0 | 0
2020-09-12 08:30 | 4.5861 | 0 | N/A | 0 | 0
2020-09-12 09:00 | 5.0733 | 0 | N/A | 0 | 0
2020-09-12 09:30 | 5.5301 | 0 | N/A | 0 | 0
2020-09-12 10:00 | 5.7134 | 0 | N/A | 0 | 0
2020-09-12 10:30 | 5.7051 | 0 | N/A | 0 | 0
2020-09-12 11:00 | 5.9827 | 0 | N/A | 0 | 0
2020-09-12 11:30 | 6.082 | 0 | N/A | 0 | 0
2020-09-12 12:00 | 6.1009 | 0 | N/A | 0 | 0
2020-09-12 12:30 | 6.1541 | 0 | N/A | 0 | 0
2020-09-12 13:00 | 6.1059 | 0 | N/A | 0 | 0
2020-09-12 13:30 | 6.2891 | 0 | N/A | 0 | 0
2020-09-12 14:00 | 5.9289 | 0 | N/A | 0 | 0
2020-09-12 14:30 | 5.7063 | 0 | N/A | 0 | 0
2020-09-12 15:00 | 5.8365 | 0 | N/A | 0 | 0
2020-09-12 15:30 | 6.1328 | 0 | N/A | 0 | 0
2020-09-12 16:00 | 6.256 | 0 | N/A | 0 | 0
2020-09-12 16:30 | 6.2991 | 0 | N/A | 0 | 0
2020-09-12 17:00 | 6.7145 | 0 | N/A | 0 | 0
2020-09-12 17:30 | 7.1839 | 0 | N/A | 0 | 0
2020-09-12 18:00 | 7.7233 | 0 | N/A | 0 | 0
2020-09-12 18:30 | 7.8833 | 0 | N/A | 0 | 0
2020-09-12 19:00 | 7.6 | 0 | N/A | 0 | 0
2020-09-12 19:30 | 7.2734 | 0 | N/A | 0 | 0
2020-09-12 20:00 | 6.8002 | 0 | N/A | 0 | 0
2020-09-12 20:30 | 6.3117 | 0 | N/A | 0 | 0
2020-09-12 21:00 | 5.9068 | 0 | N/A | 0 | 0
2020-09-12 21:30 | 6.3491 | 0 | N/A | 0 | 0
2020-09-12 22:00 | 6.5565 | 0 | N/A | 0 | 0
2020-09-12 22:30 | 6.2049 | 0 | N/A | 0 | 0
2020-09-12 23:00 | 6.2768 | 0 | N/A | 0 | 0
2020-09-12 23:30 | 6.2813 | 0 | N/A | 0 | 0
2020-09-13 | 6.7609 | 0 | N/A | 0 | 0
2020-09-13 00:30 | 5.9686 | 0 | N/A | 0 | 0
2020-09-13 01:00 | 5.2227 | 0 | N/A | 0 | 0
2020-09-13 01:30 | 5.0455 | 0 | N/A | 0 | 0
2020-09-13 02:00 | 4.5207 | 0 | N/A | 0 | 0
2020-09-13 02:30 | 3.7532 | 0 | N/A | 0 | 0
2020-09-13 03:00 | 3.3935 | 0 | N/A | 0 | 0
2020-09-13 03:30 | 3.1357 | 0 | N/A | 0 | 0
2020-09-13 04:00 | 3.0191 | 0 | N/A | 0 | 0
2020-09-13 04:30 | 2.8361 | 0 | N/A | 0 | 0
2020-09-13 05:00 | 2.7981 | 0 | N/A | 0 | 0
2020-09-13 05:30 | 2.889 | 0 | N/A | 0 | 0
2020-09-13 06:00 | 3.0563 | 0 | N/A | 0 | 0
2020-09-13 06:30 | 3.3014 | 0 | N/A | 0 | 0
2020-09-13 07:00 | 3.4229 | 0 | N/A | 0 | 0
2020-09-13 07:30 | 3.353 | 0 | N/A | 0 | 0
2020-09-13 08:00 | 3.4409 | 0 | N/A | 0 | 0
2020-09-13 08:30 | 4.008 | 0 | N/A | 0 | 0
2020-09-13 09:00 | 3.7442 | 0 | N/A | 0 | 0
2020-09-13 09:30 | 3.6359 | 0 | N/A | 0 | 0
2020-09-13 10:00 | 3.3384 | 0 | N/A | 0 | 0
2020-09-13 10:30 | 2.9956 | 0 | N/A | 0 | 0
2020-09-13 11:00 | 2.3801 | 0 | N/A | 0 | 0
2020-09-13 11:30 | 1.8801 | 0 | N/A | 0 | 0
2020-09-13 12:00 | 1.3636 | 0 | N/A | 0 | 0
2020-09-13 12:30 | 1.0322 | 0 | N/A | 0 | 0
2020-09-13 13:00 | 0.67119 | 0 | N/A | 0 | 0
2020-09-13 13:30 | 0.59225 | 0 | N/A | 0 | 0
2020-09-13 14:00 | 0.45734 | 0 | N/A | 0 | 0
2020-09-13 14:30 | 0.51403 | 0 | N/A | 0 | 0
2020-09-13 15:00 | 0.60226 | 0 | N/A | 0 | 0
2020-09-13 15:30 | 0.98159 | 0 | N/A | 0 | 0
2020-09-13 16:00 | 1.6037 | 0 | N/A | 0 | 0
2020-09-13 16:30 | 2.3979 | 0 | N/A | 0 | 0
2020-09-13 17:00 | 3.4475 | 0 | N/A | 0 | 0
2020-09-13 17:30 | 4.6662 | 0 | N/A | 0 | 0
2020-09-13 18:00 | 5.8154 | 0 | N/A | 0 | 0
2020-09-13 18:30 | 6.6827 | 0 | N/A | 0 | 0
2020-09-13 19:00 | 7.2872 | 0 | N/A | 0 | 0
2020-09-13 19:30 | 7.1141 | 0 | N/A | 0 | 0
2020-09-13 20:00 | 6.6083 | 0 | N/A | 0 | 0
2020-09-13 20:30 | 6.1491 | 0 | N/A | 0 | 0
2020-09-13 21:00 | 5.7595 | 0 | N/A | 0 | 0
2020-09-13 21:30 | 6.1643 | 0 | N/A | 0 | 0
2020-09-13 22:00 | 6.3745 | 0 | N/A | 0 | 0
2020-09-13 22:30 | 5.9482 | 0 | N/A | 0 | 0
2020-09-13 23:00 | 5.8985 | 0 | N/A | 0 | 0
2020-09-13 23:30 | 5.9256 | 0 | N/A | 0 | 0
2020-09-14 | 6.3193 | 0 | N/A | 0 | 0
2020-09-14 00:30 | 5.6304 | 0 | N/A | 0 | 0
2020-09-14 01:00 | 4.9147 | 0 | N/A | 0 | 0
2020-09-14 01:30 | 4.9031 | 0 | N/A | 0 | 0
2020-09-14 02:00 | 4.5147 | 0 | N/A | 0 | 0
2020-09-14 02:30 | 3.8689 | 0 | N/A | 0 | 0
2020-09-14 03:00 | 3.4517 | 0 | N/A | 0 | 0
2020-09-14 03:30 | 3.2019 | 0 | N/A | 0 | 0
2020-09-14 04:00 | 3.023 | 0 | N/A | 0 | 0
2020-09-14 04:30 | 2.942 | 0 | N/A | 0 | 0
2020-09-14 05:00 | 2.9282 | 0 | N/A | 0 | 0
2020-09-14 05:30 | 3.3255 | 0 | N/A | 0 | 0
2020-09-14 06:00 | 3.6263 | 0 | N/A | 0 | 0
2020-09-14 06:30 | 4.3251 | 0 | N/A | 0 | 0
2020-09-14 07:00 | 4.8462 | 0 | N/A | 0 | 0
2020-09-14 07:30 | 4.8143 | 0 | N/A | 0 | 0
2020-09-14 08:00 | 4.9634 | 0 | N/A | 0 | 0
2020-09-14 08:30 | 5.0574 | 0 | N/A | 0 | 0
2020-09-14 09:00 | 4.7577 | 0 | N/A | 0 | 0
2020-09-14 09:30 | 4.5435 | 0 | N/A | 0 | 0
2020-09-14 10:00 | 4.0409 | 0 | N/A | 0 | 0
2020-09-14 10:30 | 3.2018 | 0 | N/A | 0 | 0
2020-09-14 11:00 | 2.8311 | 0 | N/A | 0 | 0
2020-09-14 11:30 | 2.316 | 0 | N/A | 0 | 0
2020-09-14 12:00 | 2.0879 | 0 | N/A | 0 | 0
2020-09-14 12:30 | 2.0206 | 0 | N/A | 0 | 0
2020-09-14 13:00 | 1.4078 | 0 | N/A | 0 | 0
2020-09-14 13:30 | 1.3695 | 0 | N/A | 0 | 0
2020-09-14 14:00 | 1.3436 | 0 | N/A | 0 | 0
2020-09-14 14:30 | 1.2483 | 0 | N/A | 0 | 0
2020-09-14 15:00 | 1.3642 | 0 | N/A | 0 | 0
2020-09-14 15:30 | 1.6917 | 0 | N/A | 0 | 0
2020-09-14 16:00 | 1.9867 | 0 | N/A | 0 | 0
2020-09-14 16:30 | 2.4792 | 0 | N/A | 0 | 0
2020-09-14 17:00 | 3.3547 | 0 | N/A | 0 | 0
2020-09-14 17:30 | 4.5072 | 0 | N/A | 0 | 0
2020-09-14 18:00 | 5.6603 | 0 | N/A | 0 | 0
2020-09-14 18:30 | 6.5954 | 0 | N/A | 0 | 0
2020-09-14 19:00 | 7.2867 | 0 | N/A | 0 | 0
2020-09-14 19:30 | 7.097 | 0 | N/A | 0 | 0
2020-09-14 20:00 | 6.8014 | 0 | N/A | 0 | 0
2020-09-14 20:30 | 6.6089 | 0 | N/A | 0 | 0
2020-09-14 21:00 | 6.3281 | 0 | N/A | 0 | 0
2020-09-14 21:30 | 6.5926 | 0 | N/A | 0 | 0
2020-09-14 22:00 | 6.7678 | 0 | N/A | 0 | 0
2020-09-14 22:30 | 6.1333 | 0 | N/A | 0 | 0
2020-09-14 23:00 | 6.046 | 0 | N/A | 0 | 0
2020-09-14 23:30 | 6.2764 | 0 | N/A | 0 | 0
2020-09-15 | 6.6086 | 0 | N/A | 0 | 0
2020-09-15 00:30 | 5.8378 | 0 | N/A | 0 | 0
2020-09-15 01:00 | 5.0846 | 0 | N/A | 0 | 0
2020-09-15 01:30 | 4.9993 | 0 | N/A | 0 | 0
2020-09-15 02:00 | 4.4256 | 0 | N/A | 0 | 0
2020-09-15 02:30 | 3.8312 | 0 | N/A | 0 | 0
2020-09-15 03:00 | 3.5139 | 0 | N/A | 0 | 0
2020-09-15 03:30 | 3.3343 | 0 | N/A | 0 | 0
2020-09-15 04:00 | 3.2464 | 0 | N/A | 0 | 0
2020-09-15 04:30 | 3.1528 | 0 | N/A | 0 | 0
2020-09-15 05:00 | 3.186 | 0 | N/A | 0 | 0
2020-09-15 05:30 | 3.5549 | 0 | N/A | 0 | 0
2020-09-15 06:00 | 4.0067 | 0 | N/A | 0 | 0
2020-09-15 06:30 | 4.911 | 0 | N/A | 0 | 0
2020-09-15 07:00 | 5.4459 | 0 | N/A | 0 | 0
2020-09-15 07:30 | 5.5501 | 0 | N/A | 0 | 0
2020-09-15 08:00 | 5.9663 | 0 | N/A | 0 | 0
2020-09-15 08:30 | 5.6714 | 0 | N/A | 0 | 0
2020-09-15 09:00 | 4.6568 | 0 | N/A | 0 | 0
2020-09-15 09:30 | 3.5588 | 0 | N/A | 0 | 0
2020-09-15 10:00 | 2.9314 | 0 | N/A | 0 | 0
2020-09-15 10:30 | 2.185 | 0 | N/A | 0 | 0
2020-09-15 11:00 | 1.7373 | 0 | N/A | 0 | 0
2020-09-15 11:30 | 1.6397 | 0 | N/A | 0 | 0
2020-09-15 12:00 | 1.6276 | 0 | N/A | 0 | 0
2020-09-15 12:30 | 1.4336 | 0 | N/A | 0 | 0
2020-09-15 13:00 | 0.93015 | 0 | N/A | 0 | 0
2020-09-15 13:30 | 0.66306 | 0 | N/A | 0 | 0
2020-09-15 14:00 | 0.72197 | 0 | N/A | 0 | 0
2020-09-15 14:30 | 0.37157 | 0 | N/A | 0 | 0
2020-09-15 15:00 | 0.55628 | 0 | N/A | 0 | 0
2020-09-15 15:30 | 0.99338 | 0 | N/A | 0 | 0
2020-09-15 16:00 | 1.3941 | 0 | N/A | 0 | 0
2020-09-15 16:30 | 2.0724 | 0 | N/A | 0 | 0
2020-09-15 17:00 | 2.7526 | 0 | N/A | 0 | 0
2020-09-15 17:30 | 3.8674 | 0 | N/A | 0 | 0
2020-09-15 18:00 | 5.0725 | 0 | N/A | 0 | 0
2020-09-15 18:30 | 5.9597 | 0 | N/A | 0 | 0
2020-09-15 19:00 | 6.6131 | 0 | N/A | 0 | 0
2020-09-15 19:30 | 6.5647 | 0 | N/A | 0 | 0
2020-09-15 20:00 | 6.4123 | 0 | N/A | 0 | 0
2020-09-15 20:30 | 6.1975 | 0 | N/A | 0 | 0
2020-09-15 21:00 | 5.9505 | 0 | N/A | 0 | 0
2020-09-15 21:30 | 6.1482 | 0 | N/A | 0 | 0
2020-09-15 22:00 | 6.4468 | 0 | N/A | 0 | 0
2020-09-15 22:30 | 5.8234 | 0 | N/A | 0 | 0
2020-09-15 23:00 | 5.7728 | 0 | N/A | 0 | 0
2020-09-15 23:30 | 5.8868 | 0 | N/A | 0 | 0
2020-09-16 | 6.2282 | 0 | N/A | 0 | 0
2020-09-16 00:30 | 5.5019 | 0 | N/A | 0 | 0
2020-09-16 01:00 | 4.7192 | 0 | N/A | 0 | 0
2020-09-16 01:30 | 4.7117 | 0 | N/A | 0 | 0
2020-09-16 02:00 | 4.353 | 0 | N/A | 0 | 0
2020-09-16 02:30 | 3.7557 | 0 | N/A | 0 | 0
2020-09-16 03:00 | 3.4099 | 0 | N/A | 0 | 0
2020-09-16 03:30 | 3.0741 | 0 | N/A | 0 | 0
2020-09-16 04:00 | 2.9123 | 0 | N/A | 0 | 0
2020-09-16 04:30 | 2.8178 | 0 | N/A | 0 | 0
2020-09-16 05:00 | 2.9129 | 0 | N/A | 0 | 0
2020-09-16 05:30 | 3.2471 | 0 | N/A | 0 | 0
2020-09-16 06:00 | 3.7834 | 0 | N/A | 0 | 0
2020-09-16 06:30 | 4.6542 | 0 | N/A | 0 | 0
2020-09-16 07:00 | 5.1353 | 0 | N/A | 0 | 0
2020-09-16 07:30 | 4.9234 | 0 | N/A | 0 | 0
2020-09-16 08:00 | 4.8833 | 0 | N/A | 0 | 0
2020-09-16 08:30 | 4.9092 | 0 | N/A | 0 | 0
2020-09-16 09:00 | 4.0644 | 0 | N/A | 0 | 0
2020-09-16 09:30 | 3.0867 | 0 | N/A | 0 | 0
2020-09-16 10:00 | 2.4622 | 0 | N/A | 0 | 0
2020-09-16 10:30 | 1.8321 | 0 | N/A | 0 | 0
2020-09-16 11:00 | 1.4806 | 0 | N/A | 0 | 0
2020-09-16 11:30 | 2.2159 | 0 | N/A | 0 | 0
2020-09-16 12:00 | 2.4068 | 0 | N/A | 0 | 0
2020-09-16 12:30 | 2.1166 | 0 | N/A | 0 | 0
2020-09-16 13:00 | 1.909 | 0 | N/A | 0 | 0
2020-09-16 13:30 | 1.6679 | 0 | N/A | 0 | 0
2020-09-16 14:00 | 2.4036 | 0 | N/A | 0 | 0
2020-09-16 14:30 | 2.9848 | 0 | N/A | 0 | 0
2020-09-16 15:00 | 3.134 | 0 | N/A | 0 | 0
2020-09-16 15:30 | 2.5325 | 0 | N/A | 0 | 0
2020-09-16 16:00 | 2.1043 | 0 | N/A | 0 | 0
2020-09-16 16:30 | 2.5322 | 0 | N/A | 0 | 0
2020-09-16 17:00 | 3.6006 | 0 | N/A | 0 | 0
2020-09-16 17:30 | 4.4582 | 0 | N/A | 0 | 0
2020-09-16 18:00 | 5.224 | 0 | N/A | 0 | 0
2020-09-16 18:30 | 5.8607 | 0 | N/A | 0 | 0
2020-09-16 19:00 | 6.2799 | 0 | N/A | 0 | 0
2020-09-16 19:30 | 6.2927 | 0 | N/A | 0 | 0
2020-09-16 20:00 | 6.1252 | 0 | N/A | 0 | 0
2020-09-16 20:30 | 5.8369 | 0 | N/A | 0 | 0
2020-09-16 21:00 | 5.5659 | 0 | N/A | 0 | 0
2020-09-16 21:30 | 6.1107 | 0 | N/A | 0 | 0
2020-09-16 22:00 | 6.2778 | 0 | N/A | 0 | 0
2020-09-16 22:30 | 5.7791 | 0 | N/A | 0 | 0
2020-09-16 23:00 | 5.7365 | 0 | N/A | 0 | 0
2020-09-16 23:30 | 5.8309 | 0 | N/A | 0 | 0
2020-09-17 | 6.0427 | 0 | N/A | 0 | 0
2020-09-17 00:30 | 5.3275 | 0 | N/A | 0 | 0
2020-09-17 01:00 | 4.5182 | 0 | N/A | 0 | 0
2020-09-17 01:30 | 4.5749 | 0 | N/A | 0 | 0
2020-09-17 02:00 | 4.1512 | 0 | N/A | 0 | 0
2020-09-17 02:30 | 3.4635 | 0 | N/A | 0 | 0
2020-09-17 03:00 | 3.1398 | 0 | N/A | 0 | 0
2020-09-17 03:30 | 2.8175 | 0 | N/A | 0 | 0
2020-09-17 04:00 | 2.7207 | 0 | N/A | 0 | 0
2020-09-17 04:30 | 2.7256 | 0 | N/A | 0 | 0
2020-09-17 05:00 | 2.7368 | 0 | N/A | 0 | 0
2020-09-17 05:30 | 3.0441 | 0 | N/A | 0 | 0
2020-09-17 06:00 | 3.4118 | 0 | N/A | 0 | 0
2020-09-17 06:30 | 4.3879 | 0 | N/A | 0 | 0
2020-09-17 07:00 | 4.9607 | 0 | N/A | 0 | 0
2020-09-17 07:30 | 4.8635 | 0 | N/A | 0 | 0
2020-09-17 08:00 | 5.161 | 0 | N/A | 0 | 0
2020-09-17 08:30 | 5.4608 | 0 | N/A | 0 | 0
2020-09-17 09:00 | 5.6952 | 0 | N/A | 0 | 0
2020-09-17 09:30 | 5.6798 | 0 | N/A | 0 | 0
2020-09-17 10:00 | 5.332 | 0 | N/A | 0 | 0
2020-09-17 10:30 | 5.2252 | 0 | N/A | 0 | 0
2020-09-17 11:00 | 5.1602 | 0 | N/A | 0 | 0
2020-09-17 11:30 | 5.0876 | 0 | N/A | 0 | 0
2020-09-17 12:00 | 4.8125 | 0 | N/A | 0 | 0
2020-09-17 12:30 | 4.4242 | 0 | N/A | 0 | 0
2020-09-17 13:00 | 4.5274 | 0 | N/A | 0 | 0
2020-09-17 13:30 | 4.92 | 0 | N/A | 0 | 0
2020-09-17 14:00 | 4.945 | 0 | N/A | 0 | 0
2020-09-17 14:30 | 5.166 | 0 | N/A | 0 | 0
2020-09-17 15:00 | 5.2732 | 0 | N/A | 0 | 0
2020-09-17 15:30 | 5.6848 | 0 | N/A | 0 | 0
2020-09-17 16:00 | 6.0208 | 0 | N/A | 0 | 0
2020-09-17 16:30 | 5.9903 | 0 | N/A | 0 | 0
2020-09-17 17:00 | 6.1539 | 0 | N/A | 0 | 0
2020-09-17 17:30 | 6.7218 | 0 | N/A | 0 | 0
2020-09-17 18:00 | 7.6169 | 0 | N/A | 0 | 0
2020-09-17 18:30 | 7.9933 | 0 | N/A | 0 | 0
2020-09-17 19:00 | 8.06 | 0 | N/A | 0 | 0
2020-09-17 19:30 | 7.7933 | 0 | N/A | 0 | 0
2020-09-17 20:00 | 7.5367 | 0 | N/A | 0 | 0
2020-09-17 20:30 | 7.0935 | 0 | N/A | 0 | 0
2020-09-17 21:00 | 6.7206 | 0 | N/A | 0 | 0
2020-09-17 21:30 | 6.9852 | 0 | N/A | 0 | 0
2020-09-17 22:00 | 7.1122 | 0 | N/A | 0 | 0
2020-09-17 22:30 | 6.5307 | 0 | N/A | 0 | 0
2020-09-17 23:00 | 6.2393 | 0 | N/A | 0 | 0
2020-09-17 23:30 | 6.3123 | 0 | N/A | 0 | 0
2020-09-18 | 6.6186 | 0 | N/A | 0 | 0
2020-09-18 00:30 | 5.9701 | 0 | N/A | 0 | 0
2020-09-18 01:00 | 5.1193 | 0 | N/A | 0 | 0
2020-09-18 01:30 | 5.0423 | 0 | N/A | 0 | 0
2020-09-18 02:00 | 4.5119 | 0 | N/A | 0 | 0
2020-09-18 02:30 | 3.8749 | 0 | N/A | 0 | 0
2020-09-18 03:00 | 3.4536 | 0 | N/A | 0 | 0
2020-09-18 03:30 | 3.2514 | 0 | N/A | 0 | 0
2020-09-18 04:00 | 3.1246 | 0 | N/A | 0 | 0
2020-09-18 04:30 | 3.0514 | 0 | N/A | 0 | 0
2020-09-18 05:00 | 3.2261 | 0 | N/A | 0 | 0
2020-09-18 05:30 | 3.4409 | 0 | N/A | 0 | 0
2020-09-18 06:00 | 3.7708 | 0 | N/A | 0 | 0
2020-09-18 06:30 | 4.4807 | 0 | N/A | 0 | 0
2020-09-18 07:00 | 5.1307 | 0 | N/A | 0 | 0
2020-09-18 07:30 | 5.2303 | 0 | N/A | 0 | 0
2020-09-18 08:00 | 5.4934 | 0 | N/A | 0 | 0
2020-09-18 08:30 | 5.904 | 0 | N/A | 0 | 0
2020-09-18 09:00 | 5.595 | 0 | N/A | 0 | 0
2020-09-18 09:30 | 4.416 | 0 | N/A | 0 | 0
2020-09-18 10:00 | 4.4666 | 0 | N/A | 0 | 0
2020-09-18 10:30 | 4.9936 | 0 | N/A | 0 | 0
2020-09-18 11:00 | 5.1176 | 0 | N/A | 0 | 0
2020-09-18 11:30 | 5.0952 | 0 | N/A | 0 | 0
2020-09-18 12:00 | 4.5486 | 0 | N/A | 0 | 0
2020-09-18 12:30 | 3.4442 | 0 | N/A | 0 | 0
2020-09-18 13:00 | 3.8536 | 0 | N/A | 0 | 0
2020-09-18 13:30 | 2.6642 | 0 | N/A | 0 | 0
2020-09-18 14:00 | 2.9497 | 0 | N/A | 0 | 0
2020-09-18 14:30 | 3.1776 | 0 | N/A | 0 | 0
2020-09-18 15:00 | 2.9025 | 0 | N/A | 0 | 0
2020-09-18 15:30 | 2.3012 | 0 | N/A | 0 | 0
2020-09-18 16:00 | 2.5212 | 0 | N/A | 0 | 0
2020-09-18 16:30 | 2.9078 | 0 | N/A | 0 | 0
2020-09-18 17:00 | 3.2074 | 0 | N/A | 0 | 0
2020-09-18 17:30 | 3.8523 | 0 | N/A | 0 | 0
2020-09-18 18:00 | 4.86 | 0 | N/A | 0 | 0
2020-09-18 18:30 | 5.5681 | 0 | N/A | 0 | 0
2020-09-18 19:00 | 6.0771 | 0 | N/A | 0 | 0
2020-09-18 19:30 | 6.0632 | 0 | N/A | 0 | 0
2020-09-18 20:00 | 5.8175 | 0 | N/A | 0 | 0
2020-09-18 20:30 | 5.6366 | 0 | N/A | 0 | 0
2020-09-18 21:00 | 5.4054 | 0 | N/A | 0 | 0
2020-09-18 21:30 | 5.8166 | 0 | N/A | 0 | 0
2020-09-18 22:00 | 6.1079 | 0 | N/A | 0 | 0
2020-09-18 22:30 | 5.8185 | 0 | N/A | 0 | 0
2020-09-18 23:00 | 5.74 | 0 | N/A | 0 | 0
2020-09-18 23:30 | 5.862 | 0 | N/A | 0 | 0
2020-09-19 | 6.0653 | 0 | N/A | 0 | 0
2020-09-19 00:30 | 5.2008 | 0 | N/A | 0 | 0
2020-09-19 01:00 | 4.3826 | 0 | N/A | 0 | 0
2020-09-19 01:30 | 4.2667 | 0 | N/A | 0 | 0
2020-09-19 02:00 | 3.7533 | 0 | N/A | 0 | 0
2020-09-19 02:30 | 3.0708 | 0 | N/A | 0 | 0
2020-09-19 03:00 | 2.7423 | 0 | N/A | 0 | 0
2020-09-19 03:30 | 2.5838 | 0 | N/A | 0 | 0
2020-09-19 04:00 | 2.462 | 0 | N/A | 0 | 0
2020-09-19 04:30 | 2.3605 | 0 | N/A | 0 | 0
2020-09-19 05:00 | 2.3309 | 0 | N/A | 0 | 0
2020-09-19 05:30 | 2.4304 | 0 | N/A | 0 | 0
2020-09-19 06:00 | 2.5514 | 0 | N/A | 0 | 0
2020-09-19 06:30 | 2.8643 | 0 | N/A | 0 | 0
2020-09-19 07:00 | 2.9654 | 0 | N/A | 0 | 0
2020-09-19 07:30 | 2.7409 | 0 | N/A | 0 | 0
2020-09-19 08:00 | 2.4885 | 0 | N/A | 0 | 0
2020-09-19 08:30 | 2.5216 | 0 | N/A | 0 | 0
2020-09-19 09:00 | 1.7861 | 0 | N/A | 0 | 0
2020-09-19 09:30 | 1.4938 | 0 | N/A | 0 | 0
2020-09-19 10:00 | 0.8064 | 0 | N/A | 0 | 0
2020-09-19 10:30 | 0.4272 | 0 | N/A | 0 | 0
2020-09-19 11:00 | -0.30885 | 0 | N/A | 0 | 0
2020-09-19 11:30 | -0.39199 | 0 | N/A | 0 | 0
2020-09-19 12:00 | -0.48466 | 0 | N/A | 0 | 0
2020-09-19 12:30 | -0.43533 | 0 | N/A | 0 | 0
2020-09-19 13:00 | -0.28135 | 0 | N/A | 0 | 0
2020-09-19 13:30 | 0.25552 | 0 | N/A | 0 | 0
2020-09-19 14:00 | 0.32636 | 0 | N/A | 0 | 0
2020-09-19 14:30 | 1.0847 | 0 | N/A | 0 | 0
2020-09-19 15:00 | 1.5854 | 0 | N/A | 0 | 0
2020-09-19 15:30 | 1.7787 | 0 | N/A | 0 | 0
2020-09-19 16:00 | 2.1619 | 0 | N/A | 0 | 0
2020-09-19 16:30 | 2.4626 | 0 | N/A | 0 | 0
2020-09-19 17:00 | 3.5032 | 0 | N/A | 0 | 0
2020-09-19 17:30 | 3.9587 | 0 | N/A | 0 | 0
2020-09-19 18:00 | 4.7007 | 0 | N/A | 0 | 0
2020-09-19 18:30 | 5.1081 | 0 | N/A | 0 | 0
2020-09-19 19:00 | 5.2779 | 0 | N/A | 0 | 0
2020-09-19 19:30 | 5.4237 | 0 | N/A | 0 | 0
2020-09-19 20:00 | 5.3941 | 0 | N/A | 0 | 0
2020-09-19 20:30 | 4.823 | 0 | N/A | 0 | 0
2020-09-19 21:00 | 4.3928 | 0 | N/A | 0 | 0
2020-09-19 21:30 | 5.2978 | 0 | N/A | 0 | 0
2020-09-19 22:00 | 5.6485 | 0 | N/A | 0 | 0
2020-09-19 22:30 | 5.4189 | 0 | N/A | 0 | 0
2020-09-19 23:00 | 5.1859 | 0 | N/A | 0 | 0
2020-09-19 23:30 | 5.2571 | 0 | N/A | 0 | 0
2020-09-20 | 5.5444 | 0 | N/A | 0 | 0
2020-09-20 00:30 | 4.7494 | 0 | N/A | 0 | 0
2020-09-20 01:00 | 3.9302 | 0 | N/A | 0 | 0
2020-09-20 01:30 | 3.8374 | 0 | N/A | 0 | 0
2020-09-20 02:00 | 3.3682 | 0 | N/A | 0 | 0
2020-09-20 02:30 | 2.8212 | 0 | N/A | 0 | 0
2020-09-20 03:00 | 2.4452 | 0 | N/A | 0 | 0
2020-09-20 03:30 | 2.2953 | 0 | N/A | 0 | 0
2020-09-20 04:00 | 2.1568 | 0 | N/A | 0 | 0
2020-09-20 04:30 | 2.1273 | 0 | N/A | 0 | 0
2020-09-20 05:00 | 2.0376 | 0 | N/A | 0 | 0
2020-09-20 05:30 | 2.0405 | 0 | N/A | 0 | 0
2020-09-20 06:00 | 2.2031 | 0 | N/A | 0 | 0
2020-09-20 06:30 | 2.393 | 0 | N/A | 0 | 0
2020-09-20 07:00 | 2.4093 | 0 | N/A | 0 | 0
2020-09-20 07:30 | 2.3054 | 0 | N/A | 0 | 0
2020-09-20 08:00 | 2.3206 | 0 | N/A | 0 | 0
2020-09-20 08:30 | 2.3233 | 0 | N/A | 0 | 0
2020-09-20 09:00 | 2.1827 | 0 | N/A | 0 | 0
2020-09-20 09:30 | 1.8375 | 0 | N/A | 0 | 0
2020-09-20 10:00 | 1.9928 | 0 | N/A | 0 | 0
2020-09-20 10:30 | 2.6925 | 0 | N/A | 0 | 0
2020-09-20 11:00 | 3.2749 | 0 | N/A | 0 | 0
2020-09-20 11:30 | 3.8517 | 0 | N/A | 0 | 0
2020-09-20 12:00 | 3.2929 | 0 | N/A | 0 | 0
2020-09-20 12:30 | 2.3407 | 0 | N/A | 0 | 0
2020-09-20 13:00 | 2.31 | 0 | N/A | 0 | 0
2020-09-20 13:30 | 2.5181 | 0 | N/A | 0 | 0
2020-09-20 14:00 | 2.5 | 0 | N/A | 0 | 0
2020-09-20 14:30 | 2.2187 | 0 | N/A | 0 | 0
2020-09-20 15:00 | 1.756 | 0 | N/A | 0 | 0
2020-09-20 15:30 | 2.3778 | 0 | N/A | 0 | 0
2020-09-20 16:00 | 2.3741 | 0 | N/A | 0 | 0
2020-09-20 16:30 | 2.4728 | 0 | N/A | 0 | 0
2020-09-20 17:00 | 3.3998 | 0 | N/A | 0 | 0
2020-09-20 17:30 | 4.5803 | 0 | N/A | 0 | 0
2020-09-20 18:00 | 5.2662 | 0 | N/A | 0 | 0
2020-09-20 18:30 | 6.0024 | 0 | N/A | 0 | 0
2020-09-20 19:00 | 6.3216 | 0 | N/A | 0 | 0
2020-09-20 19:30 | 6.0672 | 0 | N/A | 0 | 0
2020-09-20 20:00 | 5.6414 | 0 | N/A | 0 | 0
2020-09-20 20:30 | 5.1515 | 0 | N/A | 0 | 0
2020-09-20 21:00 | 4.8191 | 0 | N/A | 0 | 0
2020-09-20 21:30 | 5.3473 | 0 | N/A | 0 | 0
2020-09-20 22:00 | 5.5621 | 0 | N/A | 0 | 0
2020-09-20 22:30 | 5.2568 | 0 | N/A | 0 | 0
2020-09-20 23:00 | 5.3051 | 0 | N/A | 0 | 0
2020-09-20 23:30 | 5.4057 | 0 | N/A | 0 | 0
2020-09-21 | 5.8229 | 0 | N/A | 0 | 0
2020-09-21 00:30 | 4.9756 | 0 | N/A | 0 | 0
2020-09-21 01:00 | 4.1535 | 0 | N/A | 0 | 0
2020-09-21 01:30 | 4.0192 | 0 | N/A | 0 | 0
2020-09-21 02:00 | 3.6354 | 0 | N/A | 0 | 0
2020-09-21 02:30 | 3.1444 | 0 | N/A | 0 | 0
2020-09-21 03:00 | 2.7918 | 0 | N/A | 0 | 0
2020-09-21 03:30 | 2.5043 | 0 | N/A | 0 | 0
2020-09-21 04:00 | 2.3866 | 0 | N/A | 0 | 0
2020-09-21 04:30 | 2.3065 | 0 | N/A | 0 | 0
2020-09-21 05:00 | 2.3596 | 0 | N/A | 0 | 0
2020-09-21 05:30 | 2.5668 | 0 | N/A | 0 | 0
2020-09-21 06:00 | 2.8255 | 0 | N/A | 0 | 0
2020-09-21 06:30 | 3.5815 | 0 | N/A | 0 | 0
2020-09-21 07:00 | 3.8655 | 0 | N/A | 0 | 0
2020-09-21 07:30 | 3.5256 | 0 | N/A | 0 | 0
2020-09-21 08:00 | 3.5601 | 0 | N/A | 0 | 0
2020-09-21 08:30 | 3.8568 | 0 | N/A | 0 | 0
2020-09-21 09:00 | 3.4101 | 0 | N/A | 0 | 0
2020-09-21 09:30 | 3.0767 | 0 | N/A | 0 | 0
2020-09-21 10:00 | 2.4745 | 0 | N/A | 0 | 0
2020-09-21 10:30 | 1.8733 | 0 | N/A | 0 | 0
2020-09-21 11:00 | 1.547 | 0 | N/A | 0 | 0
2020-09-21 11:30 | 1.2545 | 0 | N/A | 0 | 0
2020-09-21 12:00 | 1.0113 | 0 | N/A | 0 | 0
2020-09-21 12:30 | 0.87031 | 0 | N/A | 0 | 0
2020-09-21 13:00 | 0.62628 | 0 | N/A | 0 | 0
2020-09-21 13:30 | 0.69463 | 0 | N/A | 0 | 0
2020-09-21 14:00 | 0.76806 | 0 | N/A | 0 | 0
2020-09-21 14:30 | 0.86921 | 0 | N/A | 0 | 0
2020-09-21 15:00 | 0.94268 | 0 | N/A | 0 | 0
2020-09-21 15:30 | 1.3028 | 0 | N/A | 0 | 0
2020-09-21 16:00 | 2.0401 | 0 | N/A | 0 | 0
2020-09-21 16:30 | 2.881 | 0 | N/A | 0 | 0
2020-09-21 17:00 | 3.2153 | 0 | N/A | 0 | 0
2020-09-21 17:30 | 4.0876 | 0 | N/A | 0 | 0
2020-09-21 18:00 | 5.0914 | 0 | N/A | 0 | 0
2020-09-21 18:30 | 5.9679 | 0 | N/A | 0 | 0
2020-09-21 19:00 | 6.4938 | 0 | N/A | 0 | 0
2020-09-21 19:30 | 6.518 | 0 | N/A | 0 | 0
2020-09-21 20:00 | 6.2159 | 0 | N/A | 0 | 0
2020-09-21 20:30 | 5.8134 | 0 | N/A | 0 | 0
2020-09-21 21:00 | 5.5483 | 0 | N/A | 0 | 0
2020-09-21 21:30 | 5.8502 | 0 | N/A | 0 | 0
2020-09-21 22:00 | 6.1036 | 0 | N/A | 0 | 0
2020-09-21 22:30 | 5.639 | 0 | N/A | 0 | 0
2020-09-21 23:00 | 5.5586 | 0 | N/A | 0 | 0
2020-09-21 23:30 | 5.667 | 0 | N/A | 0 | 0
2020-09-22 | 5.9775 | 0 | N/A | 0 | 0
2020-09-22 00:30 | 5.1851 | 0 | N/A | 0 | 0
2020-09-22 01:00 | 4.4645 | 0 | N/A | 0 | 0
2020-09-22 01:30 | 4.3714 | 0 | N/A | 0 | 0
2020-09-22 02:00 | 3.9429 | 0 | N/A | 0 | 0
2020-09-22 02:30 | 3.385 | 0 | N/A | 0 | 0
2020-09-22 03:00 | 3.0508 | 0 | N/A | 0 | 0
2020-09-22 03:30 | 2.8555 | 0 | N/A | 0 | 0
2020-09-22 04:00 | 2.7209 | 0 | N/A | 0 | 0
2020-09-22 04:30 | 2.745 | 0 | N/A | 0 | 0
2020-09-22 05:00 | 2.7959 | 0 | N/A | 0 | 0
2020-09-22 05:30 | 3.0644 | 0 | N/A | 0 | 0
2020-09-22 06:00 | 3.3451 | 0 | N/A | 0 | 0
2020-09-22 06:30 | 4.2111 | 0 | N/A | 0 | 0
2020-09-22 07:00 | 4.8099 | 0 | N/A | 0 | 0
2020-09-22 07:30 | 4.79 | 0 | N/A | 0 | 0
2020-09-22 08:00 | 4.71 | 0 | N/A | 0 | 0
2020-09-22 08:30 | 4.8172 | 0 | N/A | 0 | 0
2020-09-22 09:00 | 4.6485 | 0 | N/A | 0 | 0
2020-09-22 09:30 | 3.9394 | 0 | N/A | 0 | 0
2020-09-22 10:00 | 4.2647 | 0 | N/A | 0 | 0
2020-09-22 10:30 | 3.9042 | 0 | N/A | 0 | 0
2020-09-22 11:00 | 3.9673 | 0 | N/A | 0 | 0
2020-09-22 11:30 | 3.4002 | 0 | N/A | 0 | 0
2020-09-22 12:00 | 4.0716 | 0 | N/A | 0 | 0
2020-09-22 12:30 | 4.7147 | 0 | N/A | 0 | 0
2020-09-22 13:00 | 4.6418 | 0 | N/A | 0 | 0
2020-09-22 13:30 | 4.3102 | 0 | N/A | 0 | 0
2020-09-22 14:00 | 3.2233 | 0 | N/A | 0 | 0
2020-09-22 14:30 | 3.4591 | 0 | N/A | 0 | 0
2020-09-22 15:00 | 3.7497 | 0 | N/A | 0 | 0
2020-09-22 15:30 | 4.6595 | 0 | N/A | 0 | 0
2020-09-22 16:00 | 3.9622 | 0 | N/A | 0 | 0
2020-09-22 16:30 | 4.2828 | 0 | N/A | 0 | 0
2020-09-22 17:00 | 4.6129 | 0 | N/A | 0 | 0
2020-09-22 17:30 | 5.8673 | 0 | N/A | 0 | 0
2020-09-22 18:00 | 6.9756 | 0 | N/A | 0 | 0
2020-09-22 18:30 | 7.9167 | 0 | N/A | 0 | 0
2020-09-22 19:00 | 8.0067 | 0 | N/A | 0 | 0
2020-09-22 19:30 | 7.84 | 0 | N/A | 0 | 0
2020-09-22 20:00 | 7.5734 | 0 | N/A | 0 | 0
2020-09-22 20:30 | 7.2636 | 0 | N/A | 0 | 0
2020-09-22 21:00 | 6.8279 | 0 | N/A | 0 | 0
2020-09-22 21:30 | 6.8178 | 0 | N/A | 0 | 0
2020-09-22 22:00 | 6.734 | 0 | N/A | 0 | 0
2020-09-22 22:30 | 6.0657 | 0 | N/A | 0 | 0
2020-09-22 23:00 | 5.8725 | 0 | N/A | 0 | 0
2020-09-22 23:30 | 6.0031 | 0 | N/A | 0 | 0
2020-09-23 | 6.2048 | 0 | N/A | 0 | 0
2020-09-23 00:30 | 5.5087 | 0 | N/A | 0 | 0
2020-09-23 01:00 | 4.707 | 0 | N/A | 0 | 0
2020-09-23 01:30 | 4.544 | 0 | N/A | 0 | 0
2020-09-23 02:00 | 4.0006 | 0 | N/A | 0 | 0
2020-09-23 02:30 | 3.4118 | 0 | N/A | 0 | 0
2020-09-23 03:00 | 3.0936 | 0 | N/A | 0 | 0
2020-09-23 03:30 | 2.9705 | 0 | N/A | 0 | 0
2020-09-23 04:00 | 2.8628 | 0 | N/A | 0 | 0
2020-09-23 04:30 | 2.88 | 0 | N/A | 0 | 0
2020-09-23 05:00 | 2.9609 | 0 | N/A | 0 | 0
2020-09-23 05:30 | 3.2642 | 0 | N/A | 0 | 0
2020-09-23 06:00 | 3.596 | 0 | N/A | 0 | 0
2020-09-23 06:30 | 4.6251 | 0 | N/A | 0 | 0
2020-09-23 07:00 | 5.087 | 0 | N/A | 0 | 0
2020-09-23 07:30 | 4.9401 | 0 | N/A | 0 | 0
2020-09-23 08:00 | 5.3749 | 0 | N/A | 0 | 0
2020-09-23 08:30 | 5.8151 | 0 | N/A | 0 | 0
2020-09-23 09:00 | 5.6756 | 0 | N/A | 0 | 0
2020-09-23 09:30 | 5.0334 | 0 | N/A | 0 | 0
2020-09-23 10:00 | 4.4623 | 0 | N/A | 0 | 0
2020-09-23 10:30 | 3.9401 | 0 | N/A | 0 | 0
2020-09-23 11:00 | 3.332 | 0 | N/A | 0 | 0
2020-09-23 11:30 | 3.1546 | 0 | N/A | 0 | 0
2020-09-23 12:00 | 3.2684 | 0 | N/A | 0 | 0
2020-09-23 12:30 | 3.3063 | 0 | N/A | 0 | 0
2020-09-23 13:00 | 3.1363 | 0 | N/A | 0 | 0
2020-09-23 13:30 | 3.1231 | 0 | N/A | 0 | 0
2020-09-23 14:00 | 2.8534 | 0 | N/A | 0 | 0
2020-09-23 14:30 | 2.8467 | 0 | N/A | 0 | 0
2020-09-23 15:00 | 3.1234 | 0 | N/A | 0 | 0
2020-09-23 15:30 | 2.7007 | 0 | N/A | 0 | 0
2020-09-23 16:00 | 3.1415 | 0 | N/A | 0 | 0
2020-09-23 16:30 | 3.8498 | 0 | N/A | 0 | 0
2020-09-23 17:00 | 4.6697 | 0 | N/A | 0 | 0
2020-09-23 17:30 | 5.6171 | 0 | N/A | 0 | 0
2020-09-23 18:00 | 6.5879 | 0 | N/A | 0 | 0
2020-09-23 18:30 | 7.1604 | 0 | N/A | 0 | 0
2020-09-23 19:00 | 7.6833 | 0 | N/A | 0 | 0
2020-09-23 19:30 | 7.48 | 0 | N/A | 0 | 0
2020-09-23 20:00 | 7.09 | 0 | N/A | 0 | 0
2020-09-23 20:30 | 6.7234 | 0 | N/A | 0 | 0
2020-09-23 21:00 | 6.3117 | 0 | N/A | 0 | 0
2020-09-23 21:30 | 6.6166 | 0 | N/A | 0 | 0
2020-09-23 22:00 | 6.8887 | 0 | N/A | 0 | 0
2020-09-23 22:30 | 6.3809 | 0 | N/A | 0 | 0
2020-09-23 23:00 | 6.2046 | 0 | N/A | 0 | 0
2020-09-23 23:30 | 6.2384 | 0 | N/A | 0 | 0
2020-09-24 | 6.5624 | 0 | N/A | 0 | 0
2020-09-24 00:30 | 5.8525 | 0 | N/A | 0 | 0
2020-09-24 01:00 | 5.0678 | 0 | N/A | 0 | 0
2020-09-24 01:30 | 4.9627 | 0 | N/A | 0 | 0
2020-09-24 02:00 | 4.4835 | 0 | N/A | 0 | 0
2020-09-24 02:30 | 3.8952 | 0 | N/A | 0 | 0
2020-09-24 03:00 | 3.5525 | 0 | N/A | 0 | 0
2020-09-24 03:30 | 3.3446 | 0 | N/A | 0 | 0
2020-09-24 04:00 | 3.1506 | 0 | N/A | 0 | 0
2020-09-24 04:30 | 3.2203 | 0 | N/A | 0 | 0
2020-09-24 05:00 | 3.2804 | 0 | N/A | 0 | 0
2020-09-24 05:30 | 3.5244 | 0 | N/A | 0 | 0
2020-09-24 06:00 | 3.9137 | 0 | N/A | 0 | 0
2020-09-24 06:30 | 4.6777 | 0 | N/A | 0 | 0
2020-09-24 07:00 | 5.0263 | 0 | N/A | 0 | 0
2020-09-24 07:30 | 4.6765 | 0 | N/A | 0 | 0
2020-09-24 08:00 | 4.5296 | 0 | N/A | 0 | 0
2020-09-24 08:30 | 4.6869 | 0 | N/A | 0 | 0
2020-09-24 09:00 | 7.0983 | 0 | N/A | 0 | 0
2020-09-24 09:30 | 6.7868 | 0 | N/A | 0 | 0
2020-09-24 10:00 | 5.2628 | 0 | N/A | 0 | 0
2020-09-24 10:30 | 5.7677 | 0 | N/A | 0 | 0
2020-09-24 11:00 | 6.198 | 0 | N/A | 0 | 0
2020-09-24 11:30 | 5.1786 | 0 | N/A | 0 | 0
2020-09-24 12:00 | 4.5228 | 0 | N/A | 0 | 0
2020-09-24 12:30 | 4.9186 | 0 | N/A | 0 | 0
2020-09-24 13:00 | 5.151 | 0 | N/A | 0 | 0
2020-09-24 13:30 | 5.0636 | 0 | N/A | 0 | 0
2020-09-24 14:00 | 4.3978 | 0 | N/A | 0 | 0
2020-09-24 14:30 | 4.4125 | 0 | N/A | 0 | 0
2020-09-24 15:00 | 5.0639 | 0 | N/A | 0 | 0
2020-09-24 15:30 | 5.9657 | 0 | N/A | 0 | 0
2020-09-24 16:00 | 6.741 | 0 | N/A | 0 | 0
2020-09-24 16:30 | 6.8546 | 0 | N/A | 0 | 0
2020-09-24 17:00 | 6.5099 | 0 | N/A | 0 | 0
2020-09-24 17:30 | 8.001 | 0 | N/A | 0 | 0
2020-09-24 18:00 | 8.4045 | 0 | N/A | 0 | 0
2020-09-24 18:30 | 7.8235 | 0 | N/A | 0 | 0
2020-09-24 19:00 | 8.0678 | 0 | N/A | 0 | 0
2020-09-24 19:30 | 7.8009 | 0 | N/A | 0 | 0
2020-09-24 20:00 | 7.3968 | 0 | N/A | 0 | 0
2020-09-24 20:30 | 7.2133 | 0 | N/A | 0 | 0
2020-09-24 21:00 | 6.7633 | 0 | N/A | 0 | 0
2020-09-24 21:30 | 7.0802 | 0 | N/A | 0 | 0
2020-09-24 22:00 | 7.2167 | 0 | N/A | 0 | 0
2020-09-24 22:30 | 6.71 | 0 | N/A | 0 | 0
2020-09-24 23:00 | 6.4502 | 0 | N/A | 0 | 0
2020-09-24 23:30 | 6.4205 | 0 | N/A | 0 | 0
2020-09-25 | 6.7073 | 0 | N/A | 0 | 0
2020-09-25 00:30 | 5.9869 | 0 | N/A | 0 | 0
2020-09-25 01:00 | 5.1142 | 0 | N/A | 0 | 0
2020-09-25 01:30 | 5.0352 | 0 | N/A | 0 | 0
2020-09-25 02:00 | 4.6595 | 0 | N/A | 0 | 0
2020-09-25 02:30 | 3.9173 | 0 | N/A | 0 | 0
2020-09-25 03:00 | 3.5576 | 0 | N/A | 0 | 0
2020-09-25 03:30 | 3.3752 | 0 | N/A | 0 | 0
2020-09-25 04:00 | 3.1876 | 0 | N/A | 0 | 0
2020-09-25 04:30 | 3.0949 | 0 | N/A | 0 | 0
2020-09-25 05:00 | 3.0869 | 0 | N/A | 0 | 0
2020-09-25 05:30 | 3.4317 | 0 | N/A | 0 | 0
2020-09-25 06:00 | 3.8594 | 0 | N/A | 0 | 0
2020-09-25 06:30 | 4.6775 | 0 | N/A | 0 | 0
2020-09-25 07:00 | 5.0452 | 0 | N/A | 0 | 0
2020-09-25 07:30 | 5.1533 | 0 | N/A | 0 | 0
2020-09-25 08:00 | 5.6069 | 0 | N/A | 0 | 0
2020-09-25 08:30 | 5.7242 | 0 | N/A | 0 | 0
2020-09-25 09:00 | 5.9316 | 0 | N/A | 0 | 0
2020-09-25 09:30 | 5.828 | 0 | N/A | 0 | 0
2020-09-25 10:00 | 5.6062 | 0 | N/A | 0 | 0
2020-09-25 10:30 | 5.7156 | 0 | N/A | 0 | 0
2020-09-25 11:00 | 5.7085 | 0 | N/A | 0 | 0
2020-09-25 11:30 | 6.1096 | 0 | N/A | 0 | 0
2020-09-25 12:00 | 5.8189 | 0 | N/A | 0 | 0
2020-09-25 12:30 | 5.8338 | 0 | N/A | 0 | 0
2020-09-25 13:00 | 6.9303 | 0 | N/A | 0 | 0
2020-09-25 13:30 | 7.8982 | 0 | N/A | 0 | 0
2020-09-25 14:00 | 8.0182 | 0 | N/A | 0 | 0
2020-09-25 14:30 | 7.9266 | 0 | N/A | 0 | 0
2020-09-25 15:00 | 6.9364 | 0 | N/A | 0 | 0
2020-09-25 15:30 | 6.248 | 0 | N/A | 0 | 0
2020-09-25 16:00 | 5.96 | 0 | N/A | 0 | 0
2020-09-25 16:30 | 5.4168 | 0 | N/A | 0 | 0
2020-09-25 17:00 | 5.7001 | 0 | N/A | 0 | 0
2020-09-25 17:30 | 6.5367 | 0 | N/A | 0 | 0
2020-09-25 18:00 | 7.5 | 0 | N/A | 0 | 0
2020-09-25 18:30 | 8.1769 | 0 | N/A | 0 | 0
2020-09-25 19:00 | 8.7021 | 0 | N/A | 0 | 0
2020-09-25 19:30 | 8.5858 | 0 | N/A | 0 | 0
2020-09-25 20:00 | 8.2173 | 0 | N/A | 0 | 0
2020-09-25 20:30 | 7.8167 | 0 | N/A | 0 | 0
2020-09-25 21:00 | 7.49 | 0 | N/A | 0 | 0
2020-09-25 21:30 | 7.9133 | 0 | N/A | 0 | 0
2020-09-25 22:00 | 8.0168 | 0 | N/A | 0 | 0
2020-09-25 22:30 | 7.5517 | 0 | N/A | 0 | 0
2020-09-25 23:00 | 7.456 | 0 | N/A | 0 | 0
2020-09-25 23:30 | 7.435 | 0 | N/A | 0 | 0
2020-09-26 | 7.7464 | 0 | N/A | 0 | 0
2020-09-26 00:30 | 6.9242 | 0 | N/A | 0 | 0
2020-09-26 01:00 | 6.038 | 0 | N/A | 0 | 0
2020-09-26 01:30 | 5.9461 | 0 | N/A | 0 | 0
2020-09-26 02:00 | 5.4448 | 0 | N/A | 0 | 0
2020-09-26 02:30 | 4.778 | 0 | N/A | 0 | 0
2020-09-26 03:00 | 4.295 | 0 | N/A | 0 | 0
2020-09-26 03:30 | 4.0622 | 0 | N/A | 0 | 0
2020-09-26 04:00 | 3.7982 | 0 | N/A | 0 | 0
2020-09-26 04:30 | 3.6317 | 0 | N/A | 0 | 0
2020-09-26 05:00 | 3.808 | 0 | N/A | 0 | 0
2020-09-26 05:30 | 3.935 | 0 | N/A | 0 | 0
2020-09-26 06:00 | 4.055 | 0 | N/A | 0 | 0
2020-09-26 06:30 | 4.4815 | 0 | N/A | 0 | 0
2020-09-26 07:00 | 4.6713 | 0 | N/A | 0 | 0
2020-09-26 07:30 | 4.1689 | 0 | N/A | 0 | 0
2020-09-26 08:00 | 4.3072 | 0 | N/A | 0 | 0
2020-09-26 08:30 | 4.0624 | 0 | N/A | 0 | 0
2020-09-26 09:00 | 4.1199 | 0 | N/A | 0 | 0
2020-09-26 09:30 | 0.08 | 0 | N/A | 0 | 0
2020-09-26 10:00 | 0 | 0 | N/A | 0 | 0
2020-09-26 10:30 | 0 | 0 | N/A | 0 | 0
2020-09-26 11:00 | 0 | 0 | N/A | 0 | 0
2020-09-26 11:30 | 0 | 0 | N/A | 0 | 0
2020-09-26 12:00 | 0 | 0 | N/A | 0 | 0
2020-09-26 12:30 | 0 | 0 | N/A | 0 | 0
2020-09-26 13:00 | 0 | 0 | N/A | 0 | 0
2020-09-26 13:30 | 0 | 0 | N/A | 0 | 0
2020-09-26 14:00 | 0 | 0 | N/A | 0 | 0
2020-09-26 14:30 | 0 | 0 | N/A | 0 | 0
2020-09-26 15:00 | 0 | 0 | N/A | 0 | 0
2020-09-26 15:30 | 0 | 0 | N/A | 0 | 0
2020-09-26 16:00 | 0 | 0 | N/A | 0 | 0
2020-09-26 16:30 | 0 | 0 | N/A | 0 | 0
2020-09-26 17:00 | 2.5945 | 0 | N/A | 0 | 0
2020-09-26 17:30 | 5.912 | 0 | N/A | 0 | 0
2020-09-26 18:00 | 6.9406 | 0 | N/A | 0 | 0
2020-09-26 18:30 | 7.5367 | 0 | N/A | 0 | 0
2020-09-26 19:00 | 7.7767 | 0 | N/A | 0 | 0
2020-09-26 19:30 | 7.5133 | 0 | N/A | 0 | 0
2020-09-26 20:00 | 7.0967 | 0 | N/A | 0 | 0
2020-09-26 20:30 | 6.7043 | 0 | N/A | 0 | 0
2020-09-26 21:00 | 6.416 | 0 | N/A | 0 | 0
2020-09-26 21:30 | 6.8454 | 0 | N/A | 0 | 0
2020-09-26 22:00 | 7.0652 | 0 | N/A | 0 | 0
2020-09-26 22:30 | 6.8265 | 0 | N/A | 0 | 0
2020-09-26 23:00 | 6.8885 | 0 | N/A | 0 | 0
2020-09-26 23:30 | 6.818 | 0 | N/A | 0 | 0
2020-09-27 | 7.2657 | 0 | N/A | 0 | 0
2020-09-27 00:30 | 6.4428 | 0 | N/A | 0 | 0
2020-09-27 01:00 | 5.574 | 0 | N/A | 0 | 0
2020-09-27 01:30 | 5.3523 | 0 | N/A | 0 | 0
2020-09-27 02:00 | 4.9426 | 0 | N/A | 0 | 0
2020-09-27 02:30 | 4.295 | 0 | N/A | 0 | 0
2020-09-27 03:00 | 3.9428 | 0 | N/A | 0 | 0
2020-09-27 03:30 | 3.6518 | 0 | N/A | 0 | 0
2020-09-27 04:00 | 3.5014 | 0 | N/A | 0 | 0
2020-09-27 04:30 | 3.3271 | 0 | N/A | 0 | 0
2020-09-27 05:00 | 3.3608 | 0 | N/A | 0 | 0
2020-09-27 05:30 | 3.3735 | 0 | N/A | 0 | 0
2020-09-27 06:00 | 3.5097 | 0 | N/A | 0 | 0
2020-09-27 06:30 | 3.7532 | 0 | N/A | 0 | 0
2020-09-27 07:00 | 3.8294 | 0 | N/A | 0 | 0
2020-09-27 07:30 | 3.4263 | 0 | N/A | 0 | 0
2020-09-27 08:00 | 3.2316 | 0 | N/A | 0 | 0
2020-09-27 08:30 | 3.0698 | 0 | N/A | 0 | 0
2020-09-27 09:00 | 3.222 | 0 | N/A | 0 | 0
2020-09-27 09:30 | 3.0786 | 0 | N/A | 0 | 0
2020-09-27 10:00 | 3.0594 | 0 | N/A | 0 | 0
2020-09-27 10:30 | 2.3402 | 0 | N/A | 0 | 0
2020-09-27 11:00 | 2.6658 | 0 | N/A | 0 | 0
2020-09-27 11:30 | 1.9591 | 0 | N/A | 0 | 0
2020-09-27 12:00 | 1.6944 | 0 | N/A | 0 | 0
2020-09-27 12:30 | 1.8192 | 0 | N/A | 0 | 0
2020-09-27 13:00 | 1.8752 | 0 | N/A | 0 | 0
2020-09-27 13:30 | 1.9471 | 0 | N/A | 0 | 0
2020-09-27 14:00 | 1.7091 | 0 | N/A | 0 | 0
2020-09-27 14:30 | 1.6855 | 0 | N/A | 0 | 0
2020-09-27 15:00 | 1.794 | 0 | N/A | 0 | 0
2020-09-27 15:30 | 1.9614 | 0 | N/A | 0 | 0
2020-09-27 16:00 | 2.3342 | 0 | N/A | 0 | 0
2020-09-27 16:30 | 3.248 | 0 | N/A | 0 | 0
2020-09-27 17:00 | 3.6958 | 0 | N/A | 0 | 0
2020-09-27 17:30 | 4.8337 | 0 | N/A | 0 | 0
2020-09-27 18:00 | 6.1921 | 0 | N/A | 0 | 0
2020-09-27 18:30 | 6.7797 | 0 | N/A | 0 | 0
2020-09-27 19:00 | 7.2274 | 0 | N/A | 0 | 0
2020-09-27 19:30 | 7.3705 | 0 | N/A | 0 | 0
2020-09-27 20:00 | 7.1011 | 0 | N/A | 0 | 0
2020-09-27 20:30 | 6.8029 | 0 | N/A | 0 | 0
2020-09-27 21:00 | 6.4031 | 0 | N/A | 0 | 0
2020-09-27 21:30 | 6.7801 | 0 | N/A | 0 | 0
2020-09-27 22:00 | 7.0667 | 0 | N/A | 0 | 0
2020-09-27 22:30 | 6.7265 | 0 | N/A | 0 | 0
2020-09-27 23:00 | 6.6005 | 0 | N/A | 0 | 0
2020-09-27 23:30 | 6.5702 | 0 | N/A | 0 | 0
2020-09-28 | 6.9395 | 0 | N/A | 0 | 0
2020-09-28 00:30 | 6.3016 | 0 | N/A | 0 | 0
2020-09-28 01:00 | 5.5258 | 0 | N/A | 0 | 0
2020-09-28 01:30 | 5.4764 | 0 | N/A | 0 | 0
2020-09-28 02:00 | 5.0884 | 0 | N/A | 0 | 0
2020-09-28 02:30 | 4.5751 | 0 | N/A | 0 | 0
2020-09-28 03:00 | 4.2305 | 0 | N/A | 0 | 0
2020-09-28 03:30 | 3.9807 | 0 | N/A | 0 | 0
2020-09-28 04:00 | 3.7864 | 0 | N/A | 0 | 0
2020-09-28 04:30 | 3.8355 | 0 | N/A | 0 | 0
2020-09-28 05:00 | 3.8816 | 0 | N/A | 0 | 0
2020-09-28 05:30 | 4.1649 | 0 | N/A | 0 | 0
2020-09-28 06:00 | 4.6551 | 0 | N/A | 0 | 0
2020-09-28 06:30 | 5.4711 | 0 | N/A | 0 | 0
2020-09-28 07:00 | 5.6582 | 0 | N/A | 0 | 0
2020-09-28 07:30 | 5.1033 | 0 | N/A | 0 | 0
2020-09-28 08:00 | 4.9675 | 0 | N/A | 0 | 0
2020-09-28 08:30 | 4.7135 | 0 | N/A | 0 | 0
2020-09-28 09:00 | 4.0967 | 0 | N/A | 0 | 0
2020-09-28 09:30 | 3.8667 | 0 | N/A | 0 | 0
2020-09-28 10:00 | 3.0233 | 0 | N/A | 0 | 0
2020-09-28 10:30 | 2.0739 | 0 | N/A | 0 | 0
2020-09-28 11:00 | 1.325 | 0 | N/A | 0 | 0
2020-09-28 11:30 | 0.91339 | 0 | N/A | 0 | 0
2020-09-28 12:00 | 0.9317 | 0 | N/A | 0 | 0
2020-09-28 12:30 | 0.73335 | 0 | N/A | 0 | 0
2020-09-28 13:00 | 0.53759 | 0 | N/A | 0 | 0
2020-09-28 13:30 | 0.65106 | 0 | N/A | 0 | 0
2020-09-28 14:00 | 0.3772 | 0 | N/A | 0 | 0
2020-09-28 14:30 | 0.62141 | 0 | N/A | 0 | 0
2020-09-28 15:00 | 0.95899 | 0 | N/A | 0 | 0
2020-09-28 15:30 | 1.3716 | 0 | N/A | 0 | 0
2020-09-28 16:00 | 1.6843 | 0 | N/A | 0 | 0
2020-09-28 16:30 | 2.1204 | 0 | N/A | 0 | 0
2020-09-28 17:00 | 2.9581 | 0 | N/A | 0 | 0
2020-09-28 17:30 | 4.129 | 0 | N/A | 0 | 0
2020-09-28 18:00 | 5.3688 | 0 | N/A | 0 | 0
2020-09-28 18:30 | 6.2806 | 0 | N/A | 0 | 0
2020-09-28 19:00 | 6.9444 | 0 | N/A | 0 | 0
2020-09-28 19:30 | 7.0073 | 0 | N/A | 0 | 0
2020-09-28 20:00 | 6.8107 | 0 | N/A | 0 | 0
2020-09-28 20:30 | 6.6314 | 0 | N/A | 0 | 0
2020-09-28 21:00 | 6.3434 | 0 | N/A | 0 | 0
2020-09-28 21:30 | 6.8232 | 0 | N/A | 0 | 0
2020-09-28 22:00 | 6.8973 | 0 | N/A | 0 | 0
2020-09-28 22:30 | 6.3461 | 0 | N/A | 0 | 0
2020-09-28 23:00 | 6.2231 | 0 | N/A | 0 | 0
2020-09-28 23:30 | 6.3519 | 0 | N/A | 0 | 0
2020-09-29 | 6.6864 | 0 | N/A | 0 | 0
2020-09-29 00:30 | 5.9195 | 0 | N/A | 0 | 0
2020-09-29 01:00 | 5.165 | 0 | N/A | 0 | 0
2020-09-29 01:30 | 5.1259 | 0 | N/A | 0 | 0
2020-09-29 02:00 | 4.7299 | 0 | N/A | 0 | 0
2020-09-29 02:30 | 4.2228 | 0 | N/A | 0 | 0
2020-09-29 03:00 | 3.7518 | 0 | N/A | 0 | 0
2020-09-29 03:30 | 3.6356 | 0 | N/A | 0 | 0
2020-09-29 04:00 | 3.4752 | 0 | N/A | 0 | 0
2020-09-29 04:30 | 3.4419 | 0 | N/A | 0 | 0
2020-09-29 05:00 | 3.5086 | 0 | N/A | 0 | 0
2020-09-29 05:30 | 3.8135 | 0 | N/A | 0 | 0
2020-09-29 06:00 | 4.2733 | 0 | N/A | 0 | 0
2020-09-29 06:30 | 5.1047 | 0 | N/A | 0 | 0
2020-09-29 07:00 | 5.5061 | 0 | N/A | 0 | 0
2020-09-29 07:30 | 5.2733 | 0 | N/A | 0 | 0
2020-09-29 08:00 | 5.1223 | 0 | N/A | 0 | 0
2020-09-29 08:30 | 4.9589 | 0 | N/A | 0 | 0
2020-09-29 09:00 | 4.3002 | 0 | N/A | 0 | 0
2020-09-29 09:30 | 4.0093 | 0 | N/A | 0 | 0
2020-09-29 10:00 | 3.342 | 0 | N/A | 0 | 0
2020-09-29 10:30 | 2.2827 | 0 | N/A | 0 | 0
2020-09-29 11:00 | 1.7597 | 0 | N/A | 0 | 0
2020-09-29 11:30 | 1.2495 | 0 | N/A | 0 | 0
2020-09-29 12:00 | 0.8675 | 0 | N/A | 0 | 0
2020-09-29 12:30 | 0.90702 | 0 | N/A | 0 | 0
2020-09-29 13:00 | 0.776 | 0 | N/A | 0 | 0
2020-09-29 13:30 | 1.127 | 0 | N/A | 0 | 0
2020-09-29 14:00 | 1.5008 | 0 | N/A | 0 | 0
2020-09-29 14:30 | 2.1731 | 0 | N/A | 0 | 0
2020-09-29 15:00 | 2.6775 | 0 | N/A | 0 | 0
2020-09-29 15:30 | 3.4474 | 0 | N/A | 0 | 0
2020-09-29 16:00 | 3.1973 | 0 | N/A | 0 | 0
2020-09-29 16:30 | 3.4046 | 0 | N/A | 0 | 0
2020-09-29 17:00 | 3.9217 | 0 | N/A | 0 | 0
2020-09-29 17:30 | 4.7369 | 0 | N/A | 0 | 0
2020-09-29 18:00 | 5.7724 | 0 | N/A | 0 | 0
2020-09-29 18:30 | 6.5264 | 0 | N/A | 0 | 0
2020-09-29 19:00 | 6.8085 | 0 | N/A | 0 | 0
2020-09-29 19:30 | 6.6893 | 0 | N/A | 0 | 0
2020-09-29 20:00 | 6.3712 | 0 | N/A | 0 | 0
2020-09-29 20:30 | 6.0955 | 0 | N/A | 0 | 0
2020-09-29 21:00 | 5.8183 | 0 | N/A | 0 | 0
2020-09-29 21:30 | 6.0644 | 0 | N/A | 0 | 0
2020-09-29 22:00 | 6.2069 | 0 | N/A | 0 | 0
2020-09-29 22:30 | 5.7941 | 0 | N/A | 0 | 0
2020-09-29 23:00 | 5.7511 | 0 | N/A | 0 | 0
2020-09-29 23:30 | 5.8648 | 0 | N/A | 0 | 0
2020-09-30 | 6.1412 | 0 | N/A | 0 | 0
2020-09-30 00:30 | 5.246 | 0 | N/A | 0 | 0
2020-09-30 01:00 | 4.3323 | 0 | N/A | 0 | 0
2020-09-30 01:30 | 4.32 | 0 | N/A | 0 | 0
2020-09-30 02:00 | 3.8828 | 0 | N/A | 0 | 0
2020-09-30 02:30 | 3.3547 | 0 | N/A | 0 | 0
2020-09-30 03:00 | 3.0573 | 0 | N/A | 0 | 0
2020-09-30 03:30 | 2.8942 | 0 | N/A | 0 | 0
2020-09-30 04:00 | 2.7229 | 0 | N/A | 0 | 0
2020-09-30 04:30 | 2.6591 | 0 | N/A | 0 | 0
2020-09-30 05:00 | 2.8095 | 0 | N/A | 0 | 0
2020-09-30 05:30 | 3.0157 | 0 | N/A | 0 | 0
2020-09-30 06:00 | 3.3854 | 0 | N/A | 0 | 0
2020-09-30 06:30 | 4.1114 | 0 | N/A | 0 | 0
2020-09-30 07:00 | 4.5243 | 0 | N/A | 0 | 0
2020-09-30 07:30 | 4.3802 | 0 | N/A | 0 | 0
2020-09-30 08:00 | 4.77 | 0 | N/A | 0 | 0
2020-09-30 08:30 | 5.1135 | 0 | N/A | 0 | 0
2020-09-30 09:00 | 5.185 | 0 | N/A | 0 | 0
2020-09-30 09:30 | 5.3473 | 0 | N/A | 0 | 0
2020-09-30 10:00 | 6.6166 | 0 | N/A | 0 | 0
2020-09-30 10:30 | 6.4769 | 0 | N/A | 0 | 0
2020-09-30 11:00 | 6.2179 | 0 | N/A | 0 | 0
2020-09-30 11:30 | 5.531 | 0 | N/A | 0 | 0
2020-09-30 12:00 | 5.1673 | 0 | N/A | 0 | 0
2020-09-30 12:30 | 5.2343 | 0 | N/A | 0 | 0
2020-09-30 13:00 | 4.4938 | 0 | N/A | 0 | 0
2020-09-30 13:30 | 4.4969 | 0 | N/A | 0 | 0
2020-09-30 14:00 | 5.1626 | 0 | N/A | 0 | 0
2020-09-30 14:30 | 5.1715 | 0 | N/A | 0 | 0
2020-09-30 15:00 | 5.3158 | 0 | N/A | 0 | 0
2020-09-30 15:30 | 5.5126 | 0 | N/A | 0 | 0
2020-09-30 16:00 | 5.0357 | 0 | N/A | 0 | 0
2020-09-30 16:30 | 4.8142 | 0 | N/A | 0 | 0
2020-09-30 17:00 | 5.2124 | 0 | N/A | 0 | 0
2020-09-30 17:30 | 5.8484 | 0 | N/A | 0 | 0
2020-09-30 18:00 | 6.4422 | 0 | N/A | 0 | 0
2020-09-30 18:30 | 6.997 | 0 | N/A | 0 | 0
2020-09-30 19:00 | 7.1334 | 0 | N/A | 0 | 0
2020-09-30 19:30 | 6.9901 | 0 | N/A | 0 | 0
2020-09-30 20:00 | 6.7201 | 0 | N/A | 0 | 0
2020-09-30 20:30 | 6.2784 | 0 | N/A | 0 | 0
2020-09-30 21:00 | 5.9151 | 0 | N/A | 0 | 0
2020-09-30 21:30 | 6.2696 | 0 | N/A | 0 | 0
2020-09-30 22:00 | 6.4885 | 0 | N/A | 0 | 0
2020-09-30 22:30 | 6.0811 | 0 | N/A | 0 | 0
2020-09-30 23:00 | 5.9803 | 0 | N/A | 0 | 0
2020-09-30 23:30 | 6.0154 | 0 | N/A | 0 | 0
2020-10-01 | 6.5076 | 0 | N/A | 0 | 0
2020-10-01 00:30 | 5.6148 | 0 | N/A | 0 | 0
2020-10-01 01:00 | 4.8729 | 0 | N/A | 0 | 0
2020-10-01 01:30 | 4.7844 | 0 | N/A | 0 | 0
2020-10-01 02:00 | 4.3666 | 0 | N/A | 0 | 0
2020-10-01 02:30 | 3.7659 | 0 | N/A | 0 | 0
2020-10-01 03:00 | 3.4209 | 0 | N/A | 0 | 0
2020-10-01 03:30 | 3.2866 | 0 | N/A | 0 | 0
2020-10-01 04:00 | 3.1221 | 0 | N/A | 0 | 0
2020-10-01 04:30 | 3.177 | 0 | N/A | 0 | 0
2020-10-01 05:00 | 3.2457 | 0 | N/A | 0 | 0
2020-10-01 05:30 | 3.5551 | 0 | N/A | 0 | 0
2020-10-01 06:00 | 4.0126 | 0 | N/A | 0 | 0
2020-10-01 06:30 | 4.7925 | 0 | N/A | 0 | 0
2020-10-01 07:00 | 5.1092 | 0 | N/A | 0 | 0
2020-10-01 07:30 | 4.7833 | 0 | N/A | 0 | 0
2020-10-01 08:00 | 4.4667 | 0 | N/A | 0 | 0
2020-10-01 08:30 | 4.3236 | 0 | N/A | 0 | 0
2020-10-01 09:00 | 4.2243 | 0 | N/A | 0 | 0
2020-10-01 09:30 | 4.0236 | 0 | N/A | 0 | 0
2020-10-01 10:00 | 3.4678 | 0 | N/A | 0 | 0
2020-10-01 10:30 | 2.2724 | 0 | N/A | 0 | 0
2020-10-01 11:00 | 2.5094 | 0 | N/A | 0 | 0
2020-10-01 11:30 | 1.9341 | 0 | N/A | 0 | 0
2020-10-01 12:00 | 1.4108 | 0 | N/A | 0 | 0
2020-10-01 12:30 | 0.88645 | 0 | N/A | 0 | 0
2020-10-01 13:00 | 0.53352 | 0 | N/A | 0 | 0
2020-10-01 13:30 | 0.2959 | 0 | N/A | 0 | 0
2020-10-01 14:00 | 0.41785 | 0 | N/A | 0 | 0
2020-10-01 14:30 | 0.55137 | 0 | N/A | 0 | 0
2020-10-01 15:00 | 0.53683 | 0 | N/A | 0 | 0
2020-10-01 15:30 | 0.86836 | 0 | N/A | 0 | 0
2020-10-01 16:00 | 1.3238 | 0 | N/A | 0 | 0
2020-10-01 16:30 | 1.9308 | 0 | N/A | 0 | 0
2020-10-01 17:00 | 2.7664 | 0 | N/A | 0 | 0
2020-10-01 17:30 | 3.7871 | 0 | N/A | 0 | 0
2020-10-01 18:00 | 4.8798 | 0 | N/A | 0 | 0
2020-10-01 18:30 | 5.8033 | 0 | N/A | 0 | 0
2020-10-01 19:00 | 6.4561 | 0 | N/A | 0 | 0
2020-10-01 19:30 | 6.5944 | 0 | N/A | 0 | 0
2020-10-01 20:00 | 6.3523 | 0 | N/A | 0 | 0
2020-10-01 20:30 | 6.1825 | 0 | N/A | 0 | 0
2020-10-01 21:00 | 6.0363 | 0 | N/A | 0 | 0
2020-10-01 21:30 | 6.3469 | 0 | N/A | 0 | 0
2020-10-01 22:00 | 6.4465 | 0 | N/A | 0 | 0
2020-10-01 22:30 | 5.9399 | 0 | N/A | 0 | 0
2020-10-01 23:00 | 5.8508 | 0 | N/A | 0 | 0
2020-10-01 23:30 | 5.8862 | 0 | N/A | 0 | 0
2020-10-02 | 6.2426 | 0 | N/A | 0 | 0
2020-10-02 00:30 | 5.4376 | 0 | N/A | 0 | 0
2020-10-02 01:00 | 4.6695 | 0 | N/A | 0 | 0
2020-10-02 01:30 | 4.6108 | 0 | N/A | 0 | 0
2020-10-02 02:00 | 4.1748 | 0 | N/A | 0 | 0
2020-10-02 02:30 | 3.5665 | 0 | N/A | 0 | 0
2020-10-02 03:00 | 3.2294 | 0 | N/A | 0 | 0
2020-10-02 03:30 | 3.0739 | 0 | N/A | 0 | 0
2020-10-02 04:00 | 2.9737 | 0 | N/A | 0 | 0
2020-10-02 04:30 | 2.8967 | 0 | N/A | 0 | 0
2020-10-02 05:00 | 2.9647 | 0 | N/A | 0 | 0
2020-10-02 05:30 | 3.251 | 0 | N/A | 0 | 0
2020-10-02 06:00 | 3.5686 | 0 | N/A | 0 | 0
2020-10-02 06:30 | 4.2871 | 0 | N/A | 0 | 0
2020-10-02 07:00 | 4.365 | 0 | N/A | 0 | 0
2020-10-02 07:30 | 3.8525 | 0 | N/A | 0 | 0
2020-10-02 08:00 | 3.88 | 0 | N/A | 0 | 0
2020-10-02 08:30 | 3.4512 | 0 | N/A | 0 | 0
2020-10-02 09:00 | 2.7144 | 0 | N/A | 0 | 0
2020-10-02 09:30 | 2.0717 | 0 | N/A | 0 | 0
2020-10-02 10:00 | 1.2144 | 0 | N/A | 0 | 0
2020-10-02 10:30 | 0.79957 | 0 | N/A | 0 | 0
2020-10-02 11:00 | 0.60093 | 0 | N/A | 0 | 0
2020-10-02 11:30 | 0.38416 | 0 | N/A | 0 | 0
2020-10-02 12:00 | 0.21731 | 0 | N/A | 0 | 0
2020-10-02 12:30 | 0.13337 | 0 | N/A | 0 | 0
2020-10-02 13:00 | -0.11175 | 0 | N/A | 0 | 0
2020-10-02 13:30 | -0.11479 | 0 | N/A | 0 | 0
2020-10-02 14:00 | 0.15232 | 0 | N/A | 0 | 0
2020-10-02 14:30 | 0.38834 | 0 | N/A | 0 | 0
2020-10-02 15:00 | 0.67991 | 0 | N/A | 0 | 0
2020-10-02 15:30 | 1.0402 | 0 | N/A | 0 | 0
2020-10-02 16:00 | 1.2535 | 0 | N/A | 0 | 0
2020-10-02 16:30 | 1.6747 | 0 | N/A | 0 | 0
2020-10-02 17:00 | 2.4083 | 0 | N/A | 0 | 0
2020-10-02 17:30 | 3.1437 | 0 | N/A | 0 | 0
2020-10-02 18:00 | 4.0141 | 0 | N/A | 0 | 0
2020-10-02 18:30 | 4.4157 | 0 | N/A | 0 | 0
2020-10-02 19:00 | 4.8211 | 0 | N/A | 0 | 0
2020-10-02 19:30 | 4.8828 | 0 | N/A | 0 | 0
2020-10-02 20:00 | 4.7484 | 0 | N/A | 0 | 0
2020-10-02 20:30 | 4.4984 | 0 | N/A | 0 | 0
2020-10-02 21:00 | 4.2561 | 0 | N/A | 0 | 0
2020-10-02 21:30 | 4.7662 | 0 | N/A | 0 | 0
2020-10-02 22:00 | 5.0263 | 0 | N/A | 0 | 0
2020-10-02 22:30 | 4.7733 | 0 | N/A | 0 | 0
2020-10-02 23:00 | 4.7305 | 0 | N/A | 0 | 0
2020-10-02 23:30 | 5.1019 | 0 | N/A | 0 | 0
2020-10-03 | 5.5204 | 0 | N/A | 0 | 0
2020-10-03 00:30 | 4.5726 | 0 | N/A | 0 | 0
2020-10-03 01:00 | 3.7117 | 0 | N/A | 0 | 0
2020-10-03 01:30 | 3.7253 | 0 | N/A | 0 | 0
2020-10-03 02:00 | 3.3019 | 0 | N/A | 0 | 0
2020-10-03 02:30 | 2.8043 | 0 | N/A | 0 | 0
2020-10-03 03:00 | 2.447 | 0 | N/A | 0 | 0
2020-10-03 03:30 | 2.3017 | 0 | N/A | 0 | 0
2020-10-03 04:00 | 2.1845 | 0 | N/A | 0 | 0
2020-10-03 04:30 | 2.1272 | 0 | N/A | 0 | 0
2020-10-03 05:00 | 2.1242 | 0 | N/A | 0 | 0
2020-10-03 05:30 | 2.16 | 0 | N/A | 0 | 0
2020-10-03 06:00 | 2.2886 | 0 | N/A | 0 | 0
2020-10-03 06:30 | 2.552 | 0 | N/A | 0 | 0
2020-10-03 07:00 | 2.3797 | 0 | N/A | 0 | 0
2020-10-03 07:30 | 2.008 | 0 | N/A | 0 | 0
2020-10-03 08:00 | 1.6779 | 0 | N/A | 0 | 0
2020-10-03 08:30 | 1.3949 | 0 | N/A | 0 | 0
2020-10-03 09:00 | 0.3095 | 0 | N/A | 0 | 0
2020-10-03 09:30 | 0 | 0 | N/A | 0 | 0
2020-10-03 10:00 | 0 | 0 | N/A | 0 | 0
2020-10-03 10:30 | 0 | 0 | N/A | 0 | 0
2020-10-03 11:00 | 0 | 0 | N/A | 0 | 0
2020-10-03 11:30 | 0 | 0 | N/A | 0 | 0
2020-10-03 12:00 | 0 | 0 | N/A | 0 | 0
2020-10-03 12:30 | 0 | 0 | N/A | 0 | 0
2020-10-03 13:00 | 0 | 0 | N/A | 0 | 0
2020-10-03 13:30 | 0 | 0 | N/A | 0 | 0
2020-10-03 14:00 | 0 | 0 | N/A | 0 | 0
2020-10-03 14:30 | 0 | 0 | N/A | 0 | 0
2020-10-03 15:00 | 0 | 0 | N/A | 0 | 0
2020-10-03 15:30 | 0.41538 | 0 | N/A | 0 | 0
2020-10-03 16:00 | 2.2838 | 0 | N/A | 0 | 0
2020-10-03 16:30 | 2.4556 | 0 | N/A | 0 | 0
2020-10-03 17:00 | 3.1724 | 0 | N/A | 0 | 0
2020-10-03 17:30 | 3.6096 | 0 | N/A | 0 | 0
2020-10-03 18:00 | 4.0175 | 0 | N/A | 0 | 0
2020-10-03 18:30 | 4.5055 | 0 | N/A | 0 | 0
2020-10-03 19:00 | 4.7442 | 0 | N/A | 0 | 0
2020-10-03 19:30 | 4.7382 | 0 | N/A | 0 | 0
2020-10-03 20:00 | 4.5238 | 0 | N/A | 0 | 0
2020-10-03 20:30 | 4.1081 | 0 | N/A | 0 | 0
2020-10-03 21:00 | 3.8184 | 0 | N/A | 0 | 0
2020-10-03 21:30 | 4.3728 | 0 | N/A | 0 | 0
2020-10-03 22:00 | 4.6032 | 0 | N/A | 0 | 0
2020-10-03 22:30 | 4.4402 | 0 | N/A | 0 | 0
2020-10-03 23:00 | 4.647 | 0 | N/A | 0 | 0
2020-10-03 23:30 | 4.9216 | 0 | N/A | 0 | 0
2020-10-04 | 5.2396 | 0 | N/A | 0 | 0
2020-10-04 00:30 | 4.3954 | 0 | N/A | 0 | 0
2020-10-04 01:00 | 3.6288 | 0 | N/A | 0 | 0
2020-10-04 01:30 | 3.6316 | 0 | N/A | 0 | 0
2020-10-04 02:00 | 3.3088 | 0 | N/A | 0 | 0
2020-10-04 03:30 | 2.6356 | 0 | N/A | 0 | 0
2020-10-04 04:00 | 2.3909 | 0 | N/A | 0 | 0
2020-10-04 04:30 | 2.163 | 0 | N/A | 0 | 0
2020-10-04 05:00 | 2.1304 | 0 | N/A | 0 | 0
2020-10-04 05:30 | 2.02 | 0 | N/A | 0 | 0
2020-10-04 06:00 | 2.0155 | 0 | N/A | 0 | 0
2020-10-04 06:30 | 2.2315 | 0 | N/A | 0 | 0
2020-10-04 07:00 | 2.2632 | 0 | N/A | 0 | 0
2020-10-04 07:30 | 2.3946 | 0 | N/A | 0 | 0
2020-10-04 08:00 | 2.5804 | 0 | N/A | 0 | 0
2020-10-04 08:30 | 2.3467 | 0 | N/A | 0 | 0
2020-10-04 09:00 | 2.385 | 0 | N/A | 0 | 0
2020-10-04 09:30 | 1.8227 | 0 | N/A | 0 | 0
2020-10-04 10:00 | 2.2418 | 0 | N/A | 0 | 0
2020-10-04 10:30 | 2.7045 | 0 | N/A | 0 | 0
2020-10-04 11:00 | 2.6672 | 0 | N/A | 0 | 0
2020-10-04 11:30 | 1.5709 | 0 | N/A | 0 | 0
2020-10-04 12:00 | 0.9347 | 0 | N/A | 0 | 0
2020-10-04 12:30 | 1.2376 | 0 | N/A | 0 | 0
2020-10-04 13:00 | 1.9992 | 0 | N/A | 0 | 0
2020-10-04 13:30 | 2.3121 | 0 | N/A | 0 | 0
2020-10-04 14:00 | 1.9108 | 0 | N/A | 0 | 0
2020-10-04 14:30 | 2.0978 | 0 | N/A | 0 | 0
2020-10-04 15:00 | 1.7666 | 0 | N/A | 0 | 0
2020-10-04 15:30 | 1.4067 | 0 | N/A | 0 | 0
2020-10-04 16:00 | 2.3625 | 0 | N/A | 0 | 0
2020-10-04 16:30 | 3.0203 | 0 | N/A | 0 | 0
2020-10-04 17:00 | 3.2229 | 0 | N/A | 0 | 0
2020-10-04 17:30 | 3.5689 | 0 | N/A | 0 | 0
2020-10-04 18:00 | 4.0672 | 0 | N/A | 0 | 0
2020-10-04 18:30 | 4.6398 | 0 | N/A | 0 | 0
2020-10-04 19:00 | 5.0149 | 0 | N/A | 0 | 0
2020-10-04 19:30 | 5.1924 | 0 | N/A | 0 | 0
2020-10-04 20:00 | 5.1699 | 0 | N/A | 0 | 0
2020-10-04 20:30 | 4.8169 | 0 | N/A | 0 | 0
2020-10-04 21:00 | 4.5371 | 0 | N/A | 0 | 0
2020-10-04 21:30 | 4.2797 | 0 | N/A | 0 | 0
2020-10-04 22:00 | 4.0431 | 0 | N/A | 0 | 0
2020-10-04 22:30 | 4.4529 | 0 | N/A | 0 | 0
2020-10-04 23:00 | 4.612 | 0 | N/A | 0 | 0
2020-10-04 23:30 | 4.2888 | 0 | N/A | 0 | 0
2020-10-05 | 4.4661 | 0 | N/A | 0 | 0
2020-10-05 00:30 | 4.898 | 0 | N/A | 0 | 0
2020-10-05 01:00 | 5.3583 | 0 | N/A | 0 | 0
2020-10-05 01:30 | 4.6108 | 0 | N/A | 0 | 0
2020-10-05 02:00 | 3.9048 | 0 | N/A | 0 | 0
2020-10-05 02:30 | 3.9374 | 0 | N/A | 0 | 0
2020-10-05 03:00 | 3.5601 | 0 | N/A | 0 | 0
2020-10-05 03:30 | 3.0573 | 0 | N/A | 0 | 0
2020-10-05 04:00 | 2.7566 | 0 | N/A | 0 | 0
2020-10-05 04:30 | 2.6311 | 0 | N/A | 0 | 0
2020-10-05 05:00 | 2.6123 | 0 | N/A | 0 | 0
2020-10-05 05:30 | 2.7608 | 0 | N/A | 0 | 0
2020-10-05 06:00 | 3.1371 | 0 | N/A | 0 | 0
2020-10-05 06:30 | 3.9839 | 0 | N/A | 0 | 0
2020-10-05 07:00 | 4.5613 | 0 | N/A | 0 | 0
2020-10-05 07:30 | 5.5385 | 0 | N/A | 0 | 0
2020-10-05 08:00 | 6.288 | 0 | N/A | 0 | 0
2020-10-05 08:30 | 6.5978 | 0 | N/A | 0 | 0
2020-10-05 09:00 | 6.5256 | 0 | N/A | 0 | 0
2020-10-05 09:30 | 6.4656 | 0 | N/A | 0 | 0
2020-10-05 10:00 | 5.952 | 0 | N/A | 0 | 0
2020-10-05 10:30 | 5.7891 | 0 | N/A | 0 | 0
2020-10-05 11:00 | 5.3951 | 0 | N/A | 0 | 0
2020-10-05 11:30 | 4.237 | 0 | N/A | 0 | 0
2020-10-05 12:00 | 4.1122 | 0 | N/A | 0 | 0
2020-10-05 12:30 | 3.8263 | 0 | N/A | 0 | 0
2020-10-05 13:00 | 3.0749 | 0 | N/A | 0 | 0
2020-10-05 13:30 | 3.2357 | 0 | N/A | 0 | 0
2020-10-05 14:00 | 3.7849 | 0 | N/A | 0 | 0
2020-10-05 14:30 | 4.4519 | 0 | N/A | 0 | 0
2020-10-05 15:00 | 4.3687 | 0 | N/A | 0 | 0
2020-10-05 15:30 | 4.9863 | 0 | N/A | 0 | 0
2020-10-05 16:00 | 5.0274 | 0 | N/A | 0 | 0
2020-10-05 16:30 | 5.1071 | 0 | N/A | 0 | 0
2020-10-05 17:00 | 4.9381 | 0 | N/A | 0 | 0
2020-10-05 17:30 | 5.3183 | 0 | N/A | 0 | 0
2020-10-05 18:00 | 6.3812 | 0 | N/A | 0 | 0
2020-10-05 18:30 | 6.9684 | 0 | N/A | 0 | 0
2020-10-05 19:00 | 7.1646 | 0 | N/A | 0 | 0
2020-10-05 19:30 | 7.106 | 0 | N/A | 0 | 0
2020-10-05 20:00 | 7.1114 | 0 | N/A | 0 | 0
2020-10-05 20:30 | 7.034 | 0 | N/A | 0 | 0
2020-10-05 21:00 | 6.768 | 0 | N/A | 0 | 0
2020-10-05 21:30 | 6.2451 | 0 | N/A | 0 | 0
2020-10-05 22:00 | 5.6949 | 0 | N/A | 0 | 0
2020-10-05 22:30 | 5.7651 | 0 | N/A | 0 | 0
2020-10-05 23:00 | 5.7939 | 0 | N/A | 0 | 0
2020-10-05 23:30 | 5.3404 | 0 | N/A | 0 | 0
2020-10-06 | 5.2452 | 0 | N/A | 0 | 0
2020-10-06 00:30 | 5.62 | 0 | N/A | 0 | 0
2020-10-06 01:00 | 6.1161 | 0 | N/A | 0 | 0
2020-10-06 01:30 | 5.4164 | 0 | N/A | 0 | 0
2020-10-06 02:00 | 4.6753 | 0 | N/A | 0 | 0
2020-10-06 02:30 | 4.696 | 0 | N/A | 0 | 0
2020-10-06 03:00 | 4.2342 | 0 | N/A | 0 | 0
2020-10-06 03:30 | 3.7235 | 0 | N/A | 0 | 0
2020-10-06 04:00 | 3.4412 | 0 | N/A | 0 | 0
2020-10-06 04:30 | 3.3297 | 0 | N/A | 0 | 0
2020-10-06 05:00 | 3.3441 | 0 | N/A | 0 | 0
2020-10-06 05:30 | 3.6646 | 0 | N/A | 0 | 0
2020-10-06 06:00 | 4.0546 | 0 | N/A | 0 | 0
2020-10-06 06:30 | 4.7773 | 0 | N/A | 0 | 0
2020-10-06 07:00 | 5.7536 | 0 | N/A | 0 | 0
2020-10-06 07:30 | 6.9835 | 0 | N/A | 0 | 0
2020-10-06 08:00 | 7.3461 | 0 | N/A | 0 | 0
2020-10-06 08:30 | 6.099 | 0 | N/A | 0 | 0
2020-10-06 09:00 | 6.4281 | 0 | N/A | 0 | 0
2020-10-06 09:30 | 5.9382 | 0 | N/A | 0 | 0
2020-10-06 10:00 | 5.5115 | 0 | N/A | 0 | 0
2020-10-06 10:30 | 4.4228 | 0 | N/A | 0 | 0
2020-10-06 11:00 | 4.5297 | 0 | N/A | 0 | 0
2020-10-06 11:30 | 3.726 | 0 | N/A | 0 | 0
2020-10-06 12:00 | 3.8337 | 0 | N/A | 0 | 0
2020-10-06 12:30 | 3.9162 | 0 | N/A | 0 | 0
2020-10-06 13:00 | 3.9705 | 0 | N/A | 0 | 0
2020-10-06 13:30 | 3.4433 | 0 | N/A | 0 | 0
2020-10-06 14:00 | 2.8303 | 0 | N/A | 0 | 0
2020-10-06 14:30 | 3.1334 | 0 | N/A | 0 | 0
2020-10-06 15:00 | 3.7934 | 0 | N/A | 0 | 0
2020-10-06 15:30 | 3.7769 | 0 | N/A | 0 | 0
2020-10-06 16:00 | 3.1057 | 0 | N/A | 0 | 0
2020-10-06 16:30 | 3.7007 | 0 | N/A | 0 | 0
2020-10-06 17:00 | 4.2485 | 0 | N/A | 0 | 0
2020-10-06 17:30 | 4.5231 | 0 | N/A | 0 | 0
2020-10-06 18:00 | 5.6709 | 0 | N/A | 0 | 0
2020-10-06 18:30 | 6.4346 | 0 | N/A | 0 | 0
2020-10-06 19:00 | 6.7363 | 0 | N/A | 0 | 0
2020-10-06 19:30 | 7.0138 | 0 | N/A | 0 | 0
2020-10-06 20:00 | 7.2441 | 0 | N/A | 0 | 0
2020-10-06 20:30 | 7.1136 | 0 | N/A | 0 | 0
2020-10-06 21:00 | 6.8277 | 0 | N/A | 0 | 0
2020-10-06 21:30 | 6.2677 | 0 | N/A | 0 | 0
2020-10-06 22:00 | 5.7351 | 0 | N/A | 0 | 0
2020-10-06 22:30 | 5.859 | 0 | N/A | 0 | 0
2020-10-06 23:00 | 5.731 | 0 | N/A | 0 | 0
2020-10-06 23:30 | 5.316 | 0 | N/A | 0 | 0
2020-10-07 | 5.2568 | 0 | N/A | 0 | 0
2020-10-07 00:30 | 5.6066 | 0 | N/A | 0 | 0
2020-10-07 01:00 | 6.0002 | 0 | N/A | 0 | 0
2020-10-07 01:30 | 5.3016 | 0 | N/A | 0 | 0
2020-10-07 02:00 | 4.5286 | 0 | N/A | 0 | 0
2020-10-07 02:30 | 4.4671 | 0 | N/A | 0 | 0
2020-10-07 03:00 | 4.1015 | 0 | N/A | 0 | 0
2020-10-07 03:30 | 3.5608 | 0 | N/A | 0 | 0
2020-10-07 04:00 | 3.2554 | 0 | N/A | 0 | 0
2020-10-07 04:30 | 3.1455 | 0 | N/A | 0 | 0
2020-10-07 05:00 | 3.1081 | 0 | N/A | 0 | 0
2020-10-07 05:30 | 3.3425 | 0 | N/A | 0 | 0
2020-10-07 06:00 | 3.67 | 0 | N/A | 0 | 0
2020-10-07 06:30 | 4.6511 | 0 | N/A | 0 | 0
2020-10-07 07:00 | 5.5433 | 0 | N/A | 0 | 0
2020-10-07 07:30 | 6.4516 | 0 | N/A | 0 | 0
2020-10-07 08:00 | 6.8545 | 0 | N/A | 0 | 0
2020-10-07 08:30 | 6.4641 | 0 | N/A | 0 | 0
2020-10-07 09:00 | 5.9652 | 0 | N/A | 0 | 0
2020-10-07 09:30 | 5.7127 | 0 | N/A | 0 | 0
2020-10-07 10:00 | 5.0272 | 0 | N/A | 0 | 0
2020-10-07 10:30 | 4.6302 | 0 | N/A | 0 | 0
2020-10-07 11:00 | 3.9042 | 0 | N/A | 0 | 0
2020-10-07 11:30 | 3.4002 | 0 | N/A | 0 | 0
2020-10-07 12:00 | 3.7871 | 0 | N/A | 0 | 0
2020-10-07 12:30 | 4.2907 | 0 | N/A | 0 | 0
2020-10-07 13:00 | 4.5833 | 0 | N/A | 0 | 0
2020-10-07 13:30 | 3.9074 | 0 | N/A | 0 | 0
2020-10-07 14:00 | 4.4053 | 0 | N/A | 0 | 0
2020-10-07 14:30 | 4.4609 | 0 | N/A | 0 | 0
2020-10-07 15:00 | 4.6135 | 0 | N/A | 0 | 0
2020-10-07 15:30 | 4.829 | 0 | N/A | 0 | 0
2020-10-07 16:00 | 4.1664 | 0 | N/A | 0 | 0
2020-10-07 16:30 | 4.2216 | 0 | N/A | 0 | 0
2020-10-07 17:00 | 4.9643 | 0 | N/A | 0 | 0
2020-10-07 17:30 | 6.0366 | 0 | N/A | 0 | 0
2020-10-07 18:00 | 6.7419 | 0 | N/A | 0 | 0
2020-10-07 18:30 | 6.6615 | 0 | N/A | 0 | 0
2020-10-07 19:00 | 6.8973 | 0 | N/A | 0 | 0
2020-10-07 19:30 | 6.8341 | 0 | N/A | 0 | 0
2020-10-07 20:00 | 6.8367 | 0 | N/A | 0 | 0
2020-10-07 20:30 | 6.4637 | 0 | N/A | 0 | 0
2020-10-07 21:00 | 6.0588 | 0 | N/A | 0 | 0
2020-10-07 21:30 | 5.4802 | 0 | N/A | 0 | 0
2020-10-07 22:00 | 4.9748 | 0 | N/A | 0 | 0
2020-10-07 22:30 | 5.1513 | 0 | N/A | 0 | 0
2020-10-07 23:00 | 5.171 | 0 | N/A | 0 | 0
2020-10-07 23:30 | 4.7716 | 0 | N/A | 0 | 0
2020-10-08 | 4.7822 | 0 | N/A | 0 | 0
2020-10-08 00:30 | 5.0936 | 0 | N/A | 0 | 0
2020-10-08 01:00 | 5.4864 | 0 | N/A | 0 | 0
2020-10-08 01:30 | 4.7855 | 0 | N/A | 0 | 0
2020-10-08 02:00 | 4.1007 | 0 | N/A | 0 | 0
2020-10-08 02:30 | 3.9642 | 0 | N/A | 0 | 0
2020-10-08 03:00 | 3.6143 | 0 | N/A | 0 | 0
2020-10-08 03:30 | 3.1928 | 0 | N/A | 0 | 0
2020-10-08 04:00 | 2.9038 | 0 | N/A | 0 | 0
2020-10-08 04:30 | 2.7258 | 0 | N/A | 0 | 0
2020-10-08 05:00 | 2.7525 | 0 | N/A | 0 | 0
2020-10-08 05:30 | 2.9207 | 0 | N/A | 0 | 0
2020-10-08 06:00 | 3.1739 | 0 | N/A | 0 | 0
2020-10-08 06:30 | 3.878 | 0 | N/A | 0 | 0
2020-10-08 07:00 | 4.6406 | 0 | N/A | 0 | 0
2020-10-08 07:30 | 5.683 | 0 | N/A | 0 | 0
2020-10-08 08:00 | 6.5349 | 0 | N/A | 0 | 0
2020-10-08 08:30 | 6.4092 | 0 | N/A | 0 | 0
2020-10-08 09:00 | 6.2966 | 0 | N/A | 0 | 0
2020-10-08 09:30 | 6.2637 | 0 | N/A | 0 | 0
2020-10-08 10:00 | 5.5905 | 0 | N/A | 0 | 0
2020-10-08 10:30 | 5.1988 | 0 | N/A | 0 | 0
2020-10-08 11:00 | 5.2698 | 0 | N/A | 0 | 0
2020-10-08 11:30 | 5.8522 | 0 | N/A | 0 | 0
2020-10-08 12:00 | 5.5921 | 0 | N/A | 0 | 0
2020-10-08 12:30 | 5.8187 | 0 | N/A | 0 | 0
2020-10-08 13:00 | 5.2724 | 0 | N/A | 0 | 0
2020-10-08 13:30 | 5.1217 | 0 | N/A | 0 | 0
2020-10-08 14:00 | 5.2025 | 0 | N/A | 0 | 0
2020-10-08 14:30 | 5.4849 | 0 | N/A | 0 | 0
2020-10-08 15:00 | 5.7836 | 0 | N/A | 0 | 0
2020-10-08 15:30 | 5.3276 | 0 | N/A | 0 | 0
2020-10-08 16:00 | 5.597 | 0 | N/A | 0 | 0
2020-10-08 16:30 | 5.75 | 0 | N/A | 0 | 0
2020-10-08 17:00 | 6.3667 | 0 | N/A | 0 | 0
2020-10-08 17:30 | 6.7934 | 0 | N/A | 0 | 0
2020-10-08 18:00 | 7.4567 | 0 | N/A | 0 | 0
2020-10-08 18:30 | 7.7733 | 0 | N/A | 0 | 0
2020-10-08 19:00 | 7.7967 | 0 | N/A | 0 | 0
2020-10-08 19:30 | 7.67 | 0 | N/A | 0 | 0
2020-10-08 20:00 | 7.5833 | 0 | N/A | 0 | 0
2020-10-08 20:30 | 7.36 | 0 | N/A | 0 | 0
2020-10-08 21:00 | 7.0133 | 0 | N/A | 0 | 0
2020-10-08 21:30 | 6.5776 | 0 | N/A | 0 | 0
2020-10-08 22:00 | 6.0302 | 0 | N/A | 0 | 0
2020-10-08 22:30 | 6.0398 | 0 | N/A | 0 | 0
2020-10-08 23:00 | 5.9848 | 0 | N/A | 0 | 0
2020-10-08 23:30 | 5.5068 | 0 | N/A | 0 | 0
2020-10-09 | 5.3452 | 0 | N/A | 0 | 0
2020-10-09 00:30 | 5.7277 | 0 | N/A | 0 | 0
2020-10-09 01:00 | 6.3919 | 0 | N/A | 0 | 0
2020-10-09 01:30 | 5.809 | 0 | N/A | 0 | 0
2020-10-09 02:00 | 5.0011 | 0 | N/A | 0 | 0
2020-10-09 02:30 | 4.8557 | 0 | N/A | 0 | 0
2020-10-09 03:00 | 4.5153 | 0 | N/A | 0 | 0
2020-10-09 03:30 | 3.9862 | 0 | N/A | 0 | 0
2020-10-09 04:00 | 3.6661 | 0 | N/A | 0 | 0
2020-10-09 04:30 | 3.5609 | 0 | N/A | 0 | 0
2020-10-09 05:00 | 3.4737 | 0 | N/A | 0 | 0
2020-10-09 05:30 | 3.8017 | 0 | N/A | 0 | 0
2020-10-09 06:00 | 4.1064 | 0 | N/A | 0 | 0
2020-10-09 06:30 | 4.8045 | 0 | N/A | 0 | 0
2020-10-09 07:00 | 5.4409 | 0 | N/A | 0 | 0
2020-10-09 07:30 | 6.4815 | 0 | N/A | 0 | 0
2020-10-09 08:00 | 7.0367 | 0 | N/A | 0 | 0
2020-10-09 08:30 | 6.684 | 0 | N/A | 0 | 0
2020-10-09 09:00 | 6.6641 | 0 | N/A | 0 | 0
2020-10-09 09:30 | 6.2302 | 0 | N/A | 0 | 0
2020-10-09 10:00 | 5.8407 | 0 | N/A | 0 | 0
2020-10-09 10:30 | 5.6439 | 0 | N/A | 0 | 0
2020-10-09 11:00 | 4.8137 | 0 | N/A | 0 | 0
2020-10-09 11:30 | 4.8401 | 0 | N/A | 0 | 0
2020-10-09 12:00 | 4.9303 | 0 | N/A | 0 | 0
2020-10-09 12:30 | 4.3934 | 0 | N/A | 0 | 0
2020-10-09 13:00 | 4.1702 | 0 | N/A | 0 | 0
2020-10-09 13:30 | 3.7134 | 0 | N/A | 0 | 0
2020-10-09 14:00 | 3.4033 | 0 | N/A | 0 | 0
2020-10-09 14:30 | 3.1907 | 0 | N/A | 0 | 0
2020-10-09 15:00 | 3.3921 | 0 | N/A | 0 | 0
2020-10-09 15:30 | 2.914 | 0 | N/A | 0 | 0
2020-10-09 16:00 | 2.8843 | 0 | N/A | 0 | 0
2020-10-09 16:30 | 3.3182 | 0 | N/A | 0 | 0
2020-10-09 17:00 | 3.8747 | 0 | N/A | 0 | 0
2020-10-09 17:30 | 4.4156 | 0 | N/A | 0 | 0
2020-10-09 18:00 | 4.7254 | 0 | N/A | 0 | 0
2020-10-09 18:30 | 5.4975 | 0 | N/A | 0 | 0
2020-10-09 19:00 | 6.066 | 0 | N/A | 0 | 0
2020-10-09 19:30 | 6.3965 | 0 | N/A | 0 | 0
2020-10-09 20:00 | 6.5123 | 0 | N/A | 0 | 0
2020-10-09 20:30 | 6.5446 | 0 | N/A | 0 | 0
2020-10-09 21:00 | 6.3629 | 0 | N/A | 0 | 0
2020-10-09 21:30 | 6.0731 | 0 | N/A | 0 | 0
2020-10-09 22:00 | 5.7968 | 0 | N/A | 0 | 0
2020-10-09 22:30 | 6.0971 | 0 | N/A | 0 | 0
2020-10-09 23:00 | 6.1304 | 0 | N/A | 0 | 0
2020-10-09 23:30 | 5.6726 | 0 | N/A | 0 | 0
2020-10-10 | 5.7285 | 0 | N/A | 0 | 0
2020-10-10 00:30 | 5.9973 | 0 | N/A | 0 | 0
2020-10-10 01:00 | 6.3878 | 0 | N/A | 0 | 0
2020-10-10 01:30 | 5.6473 | 0 | N/A | 0 | 0
2020-10-10 02:00 | 4.9348 | 0 | N/A | 0 | 0
2020-10-10 02:30 | 4.8466 | 0 | N/A | 0 | 0
2020-10-10 03:00 | 4.3699 | 0 | N/A | 0 | 0
2020-10-10 03:30 | 3.841 | 0 | N/A | 0 | 0
2020-10-10 04:00 | 3.5288 | 0 | N/A | 0 | 0
2020-10-10 04:30 | 3.3753 | 0 | N/A | 0 | 0
2020-10-10 05:00 | 3.2731 | 0 | N/A | 0 | 0
2020-10-10 05:30 | 3.3674 | 0 | N/A | 0 | 0
2020-10-10 06:00 | 3.5107 | 0 | N/A | 0 | 0
2020-10-10 06:30 | 3.9109 | 0 | N/A | 0 | 0
2020-10-10 07:00 | 4.1295 | 0 | N/A | 0 | 0
2020-10-10 07:30 | 4.6431 | 0 | N/A | 0 | 0
2020-10-10 08:00 | 4.6952 | 0 | N/A | 0 | 0
2020-10-10 08:30 | 4.1914 | 0 | N/A | 0 | 0
2020-10-10 09:00 | 3.7072 | 0 | N/A | 0 | 0
2020-10-10 09:30 | 3.1384 | 0 | N/A | 0 | 0
2020-10-10 10:00 | 2.2326 | 0 | N/A | 0 | 0
2020-10-10 10:30 | 1.5943 | 0 | N/A | 0 | 0
2020-10-10 11:00 | 1.0325 | 0 | N/A | 0 | 0
2020-10-10 11:30 | 0.6062 | 0 | N/A | 0 | 0
2020-10-10 12:00 | 0.40762 | 0 | N/A | 0 | 0
2020-10-10 12:30 | 0.44407 | 0 | N/A | 0 | 0
2020-10-10 13:00 | 0.28846 | 0 | N/A | 0 | 0
2020-10-10 13:30 | -0.30641 | 0 | N/A | 0 | 0
2020-10-10 14:00 | -0.42678 | 0 | N/A | 0 | 0
2020-10-10 14:30 | 0.35443 | 0 | N/A | 0 | 0
2020-10-10 15:00 | 0.47291 | 0 | N/A | 0 | 0
2020-10-10 15:30 | 0.59297 | 0 | N/A | 0 | 0
2020-10-10 16:00 | 1.1403 | 0 | N/A | 0 | 0
2020-10-10 16:30 | 2.1281 | 0 | N/A | 0 | 0
2020-10-10 17:00 | 2.6043 | 0 | N/A | 0 | 0
2020-10-10 17:30 | 3.0978 | 0 | N/A | 0 | 0
2020-10-10 18:00 | 3.6572 | 0 | N/A | 0 | 0
2020-10-10 18:30 | 4.3294 | 0 | N/A | 0 | 0
2020-10-10 19:00 | 4.8459 | 0 | N/A | 0 | 0
2020-10-10 19:30 | 5.2372 | 0 | N/A | 0 | 0
2020-10-10 20:00 | 5.5034 | 0 | N/A | 0 | 0
2020-10-10 20:30 | 5.4814 | 0 | N/A | 0 | 0
2020-10-10 21:00 | 5.2552 | 0 | N/A | 0 | 0
2020-10-10 21:30 | 5.0323 | 0 | N/A | 0 | 0
2020-10-10 22:00 | 4.7493 | 0 | N/A | 0 | 0
2020-10-10 22:30 | 5.191 | 0 | N/A | 0 | 0
2020-10-10 23:00 | 5.4256 | 0 | N/A | 0 | 0
2020-10-10 23:30 | 5.0429 | 0 | N/A | 0 | 0
2020-10-11 | 5.1987 | 0 | N/A | 0 | 0
2020-10-11 00:30 | 5.3534 | 0 | N/A | 0 | 0
2020-10-11 01:00 | 5.8871 | 0 | N/A | 0 | 0
2020-10-11 01:30 | 5.1858 | 0 | N/A | 0 | 0
2020-10-11 02:00 | 4.3823 | 0 | N/A | 0 | 0
2020-10-11 02:30 | 4.487 | 0 | N/A | 0 | 0
2020-10-11 03:00 | 4.0492 | 0 | N/A | 0 | 0
2020-10-11 03:30 | 3.5427 | 0 | N/A | 0 | 0
2020-10-11 04:00 | 3.207 | 0 | N/A | 0 | 0
2020-10-11 04:30 | 2.9379 | 0 | N/A | 0 | 0
2020-10-11 05:00 | 2.8435 | 0 | N/A | 0 | 0
2020-10-11 05:30 | 2.8668 | 0 | N/A | 0 | 0
2020-10-11 06:00 | 2.9979 | 0 | N/A | 0 | 0
2020-10-11 06:30 | 3.2066 | 0 | N/A | 0 | 0
2020-10-11 07:00 | 3.3262 | 0 | N/A | 0 | 0
2020-10-11 07:30 | 3.6813 | 0 | N/A | 0 | 0
2020-10-11 08:00 | 3.9152 | 0 | N/A | 0 | 0
2020-10-11 08:30 | 3.7194 | 0 | N/A | 0 | 0
2020-10-11 09:00 | 3.7708 | 0 | N/A | 0 | 0
2020-10-11 09:30 | 3.7576 | 0 | N/A | 0 | 0
2020-10-11 10:00 | 3.1971 | 0 | N/A | 0 | 0
2020-10-11 10:30 | 2.6771 | 0 | N/A | 0 | 0
2020-10-11 11:00 | 2.7356 | 0 | N/A | 0 | 0
2020-10-11 11:30 | 2.623 | 0 | N/A | 0 | 0
2020-10-11 12:00 | 2.6334 | 0 | N/A | 0 | 0
2020-10-11 12:30 | 2.2361 | 0 | N/A | 0 | 0
2020-10-11 13:00 | 1.3873 | 0 | N/A | 0 | 0
2020-10-11 13:30 | 0.9477 | 0 | N/A | 0 | 0
2020-10-11 14:00 | 0.7471 | 0 | N/A | 0 | 0
2020-10-11 14:30 | 0.67152 | 0 | N/A | 0 | 0
2020-10-11 15:00 | 0.64209 | 0 | N/A | 0 | 0
2020-10-11 15:30 | 0.90377 | 0 | N/A | 0 | 0
2020-10-11 16:00 | 0.92631 | 0 | N/A | 0 | 0
2020-10-11 16:30 | 1.4294 | 0 | N/A | 0 | 0
2020-10-11 17:00 | 2.0869 | 0 | N/A | 0 | 0
2020-10-11 17:30 | 3.2449 | 0 | N/A | 0 | 0
2020-10-11 18:00 | 4.2686 | 0 | N/A | 0 | 0
2020-10-11 18:30 | 4.8482 | 0 | N/A | 0 | 0
2020-10-11 19:00 | 4.9587 | 0 | N/A | 0 | 0
2020-10-11 19:30 | 5.5762 | 0 | N/A | 0 | 0
2020-10-11 20:00 | 5.985 | 0 | N/A | 0 | 0
2020-10-11 20:30 | 6.1998 | 0 | N/A | 0 | 0
2020-10-11 21:00 | 5.9954 | 0 | N/A | 0 | 0
2020-10-11 21:30 | 5.6405 | 0 | N/A | 0 | 0
2020-10-11 22:00 | 5.1865 | 0 | N/A | 0 | 0
2020-10-11 22:30 | 5.3558 | 0 | N/A | 0 | 0
2020-10-11 23:00 | 5.5043 | 0 | N/A | 0 | 0
2020-10-11 23:30 | 5.0541 | 0 | N/A | 0 | 0
2020-10-12 | 5.1704 | 0 | N/A | 0 | 0
2020-10-12 00:30 | 5.3842 | 0 | N/A | 0 | 0
2020-10-12 01:00 | 5.9026 | 0 | N/A | 0 | 0
2020-10-12 01:30 | 5.2046 | 0 | N/A | 0 | 0
2020-10-12 02:00 | 4.5925 | 0 | N/A | 0 | 0
2020-10-12 02:30 | 4.7068 | 0 | N/A | 0 | 0
2020-10-12 03:00 | 4.3987 | 0 | N/A | 0 | 0
2020-10-12 03:30 | 3.9341 | 0 | N/A | 0 | 0
2020-10-12 04:00 | 3.5746 | 0 | N/A | 0 | 0
2020-10-12 04:30 | 3.4135 | 0 | N/A | 0 | 0
2020-10-12 05:00 | 3.3863 | 0 | N/A | 0 | 0
2020-10-12 05:30 | 3.659 | 0 | N/A | 0 | 0
2020-10-12 06:00 | 4.0825 | 0 | N/A | 0 | 0
2020-10-12 06:30 | 4.869 | 0 | N/A | 0 | 0
2020-10-12 07:00 | 5.6996 | 0 | N/A | 0 | 0
2020-10-12 07:30 | 6.7911 | 0 | N/A | 0 | 0
2020-10-12 08:00 | 7.099 | 0 | N/A | 0 | 0
2020-10-12 08:30 | 5.9564 | 0 | N/A | 0 | 0
2020-10-12 09:00 | 5.2909 | 0 | N/A | 0 | 0
2020-10-12 09:30 | 4.9403 | 0 | N/A | 0 | 0
2020-10-12 10:00 | 4.2245 | 0 | N/A | 0 | 0
2020-10-12 10:30 | 2.6345 | 0 | N/A | 0 | 0
2020-10-12 11:00 | 1.7171 | 0 | N/A | 0 | 0
2020-10-12 11:30 | 1.8392 | 0 | N/A | 0 | 0
2020-10-12 12:00 | 1.04 | 0 | N/A | 0 | 0
2020-10-12 12:30 | 0.44338 | 0 | N/A | 0 | 0
2020-10-12 13:00 | -0.13732 | 0 | N/A | 0 | 0
2020-10-12 13:30 | -0.40672 | 0 | N/A | 0 | 0
2020-10-12 14:00 | -0.42668 | 0 | N/A | 0 | 0
2020-10-12 14:30 | -0.30046 | 0 | N/A | 0 | 0
2020-10-12 15:00 | -0.48333 | 0 | N/A | 0 | 0
2020-10-12 15:30 | -0.16007 | 0 | N/A | 0 | 0
2020-10-12 16:00 | 0.37937 | 0 | N/A | 0 | 0
2020-10-12 16:30 | 1.4821 | 0 | N/A | 0 | 0
2020-10-12 17:00 | 2.8294 | 0 | N/A | 0 | 0
2020-10-12 17:30 | 3.4912 | 0 | N/A | 0 | 0
2020-10-12 18:00 | 4.3978 | 0 | N/A | 0 | 0
2020-10-12 18:30 | 4.7158 | 0 | N/A | 0 | 0
2020-10-12 19:00 | 4.8536 | 0 | N/A | 0 | 0
2020-10-12 19:30 | 4.8811 | 0 | N/A | 0 | 0
2020-10-12 20:00 | 5.0904 | 0 | N/A | 0 | 0
2020-10-12 20:30 | 5.127 | 0 | N/A | 0 | 0
2020-10-12 21:00 | 4.9463 | 0 | N/A | 0 | 0
2020-10-12 21:30 | 4.6946 | 0 | N/A | 0 | 0
2020-10-12 22:00 | 4.3187 | 0 | N/A | 0 | 0
2020-10-12 22:30 | 4.616 | 0 | N/A | 0 | 0
2020-10-12 23:00 | 4.718 | 0 | N/A | 0 | 0
2020-10-12 23:30 | 4.3768 | 0 | N/A | 0 | 0
2020-10-13 | 4.5227 | 0 | N/A | 0 | 0
2020-10-13 00:30 | 4.958 | 0 | N/A | 0 | 0
2020-10-13 01:00 | 5.3317 | 0 | N/A | 0 | 0
2020-10-13 01:30 | 4.5943 | 0 | N/A | 0 | 0
2020-10-13 02:00 | 3.8854 | 0 | N/A | 0 | 0
2020-10-13 02:30 | 3.8818 | 0 | N/A | 0 | 0
2020-10-13 03:00 | 3.54 | 0 | N/A | 0 | 0
2020-10-13 03:30 | 3.109 | 0 | N/A | 0 | 0
2020-10-13 04:00 | 2.8249 | 0 | N/A | 0 | 0
2020-10-13 04:30 | 2.675 | 0 | N/A | 0 | 0
2020-10-13 05:00 | 2.7095 | 0 | N/A | 0 | 0
2020-10-13 05:30 | 2.8741 | 0 | N/A | 0 | 0
2020-10-13 06:00 | 3.2014 | 0 | N/A | 0 | 0
2020-10-13 06:30 | 3.8836 | 0 | N/A | 0 | 0
2020-10-13 07:00 | 4.5003 | 0 | N/A | 0 | 0
2020-10-13 07:30 | 5.4259 | 0 | N/A | 0 | 0
2020-10-13 08:00 | 5.6127 | 0 | N/A | 0 | 0
2020-10-13 08:30 | 5.2967 | 0 | N/A | 0 | 0
2020-10-13 09:00 | 4.9015 | 0 | N/A | 0 | 0
2020-10-13 09:30 | 4.3635 | 0 | N/A | 0 | 0
2020-10-13 10:00 | 5.2219 | 0 | N/A | 0 | 0
2020-10-13 10:30 | 4.6909 | 0 | N/A | 0 | 0
2020-10-13 11:00 | 4.6115 | 0 | N/A | 0 | 0
2020-10-13 11:30 | 4.7077 | 0 | N/A | 0 | 0
2020-10-13 12:00 | 4.4289 | 0 | N/A | 0 | 0
2020-10-13 12:30 | 4.2574 | 0 | N/A | 0 | 0
2020-10-13 13:00 | 4.2981 | 0 | N/A | 0 | 0
2020-10-13 13:30 | 3.9449 | 0 | N/A | 0 | 0
2020-10-13 14:00 | 3.3468 | 0 | N/A | 0 | 0
2020-10-13 14:30 | 3.5438 | 0 | N/A | 0 | 0
2020-10-13 15:00 | 3.3769 | 0 | N/A | 0 | 0
2020-10-13 15:30 | 3.2136 | 0 | N/A | 0 | 0
2020-10-13 16:00 | 2.5401 | 0 | N/A | 0 | 0
2020-10-13 16:30 | 1.3568 | 0 | N/A | 0 | 0
2020-10-13 17:00 | 1.5599 | 0 | N/A | 0 | 0
2020-10-13 17:30 | 2.3372 | 0 | N/A | 0 | 0
2020-10-13 18:00 | 3.3217 | 0 | N/A | 0 | 0
2020-10-13 18:30 | 4.3183 | 0 | N/A | 0 | 0
2020-10-13 19:00 | 4.9629 | 0 | N/A | 0 | 0
2020-10-13 19:30 | 5.4069 | 0 | N/A | 0 | 0
2020-10-13 20:00 | 5.7963 | 0 | N/A | 0 | 0
2020-10-13 20:30 | 5.9866 | 0 | N/A | 0 | 0
2020-10-13 21:00 | 5.8608 | 0 | N/A | 0 | 0
2020-10-13 21:30 | 5.6078 | 0 | N/A | 0 | 0
2020-10-13 22:00 | 5.1489 | 0 | N/A | 0 | 0
2020-10-13 22:30 | 5.4096 | 0 | N/A | 0 | 0
2020-10-13 23:00 | 5.473 | 0 | N/A | 0 | 0
2020-10-13 23:30 | 5.1477 | 0 | N/A | 0 | 0
2020-10-14 | 5.0894 | 0 | N/A | 0 | 0
2020-10-14 00:30 | 5.4737 | 0 | N/A | 0 | 0
2020-10-14 01:00 | 4.3845 | 0 | N/A | 0 | 0
2020-10-14 01:30 | 3.8255 | 0 | N/A | 0 | 0
2020-10-14 02:00 | 3.5033 | 0 | N/A | 0 | 0
2020-10-14 02:30 | 2.5918 | 0 | N/A | 0 | 0
2020-10-14 03:00 | 3.2122 | 0 | N/A | 0 | 0
2020-10-14 03:30 | 3.3393 | 0 | N/A | 0 | 0
2020-10-14 04:00 | 3.1228 | 0 | N/A | 0 | 0
2020-10-14 04:30 | 2.9906 | 0 | N/A | 0 | 0
2020-10-14 05:00 | 2.9921 | 0 | N/A | 0 | 0
2020-10-14 05:30 | 3.1351 | 0 | N/A | 0 | 0
2020-10-14 06:00 | 3.4901 | 0 | N/A | 0 | 0
2020-10-14 06:30 | 4.2053 | 0 | N/A | 0 | 0
2020-10-14 07:00 | 4.8491 | 0 | N/A | 0 | 0
2020-10-14 07:30 | 5.8404 | 0 | N/A | 0 | 0
2020-10-14 08:00 | 6.3433 | 0 | N/A | 0 | 0
2020-10-14 08:30 | 5.3172 | 0 | N/A | 0 | 0
2020-10-14 09:00 | 4.387 | 0 | N/A | 0 | 0
2020-10-14 09:30 | 3.8644 | 0 | N/A | 0 | 0
2020-10-14 10:00 | 2.5084 | 0 | N/A | 0 | 0
2020-10-14 10:30 | 1.6101 | 0 | N/A | 0 | 0
2020-10-14 11:00 | 0.9607 | 0 | N/A | 0 | 0
2020-10-14 11:30 | 0.54533 | 0 | N/A | 0 | 0
2020-10-14 12:00 | 0.53017 | 0 | N/A | 0 | 0
2020-10-14 12:30 | 0.12667 | 0 | N/A | 0 | 0
2020-10-14 13:00 | 0.18043 | 0 | N/A | 0 | 0
2020-10-14 13:30 | -0.18838 | 0 | N/A | 0 | 0
2020-10-14 14:00 | 0.22472 | 0 | N/A | 0 | 0
2020-10-14 14:30 | -0.21492 | 0 | N/A | 0 | 0
2020-10-14 15:00 | 0.70868 | 0 | N/A | 0 | 0
2020-10-14 15:30 | 0.91333 | 0 | N/A | 0 | 0
2020-10-14 16:00 | 1.1167 | 0 | N/A | 0 | 0
2020-10-14 16:30 | 1.8096 | 0 | N/A | 0 | 0
2020-10-14 17:00 | 1.7132 | 0 | N/A | 0 | 0
2020-10-14 17:30 | 2.6257 | 0 | N/A | 0 | 0
2020-10-14 18:00 | 3.1768 | 0 | N/A | 0 | 0
2020-10-14 18:30 | 3.8962 | 0 | N/A | 0 | 0
2020-10-14 19:00 | 4.3804 | 0 | N/A | 0 | 0
2020-10-14 19:30 | 4.5844 | 0 | N/A | 0 | 0
2020-10-14 20:00 | 4.7126 | 0 | N/A | 0 | 0
2020-10-14 20:30 | 4.7743 | 0 | N/A | 0 | 0
2020-10-14 21:00 | 4.6292 | 0 | N/A | 0 | 0
2020-10-14 21:30 | 4.3404 | 0 | N/A | 0 | 0
2020-10-14 22:00 | 3.9724 | 0 | N/A | 0 | 0
2020-10-14 22:30 | 4.3331 | 0 | N/A | 0 | 0
2020-10-14 23:00 | 4.453 | 0 | N/A | 0 | 0
2020-10-14 23:30 | 4.0762 | 0 | N/A | 0 | 0
2020-10-15 | 4.1785 | 0 | N/A | 0 | 0
2020-10-15 00:30 | 4.6154 | 0 | N/A | 0 | 0
2020-10-15 01:00 | 4.9935 | 0 | N/A | 0 | 0
2020-10-15 01:30 | 4.2441 | 0 | N/A | 0 | 0
2020-10-15 02:00 | 3.4753 | 0 | N/A | 0 | 0
2020-10-15 02:30 | 3.5074 | 0 | N/A | 0 | 0
2020-10-15 03:00 | 3.5252 | 0 | N/A | 0 | 0
2020-10-15 03:30 | 3.5721 | 0 | N/A | 0 | 0
2020-10-15 04:00 | 2.5419 | 0 | N/A | 0 | 0
2020-10-15 04:30 | 2.348 | 0 | N/A | 0 | 0
2020-10-15 05:00 | 2.374 | 0 | N/A | 0 | 0
2020-10-15 05:30 | 2.4789 | 0 | N/A | 0 | 0
2020-10-15 06:00 | 2.7763 | 0 | N/A | 0 | 0
2020-10-15 06:30 | 3.3726 | 0 | N/A | 0 | 0
2020-10-15 07:00 | 3.9448 | 0 | N/A | 0 | 0
2020-10-15 07:30 | 4.7739 | 0 | N/A | 0 | 0
2020-10-15 08:00 | 4.8469 | 0 | N/A | 0 | 0
2020-10-15 08:30 | 4.2768 | 0 | N/A | 0 | 0
2020-10-15 09:00 | 4.1367 | 0 | N/A | 0 | 0
2020-10-15 09:30 | 4.564 | 0 | N/A | 0 | 0
2020-10-15 10:00 | 4.2702 | 0 | N/A | 0 | 0
2020-10-15 10:30 | 4.11 | 0 | N/A | 0 | 0
2020-10-15 11:00 | 4.0469 | 0 | N/A | 0 | 0
2020-10-15 11:30 | 4.2415 | 0 | N/A | 0 | 0
2020-10-15 12:00 | 3.7935 | 0 | N/A | 0 | 0
2020-10-15 12:30 | 4.2033 | 0 | N/A | 0 | 0
2020-10-15 13:00 | 4.35 | 0 | N/A | 0 | 0
2020-10-15 13:30 | 3.7848 | 0 | N/A | 0 | 0
2020-10-15 14:00 | 3.3085 | 0 | N/A | 0 | 0
2020-10-15 14:30 | 3.2882 | 0 | N/A | 0 | 0
2020-10-15 15:00 | 3.3234 | 0 | N/A | 0 | 0
2020-10-15 15:30 | 3.362 | 0 | N/A | 0 | 0
2020-10-15 16:00 | 3.2244 | 0 | N/A | 0 | 0
2020-10-15 16:30 | 3.7745 | 0 | N/A | 0 | 0
2020-10-15 17:00 | 4.3754 | 0 | N/A | 0 | 0
2020-10-15 17:30 | 5.3026 | 0 | N/A | 0 | 0
2020-10-15 18:00 | 5.731 | 0 | N/A | 0 | 0
2020-10-15 18:30 | 6.0613 | 0 | N/A | 0 | 0
2020-10-15 19:00 | 5.983 | 0 | N/A | 0 | 0
2020-10-15 19:30 | 5.9518 | 0 | N/A | 0 | 0
2020-10-15 20:00 | 5.9837 | 0 | N/A | 0 | 0
2020-10-15 20:30 | 5.9744 | 0 | N/A | 0 | 0
2020-10-15 21:00 | 5.7855 | 0 | N/A | 0 | 0
2020-10-15 21:30 | 5.3471 | 0 | N/A | 0 | 0
2020-10-15 22:00 | 4.9639 | 0 | N/A | 0 | 0
2020-10-15 22:30 | 5.089 | 0 | N/A | 0 | 0
2020-10-15 23:00 | 5.2436 | 0 | N/A | 0 | 0
2020-10-15 23:30 | 4.7964 | 0 | N/A | 0 | 0
2020-10-16 | 4.8929 | 0 | N/A | 0 | 0
2020-10-16 00:30 | 5.3107 | 0 | N/A | 0 | 0
2020-10-16 01:00 | 5.7388 | 0 | N/A | 0 | 0
2020-10-16 01:30 | 5.0324 | 0 | N/A | 0 | 0
2020-10-16 02:00 | 4.3055 | 0 | N/A | 0 | 0
2020-10-16 02:30 | 4.3214 | 0 | N/A | 0 | 0
2020-10-16 03:00 | 3.9385 | 0 | N/A | 0 | 0
2020-10-16 03:30 | 3.4621 | 0 | N/A | 0 | 0
2020-10-16 04:00 | 3.2012 | 0 | N/A | 0 | 0
2020-10-16 04:30 | 3.1416 | 0 | N/A | 0 | 0
2020-10-16 05:00 | 3.1925 | 0 | N/A | 0 | 0
2020-10-16 05:30 | 3.4007 | 0 | N/A | 0 | 0
2020-10-16 06:00 | 3.773 | 0 | N/A | 0 | 0
2020-10-16 06:30 | 4.681 | 0 | N/A | 0 | 0
2020-10-16 07:00 | 5.5579 | 0 | N/A | 0 | 0
2020-10-16 07:30 | 6.6467 | 0 | N/A | 0 | 0
2020-10-16 08:00 | 6.6258 | 0 | N/A | 0 | 0
2020-10-16 08:30 | 5.2042 | 0 | N/A | 0 | 0
2020-10-16 09:00 | 4.3065 | 0 | N/A | 0 | 0
2020-10-16 09:30 | 3.4721 | 0 | N/A | 0 | 0
2020-10-16 10:00 | 2.6659 | 0 | N/A | 0 | 0
2020-10-16 10:30 | 2.0036 | 0 | N/A | 0 | 0
2020-10-16 11:00 | 1.9248 | 0 | N/A | 0 | 0
2020-10-16 11:30 | 1.6797 | 0 | N/A | 0 | 0
2020-10-16 12:00 | 2.0406 | 0 | N/A | 0 | 0
2020-10-16 12:30 | 2.2153 | 0 | N/A | 0 | 0
2020-10-16 13:00 | 3.0975 | 0 | N/A | 0 | 0
2020-10-16 13:30 | 3.2887 | 0 | N/A | 0 | 0
2020-10-16 14:00 | 3.1705 | 0 | N/A | 0 | 0
2020-10-16 14:30 | 3.5637 | 0 | N/A | 0 | 0
2020-10-16 15:00 | 3.898 | 0 | N/A | 0 | 0
2020-10-16 15:30 | 3.3983 | 0 | N/A | 0 | 0
2020-10-16 16:00 | 3.4398 | 0 | N/A | 0 | 0
2020-10-16 16:30 | 4.0117 | 0 | N/A | 0 | 0
2020-10-16 17:00 | 4.4526 | 0 | N/A | 0 | 0
2020-10-16 17:30 | 5.1324 | 0 | N/A | 0 | 0
2020-10-16 18:00 | 5.6054 | 0 | N/A | 0 | 0
2020-10-16 18:30 | 5.8689 | 0 | N/A | 0 | 0
2020-10-16 19:00 | 5.8793 | 0 | N/A | 0 | 0
2020-10-16 19:30 | 6.0515 | 0 | N/A | 0 | 0
2020-10-16 20:00 | 6.0251 | 0 | N/A | 0 | 0
2020-10-16 20:30 | 5.8464 | 0 | N/A | 0 | 0
2020-10-16 21:00 | 5.6382 | 0 | N/A | 0 | 0
2020-10-16 21:30 | 5.3559 | 0 | N/A | 0 | 0
2020-10-16 22:00 | 4.9935 | 0 | N/A | 0 | 0
2020-10-16 22:30 | 5.3282 | 0 | N/A | 0 | 0
2020-10-16 23:00 | 5.3606 | 0 | N/A | 0 | 0
2020-10-16 23:30 | 4.9928 | 0 | N/A | 0 | 0
2020-10-17 | 4.9586 | 0 | N/A | 0 | 0
2020-10-17 00:30 | 5.3561 | 0 | N/A | 0 | 0
2020-10-17 01:00 | 5.5984 | 0 | N/A | 0 | 0
2020-10-17 01:30 | 4.7391 | 0 | N/A | 0 | 0
2020-10-17 02:00 | 3.9238 | 0 | N/A | 0 | 0
2020-10-17 02:30 | 3.8272 | 0 | N/A | 0 | 0
2020-10-17 03:00 | 3.4534 | 0 | N/A | 0 | 0
2020-10-17 03:30 | 2.9629 | 0 | N/A | 0 | 0
2020-10-17 04:00 | 2.6422 | 0 | N/A | 0 | 0
2020-10-17 04:30 | 2.4766 | 0 | N/A | 0 | 0
2020-10-17 05:00 | 2.4436 | 0 | N/A | 0 | 0
2020-10-17 05:30 | 2.4885 | 0 | N/A | 0 | 0
2020-10-17 06:00 | 2.5987 | 0 | N/A | 0 | 0
2020-10-17 06:30 | 2.8167 | 0 | N/A | 0 | 0
2020-10-17 07:00 | 3.1143 | 0 | N/A | 0 | 0
2020-10-17 07:30 | 3.4256 | 0 | N/A | 0 | 0
2020-10-17 08:00 | 3.72 | 0 | N/A | 0 | 0
2020-10-17 08:30 | 3.4097 | 0 | N/A | 0 | 0
2020-10-17 09:00 | 3.8179 | 0 | N/A | 0 | 0
2020-10-17 09:30 | 4.1037 | 0 | N/A | 0 | 0
2020-10-17 10:00 | 3.8579 | 0 | N/A | 0 | 0
2020-10-17 10:30 | 3.7709 | 0 | N/A | 0 | 0
2020-10-17 11:00 | 3.9981 | 0 | N/A | 0 | 0
2020-10-17 11:30 | 3.8131 | 0 | N/A | 0 | 0
2020-10-17 12:00 | 4.088 | 0 | N/A | 0 | 0
2020-10-17 12:30 | 4.05 | 0 | N/A | 0 | 0
2020-10-17 13:00 | 4.12 | 0 | N/A | 0 | 0
2020-10-17 13:30 | 3.7025 | 0 | N/A | 0 | 0
2020-10-17 14:00 | 2.8661 | 0 | N/A | 0 | 0
2020-10-17 14:30 | 2.5593 | 0 | N/A | 0 | 0
2020-10-17 15:00 | 2.311 | 0 | N/A | 0 | 0
2020-10-17 15:30 | 2.4089 | 0 | N/A | 0 | 0
2020-10-17 16:00 | 2.2763 | 0 | N/A | 0 | 0
2020-10-17 16:30 | 2.7444 | 0 | N/A | 0 | 0
2020-10-17 17:00 | 2.9302 | 0 | N/A | 0 | 0
2020-10-17 17:30 | 3.2279 | 0 | N/A | 0 | 0
2020-10-17 18:00 | 4.1251 | 0 | N/A | 0 | 0
2020-10-17 18:30 | 4.6183 | 0 | N/A | 0 | 0
2020-10-17 19:00 | 5.1177 | 0 | N/A | 0 | 0
2020-10-17 19:30 | 5.7378 | 0 | N/A | 0 | 0
2020-10-17 20:00 | 5.7869 | 0 | N/A | 0 | 0
2020-10-17 20:30 | 5.6493 | 0 | N/A | 0 | 0
2020-10-17 21:00 | 5.4687 | 0 | N/A | 0 | 0
2020-10-17 21:30 | 5.1694 | 0 | N/A | 0 | 0
2020-10-17 22:00 | 4.9107 | 0 | N/A | 0 | 0
2020-10-17 22:30 | 5.2798 | 0 | N/A | 0 | 0
2020-10-17 23:00 | 5.5181 | 0 | N/A | 0 | 0
2020-10-17 23:30 | 5.1218 | 0 | N/A | 0 | 0
2020-10-18 | 5.0787 | 0 | N/A | 0 | 0
2020-10-18 00:30 | 5.4901 | 0 | N/A | 0 | 0
2020-10-18 01:00 | 5.8904 | 0 | N/A | 0 | 0
2020-10-18 01:30 | 5.1749 | 0 | N/A | 0 | 0
2020-10-18 02:00 | 4.2635 | 0 | N/A | 0 | 0
2020-10-18 02:30 | 4.2083 | 0 | N/A | 0 | 0
2020-10-18 03:00 | 3.8001 | 0 | N/A | 0 | 0
2020-10-18 03:30 | 3.2342 | 0 | N/A | 0 | 0
2020-10-18 04:00 | 2.9945 | 0 | N/A | 0 | 0
2020-10-18 04:30 | 2.811 | 0 | N/A | 0 | 0
2020-10-18 05:00 | 2.7033 | 0 | N/A | 0 | 0
2020-10-18 05:30 | 2.8322 | 0 | N/A | 0 | 0
2020-10-18 06:00 | 2.8409 | 0 | N/A | 0 | 0
2020-10-18 06:30 | 3.1343 | 0 | N/A | 0 | 0
2020-10-18 07:00 | 3.402 | 0 | N/A | 0 | 0
2020-10-18 07:30 | 3.742 | 0 | N/A | 0 | 0
2020-10-18 08:00 | 3.7401 | 0 | N/A | 0 | 0
2020-10-18 08:30 | 3.3565 | 0 | N/A | 0 | 0
2020-10-18 09:00 | 3.6144 | 0 | N/A | 0 | 0
2020-10-18 09:30 | 3.9782 | 0 | N/A | 0 | 0
2020-10-18 10:00 | 4.1162 | 0 | N/A | 0 | 0
2020-10-18 10:30 | 4.2024 | 0 | N/A | 0 | 0
2020-10-18 11:00 | 3.8674 | 0 | N/A | 0 | 0
2020-10-18 11:30 | 3.7113 | 0 | N/A | 0 | 0
2020-10-18 12:00 | 3.4532 | 0 | N/A | 0 | 0
2020-10-18 12:30 | 3.232 | 0 | N/A | 0 | 0
2020-10-18 13:00 | 2.7197 | 0 | N/A | 0 | 0
2020-10-18 13:30 | 2.2534 | 0 | N/A | 0 | 0
2020-10-18 14:00 | 1.9108 | 0 | N/A | 0 | 0
2020-10-18 14:30 | 2.0345 | 0 | N/A | 0 | 0
2020-10-18 15:00 | 2.5367 | 0 | N/A | 0 | 0
2020-10-18 15:30 | 3.2014 | 0 | N/A | 0 | 0
2020-10-18 16:00 | 3.4684 | 0 | N/A | 0 | 0
2020-10-18 16:30 | 3.8427 | 0 | N/A | 0 | 0
2020-10-18 17:00 | 4.151 | 0 | N/A | 0 | 0
2020-10-18 17:30 | 4.5715 | 0 | N/A | 0 | 0
2020-10-18 18:00 | 5.2156 | 0 | N/A | 0 | 0
2020-10-18 18:30 | 5.8563 | 0 | N/A | 0 | 0
2020-10-18 19:00 | 6.3791 | 0 | N/A | 0 | 0
2020-10-18 19:30 | 6.683 | 0 | N/A | 0 | 0
2020-10-18 20:00 | 6.5941 | 0 | N/A | 0 | 0
2020-10-18 20:30 | 6.2515 | 0 | N/A | 0 | 0
2020-10-18 21:00 | 6.0115 | 0 | N/A | 0 | 0
2020-10-18 21:30 | 5.6914 | 0 | N/A | 0 | 0
2020-10-18 22:00 | 5.3094 | 0 | N/A | 0 | 0
2020-10-18 22:30 | 5.5131 | 0 | N/A | 0 | 0
2020-10-18 23:00 | 5.5668 | 0 | N/A | 0 | 0
2020-10-18 23:30 | 5.1719 | 0 | N/A | 0 | 0
2020-10-19 | 5.1572 | 0 | N/A | 0 | 0
2020-10-19 00:30 | 5.4681 | 0 | N/A | 0 | 0
2020-10-19 01:00 | 6.0084 | 0 | N/A | 0 | 0
2020-10-19 01:30 | 5.3402 | 0 | N/A | 0 | 0
2020-10-19 02:00 | 4.6685 | 0 | N/A | 0 | 0
2020-10-19 02:30 | 4.6873 | 0 | N/A | 0 | 0
2020-10-19 03:00 | 4.1692 | 0 | N/A | 0 | 0
2020-10-19 03:30 | 3.6584 | 0 | N/A | 0 | 0
2020-10-19 04:00 | 3.3564 | 0 | N/A | 0 | 0
2020-10-19 04:30 | 3.2005 | 0 | N/A | 0 | 0
2020-10-19 05:00 | 3.1655 | 0 | N/A | 0 | 0
2020-10-19 05:30 | 3.3767 | 0 | N/A | 0 | 0
2020-10-19 06:00 | 3.6746 | 0 | N/A | 0 | 0
2020-10-19 06:30 | 4.5351 | 0 | N/A | 0 | 0
2020-10-19 07:00 | 5.477 | 0 | N/A | 0 | 0
2020-10-19 07:30 | 6.75 | 0 | N/A | 0 | 0
2020-10-19 08:00 | 7.0297 | 0 | N/A | 0 | 0
2020-10-19 08:30 | 6.1723 | 0 | N/A | 0 | 0
2020-10-19 09:00 | 5.1188 | 0 | N/A | 0 | 0
2020-10-19 09:30 | 4.8931 | 0 | N/A | 0 | 0
2020-10-19 10:00 | 4.3792 | 0 | N/A | 0 | 0
2020-10-19 10:30 | 4.46 | 0 | N/A | 0 | 0
2020-10-19 11:00 | 4.756 | 0 | N/A | 0 | 0
2020-10-19 11:30 | 4.6822 | 0 | N/A | 0 | 0
2020-10-19 12:00 | 4.4861 | 0 | N/A | 0 | 0
2020-10-19 12:30 | 3.8107 | 0 | N/A | 0 | 0
2020-10-19 13:00 | 3.4143 | 0 | N/A | 0 | 0
2020-10-19 13:30 | 3.9867 | 0 | N/A | 0 | 0
2020-10-19 14:00 | 3.5967 | 0 | N/A | 0 | 0
2020-10-19 14:30 | 3.4524 | 0 | N/A | 0 | 0
2020-10-19 15:00 | 3.7444 | 0 | N/A | 0 | 0
2020-10-19 15:30 | 3.1984 | 0 | N/A | 0 | 0
2020-10-19 16:00 | 3.4672 | 0 | N/A | 0 | 0
2020-10-19 16:30 | 3.3737 | 0 | N/A | 0 | 0
2020-10-19 17:00 | 3.5752 | 0 | N/A | 0 | 0
2020-10-19 17:30 | 4.5229 | 0 | N/A | 0 | 0
2020-10-19 18:00 | 5.4097 | 0 | N/A | 0 | 0
2020-10-19 18:30 | 5.7996 | 0 | N/A | 0 | 0
2020-10-19 19:00 | 5.9728 | 0 | N/A | 0 | 0
2020-10-19 19:30 | 6.2934 | 0 | N/A | 0 | 0
2020-10-19 20:00 | 6.3373 | 0 | N/A | 0 | 0
2020-10-19 20:30 | 6.3304 | 0 | N/A | 0 | 0
2020-10-19 21:00 | 6.1404 | 0 | N/A | 0 | 0
2020-10-19 21:30 | 5.7373 | 0 | N/A | 0 | 0
2020-10-19 22:00 | 5.2282 | 0 | N/A | 0 | 0
2020-10-19 22:30 | 5.4193 | 0 | N/A | 0 | 0
2020-10-19 23:00 | 5.3755 | 0 | N/A | 0 | 0
2020-10-19 23:30 | 4.9772 | 0 | N/A | 0 | 0
2020-10-20 | 4.912 | 0 | N/A | 0 | 0
2020-10-20 00:30 | 5.2856 | 0 | N/A | 0 | 0
2020-10-20 01:00 | 5.8016 | 0 | N/A | 0 | 0
2020-10-20 01:30 | 5.1446 | 0 | N/A | 0 | 0
2020-10-20 02:00 | 4.4524 | 0 | N/A | 0 | 0
2020-10-20 02:30 | 4.3266 | 0 | N/A | 0 | 0
2020-10-20 03:00 | 4.0558 | 0 | N/A | 0 | 0
2020-10-20 03:30 | 3.5636 | 0 | N/A | 0 | 0
2020-10-20 04:00 | 3.2971 | 0 | N/A | 0 | 0
2020-10-20 04:30 | 3.2337 | 0 | N/A | 0 | 0
2020-10-20 05:00 | 3.2731 | 0 | N/A | 0 | 0
2020-10-20 05:30 | 3.6532 | 0 | N/A | 0 | 0
2020-10-20 06:00 | 4.0395 | 0 | N/A | 0 | 0
2020-10-20 06:30 | 4.8895 | 0 | N/A | 0 | 0
2020-10-20 07:00 | 5.8503 | 0 | N/A | 0 | 0
2020-10-20 07:30 | 7.0101 | 0 | N/A | 0 | 0
2020-10-20 08:00 | 6.7509 | 0 | N/A | 0 | 0
2020-10-20 08:30 | 5.4568 | 0 | N/A | 0 | 0
2020-10-20 09:00 | 5.0045 | 0 | N/A | 0 | 0
2020-10-20 09:30 | 4.4508 | 0 | N/A | 0 | 0
2020-10-20 10:00 | 3.6943 | 0 | N/A | 0 | 0
2020-10-20 10:30 | 3.0305 | 0 | N/A | 0 | 0
2020-10-20 11:00 | 2.87 | 0 | N/A | 0 | 0
2020-10-20 11:30 | 2.174 | 0 | N/A | 0 | 0
2020-10-20 12:00 | 1.8327 | 0 | N/A | 0 | 0
2020-10-20 12:30 | 1.37 | 0 | N/A | 0 | 0
2020-10-20 13:00 | 0.82802 | 0 | N/A | 0 | 0
2020-10-20 13:30 | 0.95348 | 0 | N/A | 0 | 0
2020-10-20 14:00 | 0.98692 | 0 | N/A | 0 | 0
2020-10-20 14:30 | 1.0524 | 0 | N/A | 0 | 0
2020-10-20 15:00 | 0.87321 | 0 | N/A | 0 | 0
2020-10-20 15:30 | 0.15118 | 0 | N/A | 0 | 0
2020-10-20 16:00 | 0.61351 | 0 | N/A | 0 | 0
2020-10-20 16:30 | 1.3848 | 0 | N/A | 0 | 0
2020-10-20 17:00 | 1.8814 | 0 | N/A | 0 | 0
2020-10-20 17:30 | 3.0852 | 0 | N/A | 0 | 0
2020-10-20 18:00 | 3.7001 | 0 | N/A | 0 | 0
2020-10-20 18:30 | 4.1781 | 0 | N/A | 0 | 0
2020-10-20 19:00 | 4.6101 | 0 | N/A | 0 | 0
2020-10-20 19:30 | 5.0836 | 0 | N/A | 0 | 0
2020-10-20 20:00 | 5.5796 | 0 | N/A | 0 | 0
2020-10-20 20:30 | 5.6297 | 0 | N/A | 0 | 0
2020-10-20 21:00 | 5.5646 | 0 | N/A | 0 | 0
2020-10-20 21:30 | 5.235 | 0 | N/A | 0 | 0
2020-10-20 22:00 | 4.8989 | 0 | N/A | 0 | 0
2020-10-20 22:30 | 5.1175 | 0 | N/A | 0 | 0
2020-10-20 23:00 | 5.1782 | 0 | N/A | 0 | 0
2020-10-20 23:30 | 4.8119 | 0 | N/A | 0 | 0
2020-10-21 | 4.7309 | 0 | N/A | 0 | 0
2020-10-21 00:30 | 5.021 | 0 | N/A | 0 | 0
2020-10-21 01:00 | 5.4635 | 0 | N/A | 0 | 0
2020-10-21 01:30 | 4.7696 | 0 | N/A | 0 | 0
2020-10-21 02:00 | 4.1089 | 0 | N/A | 0 | 0
2020-10-21 02:30 | 4.0825 | 0 | N/A | 0 | 0
2020-10-21 03:00 | 3.6219 | 0 | N/A | 0 | 0
2020-10-21 03:30 | 3.2507 | 0 | N/A | 0 | 0
2020-10-21 04:00 | 3.0416 | 0 | N/A | 0 | 0
2020-10-21 04:30 | 2.9412 | 0 | N/A | 0 | 0
2020-10-21 05:00 | 2.9622 | 0 | N/A | 0 | 0
2020-10-21 05:30 | 3.3209 | 0 | N/A | 0 | 0
2020-10-21 06:00 | 3.6713 | 0 | N/A | 0 | 0
2020-10-21 06:30 | 4.4836 | 0 | N/A | 0 | 0
2020-10-21 07:00 | 5.2358 | 0 | N/A | 0 | 0
2020-10-21 07:30 | 6.2503 | 0 | N/A | 0 | 0
2020-10-21 08:00 | 6.4841 | 0 | N/A | 0 | 0
2020-10-21 08:30 | 5.0175 | 0 | N/A | 0 | 0
2020-10-21 09:00 | 4.5367 | 0 | N/A | 0 | 0
2020-10-21 09:30 | 3.46 | 0 | N/A | 0 | 0
2020-10-21 10:00 | 2.3544 | 0 | N/A | 0 | 0
2020-10-21 10:30 | 1.9834 | 0 | N/A | 0 | 0
2020-10-21 11:00 | 1.9901 | 0 | N/A | 0 | 0
2020-10-21 11:30 | 1.89 | 0 | N/A | 0 | 0
2020-10-21 12:00 | 1.3334 | 0 | N/A | 0 | 0
2020-10-21 12:30 | 1.2481 | 0 | N/A | 0 | 0
2020-10-21 13:00 | 1.0367 | 0 | N/A | 0 | 0
2020-10-21 13:30 | 1.1869 | 0 | N/A | 0 | 0
2020-10-21 14:00 | 1.2628 | 0 | N/A | 0 | 0
2020-10-21 14:30 | 0.63949 | 0 | N/A | 0 | 0
2020-10-21 15:00 | 0.88727 | 0 | N/A | 0 | 0
2020-10-21 15:30 | 1.3692 | 0 | N/A | 0 | 0
2020-10-21 16:00 | 2.0338 | 0 | N/A | 0 | 0
2020-10-21 16:30 | 1.6004 | 0 | N/A | 0 | 0
2020-10-21 17:00 | 2.5564 | 0 | N/A | 0 | 0
2020-10-21 17:30 | 3.2951 | 0 | N/A | 0 | 0
2020-10-21 18:00 | 3.5082 | 0 | N/A | 0 | 0
2020-10-21 18:30 | 4.1093 | 0 | N/A | 0 | 0
2020-10-21 19:00 | 4.5969 | 0 | N/A | 0 | 0
2020-10-21 19:30 | 4.9818 | 0 | N/A | 0 | 0
2020-10-21 20:00 | 5.401 | 0 | N/A | 0 | 0
2020-10-21 20:30 | 5.6128 | 0 | N/A | 0 | 0
2020-10-21 21:00 | 5.4854 | 0 | N/A | 0 | 0
2020-10-21 21:30 | 5.2223 | 0 | N/A | 0 | 0
2020-10-21 22:00 | 4.822 | 0 | N/A | 0 | 0
2020-10-21 22:30 | 5.0516 | 0 | N/A | 0 | 0
2020-10-21 23:00 | 5.1195 | 0 | N/A | 0 | 0
2020-10-21 23:30 | 4.6964 | 0 | N/A | 0 | 0
2020-10-22 | 4.7489 | 0 | N/A | 0 | 0
2020-10-22 00:30 | 5.0666 | 0 | N/A | 0 | 0
2020-10-22 01:00 | 5.5106 | 0 | N/A | 0 | 0
2020-10-22 01:30 | 4.8001 | 0 | N/A | 0 | 0
2020-10-22 02:00 | 3.9303 | 0 | N/A | 0 | 0
2020-10-22 02:30 | 3.9199 | 0 | N/A | 0 | 0
2020-10-22 03:00 | 3.5831 | 0 | N/A | 0 | 0
2020-10-22 03:30 | 3.2294 | 0 | N/A | 0 | 0
2020-10-22 04:00 | 3.0035 | 0 | N/A | 0 | 0
2020-10-22 04:30 | 2.8984 | 0 | N/A | 0 | 0
2020-10-22 05:00 | 2.9355 | 0 | N/A | 0 | 0
2020-10-22 05:30 | 3.2392 | 0 | N/A | 0 | 0
2020-10-22 06:00 | 3.5759 | 0 | N/A | 0 | 0
2020-10-22 06:30 | 4.3115 | 0 | N/A | 0 | 0
2020-10-22 07:00 | 5.3798 | 0 | N/A | 0 | 0
2020-10-22 07:30 | 6.44 | 0 | N/A | 0 | 0
2020-10-22 08:00 | 6.3387 | 0 | N/A | 0 | 0
2020-10-22 08:30 | 4.9703 | 0 | N/A | 0 | 0
2020-10-22 09:00 | 3.9638 | 0 | N/A | 0 | 0
2020-10-22 09:30 | 3.2031 | 0 | N/A | 0 | 0
2020-10-22 10:00 | 2.1907 | 0 | N/A | 0 | 0
2020-10-22 10:30 | 1.924 | 0 | N/A | 0 | 0
2020-10-22 11:00 | 1.3689 | 0 | N/A | 0 | 0
2020-10-22 11:30 | 0.97082 | 0 | N/A | 0 | 0
2020-10-22 12:00 | 0.57877 | 0 | N/A | 0 | 0
2020-10-22 12:30 | 0.54497 | 0 | N/A | 0 | 0
2020-10-22 13:00 | 0.40973 | 0 | N/A | 0 | 0
2020-10-22 13:30 | 0.43729 | 0 | N/A | 0 | 0
2020-10-22 14:00 | 0.95975 | 0 | N/A | 0 | 0
2020-10-22 14:30 | 0.92569 | 0 | N/A | 0 | 0
2020-10-22 15:00 | 0.4272 | 0 | N/A | 0 | 0
2020-10-22 15:30 | 0.37667 | 0 | N/A | 0 | 0
2020-10-22 16:00 | 0.56192 | 0 | N/A | 0 | 0
2020-10-22 16:30 | 1.3426 | 0 | N/A | 0 | 0
2020-10-22 17:00 | 1.582 | 0 | N/A | 0 | 0
2020-10-22 17:30 | 1.9196 | 0 | N/A | 0 | 0
2020-10-22 18:00 | 3.0509 | 0 | N/A | 0 | 0
2020-10-22 18:30 | 3.7242 | 0 | N/A | 0 | 0
2020-10-22 19:00 | 4.2326 | 0 | N/A | 0 | 0
2020-10-22 19:30 | 4.4368 | 0 | N/A | 0 | 0
2020-10-22 20:00 | 4.7619 | 0 | N/A | 0 | 0
2020-10-22 20:30 | 4.8943 | 0 | N/A | 0 | 0
2020-10-22 21:00 | 4.7826 | 0 | N/A | 0 | 0
2020-10-22 21:30 | 4.6336 | 0 | N/A | 0 | 0
2020-10-22 22:00 | 4.319 | 0 | N/A | 0 | 0
2020-10-22 22:30 | 4.6348 | 0 | N/A | 0 | 0
2020-10-22 23:00 | 4.7206 | 0 | N/A | 0 | 0
2020-10-22 23:30 | 4.3017 | 0 | N/A | 0 | 0
2020-10-23 | 4.3342 | 0 | N/A | 0 | 0
2020-10-23 00:30 | 4.6083 | 0 | N/A | 0 | 0
2020-10-23 01:00 | 4.9591 | 0 | N/A | 0 | 0
2020-10-23 01:30 | 4.2827 | 0 | N/A | 0 | 0
2020-10-23 02:00 | 3.5098 | 0 | N/A | 0 | 0
2020-10-23 02:30 | 3.4484 | 0 | N/A | 0 | 0
2020-10-23 03:00 | 3.066 | 0 | N/A | 0 | 0
2020-10-23 03:30 | 2.5564 | 0 | N/A | 0 | 0
2020-10-23 04:00 | 2.4032 | 0 | N/A | 0 | 0
2020-10-23 04:30 | 2.3436 | 0 | N/A | 0 | 0
2020-10-23 05:00 | 2.3012 | 0 | N/A | 0 | 0
2020-10-23 05:30 | 2.3508 | 0 | N/A | 0 | 0
2020-10-23 06:00 | 2.5467 | 0 | N/A | 0 | 0
2020-10-23 06:30 | 2.943 | 0 | N/A | 0 | 0
2020-10-23 07:00 | 3.0906 | 0 | N/A | 0 | 0
2020-10-23 07:30 | 3.4687 | 0 | N/A | 0 | 0
2020-10-23 08:00 | 3.5972 | 0 | N/A | 0 | 0
2020-10-23 08:30 | 3.196 | 0 | N/A | 0 | 0
2020-10-23 09:00 | 3.3668 | 0 | N/A | 0 | 0
2020-10-23 09:30 | 3.4164 | 0 | N/A | 0 | 0
2020-10-23 10:00 | 3.4408 | 0 | N/A | 0 | 0
2020-10-23 10:30 | 2.5358 | 0 | N/A | 0 | 0
2020-10-23 11:00 | 2.8326 | 0 | N/A | 0 | 0
2020-10-23 11:30 | 2.8379 | 0 | N/A | 0 | 0
2020-10-23 12:00 | 2.5498 | 0 | N/A | 0 | 0
2020-10-23 12:30 | 2.0168 | 0 | N/A | 0 | 0
2020-10-23 13:00 | 1.9102 | 0 | N/A | 0 | 0
2020-10-23 13:30 | 1.7774 | 0 | N/A | 0 | 0
2020-10-23 14:00 | 0.56356 | 0 | N/A | 0 | 0
2020-10-23 14:30 | -0.24058 | 0 | N/A | 0 | 0
2020-10-23 15:00 | -0.24299 | 0 | N/A | 0 | 0
2020-10-23 15:30 | -0.21792 | 0 | N/A | 0 | 0
2020-10-23 16:00 | 1.3873 | 0 | N/A | 0 | 0
2020-10-23 16:30 | 2.8209 | 0 | N/A | 0 | 0
2020-10-23 17:00 | 3.182 | 0 | N/A | 0 | 0
2020-10-23 17:30 | 3.8258 | 0 | N/A | 0 | 0
2020-10-23 18:00 | 4.3094 | 0 | N/A | 0 | 0
2020-10-23 18:30 | 4.5265 | 0 | N/A | 0 | 0
2020-10-23 19:00 | 4.5985 | 0 | N/A | 0 | 0
2020-10-23 19:30 | 4.6548 | 0 | N/A | 0 | 0
2020-10-23 20:00 | 4.613 | 0 | N/A | 0 | 0
2020-10-23 20:30 | 4.5344 | 0 | N/A | 0 | 0
2020-10-23 21:00 | 4.4326 | 0 | N/A | 0 | 0
2020-10-23 21:30 | 4.1697 | 0 | N/A | 0 | 0
2020-10-23 22:00 | 3.8698 | 0 | N/A | 0 | 0
2020-10-23 22:30 | 4.3553 | 0 | N/A | 0 | 0
2020-10-23 23:00 | 4.493 | 0 | N/A | 0 | 0
2020-10-23 23:30 | 4.3194 | 0 | N/A | 0 | 0
2020-10-24 | 4.231 | 0 | N/A | 0 | 0
2020-10-24 00:30 | 4.7383 | 0 | N/A | 0 | 0
2020-10-24 01:00 | 5.2055 | 0 | N/A | 0 | 0
2020-10-24 01:30 | 4.4153 | 0 | N/A | 0 | 0
2020-10-24 02:00 | 3.6913 | 0 | N/A | 0 | 0
2020-10-24 02:30 | 3.6546 | 0 | N/A | 0 | 0
2020-10-24 03:00 | 3.2831 | 0 | N/A | 0 | 0
2020-10-24 03:30 | 2.8937 | 0 | N/A | 0 | 0
2020-10-24 04:00 | 2.6 | 0 | N/A | 0 | 0
2020-10-24 04:30 | 2.5311 | 0 | N/A | 0 | 0
2020-10-24 05:00 | 2.4949 | 0 | N/A | 0 | 0
2020-10-24 05:30 | 2.5036 | 0 | N/A | 0 | 0
2020-10-24 06:00 | 2.578 | 0 | N/A | 0 | 0
2020-10-24 06:30 | 2.96 | 0 | N/A | 0 | 0
2020-10-24 07:00 | 3.1328 | 0 | N/A | 0 | 0
2020-10-24 07:30 | 3.4576 | 0 | N/A | 0 | 0
2020-10-24 08:00 | 3.7644 | 0 | N/A | 0 | 0
2020-10-24 08:30 | 3.9286 | 0 | N/A | 0 | 0
2020-10-24 09:00 | 4.505 | 0 | N/A | 0 | 0
2020-10-24 09:30 | 4.6644 | 0 | N/A | 0 | 0
2020-10-24 10:00 | 4.1715 | 0 | N/A | 0 | 0
2020-10-24 10:30 | 3.1273 | 0 | N/A | 0 | 0
2020-10-24 11:00 | 2.6366 | 0 | N/A | 0 | 0
2020-10-24 11:30 | 3.0078 | 0 | N/A | 0 | 0
2020-10-24 12:00 | 3.6302 | 0 | N/A | 0 | 0
2020-10-24 12:30 | 3.4581 | 0 | N/A | 0 | 0
2020-10-24 13:00 | 2.028 | 0 | N/A | 0 | 0
2020-10-24 13:30 | 2.6819 | 0 | N/A | 0 | 0
2020-10-24 14:00 | 1.7948 | 0 | N/A | 0 | 0
2020-10-24 14:30 | 2.5443 | 0 | N/A | 0 | 0
2020-10-24 15:00 | 2.9587 | 0 | N/A | 0 | 0
2020-10-24 15:30 | 3.1306 | 0 | N/A | 0 | 0
2020-10-24 16:00 | 2.1763 | 0 | N/A | 0 | 0
2020-10-24 16:30 | 1.8844 | 0 | N/A | 0 | 0
2020-10-24 17:00 | 2.5197 | 0 | N/A | 0 | 0
2020-10-24 17:30 | 3.7547 | 0 | N/A | 0 | 0
2020-10-24 18:00 | 4.5314 | 0 | N/A | 0 | 0
2020-10-24 18:30 | 5.0445 | 0 | N/A | 0 | 0
2020-10-24 19:00 | 5.6682 | 0 | N/A | 0 | 0
2020-10-24 19:30 | 5.6602 | 0 | N/A | 0 | 0
2020-10-24 20:00 | 5.5825 | 0 | N/A | 0 | 0
2020-10-24 20:30 | 5.5624 | 0 | N/A | 0 | 0
2020-10-24 21:00 | 5.496 | 0 | N/A | 0 | 0
2020-10-24 21:30 | 5.3428 | 0 | N/A | 0 | 0
2020-10-24 22:00 | 5.1735 | 0 | N/A | 0 | 0
2020-10-24 22:30 | 5.5909 | 0 | N/A | 0 | 0
2020-10-24 23:00 | 5.947 | 0 | N/A | 0 | 0
2020-10-24 23:30 | 5.607 | 0 | N/A | 0 | 0
2020-10-25 | 5.4493 | 0 | N/A | 0 | 0
2020-10-25 00:30 | 5.7708 | 0 | N/A | 0 | 0
2020-10-25 01:00 | 6.2619 | 0 | N/A | 0 | 0
2020-10-25 01:30 | 5.4844 | 0 | N/A | 0 | 0
2020-10-25 02:00 | 4.6764 | 0 | N/A | 0 | 0
2020-10-25 02:30 | 4.5571 | 0 | N/A | 0 | 0
2020-10-25 03:00 | 4.2485 | 0 | N/A | 0 | 0
2020-10-25 03:30 | 3.8061 | 0 | N/A | 0 | 0
2020-10-25 04:00 | 3.4648 | 0 | N/A | 0 | 0
2020-10-25 04:30 | 3.2197 | 0 | N/A | 0 | 0
2020-10-25 05:00 | 3.1856 | 0 | N/A | 0 | 0
2020-10-25 05:30 | 3.216 | 0 | N/A | 0 | 0
2020-10-25 06:00 | 3.3152 | 0 | N/A | 0 | 0
2020-10-25 06:30 | 3.6453 | 0 | N/A | 0 | 0
2020-10-25 07:00 | 3.7892 | 0 | N/A | 0 | 0
2020-10-25 07:30 | 4.1988 | 0 | N/A | 0 | 0
2020-10-25 08:00 | 4.2426 | 0 | N/A | 0 | 0
2020-10-25 08:30 | 3.8844 | 0 | N/A | 0 | 0
2020-10-25 09:00 | 3.8336 | 0 | N/A | 0 | 0
2020-10-25 09:30 | 3.4145 | 0 | N/A | 0 | 0
2020-10-25 10:00 | 3.6123 | 0 | N/A | 0 | 0
2020-10-25 10:30 | 3.3966 | 0 | N/A | 0 | 0
2020-10-25 11:00 | 3.1917 | 0 | N/A | 0 | 0
2020-10-25 11:30 | 2.9144 | 0 | N/A | 0 | 0
2020-10-25 12:00 | 2.6177 | 0 | N/A | 0 | 0
2020-10-25 12:30 | 2.2675 | 0 | N/A | 0 | 0
2020-10-25 13:00 | 2.0789 | 0 | N/A | 0 | 0
2020-10-25 13:30 | 2.6469 | 0 | N/A | 0 | 0
2020-10-25 14:00 | 2.8408 | 0 | N/A | 0 | 0
2020-10-25 14:30 | 2.8496 | 0 | N/A | 0 | 0
2020-10-25 15:00 | 3.1308 | 0 | N/A | 0 | 0
2020-10-25 15:30 | 3.8018 | 0 | N/A | 0 | 0
2020-10-25 16:00 | 4.7031 | 0 | N/A | 0 | 0
2020-10-25 16:30 | 5.1756 | 0 | N/A | 0 | 0
2020-10-25 17:00 | 5.7724 | 0 | N/A | 0 | 0
2020-10-25 17:30 | 6.4102 | 0 | N/A | 0 | 0
2020-10-25 18:00 | 7.0885 | 0 | N/A | 0 | 0
2020-10-25 18:30 | 7.6305 | 0 | N/A | 0 | 0
2020-10-25 19:00 | 7.6107 | 0 | N/A | 0 | 0
2020-10-25 19:30 | 7.6076 | 0 | N/A | 0 | 0
2020-10-25 20:00 | 7.4707 | 0 | N/A | 0 | 0
2020-10-25 20:30 | 7.0747 | 0 | N/A | 0 | 0
2020-10-25 21:00 | 6.6959 | 0 | N/A | 0 | 0
2020-10-25 21:30 | 6.2156 | 0 | N/A | 0 | 0
2020-10-25 22:00 | 5.7619 | 0 | N/A | 0 | 0
2020-10-25 22:30 | 5.7931 | 0 | N/A | 0 | 0
2020-10-25 23:00 | 5.7801 | 0 | N/A | 0 | 0
2020-10-25 23:30 | 5.3321 | 0 | N/A | 0 | 0
2020-10-26 | 5.3858 | 0 | N/A | 0 | 0
2020-10-26 00:30 | 5.7294 | 0 | N/A | 0 | 0
2020-10-26 01:00 | 6.2816 | 0 | N/A | 0 | 0
2020-10-26 01:30 | 5.6627 | 0 | N/A | 0 | 0
2020-10-26 02:00 | 4.9416 | 0 | N/A | 0 | 0
2020-10-26 02:30 | 4.978 | 0 | N/A | 0 | 0
2020-10-26 03:00 | 4.6117 | 0 | N/A | 0 | 0
2020-10-26 03:30 | 4.0169 | 0 | N/A | 0 | 0
2020-10-26 04:00 | 3.6907 | 0 | N/A | 0 | 0
2020-10-26 04:30 | 3.4289 | 0 | N/A | 0 | 0
2020-10-26 05:00 | 3.4791 | 0 | N/A | 0 | 0
2020-10-26 05:30 | 3.7059 | 0 | N/A | 0 | 0
2020-10-26 06:00 | 4.1248 | 0 | N/A | 0 | 0
2020-10-26 06:30 | 4.9016 | 0 | N/A | 0 | 0
2020-10-26 07:00 | 5.9118 | 0 | N/A | 0 | 0
2020-10-26 07:30 | 7.2202 | 0 | N/A | 0 | 0
2020-10-26 08:00 | 7.4766 | 0 | N/A | 0 | 0
2020-10-26 08:30 | 6.7146 | 0 | N/A | 0 | 0
2020-10-26 09:00 | 6.2952 | 0 | N/A | 0 | 0
2020-10-26 09:30 | 5.6723 | 0 | N/A | 0 | 0
2020-10-26 10:00 | 4.4872 | 0 | N/A | 0 | 0
2020-10-26 10:30 | 3.4103 | 0 | N/A | 0 | 0
2020-10-26 11:00 | 3.3086 | 0 | N/A | 0 | 0
2020-10-26 11:30 | 3.0546 | 0 | N/A | 0 | 0
2020-10-26 12:00 | 2.6705 | 0 | N/A | 0 | 0
2020-10-26 12:30 | 2.0391 | 0 | N/A | 0 | 0
2020-10-26 13:00 | 1.6532 | 0 | N/A | 0 | 0
2020-10-26 13:30 | 1.5175 | 0 | N/A | 0 | 0
2020-10-26 14:00 | 1.5373 | 0 | N/A | 0 | 0
2020-10-26 14:30 | 1.5607 | 0 | N/A | 0 | 0
2020-10-26 15:00 | 1.6977 | 0 | N/A | 0 | 0
2020-10-26 15:30 | 1.8071 | 0 | N/A | 0 | 0
2020-10-26 16:00 | 2.6633 | 0 | N/A | 0 | 0
2020-10-26 16:30 | 3.2554 | 0 | N/A | 0 | 0
2020-10-26 17:00 | 3.7996 | 0 | N/A | 0 | 0
2020-10-26 17:30 | 4.43 | 0 | N/A | 0 | 0
2020-10-26 18:00 | 4.8755 | 0 | N/A | 0 | 0
2020-10-26 18:30 | 5.5041 | 0 | N/A | 0 | 0
2020-10-26 19:00 | 5.7485 | 0 | N/A | 0 | 0
2020-10-26 19:30 | 6.2492 | 0 | N/A | 0 | 0
2020-10-26 20:00 | 6.5329 | 0 | N/A | 0 | 0
2020-10-26 20:30 | 6.5819 | 0 | N/A | 0 | 0
2020-10-26 21:00 | 6.468 | 0 | N/A | 0 | 0
2020-10-26 21:30 | 6.0705 | 0 | N/A | 0 | 0
2020-10-26 22:00 | 5.5919 | 0 | N/A | 0 | 0
2020-10-26 22:30 | 5.7588 | 0 | N/A | 0 | 0
2020-10-26 23:00 | 5.6996 | 0 | N/A | 0 | 0
2020-10-26 23:30 | 5.2004 | 0 | N/A | 0 | 0
2020-10-27 | 5.1344 | 0 | N/A | 0 | 0
2020-10-27 00:30 | 5.3958 | 0 | N/A | 0 | 0
2020-10-27 01:00 | 5.9369 | 0 | N/A | 0 | 0
2020-10-27 01:30 | 5.3135 | 0 | N/A | 0 | 0
2020-10-27 02:00 | 4.6564 | 0 | N/A | 0 | 0
2020-10-27 02:30 | 4.6055 | 0 | N/A | 0 | 0
2020-10-27 03:00 | 4.1661 | 0 | N/A | 0 | 0
2020-10-27 03:30 | 3.7247 | 0 | N/A | 0 | 0
2020-10-27 04:00 | 3.3412 | 0 | N/A | 0 | 0
2020-10-27 04:30 | 3.2189 | 0 | N/A | 0 | 0
2020-10-27 05:00 | 3.3202 | 0 | N/A | 0 | 0
2020-10-27 05:30 | 3.5933 | 0 | N/A | 0 | 0
2020-10-27 06:00 | 3.8752 | 0 | N/A | 0 | 0
2020-10-27 06:30 | 4.7347 | 0 | N/A | 0 | 0
2020-10-27 07:00 | 5.6048 | 0 | N/A | 0 | 0
2020-10-27 07:30 | 6.697 | 0 | N/A | 0 | 0
2020-10-27 08:00 | 6.8112 | 0 | N/A | 0 | 0
2020-10-27 08:30 | 5.92 | 0 | N/A | 0 | 0
2020-10-27 09:00 | 4.9339 | 0 | N/A | 0 | 0
2020-10-27 09:30 | 4.4447 | 0 | N/A | 0 | 0
2020-10-27 10:00 | 3.7568 | 0 | N/A | 0 | 0
2020-10-27 10:30 | 3.3914 | 0 | N/A | 0 | 0
2020-10-27 11:00 | 3.3512 | 0 | N/A | 0 | 0
2020-10-27 11:30 | 2.8754 | 0 | N/A | 0 | 0
2020-10-27 12:00 | 2.8679 | 0 | N/A | 0 | 0
2020-10-27 12:30 | 2.4609 | 0 | N/A | 0 | 0
2020-10-27 13:00 | 1.8813 | 0 | N/A | 0 | 0
2020-10-27 13:30 | 2.0402 | 0 | N/A | 0 | 0
2020-10-27 14:00 | 1.8334 | 0 | N/A | 0 | 0
2020-10-27 14:30 | 1.7934 | 0 | N/A | 0 | 0
2020-10-27 15:00 | 1.6395 | 0 | N/A | 0 | 0
2020-10-27 15:30 | 1.8538 | 0 | N/A | 0 | 0
2020-10-27 16:00 | 1.7418 | 0 | N/A | 0 | 0
2020-10-27 16:30 | 2.215 | 0 | N/A | 0 | 0
2020-10-27 17:00 | 3.184 | 0 | N/A | 0 | 0
2020-10-27 17:30 | 4.1819 | 0 | N/A | 0 | 0
2020-10-27 18:00 | 5.0253 | 0 | N/A | 0 | 0
2020-10-27 18:30 | 5.4698 | 0 | N/A | 0 | 0
2020-10-27 19:00 | 5.5755 | 0 | N/A | 0 | 0
2020-10-27 19:30 | 5.606 | 0 | N/A | 0 | 0
2020-10-27 20:00 | 5.8147 | 0 | N/A | 0 | 0
2020-10-27 20:30 | 5.9213 | 0 | N/A | 0 | 0
2020-10-27 21:00 | 5.8552 | 0 | N/A | 0 | 0
2020-10-27 21:30 | 5.5155 | 0 | N/A | 0 | 0
2020-10-27 22:00 | 5.0265 | 0 | N/A | 0 | 0
2020-10-27 22:30 | 5.1844 | 0 | N/A | 0 | 0
2020-10-27 23:00 | 5.2629 | 0 | N/A | 0 | 0
2020-10-27 23:30 | 4.8385 | 0 | N/A | 0 | 0
2020-10-28 | 4.8001 | 0 | N/A | 0 | 0
2020-10-28 00:30 | 5.2243 | 0 | N/A | 0 | 0
2020-10-28 01:00 | 5.6804 | 0 | N/A | 0 | 0
2020-10-28 01:30 | 4.9305 | 0 | N/A | 0 | 0
2020-10-28 02:00 | 4.1178 | 0 | N/A | 0 | 0
2020-10-28 02:30 | 4.0339 | 0 | N/A | 0 | 0
2020-10-28 03:00 | 3.6787 | 0 | N/A | 0 | 0
2020-10-28 03:30 | 3.3111 | 0 | N/A | 0 | 0
2020-10-28 04:00 | 3.0379 | 0 | N/A | 0 | 0
2020-10-28 04:30 | 2.8765 | 0 | N/A | 0 | 0
2020-10-28 05:00 | 2.9579 | 0 | N/A | 0 | 0
2020-10-28 05:30 | 3.2418 | 0 | N/A | 0 | 0
2020-10-28 06:00 | 3.5379 | 0 | N/A | 0 | 0
2020-10-28 06:30 | 4.3627 | 0 | N/A | 0 | 0
2020-10-28 07:00 | 5.4045 | 0 | N/A | 0 | 0
2020-10-28 07:30 | 6.3333 | 0 | N/A | 0 | 0
2020-10-28 08:00 | 6.4344 | 0 | N/A | 0 | 0
2020-10-28 08:30 | 5.242 | 0 | N/A | 0 | 0
2020-10-28 09:00 | 4.3274 | 0 | N/A | 0 | 0
2020-10-28 09:30 | 3.0373 | 0 | N/A | 0 | 0
2020-10-28 10:00 | 2.269 | 0 | N/A | 0 | 0
2020-10-28 10:30 | 1.638 | 0 | N/A | 0 | 0
2020-10-28 11:00 | 1.4886 | 0 | N/A | 0 | 0
2020-10-28 11:30 | 1.4173 | 0 | N/A | 0 | 0
2020-10-28 12:00 | 1.4835 | 0 | N/A | 0 | 0
2020-10-28 12:30 | 1.1934 | 0 | N/A | 0 | 0
2020-10-28 13:00 | 0.99206 | 0 | N/A | 0 | 0
2020-10-28 13:30 | 1.0263 | 0 | N/A | 0 | 0
2020-10-28 14:00 | 0.94475 | 0 | N/A | 0 | 0
2020-10-28 14:30 | 0.9424 | 0 | N/A | 0 | 0
2020-10-28 15:00 | 0.95968 | 0 | N/A | 0 | 0
2020-10-28 15:30 | 1.0024 | 0 | N/A | 0 | 0
2020-10-28 16:00 | 0.97037 | 0 | N/A | 0 | 0
2020-10-28 16:30 | 0.84481 | 0 | N/A | 0 | 0
2020-10-28 17:00 | 1.8413 | 0 | N/A | 0 | 0
2020-10-28 17:30 | 2.5659 | 0 | N/A | 0 | 0
2020-10-28 18:00 | 3.8173 | 0 | N/A | 0 | 0
2020-10-28 18:30 | 4.3672 | 0 | N/A | 0 | 0
2020-10-28 19:00 | 4.6334 | 0 | N/A | 0 | 0
2020-10-28 19:30 | 4.6478 | 0 | N/A | 0 | 0
2020-10-28 20:00 | 4.7794 | 0 | N/A | 0 | 0
2020-10-28 20:30 | 4.8368 | 0 | N/A | 0 | 0
2020-10-28 21:00 | 4.8936 | 0 | N/A | 0 | 0
2020-10-28 21:30 | 4.6449 | 0 | N/A | 0 | 0
2020-10-28 22:00 | 4.309 | 0 | N/A | 0 | 0
2020-10-28 22:30 | 4.6223 | 0 | N/A | 0 | 0
2020-10-28 23:00 | 4.7516 | 0 | N/A | 0 | 0
2020-10-28 23:30 | 4.4413 | 0 | N/A | 0 | 0
2020-10-29 | 4.4892 | 0 | N/A | 0 | 0
2020-10-29 00:30 | 4.7313 | 0 | N/A | 0 | 0
2020-10-29 01:00 | 5.2548 | 0 | N/A | 0 | 0
2020-10-29 01:30 | 4.5049 | 0 | N/A | 0 | 0
2020-10-29 02:00 | 3.7741 | 0 | N/A | 0 | 0
2020-10-29 02:30 | 3.697 | 0 | N/A | 0 | 0
2020-10-29 03:00 | 3.3569 | 0 | N/A | 0 | 0
2020-10-29 03:30 | 3.0166 | 0 | N/A | 0 | 0
2020-10-29 04:00 | 2.7506 | 0 | N/A | 0 | 0
2020-10-29 04:30 | 2.7183 | 0 | N/A | 0 | 0
2020-10-29 05:00 | 2.749 | 0 | N/A | 0 | 0
2020-10-29 05:30 | 2.9986 | 0 | N/A | 0 | 0
2020-10-29 06:00 | 3.4295 | 0 | N/A | 0 | 0
2020-10-29 06:30 | 4.1176 | 0 | N/A | 0 | 0
2020-10-29 07:00 | 4.9101 | 0 | N/A | 0 | 0
2020-10-29 07:30 | 5.8701 | 0 | N/A | 0 | 0
2020-10-29 08:00 | 5.5776 | 0 | N/A | 0 | 0
2020-10-29 08:30 | 4.1906 | 0 | N/A | 0 | 0
2020-10-29 09:00 | 3.0881 | 0 | N/A | 0 | 0
2020-10-29 09:30 | 2.0908 | 0 | N/A | 0 | 0
2020-10-29 10:00 | 1.4166 | 0 | N/A | 0 | 0
2020-10-29 10:30 | 0.86529 | 0 | N/A | 0 | 0
2020-10-29 11:00 | 1.2987 | 0 | N/A | 0 | 0
2020-10-29 11:30 | 1.2042 | 0 | N/A | 0 | 0
2020-10-29 12:00 | 2.5686 | 0 | N/A | 0 | 0
2020-10-29 12:30 | 3.3468 | 0 | N/A | 0 | 0
2020-10-29 13:00 | 2.4474 | 0 | N/A | 0 | 0
2020-10-29 13:30 | 1.5013 | 0 | N/A | 0 | 0
2020-10-29 14:00 | 2.2001 | 0 | N/A | 0 | 0
2020-10-29 14:30 | 2.8572 | 0 | N/A | 0 | 0
2020-10-29 15:00 | 3.3607 | 0 | N/A | 0 | 0
2020-10-29 15:30 | 3.3933 | 0 | N/A | 0 | 0
2020-10-29 16:00 | 3.4376 | 0 | N/A | 0 | 0
2020-10-29 16:30 | 3.8888 | 0 | N/A | 0 | 0
2020-10-29 17:00 | 4.3319 | 0 | N/A | 0 | 0
2020-10-29 17:30 | 4.859 | 0 | N/A | 0 | 0
2020-10-29 18:00 | 5.5364 | 0 | N/A | 0 | 0
2020-10-29 18:30 | 5.6908 | 0 | N/A | 0 | 0
2020-10-29 19:00 | 5.8728 | 0 | N/A | 0 | 0
2020-10-29 19:30 | 5.9346 | 0 | N/A | 0 | 0
2020-10-29 20:00 | 5.9276 | 0 | N/A | 0 | 0
2020-10-29 20:30 | 5.7632 | 0 | N/A | 0 | 0
2020-10-29 21:00 | 5.6023 | 0 | N/A | 0 | 0
2020-10-29 21:30 | 5.241 | 0 | N/A | 0 | 0
2020-10-29 22:00 | 4.8217 | 0 | N/A | 0 | 0
2020-10-29 22:30 | 5.0402 | 0 | N/A | 0 | 0
2020-10-29 23:00 | 5.0456 | 0 | N/A | 0 | 0
2020-10-29 23:30 | 4.5804 | 0 | N/A | 0 | 0
2020-10-30 | 4.5551 | 0 | N/A | 0 | 0
2020-10-30 00:30 | 4.9422 | 0 | N/A | 0 | 0
2020-10-30 01:00 | 5.4687 | 0 | N/A | 0 | 0
2020-10-30 01:30 | 4.6698 | 0 | N/A | 0 | 0
2020-10-30 02:00 | 3.8542 | 0 | N/A | 0 | 0
2020-10-30 02:30 | 3.7434 | 0 | N/A | 0 | 0
2020-10-30 03:00 | 3.4098 | 0 | N/A | 0 | 0
2020-10-30 03:30 | 3.0159 | 0 | N/A | 0 | 0
2020-10-30 04:00 | 2.7514 | 0 | N/A | 0 | 0
2020-10-30 04:30 | 2.6537 | 0 | N/A | 0 | 0
2020-10-30 05:00 | 2.7497 | 0 | N/A | 0 | 0
2020-10-30 05:30 | 2.9606 | 0 | N/A | 0 | 0
2020-10-30 06:00 | 3.3274 | 0 | N/A | 0 | 0
2020-10-30 06:30 | 4.0717 | 0 | N/A | 0 | 0
2020-10-30 07:00 | 4.7544 | 0 | N/A | 0 | 0
2020-10-30 07:30 | 5.5282 | 0 | N/A | 0 | 0
2020-10-30 08:00 | 5.4367 | 0 | N/A | 0 | 0
2020-10-30 08:30 | 4.4571 | 0 | N/A | 0 | 0
2020-10-30 09:00 | 3.9036 | 0 | N/A | 0 | 0
2020-10-30 09:30 | 3.661 | 0 | N/A | 0 | 0
2020-10-30 10:00 | 3.1524 | 0 | N/A | 0 | 0
2020-10-30 10:30 | 2.442 | 0 | N/A | 0 | 0
2020-10-30 11:00 | 1.2844 | 0 | N/A | 0 | 0
2020-10-30 11:30 | 0.99242 | 0 | N/A | 0 | 0
2020-10-30 12:00 | 0.9486 | 0 | N/A | 0 | 0
2020-10-30 12:30 | 0.96083 | 0 | N/A | 0 | 0
2020-10-30 13:00 | 0.66667 | 0 | N/A | 0 | 0
2020-10-30 13:30 | 0.36408 | 0 | N/A | 0 | 0
2020-10-30 14:00 | 0.47001 | 0 | N/A | 0 | 0
2020-10-30 14:30 | 0.56715 | 0 | N/A | 0 | 0
2020-10-30 15:00 | 0.55753 | 0 | N/A | 0 | 0
2020-10-30 15:30 | 0.95695 | 0 | N/A | 0 | 0
2020-10-30 16:00 | 0.762 | 0 | N/A | 0 | 0
2020-10-30 16:30 | 0.92073 | 0 | N/A | 0 | 0
2020-10-30 17:00 | 1.1488 | 0 | N/A | 0 | 0
2020-10-30 17:30 | 1.6161 | 0 | N/A | 0 | 0
2020-10-30 18:00 | 2.5427 | 0 | N/A | 0 | 0
2020-10-30 18:30 | 3.4283 | 0 | N/A | 0 | 0
2020-10-30 19:00 | 3.9915 | 0 | N/A | 0 | 0
2020-10-30 19:30 | 4.469 | 0 | N/A | 0 | 0
2020-10-30 20:00 | 4.8923 | 0 | N/A | 0 | 0
2020-10-30 20:30 | 5.0351 | 0 | N/A | 0 | 0
2020-10-30 21:00 | 4.9971 | 0 | N/A | 0 | 0
2020-10-30 21:30 | 4.7875 | 0 | N/A | 0 | 0
2020-10-30 22:00 | 4.4847 | 0 | N/A | 0 | 0
2020-10-30 22:30 | 4.862 | 0 | N/A | 0 | 0
2020-10-30 23:00 | 5.0021 | 0 | N/A | 0 | 0
2020-10-30 23:30 | 4.6552 | 0 | N/A | 0 | 0
2020-10-31 | 4.6336 | 0 | N/A | 0 | 0
2020-10-31 00:30 | 4.961 | 0 | N/A | 0 | 0
2020-10-31 01:00 | 5.4108 | 0 | N/A | 0 | 0
2020-10-31 01:30 | 4.529 | 0 | N/A | 0 | 0
2020-10-31 02:00 | 3.6967 | 0 | N/A | 0 | 0
2020-10-31 02:30 | 3.6342 | 0 | N/A | 0 | 0
2020-10-31 03:00 | 3.2512 | 0 | N/A | 0 | 0
2020-10-31 03:30 | 2.8838 | 0 | N/A | 0 | 0
2020-10-31 04:00 | 2.6604 | 0 | N/A | 0 | 0
2020-10-31 04:30 | 2.6053 | 0 | N/A | 0 | 0
2020-10-31 05:00 | 2.5025 | 0 | N/A | 0 | 0
2020-10-31 05:30 | 2.5371 | 0 | N/A | 0 | 0
2020-10-31 06:00 | 2.7101 | 0 | N/A | 0 | 0
2020-10-31 06:30 | 3.1048 | 0 | N/A | 0 | 0
2020-10-31 07:00 | 3.3802 | 0 | N/A | 0 | 0
2020-10-31 07:30 | 3.8107 | 0 | N/A | 0 | 0
2020-10-31 08:00 | 4.0946 | 0 | N/A | 0 | 0
2020-10-31 08:30 | 3.7615 | 0 | N/A | 0 | 0
2020-10-31 09:00 | 3.5747 | 0 | N/A | 0 | 0
2020-10-31 09:30 | 3.3948 | 0 | N/A | 0 | 0
2020-10-31 10:00 | 2.8404 | 0 | N/A | 0 | 0
2020-10-31 10:30 | 2.9351 | 0 | N/A | 0 | 0
2020-10-31 11:00 | 2.7156 | 0 | N/A | 0 | 0
2020-10-31 11:30 | 2.2717 | 0 | N/A | 0 | 0
2020-10-31 12:00 | 1.9479 | 0 | N/A | 0 | 0
2020-10-31 12:30 | 1.7348 | 0 | N/A | 0 | 0
2020-10-31 13:00 | 1.486 | 0 | N/A | 0 | 0
2020-10-31 13:30 | 1.4965 | 0 | N/A | 0 | 0
2020-10-31 14:00 | 1.5384 | 0 | N/A | 0 | 0
2020-10-31 14:30 | 1.1275 | 0 | N/A | 0 | 0
2020-10-31 15:00 | 1.3686 | 0 | N/A | 0 | 0
2020-10-31 15:30 | 1.6568 | 0 | N/A | 0 | 0
2020-10-31 16:00 | 1.3642 | 0 | N/A | 0 | 0
2020-10-31 16:30 | 1.9538 | 0 | N/A | 0 | 0
2020-10-31 17:00 | 2.1407 | 0 | N/A | 0 | 0
2020-10-31 17:30 | 2.5236 | 0 | N/A | 0 | 0
2020-10-31 18:00 | 3.0741 | 0 | N/A | 0 | 0
2020-10-31 18:30 | 3.6469 | 0 | N/A | 0 | 0
2020-10-31 19:00 | 4.1093 | 0 | N/A | 0 | 0
2020-10-31 19:30 | 4.536 | 0 | N/A | 0 | 0
2020-10-31 20:00 | 4.8691 | 0 | N/A | 0 | 0
2020-10-31 20:30 | 4.8814 | 0 | N/A | 0 | 0
2020-10-31 21:00 | 4.9628 | 0 | N/A | 0 | 0
2020-10-31 21:30 | 4.7632 | 0 | N/A | 0 | 0
2020-10-31 22:00 | 4.5045 | 0 | N/A | 0 | 0
2020-10-31 22:30 | 4.7997 | 0 | N/A | 0 | 0
2020-10-31 23:00 | 5.0757 | 0 | N/A | 0 | 0
2020-10-31 23:30 | 4.8513 | 0 | N/A | 0 | 0
2020-11-01 | 4.884 | 0 | N/A | 0 | 0
2020-11-01 00:30 | 5.1281 | 0 | N/A | 0 | 0
2020-11-01 01:00 | 5.628 | 0 | N/A | 0 | 0
2020-11-01 01:30 | 4.8473 | 0 | N/A | 0 | 0
2020-11-01 02:00 | 4.0508 | 0 | N/A | 0 | 0
2020-11-01 02:30 | 3.9993 | 0 | N/A | 0 | 0
2020-11-01 03:00 | 3.6747 | 0 | N/A | 0 | 0
2020-11-01 03:30 | 3.1965 | 0 | N/A | 0 | 0
2020-11-01 04:00 | 2.8951 | 0 | N/A | 0 | 0
2020-11-01 04:30 | 2.7236 | 0 | N/A | 0 | 0
2020-11-01 05:00 | 2.6964 | 0 | N/A | 0 | 0
2020-11-01 05:30 | 2.6768 | 0 | N/A | 0 | 0
2020-11-01 06:00 | 2.8631 | 0 | N/A | 0 | 0
2020-11-01 06:30 | 3.0794 | 0 | N/A | 0 | 0
2020-11-01 07:00 | 3.3139 | 0 | N/A | 0 | 0
2020-11-01 07:30 | 3.5498 | 0 | N/A | 0 | 0
2020-11-01 08:00 | 3.821 | 0 | N/A | 0 | 0
2020-11-01 08:30 | 3.7664 | 0 | N/A | 0 | 0
2020-11-01 09:00 | 3.7757 | 0 | N/A | 0 | 0
2020-11-01 09:30 | 3.4 | 0 | N/A | 0 | 0
2020-11-01 10:00 | 2.7979 | 0 | N/A | 0 | 0
2020-11-01 10:30 | 1.6288 | 0 | N/A | 0 | 0
2020-11-01 11:00 | 0.75097 | 0 | N/A | 0 | 0
2020-11-01 11:30 | 0.37529 | 0 | N/A | 0 | 0
2020-11-01 12:00 | -0.3772 | 0 | N/A | 0 | 0
2020-11-01 12:30 | -0.43139 | 0 | N/A | 0 | 0
2020-11-01 13:00 | -0.60386 | 0 | N/A | 0 | 0
2020-11-01 13:30 | -0.73685 | 0 | N/A | 0 | 0
2020-11-01 14:00 | -0.92897 | 0 | N/A | 0 | 0
2020-11-01 14:30 | -0.90363 | 0 | N/A | 0 | 0
2020-11-01 15:00 | -0.77521 | 0 | N/A | 0 | 0
2020-11-01 15:30 | -0.65178 | 0 | N/A | 0 | 0
2020-11-01 16:00 | -0.45726 | 0 | N/A | 0 | 0
2020-11-01 16:30 | 0.39036 | 0 | N/A | 0 | 0
2020-11-01 17:00 | 0.76269 | 0 | N/A | 0 | 0
2020-11-01 17:30 | 1.6089 | 0 | N/A | 0 | 0
2020-11-01 18:00 | 2.5038 | 0 | N/A | 0 | 0
2020-11-01 18:30 | 3.2825 | 0 | N/A | 0 | 0
2020-11-01 19:00 | 3.8236 | 0 | N/A | 0 | 0
2020-11-01 19:30 | 4.1705 | 0 | N/A | 0 | 0
2020-11-01 20:00 | 4.479 | 0 | N/A | 0 | 0
2020-11-01 20:30 | 4.4786 | 0 | N/A | 0 | 0
2020-11-01 21:00 | 4.4427 | 0 | N/A | 0 | 0
2020-11-01 21:30 | 4.374 | 0 | N/A | 0 | 0
2020-11-01 22:00 | 4.0857 | 0 | N/A | 0 | 0
2020-11-01 22:30 | 4.4511 | 0 | N/A | 0 | 0
2020-11-01 23:00 | 4.5898 | 0 | N/A | 0 | 0
2020-11-01 23:30 | 4.3375 | 0 | N/A | 0 | 0
2020-11-02 | 4.4087 | 0 | N/A | 0 | 0
2020-11-02 00:30 | 4.6733 | 0 | N/A | 0 | 0
2020-11-02 01:00 | 5.2617 | 0 | N/A | 0 | 0
2020-11-02 01:30 | 4.6999 | 0 | N/A | 0 | 0
2020-11-02 02:00 | 4.0032 | 0 | N/A | 0 | 0
2020-11-02 02:30 | 4.0608 | 0 | N/A | 0 | 0
2020-11-02 03:00 | 3.7485 | 0 | N/A | 0 | 0
2020-11-02 03:30 | 3.2435 | 0 | N/A | 0 | 0
2020-11-02 04:00 | 2.9329 | 0 | N/A | 0 | 0
2020-11-02 04:30 | 2.8844 | 0 | N/A | 0 | 0
2020-11-02 05:00 | 2.7771 | 0 | N/A | 0 | 0
2020-11-02 05:30 | 2.8777 | 0 | N/A | 0 | 0
2020-11-02 06:00 | 3.1596 | 0 | N/A | 0 | 0
2020-11-02 06:30 | 3.7348 | 0 | N/A | 0 | 0
2020-11-02 07:00 | 4.2431 | 0 | N/A | 0 | 0
2020-11-02 07:30 | 4.7137 | 0 | N/A | 0 | 0
2020-11-02 08:00 | 4.5093 | 0 | N/A | 0 | 0
2020-11-02 08:30 | 3.295 | 0 | N/A | 0 | 0
2020-11-02 09:00 | 2.4851 | 0 | N/A | 0 | 0
2020-11-02 09:30 | 1.7444 | 0 | N/A | 0 | 0
2020-11-02 10:00 | 0.8865 | 0 | N/A | 0 | 0
2020-11-02 10:30 | 0.40565 | 0 | N/A | 0 | 0
2020-11-02 11:00 | -0.26053 | 0 | N/A | 0 | 0
2020-11-02 11:30 | -0.35673 | 0 | N/A | 0 | 0
2020-11-02 12:00 | -0.46306 | 0 | N/A | 0 | 0
2020-11-02 12:30 | -0.6476 | 0 | N/A | 0 | 0
2020-11-02 13:00 | -0.74985 | 0 | N/A | 0 | 0
2020-11-02 13:30 | -0.79736 | 0 | N/A | 0 | 0
2020-11-02 14:00 | -0.78376 | 0 | N/A | 0 | 0
2020-11-02 14:30 | -0.78847 | 0 | N/A | 0 | 0
2020-11-02 15:00 | -0.6845 | 0 | N/A | 0 | 0
2020-11-02 15:30 | -0.52469 | 0 | N/A | 0 | 0
2020-11-02 16:00 | -0.25353 | 0 | N/A | 0 | 0
2020-11-02 16:30 | 0.25095 | 0 | N/A | 0 | 0
2020-11-02 17:00 | 0.87912 | 0 | N/A | 0 | 0
2020-11-02 17:30 | 1.7966 | 0 | N/A | 0 | 0
2020-11-02 18:00 | 2.6728 | 0 | N/A | 0 | 0
2020-11-02 18:30 | 3.3689 | 0 | N/A | 0 | 0
2020-11-02 19:00 | 3.82 | 0 | N/A | 0 | 0
2020-11-02 19:30 | 4.0213 | 0 | N/A | 0 | 0
2020-11-02 20:00 | 4.1692 | 0 | N/A | 0 | 0
2020-11-02 20:30 | 4.2423 | 0 | N/A | 0 | 0
2020-11-02 21:00 | 4.1941 | 0 | N/A | 0 | 0
2020-11-02 21:30 | 3.9113 | 0 | N/A | 0 | 0
2020-11-02 22:00 | 3.6605 | 0 | N/A | 0 | 0
2020-11-02 22:30 | 3.9966 | 0 | N/A | 0 | 0
2020-11-02 23:00 | 4.1611 | 0 | N/A | 0 | 0
2020-11-02 23:30 | 3.8516 | 0 | N/A | 0 | 0
2020-11-03 | 3.8808 | 0 | N/A | 0 | 0
2020-11-03 00:30 | 4.3999 | 0 | N/A | 0 | 0
2020-11-03 01:00 | 4.6827 | 0 | N/A | 0 | 0
2020-11-03 01:30 | 3.7513 | 0 | N/A | 0 | 0
2020-11-03 02:00 | 3.0581 | 0 | N/A | 0 | 0
2020-11-03 02:30 | 3.0511 | 0 | N/A | 0 | 0
2020-11-03 03:00 | 2.7456 | 0 | N/A | 0 | 0
2020-11-03 03:30 | 2.4505 | 0 | N/A | 0 | 0
2020-11-03 04:00 | 2.2326 | 0 | N/A | 0 | 0
2020-11-03 04:30 | 2.1084 | 0 | N/A | 0 | 0
2020-11-03 05:00 | 2.0853 | 0 | N/A | 0 | 0
2020-11-03 05:30 | 2.1968 | 0 | N/A | 0 | 0
2020-11-03 06:00 | 2.3375 | 0 | N/A | 0 | 0
2020-11-03 06:30 | 2.5959 | 0 | N/A | 0 | 0
2020-11-03 07:00 | 2.473 | 0 | N/A | 0 | 0
2020-11-03 07:30 | 2.5272 | 0 | N/A | 0 | 0
2020-11-03 08:00 | 2.5724 | 0 | N/A | 0 | 0
2020-11-03 08:30 | 1.8935 | 0 | N/A | 0 | 0
2020-11-03 09:00 | 1.4646 | 0 | N/A | 0 | 0
2020-11-03 09:30 | 1.1274 | 0 | N/A | 0 | 0
2020-11-03 10:00 | 0.78696 | 0 | N/A | 0 | 0
2020-11-03 10:30 | 0.27729 | 0 | N/A | 0 | 0
2020-11-03 11:00 | -0.15563 | 0 | N/A | 0 | 0
2020-11-03 11:30 | -0.37205 | 0 | N/A | 0 | 0
2020-11-03 12:00 | -0.58266 | 0 | N/A | 0 | 0
2020-11-03 12:30 | -0.72774 | 0 | N/A | 0 | 0
2020-11-03 13:00 | -0.65816 | 0 | N/A | 0 | 0
2020-11-03 13:30 | -0.69592 | 0 | N/A | 0 | 0
2020-11-03 14:00 | -0.79845 | 0 | N/A | 0 | 0
2020-11-03 14:30 | -0.68066 | 0 | N/A | 0 | 0
2020-11-03 15:00 | -0.10006 | 0 | N/A | 0 | 0
2020-11-03 15:30 | 0.95973 | 0 | N/A | 0 | 0
2020-11-03 16:00 | 0.1297 | 0 | N/A | 0 | 0
2020-11-03 16:30 | 0.73884 | 0 | N/A | 0 | 0
2020-11-03 17:00 | 1.3786 | 0 | N/A | 0 | 0
2020-11-03 17:30 | 2.4861 | 0 | N/A | 0 | 0
2020-11-03 18:00 | 3.1587 | 0 | N/A | 0 | 0
2020-11-03 18:30 | 4.1373 | 0 | N/A | 0 | 0
2020-11-03 19:00 | 4.7237 | 0 | N/A | 0 | 0
2020-11-03 19:30 | 4.8525 | 0 | N/A | 0 | 0
2020-11-03 20:00 | 4.714 | 0 | N/A | 0 | 0
2020-11-03 20:30 | 4.5896 | 0 | N/A | 0 | 0
2020-11-03 21:00 | 4.4629 | 0 | N/A | 0 | 0
2020-11-03 21:30 | 4.0677 | 0 | N/A | 0 | 0
2020-11-03 22:00 | 3.7624 | 0 | N/A | 0 | 0
2020-11-03 22:30 | 4.0883 | 0 | N/A | 0 | 0
2020-11-03 23:00 | 4.1735 | 0 | N/A | 0 | 0
2020-11-03 23:30 | 3.85 | 0 | N/A | 0 | 0
2020-11-04 | 3.9667 | 0 | N/A | 0 | 0
2020-11-04 00:30 | 4.3629 | 0 | N/A | 0 | 0
2020-11-04 01:00 | 4.7405 | 0 | N/A | 0 | 0
2020-11-04 01:30 | 3.9477 | 0 | N/A | 0 | 0
2020-11-04 02:00 | 3.2558 | 0 | N/A | 0 | 0
2020-11-04 02:30 | 3.0743 | 0 | N/A | 0 | 0
2020-11-04 03:00 | 2.6849 | 0 | N/A | 0 | 0
2020-11-04 03:30 | 2.4231 | 0 | N/A | 0 | 0
2020-11-04 04:00 | 2.1959 | 0 | N/A | 0 | 0
2020-11-04 04:30 | 2.1756 | 0 | N/A | 0 | 0
2020-11-04 05:00 | 2.1273 | 0 | N/A | 0 | 0
2020-11-04 05:30 | 2.3409 | 0 | N/A | 0 | 0
2020-11-04 06:00 | 2.5919 | 0 | N/A | 0 | 0
2020-11-04 06:30 | 3.0548 | 0 | N/A | 0 | 0
2020-11-04 07:00 | 3.4206 | 0 | N/A | 0 | 0
2020-11-04 07:30 | 4.2278 | 0 | N/A | 0 | 0
2020-11-04 08:00 | 4.4376 | 0 | N/A | 0 | 0
2020-11-04 08:30 | 5.35 | 0 | N/A | 0 | 0
2020-11-04 09:00 | 5.5169 | 0 | N/A | 0 | 0
2020-11-04 09:30 | 5.4536 | 0 | N/A | 0 | 0
2020-11-04 10:00 | 5.29 | 0 | N/A | 0 | 0
2020-11-04 10:30 | 4.5235 | 0 | N/A | 0 | 0
2020-11-04 11:00 | 3.5883 | 0 | N/A | 0 | 0
2020-11-04 11:30 | 3.5879 | 0 | N/A | 0 | 0
2020-11-04 12:00 | 4.0338 | 0 | N/A | 0 | 0
2020-11-04 12:30 | 3.9168 | 0 | N/A | 0 | 0
2020-11-04 13:00 | 3.5991 | 0 | N/A | 0 | 0
2020-11-04 13:30 | 3.4291 | 0 | N/A | 0 | 0
2020-11-04 14:00 | 2.8754 | 0 | N/A | 0 | 0
2020-11-04 14:30 | 2.6954 | 0 | N/A | 0 | 0
2020-11-04 15:00 | 3.1883 | 0 | N/A | 0 | 0
2020-11-04 15:30 | 2.9131 | 0 | N/A | 0 | 0
2020-11-04 16:00 | 3.0043 | 0 | N/A | 0 | 0
2020-11-04 16:30 | 3.2044 | 0 | N/A | 0 | 0
2020-11-04 17:00 | 3.9495 | 0 | N/A | 0 | 0
2020-11-04 17:30 | 4.6435 | 0 | N/A | 0 | 0
2020-11-04 18:00 | 5.1104 | 0 | N/A | 0 | 0
2020-11-04 18:30 | 5.2178 | 0 | N/A | 0 | 0
2020-11-04 19:00 | 5.1065 | 0 | N/A | 0 | 0
2020-11-04 19:30 | 5.3125 | 0 | N/A | 0 | 0
2020-11-04 20:00 | 5.5124 | 0 | N/A | 0 | 0
2020-11-04 20:30 | 5.6403 | 0 | N/A | 0 | 0
2020-11-04 21:00 | 5.4675 | 0 | N/A | 0 | 0
2020-11-04 21:30 | 5.0626 | 0 | N/A | 0 | 0
2020-11-04 22:00 | 4.6161 | 0 | N/A | 0 | 0
2020-11-04 22:30 | 4.9039 | 0 | N/A | 0 | 0
2020-11-04 23:00 | 4.9958 | 0 | N/A | 0 | 0
2020-11-04 23:30 | 4.4626 | 0 | N/A | 0 | 0
2020-11-05 | 4.4891 | 0 | N/A | 0 | 0
2020-11-05 00:30 | 4.9136 | 0 | N/A | 0 | 0
2020-11-05 01:00 | 5.5565 | 0 | N/A | 0 | 0
2020-11-05 01:30 | 4.7013 | 0 | N/A | 0 | 0
2020-11-05 02:00 | 3.9654 | 0 | N/A | 0 | 0
2020-11-05 02:30 | 3.8765 | 0 | N/A | 0 | 0
2020-11-05 03:00 | 3.4987 | 0 | N/A | 0 | 0
2020-11-05 03:30 | 3.1524 | 0 | N/A | 0 | 0
2020-11-05 04:00 | 2.8668 | 0 | N/A | 0 | 0
2020-11-05 04:30 | 2.7315 | 0 | N/A | 0 | 0
2020-11-05 05:00 | 2.778 | 0 | N/A | 0 | 0
2020-11-05 05:30 | 3.0409 | 0 | N/A | 0 | 0
2020-11-05 06:00 | 3.5047 | 0 | N/A | 0 | 0
2020-11-05 06:30 | 4.297 | 0 | N/A | 0 | 0
2020-11-05 07:00 | 4.7961 | 0 | N/A | 0 | 0
2020-11-05 07:30 | 5.6165 | 0 | N/A | 0 | 0
2020-11-05 08:00 | 5.668 | 0 | N/A | 0 | 0
2020-11-05 08:30 | 4.4241 | 0 | N/A | 0 | 0
2020-11-05 09:00 | 4.1121 | 0 | N/A | 0 | 0
2020-11-05 09:30 | 3.7878 | 0 | N/A | 0 | 0
2020-11-05 10:00 | 3.1322 | 0 | N/A | 0 | 0
2020-11-05 10:30 | 3.3988 | 0 | N/A | 0 | 0
2020-11-05 11:00 | 2.5515 | 0 | N/A | 0 | 0
2020-11-05 11:30 | 2.5405 | 0 | N/A | 0 | 0
2020-11-05 12:00 | 2.8316 | 0 | N/A | 0 | 0
2020-11-05 12:30 | 2.7284 | 0 | N/A | 0 | 0
2020-11-05 13:00 | 2.1212 | 0 | N/A | 0 | 0
2020-11-05 13:30 | 2.6004 | 0 | N/A | 0 | 0
2020-11-05 14:00 | 2.4007 | 0 | N/A | 0 | 0
2020-11-05 14:30 | 1.5092 | 0 | N/A | 0 | 0
2020-11-05 15:00 | 1.9683 | 0 | N/A | 0 | 0
2020-11-05 15:30 | 1.7344 | 0 | N/A | 0 | 0
2020-11-05 16:00 | 2.3201 | 0 | N/A | 0 | 0
2020-11-05 16:30 | 2.2761 | 0 | N/A | 0 | 0
2020-11-05 17:00 | 3.0523 | 0 | N/A | 0 | 0
2020-11-05 17:30 | 3.0663 | 0 | N/A | 0 | 0
2020-11-05 18:00 | 3.6239 | 0 | N/A | 0 | 0
2020-11-05 18:30 | 4.3444 | 0 | N/A | 0 | 0
2020-11-05 19:00 | 4.9577 | 0 | N/A | 0 | 0
2020-11-05 19:30 | 5.4147 | 0 | N/A | 0 | 0
2020-11-05 20:00 | 5.6359 | 0 | N/A | 0 | 0
2020-11-05 20:30 | 5.8281 | 0 | N/A | 0 | 0
2020-11-05 21:00 | 5.9282 | 0 | N/A | 0 | 0
2020-11-05 21:30 | 5.6639 | 0 | N/A | 0 | 0
2020-11-05 22:00 | 5.3452 | 0 | N/A | 0 | 0
2020-11-05 22:30 | 5.5302 | 0 | N/A | 0 | 0
2020-11-05 23:00 | 5.492 | 0 | N/A | 0 | 0
2020-11-05 23:30 | 4.9457 | 0 | N/A | 0 | 0
2020-11-06 | 4.9703 | 0 | N/A | 0 | 0
2020-11-06 00:30 | 5.291 | 0 | N/A | 0 | 0
2020-11-06 01:00 | 5.7528 | 0 | N/A | 0 | 0
2020-11-06 01:30 | 4.9816 | 0 | N/A | 0 | 0
2020-11-06 02:00 | 4.0123 | 0 | N/A | 0 | 0
2020-11-06 02:30 | 3.8777 | 0 | N/A | 0 | 0
2020-11-06 03:00 | 3.5762 | 0 | N/A | 0 | 0
2020-11-06 03:30 | 3.1018 | 0 | N/A | 0 | 0
2020-11-06 04:00 | 2.9395 | 0 | N/A | 0 | 0
2020-11-06 04:30 | 2.8273 | 0 | N/A | 0 | 0
2020-11-06 05:00 | 2.8983 | 0 | N/A | 0 | 0
2020-11-06 05:30 | 3.1108 | 0 | N/A | 0 | 0
2020-11-06 06:00 | 3.3878 | 0 | N/A | 0 | 0
2020-11-06 06:30 | 4.1862 | 0 | N/A | 0 | 0
2020-11-06 07:00 | 5.0713 | 0 | N/A | 0 | 0
2020-11-06 07:30 | 6.0234 | 0 | N/A | 0 | 0
2020-11-06 08:00 | 6.1504 | 0 | N/A | 0 | 0
2020-11-06 08:30 | 5.0658 | 0 | N/A | 0 | 0
2020-11-06 09:00 | 4.7605 | 0 | N/A | 0 | 0
2020-11-06 09:30 | 4.6189 | 0 | N/A | 0 | 0
2020-11-06 10:00 | 4.4621 | 0 | N/A | 0 | 0
2020-11-06 10:30 | 4.1267 | 0 | N/A | 0 | 0
2020-11-06 11:00 | 3.712 | 0 | N/A | 0 | 0
2020-11-06 11:30 | 3.8841 | 0 | N/A | 0 | 0
2020-11-06 12:00 | 3.7669 | 0 | N/A | 0 | 0
2020-11-06 12:30 | 3.4354 | 0 | N/A | 0 | 0
2020-11-06 13:00 | 2.9834 | 0 | N/A | 0 | 0
2020-11-06 13:30 | 2.7969 | 0 | N/A | 0 | 0
2020-11-06 14:00 | 2.9006 | 0 | N/A | 0 | 0
2020-11-06 14:30 | 3.3402 | 0 | N/A | 0 | 0
2020-11-06 15:00 | 3.8234 | 0 | N/A | 0 | 0
2020-11-06 15:30 | 3.6767 | 0 | N/A | 0 | 0
2020-11-06 16:00 | 2.3597 | 0 | N/A | 0 | 0
2020-11-06 16:30 | 3.4398 | 0 | N/A | 0 | 0
2020-11-06 17:00 | 4.3743 | 0 | N/A | 0 | 0
2020-11-06 17:30 | 4.605 | 0 | N/A | 0 | 0
2020-11-06 18:00 | 5.1881 | 0 | N/A | 0 | 0
2020-11-06 18:30 | 5.3605 | 0 | N/A | 0 | 0
2020-11-06 19:00 | 5.7035 | 0 | N/A | 0 | 0
2020-11-06 19:30 | 5.8868 | 0 | N/A | 0 | 0
2020-11-06 20:00 | 5.9427 | 0 | N/A | 0 | 0
2020-11-06 20:30 | 5.9507 | 0 | N/A | 0 | 0
2020-11-06 21:00 | 5.863 | 0 | N/A | 0 | 0
2020-11-06 21:30 | 5.4802 | 0 | N/A | 0 | 0
2020-11-06 22:00 | 5.0787 | 0 | N/A | 0 | 0
2020-11-06 22:30 | 5.4015 | 0 | N/A | 0 | 0
2020-11-06 23:00 | 5.4984 | 0 | N/A | 0 | 0
2020-11-06 23:30 | 5.1071 | 0 | N/A | 0 | 0
2020-11-07 | 4.9829 | 0 | N/A | 0 | 0
2020-11-07 00:30 | 5.3517 | 0 | N/A | 0 | 0
2020-11-07 01:00 | 5.7446 | 0 | N/A | 0 | 0
2020-11-07 01:30 | 4.9054 | 0 | N/A | 0 | 0
2020-11-07 02:00 | 4.0701 | 0 | N/A | 0 | 0
2020-11-07 02:30 | 3.9502 | 0 | N/A | 0 | 0
2020-11-07 03:00 | 3.5642 | 0 | N/A | 0 | 0
2020-11-07 03:30 | 3.1568 | 0 | N/A | 0 | 0
2020-11-07 04:00 | 2.9604 | 0 | N/A | 0 | 0
2020-11-07 04:30 | 2.7932 | 0 | N/A | 0 | 0
2020-11-07 05:00 | 2.739 | 0 | N/A | 0 | 0
2020-11-07 05:30 | 2.7893 | 0 | N/A | 0 | 0
2020-11-07 06:00 | 2.9511 | 0 | N/A | 0 | 0
2020-11-07 06:30 | 3.2438 | 0 | N/A | 0 | 0
2020-11-07 07:00 | 3.6195 | 0 | N/A | 0 | 0
2020-11-07 07:30 | 3.8322 | 0 | N/A | 0 | 0
2020-11-07 08:00 | 3.9537 | 0 | N/A | 0 | 0
2020-11-07 08:30 | 3.4012 | 0 | N/A | 0 | 0
2020-11-07 09:00 | 3.0736 | 0 | N/A | 0 | 0
2020-11-07 09:30 | 3.0211 | 0 | N/A | 0 | 0
2020-11-07 10:00 | 3.1735 | 0 | N/A | 0 | 0
2020-11-07 10:30 | 3.2202 | 0 | N/A | 0 | 0
2020-11-07 11:00 | 2.6169 | 0 | N/A | 0 | 0
2020-11-07 11:30 | 2.1834 | 0 | N/A | 0 | 0
2020-11-07 12:00 | 1.8763 | 0 | N/A | 0 | 0
2020-11-07 12:30 | 1.4898 | 0 | N/A | 0 | 0
2020-11-07 13:00 | 1.2202 | 0 | N/A | 0 | 0
2020-11-07 13:30 | 0.90841 | 0 | N/A | 0 | 0
2020-11-07 14:00 | 0.84677 | 0 | N/A | 0 | 0
2020-11-07 14:30 | 0.68447 | 0 | N/A | 0 | 0
2020-11-07 15:00 | 0.32906 | 0 | N/A | 0 | 0
2020-11-07 15:30 | -0.31349 | 0 | N/A | 0 | 0
2020-11-07 16:00 | -0.36063 | 0 | N/A | 0 | 0
2020-11-07 16:30 | 0.41958 | 0 | N/A | 0 | 0
2020-11-07 17:00 | 0.71574 | 0 | N/A | 0 | 0
2020-11-07 17:30 | 1.3104 | 0 | N/A | 0 | 0
2020-11-07 18:00 | 2.4314 | 0 | N/A | 0 | 0
2020-11-07 18:30 | 3.247 | 0 | N/A | 0 | 0
2020-11-07 19:00 | 3.9799 | 0 | N/A | 0 | 0
2020-11-07 19:30 | 4.467 | 0 | N/A | 0 | 0
2020-11-07 20:00 | 4.8482 | 0 | N/A | 0 | 0
2020-11-07 20:30 | 5.0703 | 0 | N/A | 0 | 0
2020-11-07 21:00 | 5.3298 | 0 | N/A | 0 | 0
2020-11-07 21:30 | 5.2277 | 0 | N/A | 0 | 0
2020-11-07 22:00 | 4.8991 | 0 | N/A | 0 | 0
2020-11-07 22:30 | 5.3882 | 0 | N/A | 0 | 0
2020-11-07 23:00 | 5.4245 | 0 | N/A | 0 | 0
2020-11-07 23:30 | 5.1099 | 0 | N/A | 0 | 0
2020-11-08 | 5.0389 | 0 | N/A | 0 | 0
2020-11-08 00:30 | 5.2771 | 0 | N/A | 0 | 0
2020-11-08 01:00 | 5.6751 | 0 | N/A | 0 | 0
2020-11-08 01:30 | 4.9937 | 0 | N/A | 0 | 0
2020-11-08 02:00 | 4.2125 | 0 | N/A | 0 | 0
2020-11-08 02:30 | 4.1291 | 0 | N/A | 0 | 0
2020-11-08 03:00 | 3.7802 | 0 | N/A | 0 | 0
2020-11-08 03:30 | 3.2732 | 0 | N/A | 0 | 0
2020-11-08 04:00 | 2.9951 | 0 | N/A | 0 | 0
2020-11-08 04:30 | 2.765 | 0 | N/A | 0 | 0
2020-11-08 05:00 | 2.6584 | 0 | N/A | 0 | 0
2020-11-08 05:30 | 2.7417 | 0 | N/A | 0 | 0
2020-11-08 06:00 | 2.7594 | 0 | N/A | 0 | 0
2020-11-08 06:30 | 3.0409 | 0 | N/A | 0 | 0
2020-11-08 07:00 | 3.1352 | 0 | N/A | 0 | 0
2020-11-08 07:30 | 3.2666 | 0 | N/A | 0 | 0
2020-11-08 08:00 | 3.0829 | 0 | N/A | 0 | 0
2020-11-08 08:30 | 2.4782 | 0 | N/A | 0 | 0
2020-11-08 09:00 | 1.974 | 0 | N/A | 0 | 0
2020-11-08 09:30 | 1.4072 | 0 | N/A | 0 | 0
2020-11-08 10:00 | 0.81989 | 0 | N/A | 0 | 0
2020-11-08 10:30 | 0.43381 | 0 | N/A | 0 | 0
2020-11-08 11:00 | -0.33812 | 0 | N/A | 0 | 0
2020-11-08 11:30 | -0.41751 | 0 | N/A | 0 | 0
2020-11-08 12:00 | -0.55479 | 0 | N/A | 0 | 0
2020-11-08 12:30 | -0.72524 | 0 | N/A | 0 | 0
2020-11-08 13:00 | -0.84035 | 0 | N/A | 0 | 0
2020-11-08 13:30 | -0.91768 | 0 | N/A | 0 | 0
2020-11-08 14:00 | -1.0134 | 0 | N/A | 0 | 0
2020-11-08 14:30 | -1.0095 | 0 | N/A | 0 | 0
2020-11-08 15:00 | -0.91782 | 0 | N/A | 0 | 0
2020-11-08 15:30 | -0.79725 | 0 | N/A | 0 | 0
2020-11-08 16:00 | -0.46745 | 0 | N/A | 0 | 0
2020-11-08 16:30 | -0.22699 | 0 | N/A | 0 | 0
2020-11-08 17:00 | 0.45404 | 0 | N/A | 0 | 0
2020-11-08 17:30 | 1.3348 | 0 | N/A | 0 | 0
2020-11-08 18:00 | 2.2568 | 0 | N/A | 0 | 0
2020-11-08 18:30 | 3.0096 | 0 | N/A | 0 | 0
2020-11-08 19:00 | 3.6255 | 0 | N/A | 0 | 0
2020-11-08 19:30 | 3.9096 | 0 | N/A | 0 | 0
2020-11-08 20:00 | 4.0887 | 0 | N/A | 0 | 0
2020-11-08 20:30 | 4.0581 | 0 | N/A | 0 | 0
2020-11-08 21:00 | 4.1052 | 0 | N/A | 0 | 0
2020-11-08 21:30 | 4.0287 | 0 | N/A | 0 | 0
2020-11-08 22:00 | 3.7125 | 0 | N/A | 0 | 0
2020-11-08 22:30 | 3.9645 | 0 | N/A | 0 | 0
2020-11-08 23:00 | 4.1328 | 0 | N/A | 0 | 0
2020-11-08 23:30 | 3.902 | 0 | N/A | 0 | 0
2020-11-09 | 3.9157 | 0 | N/A | 0 | 0
2020-11-09 00:30 | 4.2554 | 0 | N/A | 0 | 0
2020-11-09 01:00 | 4.8022 | 0 | N/A | 0 | 0
2020-11-09 01:30 | 4.1521 | 0 | N/A | 0 | 0
2020-11-09 02:00 | 3.4725 | 0 | N/A | 0 | 0
2020-11-09 02:30 | 3.4513 | 0 | N/A | 0 | 0
2020-11-09 03:00 | 3.1325 | 0 | N/A | 0 | 0
2020-11-09 03:30 | 2.672 | 0 | N/A | 0 | 0
2020-11-09 04:00 | 2.4575 | 0 | N/A | 0 | 0
2020-11-09 04:30 | 2.2779 | 0 | N/A | 0 | 0
2020-11-09 05:00 | 2.2305 | 0 | N/A | 0 | 0
2020-11-09 05:30 | 2.4613 | 0 | N/A | 0 | 0
2020-11-09 06:00 | 2.7641 | 0 | N/A | 0 | 0
2020-11-09 06:30 | 3.359 | 0 | N/A | 0 | 0
2020-11-09 07:00 | 3.8381 | 0 | N/A | 0 | 0
2020-11-09 07:30 | 4.5394 | 0 | N/A | 0 | 0
2020-11-09 08:00 | 4.46 | 0 | N/A | 0 | 0
2020-11-09 08:30 | 3.288 | 0 | N/A | 0 | 0
2020-11-09 09:00 | 2.5761 | 0 | N/A | 0 | 0
2020-11-09 09:30 | 1.7012 | 0 | N/A | 0 | 0
2020-11-09 10:00 | 0.82003 | 0 | N/A | 0 | 0
2020-11-09 10:30 | 0.32092 | 0 | N/A | 0 | 0
2020-11-09 11:00 | 0.35593 | 0 | N/A | 0 | 0
2020-11-09 11:30 | 0.38703 | 0 | N/A | 0 | 0
2020-11-09 12:00 | -0.41485 | 0 | N/A | 0 | 0
2020-11-09 12:30 | -0.44258 | 0 | N/A | 0 | 0
2020-11-09 13:00 | -0.4682 | 0 | N/A | 0 | 0
2020-11-09 13:30 | -0.54181 | 0 | N/A | 0 | 0
2020-11-09 14:00 | -0.50334 | 0 | N/A | 0 | 0
2020-11-09 14:30 | -0.48718 | 0 | N/A | 0 | 0
2020-11-09 15:00 | -0.44453 | 0 | N/A | 0 | 0
2020-11-09 15:30 | -0.39702 | 0 | N/A | 0 | 0
2020-11-09 16:00 | 0.33415 | 0 | N/A | 0 | 0
2020-11-09 16:30 | 0.6654 | 0 | N/A | 0 | 0
2020-11-09 17:00 | 1.1567 | 0 | N/A | 0 | 0
2020-11-09 17:30 | 2.6233 | 0 | N/A | 0 | 0
2020-11-09 18:00 | 3.7942 | 0 | N/A | 0 | 0
2020-11-09 18:30 | 3.9115 | 0 | N/A | 0 | 0
2020-11-09 19:00 | 3.8852 | 0 | N/A | 0 | 0
2020-11-09 19:30 | 4.0473 | 0 | N/A | 0 | 0
2020-11-09 20:00 | 4.2548 | 0 | N/A | 0 | 0
2020-11-09 20:30 | 4.2505 | 0 | N/A | 0 | 0
2020-11-09 21:00 | 4.1927 | 0 | N/A | 0 | 0
2020-11-09 21:30 | 3.9433 | 0 | N/A | 0 | 0
2020-11-09 22:00 | 3.601 | 0 | N/A | 0 | 0
2020-11-09 22:30 | 3.9252 | 0 | N/A | 0 | 0
2020-11-09 23:00 | 4.0681 | 0 | N/A | 0 | 0
2020-11-09 23:30 | 3.8674 | 0 | N/A | 0 | 0
2020-11-10 | 3.9477 | 0 | N/A | 0 | 0
2020-11-10 00:30 | 4.29 | 0 | N/A | 0 | 0
2020-11-10 01:00 | 4.6282 | 0 | N/A | 0 | 0
2020-11-10 01:30 | 3.7967 | 0 | N/A | 0 | 0
2020-11-10 02:00 | 3.0996 | 0 | N/A | 0 | 0
2020-11-10 02:30 | 3.0783 | 0 | N/A | 0 | 0
2020-11-10 03:00 | 2.6596 | 0 | N/A | 0 | 0
2020-11-10 03:30 | 2.3817 | 0 | N/A | 0 | 0
2020-11-10 04:00 | 2.2015 | 0 | N/A | 0 | 0
2020-11-10 04:30 | 2.1063 | 0 | N/A | 0 | 0
2020-11-10 05:00 | 2.1388 | 0 | N/A | 0 | 0
2020-11-10 05:30 | 2.2786 | 0 | N/A | 0 | 0
2020-11-10 06:00 | 2.5168 | 0 | N/A | 0 | 0
2020-11-10 06:30 | 2.9564 | 0 | N/A | 0 | 0
2020-11-10 07:00 | 3.1947 | 0 | N/A | 0 | 0
2020-11-10 07:30 | 4.0101 | 0 | N/A | 0 | 0
2020-11-10 08:00 | 3.8034 | 0 | N/A | 0 | 0
2020-11-10 08:30 | 2.9321 | 0 | N/A | 0 | 0
2020-11-10 09:00 | 2.1519 | 0 | N/A | 0 | 0
2020-11-10 09:30 | 1.5344 | 0 | N/A | 0 | 0
2020-11-10 10:00 | 0.95632 | 0 | N/A | 0 | 0
2020-11-10 10:30 | 0.66145 | 0 | N/A | 0 | 0
2020-11-10 11:00 | 0.53259 | 0 | N/A | 0 | 0
2020-11-10 11:30 | 0.48677 | 0 | N/A | 0 | 0
2020-11-10 12:00 | 0.55415 | 0 | N/A | 0 | 0
2020-11-10 12:30 | 0.60828 | 0 | N/A | 0 | 0
2020-11-10 13:00 | 0.59076 | 0 | N/A | 0 | 0
2020-11-10 13:30 | 0.59409 | 0 | N/A | 0 | 0
2020-11-10 14:00 | 0.64827 | 0 | N/A | 0 | 0
2020-11-10 14:30 | 0.72029 | 0 | N/A | 0 | 0
2020-11-10 15:00 | 0.8886 | 0 | N/A | 0 | 0
2020-11-10 15:30 | 0.91327 | 0 | N/A | 0 | 0
2020-11-10 16:00 | 1.1763 | 0 | N/A | 0 | 0
2020-11-10 16:30 | 1.8078 | 0 | N/A | 0 | 0
2020-11-10 17:00 | 2.2624 | 0 | N/A | 0 | 0
2020-11-10 17:30 | 3.0616 | 0 | N/A | 0 | 0
2020-11-10 18:00 | 4.0623 | 0 | N/A | 0 | 0
2020-11-10 18:30 | 4.694 | 0 | N/A | 0 | 0
2020-11-10 19:00 | 5.1536 | 0 | N/A | 0 | 0
2020-11-10 19:30 | 5.3001 | 0 | N/A | 0 | 0
2020-11-10 20:00 | 5.2033 | 0 | N/A | 0 | 0
2020-11-10 20:30 | 5.02 | 0 | N/A | 0 | 0
2020-11-10 21:00 | 4.8833 | 0 | N/A | 0 | 0
2020-11-10 21:30 | 4.4241 | 0 | N/A | 0 | 0
2020-11-10 22:00 | 4.0787 | 0 | N/A | 0 | 0
2020-11-10 22:30 | 4.3647 | 0 | N/A | 0 | 0
2020-11-10 23:00 | 4.4963 | 0 | N/A | 0 | 0
2020-11-10 23:30 | 4.1015 | 0 | N/A | 0 | 0
2020-11-11 | 4.0628 | 0 | N/A | 0 | 0
2020-11-11 00:30 | 4.5721 | 0 | N/A | 0 | 0
2020-11-11 01:00 | 4.7242 | 0 | N/A | 0 | 0
2020-11-11 01:30 | 3.7115 | 0 | N/A | 0 | 0
2020-11-11 02:00 | 3.0661 | 0 | N/A | 0 | 0
2020-11-11 02:30 | 2.9942 | 0 | N/A | 0 | 0
2020-11-11 03:00 | 2.6932 | 0 | N/A | 0 | 0
2020-11-11 03:30 | 2.4594 | 0 | N/A | 0 | 0
2020-11-11 04:00 | 2.3214 | 0 | N/A | 0 | 0
2020-11-11 04:30 | 2.2392 | 0 | N/A | 0 | 0
2020-11-11 05:00 | 2.2944 | 0 | N/A | 0 | 0
2020-11-11 05:30 | 2.2991 | 0 | N/A | 0 | 0
2020-11-11 06:00 | 2.5495 | 0 | N/A | 0 | 0
2020-11-11 06:30 | 2.9704 | 0 | N/A | 0 | 0
2020-11-11 07:00 | 3.3314 | 0 | N/A | 0 | 0
2020-11-11 07:30 | 4.347 | 0 | N/A | 0 | 0
2020-11-11 08:00 | 4.6735 | 0 | N/A | 0 | 0
2020-11-11 08:30 | 4.2883 | 0 | N/A | 0 | 0
2020-11-11 09:00 | 4.4651 | 0 | N/A | 0 | 0
2020-11-11 09:30 | 4.1956 | 0 | N/A | 0 | 0
2020-11-11 10:00 | 3.7978 | 0 | N/A | 0 | 0
2020-11-11 10:30 | 3.9516 | 0 | N/A | 0 | 0
2020-11-11 11:00 | 3.5265 | 0 | N/A | 0 | 0
2020-11-11 11:30 | 3.239 | 0 | N/A | 0 | 0
2020-11-11 12:00 | 3.6809 | 0 | N/A | 0 | 0
2020-11-11 12:30 | 3.4251 | 0 | N/A | 0 | 0
2020-11-11 13:00 | 3.9967 | 0 | N/A | 0 | 0
2020-11-11 13:30 | 4.33 | 0 | N/A | 0 | 0
2020-11-11 14:00 | 4.3413 | 0 | N/A | 0 | 0
2020-11-11 14:30 | 4.5178 | 0 | N/A | 0 | 0
2020-11-11 15:00 | 4.4533 | 0 | N/A | 0 | 0
2020-11-11 15:30 | 4.3293 | 0 | N/A | 0 | 0
2020-11-11 16:00 | 4.4055 | 0 | N/A | 0 | 0
2020-11-11 16:30 | 4.3046 | 0 | N/A | 0 | 0
2020-11-11 17:00 | 4.4139 | 0 | N/A | 0 | 0
2020-11-11 17:30 | 4.2462 | 0 | N/A | 0 | 0
2020-11-11 18:00 | 5.1566 | 0 | N/A | 0 | 0
2020-11-11 18:30 | 5.1171 | 0 | N/A | 0 | 0
2020-11-11 19:00 | 4.2921 | 0 | N/A | 0 | 0
2020-11-11 19:30 | 4.2298 | 0 | N/A | 0 | 0
2020-11-11 20:00 | 4.6779 | 0 | N/A | 0 | 0
2020-11-11 20:30 | 4.7193 | 0 | N/A | 0 | 0
2020-11-11 21:00 | 4.5803 | 0 | N/A | 0 | 0
2020-11-11 21:30 | 4.2453 | 0 | N/A | 0 | 0
2020-11-11 22:00 | 3.884 | 0 | N/A | 0 | 0
2020-11-11 22:30 | 4.2153 | 0 | N/A | 0 | 0
2020-11-11 23:00 | 4.3838 | 0 | N/A | 0 | 0
2020-11-11 23:30 | 4.0124 | 0 | N/A | 0 | 0
2020-11-12 | 4.1254 | 0 | N/A | 0 | 0
2020-11-12 00:30 | 4.5903 | 0 | N/A | 0 | 0
2020-11-12 01:00 | 4.9696 | 0 | N/A | 0 | 0
2020-11-12 01:30 | 4.0927 | 0 | N/A | 0 | 0
2020-11-12 02:00 | 3.3165 | 0 | N/A | 0 | 0
2020-11-12 02:30 | 3.256 | 0 | N/A | 0 | 0
2020-11-12 03:00 | 2.9243 | 0 | N/A | 0 | 0
2020-11-12 03:30 | 2.5429 | 0 | N/A | 0 | 0
2020-11-12 04:00 | 2.3117 | 0 | N/A | 0 | 0
2020-11-12 04:30 | 2.2317 | 0 | N/A | 0 | 0
2020-11-12 05:00 | 2.2694 | 0 | N/A | 0 | 0
2020-11-12 05:30 | 2.3916 | 0 | N/A | 0 | 0
2020-11-12 06:00 | 2.6762 | 0 | N/A | 0 | 0
2020-11-12 06:30 | 3.1751 | 0 | N/A | 0 | 0
2020-11-12 07:00 | 3.5442 | 0 | N/A | 0 | 0
2020-11-12 07:30 | 3.9872 | 0 | N/A | 0 | 0
2020-11-12 08:00 | 3.7531 | 0 | N/A | 0 | 0
2020-11-12 08:30 | 2.9083 | 0 | N/A | 0 | 0
2020-11-12 09:00 | 2.574 | 0 | N/A | 0 | 0
2020-11-12 09:30 | 2.5586 | 0 | N/A | 0 | 0
2020-11-12 10:00 | 2.587 | 0 | N/A | 0 | 0
2020-11-12 10:30 | 1.7608 | 0 | N/A | 0 | 0
2020-11-12 11:00 | 1.8134 | 0 | N/A | 0 | 0
2020-11-12 11:30 | 1.79 | 0 | N/A | 0 | 0
2020-11-12 12:00 | 1.5233 | 0 | N/A | 0 | 0
2020-11-12 12:30 | 1.8672 | 0 | N/A | 0 | 0
2020-11-12 13:00 | 2.4301 | 0 | N/A | 0 | 0
2020-11-12 13:30 | 2.1968 | 0 | N/A | 0 | 0
2020-11-12 14:00 | 2.2033 | 0 | N/A | 0 | 0
2020-11-12 14:30 | 2.0567 | 0 | N/A | 0 | 0
2020-11-12 15:00 | 1.8801 | 0 | N/A | 0 | 0
2020-11-12 15:30 | 2.5067 | 0 | N/A | 0 | 0
2020-11-12 16:00 | 2.8702 | 0 | N/A | 0 | 0
2020-11-12 16:30 | 3.3079 | 0 | N/A | 0 | 0
2020-11-12 17:00 | 3.2325 | 0 | N/A | 0 | 0
2020-11-12 17:30 | 3.9561 | 0 | N/A | 0 | 0
2020-11-12 18:00 | 4.5323 | 0 | N/A | 0 | 0
2020-11-12 18:30 | 4.5169 | 0 | N/A | 0 | 0
2020-11-12 19:00 | 4.6983 | 0 | N/A | 0 | 0
2020-11-12 19:30 | 4.6625 | 0 | N/A | 0 | 0
2020-11-12 20:00 | 4.8883 | 0 | N/A | 0 | 0
2020-11-12 20:30 | 4.8847 | 0 | N/A | 0 | 0
2020-11-12 21:00 | 4.8501 | 0 | N/A | 0 | 0
2020-11-12 21:30 | 4.6085 | 0 | N/A | 0 | 0
2020-11-12 22:00 | 4.286 | 0 | N/A | 0 | 0
2020-11-12 22:30 | 4.6057 | 0 | N/A | 0 | 0
2020-11-12 23:00 | 4.7471 | 0 | N/A | 0 | 0
2020-11-12 23:30 | 4.4504 | 0 | N/A | 0 | 0
2020-11-13 | 4.4887 | 0 | N/A | 0 | 0
2020-11-13 00:30 | 4.8455 | 0 | N/A | 0 | 0
2020-11-13 01:00 | 5.3094 | 0 | N/A | 0 | 0
2020-11-13 01:30 | 4.3342 | 0 | N/A | 0 | 0
2020-11-13 02:00 | 3.5181 | 0 | N/A | 0 | 0
2020-11-13 02:30 | 3.4151 | 0 | N/A | 0 | 0
2020-11-13 03:00 | 3.1406 | 0 | N/A | 0 | 0
2020-11-13 03:30 | 2.7109 | 0 | N/A | 0 | 0
2020-11-13 04:00 | 2.5302 | 0 | N/A | 0 | 0
2020-11-13 04:30 | 2.4473 | 0 | N/A | 0 | 0
2020-11-13 05:00 | 2.4863 | 0 | N/A | 0 | 0
2020-11-13 05:30 | 2.6095 | 0 | N/A | 0 | 0
2020-11-13 06:00 | 2.8834 | 0 | N/A | 0 | 0
2020-11-13 06:30 | 3.4628 | 0 | N/A | 0 | 0
2020-11-13 07:00 | 3.8922 | 0 | N/A | 0 | 0
2020-11-13 07:30 | 4.4568 | 0 | N/A | 0 | 0
2020-11-13 08:00 | 4.0697 | 0 | N/A | 0 | 0
2020-11-13 08:30 | 3.1571 | 0 | N/A | 0 | 0
2020-11-13 09:00 | 2.7149 | 0 | N/A | 0 | 0
2020-11-13 09:30 | 2.7173 | 0 | N/A | 0 | 0
2020-11-13 10:00 | 2.5771 | 0 | N/A | 0 | 0
2020-11-13 10:30 | 2.1906 | 0 | N/A | 0 | 0
2020-11-13 11:00 | 1.9467 | 0 | N/A | 0 | 0
2020-11-13 11:30 | 1.4 | 0 | N/A | 0 | 0
2020-11-13 12:00 | 0.66667 | 0 | N/A | 0 | 0
2020-11-13 12:30 | 1.0134 | 0 | N/A | 0 | 0
2020-11-13 13:00 | 0.99443 | 0 | N/A | 0 | 0
2020-11-13 13:30 | 1.1269 | 0 | N/A | 0 | 0
2020-11-13 14:00 | 1.1405 | 0 | N/A | 0 | 0
2020-11-13 14:30 | 1.8342 | 0 | N/A | 0 | 0
2020-11-13 15:00 | 2.2473 | 0 | N/A | 0 | 0
2020-11-13 15:30 | 2.3045 | 0 | N/A | 0 | 0
2020-11-13 16:00 | 2.0446 | 0 | N/A | 0 | 0
2020-11-13 16:30 | 1.9197 | 0 | N/A | 0 | 0
2020-11-13 17:00 | 2.5831 | 0 | N/A | 0 | 0
2020-11-13 17:30 | 2.9443 | 0 | N/A | 0 | 0
2020-11-13 18:00 | 3.7055 | 0 | N/A | 0 | 0
2020-11-13 18:30 | 4.056 | 0 | N/A | 0 | 0
2020-11-13 19:00 | 4.4397 | 0 | N/A | 0 | 0
2020-11-13 19:30 | 4.7128 | 0 | N/A | 0 | 0
2020-11-13 20:00 | 4.8541 | 0 | N/A | 0 | 0
2020-11-13 20:30 | 4.9701 | 0 | N/A | 0 | 0
2020-11-13 21:00 | 4.9947 | 0 | N/A | 0 | 0
2020-11-13 21:30 | 4.7652 | 0 | N/A | 0 | 0
2020-11-13 22:00 | 4.4812 | 0 | N/A | 0 | 0
2020-11-13 22:30 | 4.8403 | 0 | N/A | 0 | 0
2020-11-13 23:00 | 5.0281 | 0 | N/A | 0 | 0
2020-11-13 23:30 | 4.5421 | 0 | N/A | 0 | 0
2020-11-14 | 4.6398 | 0 | N/A | 0 | 0
2020-11-14 00:30 | 5.0762 | 0 | N/A | 0 | 0
2020-11-14 01:00 | 5.3498 | 0 | N/A | 0 | 0
2020-11-14 01:30 | 4.4158 | 0 | N/A | 0 | 0
2020-11-14 02:00 | 3.6045 | 0 | N/A | 0 | 0
2020-11-14 02:30 | 3.5112 | 0 | N/A | 0 | 0
2020-11-14 03:00 | 3.0754 | 0 | N/A | 0 | 0
2020-11-14 03:30 | 2.7224 | 0 | N/A | 0 | 0
2020-11-14 04:00 | 2.5976 | 0 | N/A | 0 | 0
2020-11-14 04:30 | 2.4086 | 0 | N/A | 0 | 0
2020-11-14 05:00 | 2.4096 | 0 | N/A | 0 | 0
2020-11-14 05:30 | 2.5495 | 0 | N/A | 0 | 0
2020-11-14 06:00 | 2.5903 | 0 | N/A | 0 | 0
2020-11-14 06:30 | 2.8239 | 0 | N/A | 0 | 0
2020-11-14 07:00 | 3.0626 | 0 | N/A | 0 | 0
2020-11-14 07:30 | 3.2675 | 0 | N/A | 0 | 0
2020-11-14 08:00 | 3.4557 | 0 | N/A | 0 | 0
2020-11-14 08:30 | 3.0778 | 0 | N/A | 0 | 0
2020-11-14 09:00 | 2.947 | 0 | N/A | 0 | 0
2020-11-14 09:30 | 2.8319 | 0 | N/A | 0 | 0
2020-11-14 10:00 | 2.4021 | 0 | N/A | 0 | 0
2020-11-14 10:30 | 2.1318 | 0 | N/A | 0 | 0
2020-11-14 11:00 | 1.3732 | 0 | N/A | 0 | 0
2020-11-14 11:30 | 1.2413 | 0 | N/A | 0 | 0
2020-11-14 12:00 | 0.74276 | 0 | N/A | 0 | 0
2020-11-14 12:30 | 0.81993 | 0 | N/A | 0 | 0
2020-11-14 13:00 | 0.69116 | 0 | N/A | 0 | 0
2020-11-14 13:30 | 0.5201 | 0 | N/A | 0 | 0
2020-11-14 14:00 | -0.361 | 0 | N/A | 0 | 0
2020-11-14 14:30 | -0.50567 | 0 | N/A | 0 | 0
2020-11-14 15:00 | -0.42065 | 0 | N/A | 0 | 0
2020-11-14 15:30 | -0.43403 | 0 | N/A | 0 | 0
2020-11-14 16:00 | -0.44876 | 0 | N/A | 0 | 0
2020-11-14 16:30 | -0.26373 | 0 | N/A | 0 | 0
2020-11-14 17:00 | 0.44322 | 0 | N/A | 0 | 0
2020-11-14 17:30 | 1.3219 | 0 | N/A | 0 | 0
2020-11-14 18:00 | 1.9672 | 0 | N/A | 0 | 0
2020-11-14 18:30 | 2.9487 | 0 | N/A | 0 | 0
2020-11-14 19:00 | 3.6479 | 0 | N/A | 0 | 0
2020-11-14 19:30 | 3.7054 | 0 | N/A | 0 | 0
2020-11-14 20:00 | 4.075 | 0 | N/A | 0 | 0
2020-11-14 20:30 | 4.0398 | 0 | N/A | 0 | 0
2020-11-14 21:00 | 4.0406 | 0 | N/A | 0 | 0
2020-11-14 21:30 | 3.9006 | 0 | N/A | 0 | 0
2020-11-14 22:00 | 3.6248 | 0 | N/A | 0 | 0
2020-11-14 22:30 | 4.1007 | 0 | N/A | 0 | 0
2020-11-14 23:00 | 4.381 | 0 | N/A | 0 | 0
2020-11-14 23:30 | 4.1352 | 0 | N/A | 0 | 0
2020-11-15 | 4.2879 | 0 | N/A | 0 | 0
2020-11-15 00:30 | 4.4744 | 0 | N/A | 0 | 0
2020-11-15 01:00 | 4.9356 | 0 | N/A | 0 | 0
2020-11-15 01:30 | 4.2101 | 0 | N/A | 0 | 0
2020-11-15 02:00 | 3.4092 | 0 | N/A | 0 | 0
2020-11-15 02:30 | 3.3197 | 0 | N/A | 0 | 0
2020-11-15 03:00 | 3.0044 | 0 | N/A | 0 | 0
2020-11-15 03:30 | 2.5641 | 0 | N/A | 0 | 0
2020-11-15 04:00 | 2.3003 | 0 | N/A | 0 | 0
2020-11-15 04:30 | 2.1223 | 0 | N/A | 0 | 0
2020-11-15 05:00 | 2.0858 | 0 | N/A | 0 | 0
2020-11-15 05:30 | 2.1091 | 0 | N/A | 0 | 0
2020-11-15 06:00 | 2.1476 | 0 | N/A | 0 | 0
2020-11-15 06:30 | 2.2705 | 0 | N/A | 0 | 0
2020-11-15 07:00 | 2.4887 | 0 | N/A | 0 | 0
2020-11-15 07:30 | 2.5111 | 0 | N/A | 0 | 0
2020-11-15 08:00 | 2.9023 | 0 | N/A | 0 | 0
2020-11-15 08:30 | 3.032 | 0 | N/A | 0 | 0
2020-11-15 09:00 | 1.7922 | 0 | N/A | 0 | 0
2020-11-15 09:30 | 1.3647 | 0 | N/A | 0 | 0
2020-11-15 10:00 | 1.2237 | 0 | N/A | 0 | 0
2020-11-15 10:30 | 1.6493 | 0 | N/A | 0 | 0
2020-11-15 11:00 | 1.4808 | 0 | N/A | 0 | 0
2020-11-15 11:30 | 0.3976 | 0 | N/A | 0 | 0
2020-11-15 12:00 | 0.24911 | 0 | N/A | 0 | 0
2020-11-15 12:30 | 0.56602 | 0 | N/A | 0 | 0
2020-11-15 13:00 | 1.1254 | 0 | N/A | 0 | 0
2020-11-15 13:30 | 1.7455 | 0 | N/A | 0 | 0
2020-11-15 14:00 | 1.1036 | 0 | N/A | 0 | 0
2020-11-15 14:30 | 0.72745 | 0 | N/A | 0 | 0
2020-11-15 15:00 | 1.4202 | 0 | N/A | 0 | 0
2020-11-15 15:30 | 2.3115 | 0 | N/A | 0 | 0
2020-11-15 16:00 | 2.3281 | 0 | N/A | 0 | 0
2020-11-15 16:30 | 1.6408 | 0 | N/A | 0 | 0
2020-11-15 17:00 | 1.0417 | 0 | N/A | 0 | 0
2020-11-15 17:30 | 1.566 | 0 | N/A | 0 | 0
2020-11-15 18:00 | 2.5509 | 0 | N/A | 0 | 0
2020-11-15 18:30 | 3.4266 | 0 | N/A | 0 | 0
2020-11-15 19:00 | 4.0997 | 0 | N/A | 0 | 0
2020-11-15 19:30 | 4.1439 | 0 | N/A | 0 | 0
2020-11-15 20:00 | 4.2194 | 0 | N/A | 0 | 0
2020-11-15 20:30 | 4.1531 | 0 | N/A | 0 | 0
2020-11-15 21:00 | 4.2064 | 0 | N/A | 0 | 0
2020-11-15 21:30 | 3.9294 | 0 | N/A | 0 | 0
2020-11-15 22:00 | 3.5928 | 0 | N/A | 0 | 0
2020-11-15 22:30 | 3.9974 | 0 | N/A | 0 | 0
2020-11-15 23:00 | 4.1547 | 0 | N/A | 0 | 0
2020-11-15 23:30 | 3.8257 | 0 | N/A | 0 | 0
2020-11-16 | 3.9557 | 0 | N/A | 0 | 0
2020-11-16 00:30 | 4.3309 | 0 | N/A | 0 | 0
2020-11-16 01:00 | 4.8586 | 0 | N/A | 0 | 0
2020-11-16 01:30 | 4.0014 | 0 | N/A | 0 | 0
2020-11-16 02:00 | 3.2971 | 0 | N/A | 0 | 0
2020-11-16 02:30 | 3.218 | 0 | N/A | 0 | 0
2020-11-16 03:00 | 2.8381 | 0 | N/A | 0 | 0
2020-11-16 03:30 | 2.468 | 0 | N/A | 0 | 0
2020-11-16 04:00 | 2.2497 | 0 | N/A | 0 | 0
2020-11-16 04:30 | 2.1561 | 0 | N/A | 0 | 0
2020-11-16 05:00 | 2.1778 | 0 | N/A | 0 | 0
2020-11-16 05:30 | 2.3471 | 0 | N/A | 0 | 0
2020-11-16 06:00 | 2.5788 | 0 | N/A | 0 | 0
2020-11-16 06:30 | 3.0989 | 0 | N/A | 0 | 0
2020-11-16 07:00 | 3.4406 | 0 | N/A | 0 | 0
2020-11-16 07:30 | 3.6964 | 0 | N/A | 0 | 0
2020-11-16 08:00 | 3.4591 | 0 | N/A | 0 | 0
2020-11-16 08:30 | 2.5468 | 0 | N/A | 0 | 0
2020-11-16 09:00 | 1.9107 | 0 | N/A | 0 | 0
2020-11-16 09:30 | 1.5847 | 0 | N/A | 0 | 0
2020-11-16 10:00 | 0.98338 | 0 | N/A | 0 | 0
2020-11-16 10:30 | 0.44668 | 0 | N/A | 0 | 0
2020-11-16 11:00 | 0.16087 | 0 | N/A | 0 | 0
2020-11-16 11:30 | 0.074907 | 0 | N/A | 0 | 0
2020-11-16 12:00 | -0.070079 | 0 | N/A | 0 | 0
2020-11-16 12:30 | 0.050772 | 0 | N/A | 0 | 0
2020-11-16 13:00 | -0.096148 | 0 | N/A | 0 | 0
2020-11-16 13:30 | -0.2594 | 0 | N/A | 0 | 0
2020-11-16 14:00 | -0.23113 | 0 | N/A | 0 | 0
2020-11-16 14:30 | -0.2138 | 0 | N/A | 0 | 0
2020-11-16 15:00 | -0.077316 | 0 | N/A | 0 | 0
2020-11-16 15:30 | -0.30696 | 0 | N/A | 0 | 0
2020-11-16 16:00 | -0.18812 | 0 | N/A | 0 | 0
2020-11-16 16:30 | 0.32128 | 0 | N/A | 0 | 0
2020-11-16 17:00 | 1.2534 | 0 | N/A | 0 | 0
2020-11-16 17:30 | 1.8139 | 0 | N/A | 0 | 0
2020-11-16 18:00 | 2.9938 | 0 | N/A | 0 | 0
2020-11-16 18:30 | 3.2997 | 0 | N/A | 0 | 0
2020-11-16 19:00 | 3.888 | 0 | N/A | 0 | 0
2020-11-16 19:30 | 4.1218 | 0 | N/A | 0 | 0
2020-11-16 20:00 | 4.3315 | 0 | N/A | 0 | 0
2020-11-16 20:30 | 4.4633 | 0 | N/A | 0 | 0
2020-11-16 21:00 | 4.4971 | 0 | N/A | 0 | 0
2020-11-16 21:30 | 4.2712 | 0 | N/A | 0 | 0
2020-11-16 22:00 | 3.9693 | 0 | N/A | 0 | 0
2020-11-16 22:30 | 4.2786 | 0 | N/A | 0 | 0
2020-11-16 23:00 | 4.4727 | 0 | N/A | 0 | 0
2020-11-16 23:30 | 4.2762 | 0 | N/A | 0 | 0
2020-11-17 | 4.3233 | 0 | N/A | 0 | 0
2020-11-17 00:30 | 4.5658 | 0 | N/A | 0 | 0
2020-11-17 01:00 | 5.0491 | 0 | N/A | 0 | 0
2020-11-17 01:30 | 4.2485 | 0 | N/A | 0 | 0
2020-11-17 02:00 | 3.5204 | 0 | N/A | 0 | 0
2020-11-17 02:30 | 3.5765 | 0 | N/A | 0 | 0
2020-11-17 03:00 | 3.3101 | 0 | N/A | 0 | 0
2020-11-17 03:30 | 2.9007 | 0 | N/A | 0 | 0
2020-11-17 04:00 | 2.6808 | 0 | N/A | 0 | 0
2020-11-17 04:30 | 2.5491 | 0 | N/A | 0 | 0
2020-11-17 05:00 | 2.5113 | 0 | N/A | 0 | 0
2020-11-17 05:30 | 2.775 | 0 | N/A | 0 | 0
2020-11-17 06:00 | 3.0606 | 0 | N/A | 0 | 0
2020-11-17 06:30 | 3.6743 | 0 | N/A | 0 | 0
2020-11-17 07:00 | 4.0173 | 0 | N/A | 0 | 0
2020-11-17 07:30 | 4.5407 | 0 | N/A | 0 | 0
2020-11-17 08:00 | 4.2385 | 0 | N/A | 0 | 0
2020-11-17 08:30 | 3.3295 | 0 | N/A | 0 | 0
2020-11-17 09:00 | 3.1555 | 0 | N/A | 0 | 0
2020-11-17 09:30 | 2.5805 | 0 | N/A | 0 | 0
2020-11-17 10:00 | 2.0922 | 0 | N/A | 0 | 0
2020-11-17 10:30 | 1.4074 | 0 | N/A | 0 | 0
2020-11-17 11:00 | 1.0867 | 0 | N/A | 0 | 0
2020-11-17 11:30 | 0.85667 | 0 | N/A | 0 | 0
2020-11-17 12:00 | 1.1 | 0 | N/A | 0 | 0
2020-11-17 12:30 | 1.2236 | 0 | N/A | 0 | 0
2020-11-17 13:00 | 1.0568 | 0 | N/A | 0 | 0
2020-11-17 13:30 | 0.94714 | 0 | N/A | 0 | 0
2020-11-17 14:00 | 0.98672 | 0 | N/A | 0 | 0
2020-11-17 14:30 | 1.24 | 0 | N/A | 0 | 0
2020-11-17 15:00 | 0.57048 | 0 | N/A | 0 | 0
2020-11-17 15:30 | 0.80017 | 0 | N/A | 0 | 0
2020-11-17 16:00 | 0.89349 | 0 | N/A | 0 | 0
2020-11-17 16:30 | 1.7159 | 0 | N/A | 0 | 0
2020-11-17 17:00 | 2.0416 | 0 | N/A | 0 | 0
2020-11-17 17:30 | 3.4084 | 0 | N/A | 0 | 0
2020-11-17 18:00 | 4.646 | 0 | N/A | 0 | 0
2020-11-17 18:30 | 4.2719 | 0 | N/A | 0 | 0
2020-11-17 19:00 | 3.7299 | 0 | N/A | 0 | 0
2020-11-17 19:30 | 3.9217 | 0 | N/A | 0 | 0
2020-11-17 20:00 | 4.0432 | 0 | N/A | 0 | 0
2020-11-17 20:30 | 4.1092 | 0 | N/A | 0 | 0
2020-11-17 21:00 | 4.2057 | 0 | N/A | 0 | 0
2020-11-17 21:30 | 4.0784 | 0 | N/A | 0 | 0
2020-11-17 22:00 | 3.8106 | 0 | N/A | 0 | 0
2020-11-17 22:30 | 4.2297 | 0 | N/A | 0 | 0
2020-11-17 23:00 | 4.4611 | 0 | N/A | 0 | 0
2020-11-17 23:30 | 4.1279 | 0 | N/A | 0 | 0
2020-11-18 | 4.1254 | 0 | N/A | 0 | 0
2020-11-18 00:30 | 4.6138 | 0 | N/A | 0 | 0
2020-11-18 01:00 | 4.9799 | 0 | N/A | 0 | 0
2020-11-18 01:30 | 4.0258 | 0 | N/A | 0 | 0
2020-11-18 02:00 | 3.2869 | 0 | N/A | 0 | 0
2020-11-18 02:30 | 3.2778 | 0 | N/A | 0 | 0
2020-11-18 03:00 | 2.9392 | 0 | N/A | 0 | 0
2020-11-18 03:30 | 2.6078 | 0 | N/A | 0 | 0
2020-11-18 04:00 | 2.4498 | 0 | N/A | 0 | 0
2020-11-18 04:30 | 2.3929 | 0 | N/A | 0 | 0
2020-11-18 05:00 | 2.3919 | 0 | N/A | 0 | 0
2020-11-18 05:30 | 2.592 | 0 | N/A | 0 | 0
2020-11-18 06:00 | 2.8951 | 0 | N/A | 0 | 0
2020-11-18 06:30 | 3.4641 | 0 | N/A | 0 | 0
2020-11-18 07:00 | 3.8268 | 0 | N/A | 0 | 0
2020-11-18 07:30 | 4.2774 | 0 | N/A | 0 | 0
2020-11-18 08:00 | 3.9115 | 0 | N/A | 0 | 0
2020-11-18 08:30 | 2.7858 | 0 | N/A | 0 | 0
2020-11-18 09:00 | 2.1643 | 0 | N/A | 0 | 0
2020-11-18 09:30 | 1.5601 | 0 | N/A | 0 | 0
2020-11-18 10:00 | 0.92 | 0 | N/A | 0 | 0
2020-11-18 10:30 | 0.43333 | 0 | N/A | 0 | 0
2020-11-18 11:00 | 0.42668 | 0 | N/A | 0 | 0
2020-11-18 11:30 | 0.41049 | 0 | N/A | 0 | 0
2020-11-18 12:00 | 0.27514 | 0 | N/A | 0 | 0
2020-11-18 12:30 | 0.19734 | 0 | N/A | 0 | 0
2020-11-18 13:00 | 0.31805 | 0 | N/A | 0 | 0
2020-11-18 13:30 | -0.49587 | 0 | N/A | 0 | 0
2020-11-18 14:00 | -0.56576 | 0 | N/A | 0 | 0
2020-11-18 14:30 | -0.55306 | 0 | N/A | 0 | 0
2020-11-18 15:00 | -0.44204 | 0 | N/A | 0 | 0
2020-11-18 15:30 | -0.25959 | 0 | N/A | 0 | 0
2020-11-18 16:00 | 0.14851 | 0 | N/A | 0 | 0
2020-11-18 16:30 | 0.52069 | 0 | N/A | 0 | 0
2020-11-18 17:00 | 1.3131 | 0 | N/A | 0 | 0
2020-11-18 17:30 | 2.3305 | 0 | N/A | 0 | 0
2020-11-18 18:00 | 3.4033 | 0 | N/A | 0 | 0
2020-11-18 18:30 | 4.3567 | 0 | N/A | 0 | 0
2020-11-18 19:00 | 4.4639 | 0 | N/A | 0 | 0
2020-11-18 19:30 | 4.5378 | 0 | N/A | 0 | 0
2020-11-18 20:00 | 4.4949 | 0 | N/A | 0 | 0
2020-11-18 20:30 | 4.4739 | 0 | N/A | 0 | 0
2020-11-18 21:00 | 4.392 | 0 | N/A | 0 | 0
2020-11-18 21:30 | 4.0741 | 0 | N/A | 0 | 0
2020-11-18 22:00 | 3.7105 | 0 | N/A | 0 | 0
2020-11-18 22:30 | 4.0563 | 0 | N/A | 0 | 0
2020-11-18 23:00 | 4.206 | 0 | N/A | 0 | 0
2020-11-18 23:30 | 3.9053 | 0 | N/A | 0 | 0
2020-11-19 | 3.9601 | 0 | N/A | 0 | 0
2020-11-19 00:30 | 4.3694 | 0 | N/A | 0 | 0
2020-11-19 01:00 | 4.6475 | 0 | N/A | 0 | 0
2020-11-19 01:30 | 3.6925 | 0 | N/A | 0 | 0
2020-11-19 02:00 | 3.023 | 0 | N/A | 0 | 0
2020-11-19 02:30 | 2.9882 | 0 | N/A | 0 | 0
2020-11-19 03:00 | 2.6384 | 0 | N/A | 0 | 0
2020-11-19 03:30 | 2.386 | 0 | N/A | 0 | 0
2020-11-19 04:00 | 2.2339 | 0 | N/A | 0 | 0
2020-11-19 04:30 | 2.1245 | 0 | N/A | 0 | 0
2020-11-19 05:00 | 2.162 | 0 | N/A | 0 | 0
2020-11-19 05:30 | 2.324 | 0 | N/A | 0 | 0
2020-11-19 06:00 | 2.6219 | 0 | N/A | 0 | 0
2020-11-19 06:30 | 3.0778 | 0 | N/A | 0 | 0
2020-11-19 07:00 | 3.3384 | 0 | N/A | 0 | 0
2020-11-19 07:30 | 3.83 | 0 | N/A | 0 | 0
2020-11-19 08:00 | 3.4947 | 0 | N/A | 0 | 0
2020-11-19 08:30 | 2.534 | 0 | N/A | 0 | 0
2020-11-19 09:00 | 1.8567 | 0 | N/A | 0 | 0
2020-11-19 09:30 | 1.4579 | 0 | N/A | 0 | 0
2020-11-19 10:00 | 0.87258 | 0 | N/A | 0 | 0
2020-11-19 10:30 | 0.77995 | 0 | N/A | 0 | 0
2020-11-19 11:00 | 0.91848 | 0 | N/A | 0 | 0
2020-11-19 11:30 | 0.76983 | 0 | N/A | 0 | 0
2020-11-19 12:00 | 1.1733 | 0 | N/A | 0 | 0
2020-11-19 12:30 | 0.84606 | 0 | N/A | 0 | 0
2020-11-19 13:00 | 0.36347 | 0 | N/A | 0 | 0
2020-11-19 13:30 | 0.45083 | 0 | N/A | 0 | 0
2020-11-19 14:00 | 0.63635 | 0 | N/A | 0 | 0
2020-11-19 14:30 | 0.70118 | 0 | N/A | 0 | 0
2020-11-19 15:00 | 0.91706 | 0 | N/A | 0 | 0
2020-11-19 15:30 | 0.96479 | 0 | N/A | 0 | 0
2020-11-19 16:00 | 1.6115 | 0 | N/A | 0 | 0
2020-11-19 16:30 | 2.8594 | 0 | N/A | 0 | 0
2020-11-19 17:00 | 2.9953 | 0 | N/A | 0 | 0
2020-11-19 17:30 | 3.3995 | 0 | N/A | 0 | 0
2020-11-19 18:00 | 4.6048 | 0 | N/A | 0 | 0
2020-11-19 18:30 | 5.1606 | 0 | N/A | 0 | 0
2020-11-19 19:00 | 5.7368 | 0 | N/A | 0 | 0
2020-11-19 19:30 | 5.9053 | 0 | N/A | 0 | 0
2020-11-19 20:00 | 5.441 | 0 | N/A | 0 | 0
2020-11-19 20:30 | 5.2402 | 0 | N/A | 0 | 0
2020-11-19 21:00 | 4.98 | 0 | N/A | 0 | 0
2020-11-19 21:30 | 4.7035 | 0 | N/A | 0 | 0
2020-11-19 22:00 | 4.2879 | 0 | N/A | 0 | 0
2020-11-19 22:30 | 4.491 | 0 | N/A | 0 | 0
2020-11-19 23:00 | 4.4974 | 0 | N/A | 0 | 0
2020-11-19 23:30 | 4.101 | 0 | N/A | 0 | 0
2020-11-20 | 4.1233 | 0 | N/A | 0 | 0
2020-11-20 00:30 | 4.5393 | 0 | N/A | 0 | 0
2020-11-20 01:00 | 4.6832 | 0 | N/A | 0 | 0
2020-11-20 01:30 | 3.7057 | 0 | N/A | 0 | 0
2020-11-20 02:00 | 3.0217 | 0 | N/A | 0 | 0
2020-11-20 02:30 | 3.0085 | 0 | N/A | 0 | 0
2020-11-20 03:00 | 2.7254 | 0 | N/A | 0 | 0
2020-11-20 03:30 | 2.813 | 0 | N/A | 0 | 0
2020-11-20 04:00 | 2.8587 | 0 | N/A | 0 | 0
2020-11-20 04:30 | 2.8449 | 0 | N/A | 0 | 0
2020-11-20 05:00 | 2.8741 | 0 | N/A | 0 | 0
2020-11-20 05:30 | 3.0287 | 0 | N/A | 0 | 0
2020-11-20 06:00 | 3.2098 | 0 | N/A | 0 | 0
2020-11-20 06:30 | 3.6591 | 0 | N/A | 0 | 0
2020-11-20 07:00 | 3.968 | 0 | N/A | 0 | 0
2020-11-20 07:30 | 4.4864 | 0 | N/A | 0 | 0
2020-11-20 08:00 | 4.3635 | 0 | N/A | 0 | 0
2020-11-20 08:30 | 3.4033 | 0 | N/A | 0 | 0
2020-11-20 09:00 | 2.2167 | 0 | N/A | 0 | 0
2020-11-20 09:30 | 1.8581 | 0 | N/A | 0 | 0
2020-11-20 10:00 | 1.1208 | 0 | N/A | 0 | 0
2020-11-20 10:30 | 0.49226 | 0 | N/A | 0 | 0
2020-11-20 11:00 | 0.3134 | 0 | N/A | 0 | 0
2020-11-20 11:30 | 0.35667 | 0 | N/A | 0 | 0
2020-11-20 12:00 | -0.3668 | 0 | N/A | 0 | 0
2020-11-20 12:30 | -0.37959 | 0 | N/A | 0 | 0
2020-11-20 13:00 | -0.474 | 0 | N/A | 0 | 0
2020-11-20 13:30 | -0.49035 | 0 | N/A | 0 | 0
2020-11-20 14:00 | -0.45256 | 0 | N/A | 0 | 0
2020-11-20 14:30 | -0.41 | 0 | N/A | 0 | 0
2020-11-20 15:00 | 0.38326 | 0 | N/A | 0 | 0
2020-11-20 15:30 | 0.39097 | 0 | N/A | 0 | 0
2020-11-20 16:00 | 0.63793 | 0 | N/A | 0 | 0
2020-11-20 16:30 | 0.57001 | 0 | N/A | 0 | 0
2020-11-20 17:00 | 1.0837 | 0 | N/A | 0 | 0
2020-11-20 17:30 | 1.5538 | 0 | N/A | 0 | 0
2020-11-20 18:00 | 2.338 | 0 | N/A | 0 | 0
2020-11-20 18:30 | 3.1409 | 0 | N/A | 0 | 0
2020-11-20 19:00 | 3.5838 | 0 | N/A | 0 | 0
2020-11-20 19:30 | 3.9834 | 0 | N/A | 0 | 0
2020-11-20 20:00 | 4.0551 | 0 | N/A | 0 | 0
2020-11-20 20:30 | 4.0234 | 0 | N/A | 0 | 0
2020-11-20 21:00 | 4.0491 | 0 | N/A | 0 | 0
2020-11-20 21:30 | 3.9185 | 0 | N/A | 0 | 0
2020-11-20 22:00 | 3.6583 | 0 | N/A | 0 | 0
2020-11-20 22:30 | 4.0576 | 0 | N/A | 0 | 0
2020-11-20 23:00 | 4.2628 | 0 | N/A | 0 | 0
2020-11-20 23:30 | 3.9268 | 0 | N/A | 0 | 0
2020-11-21 | 4.0788 | 0 | N/A | 0 | 0
2020-11-21 00:30 | 4.5087 | 0 | N/A | 0 | 0
2020-11-21 01:00 | 4.8658 | 0 | N/A | 0 | 0
2020-11-21 01:30 | 3.8393 | 0 | N/A | 0 | 0
2020-11-21 02:00 | 3.0699 | 0 | N/A | 0 | 0
2020-11-21 02:30 | 2.9891 | 0 | N/A | 0 | 0
2020-11-21 03:00 | 2.7081 | 0 | N/A | 0 | 0
2020-11-21 03:30 | 2.397 | 0 | N/A | 0 | 0
2020-11-21 04:00 | 2.2644 | 0 | N/A | 0 | 0
2020-11-21 04:30 | 2.1788 | 0 | N/A | 0 | 0
2020-11-21 05:00 | 2.2294 | 0 | N/A | 0 | 0
2020-11-21 05:30 | 2.2484 | 0 | N/A | 0 | 0
2020-11-21 06:00 | 2.374 | 0 | N/A | 0 | 0
2020-11-21 06:30 | 2.3865 | 0 | N/A | 0 | 0
2020-11-21 07:00 | 2.4582 | 0 | N/A | 0 | 0
2020-11-21 07:30 | 2.5564 | 0 | N/A | 0 | 0
2020-11-21 08:00 | 2.4336 | 0 | N/A | 0 | 0
2020-11-21 08:30 | 2.357 | 0 | N/A | 0 | 0
2020-11-21 09:00 | 1.7523 | 0 | N/A | 0 | 0
2020-11-21 09:30 | 1.5144 | 0 | N/A | 0 | 0
2020-11-21 10:00 | 1.3301 | 0 | N/A | 0 | 0
2020-11-21 10:30 | 1.5494 | 0 | N/A | 0 | 0
2020-11-21 11:00 | 1.2933 | 0 | N/A | 0 | 0
2020-11-21 11:30 | 0.84294 | 0 | N/A | 0 | 0
2020-11-21 12:00 | 1.1637 | 0 | N/A | 0 | 0
2020-11-21 12:30 | 1.55 | 0 | N/A | 0 | 0
2020-11-21 13:00 | 1.6216 | 0 | N/A | 0 | 0
2020-11-21 13:30 | 1.8624 | 0 | N/A | 0 | 0
2020-11-21 14:00 | 1.2965 | 0 | N/A | 0 | 0
2020-11-21 14:30 | 1.5518 | 0 | N/A | 0 | 0
2020-11-21 15:00 | 0.96779 | 0 | N/A | 0 | 0
2020-11-21 15:30 | 0.40012 | 0 | N/A | 0 | 0
2020-11-21 16:00 | 1.6971 | 0 | N/A | 0 | 0
2020-11-21 16:30 | 2.2475 | 0 | N/A | 0 | 0
2020-11-21 17:00 | 2.8438 | 0 | N/A | 0 | 0
2020-11-21 17:30 | 3.0977 | 0 | N/A | 0 | 0
2020-11-21 18:00 | 3.3009 | 0 | N/A | 0 | 0
2020-11-21 18:30 | 3.8887 | 0 | N/A | 0 | 0
2020-11-21 19:00 | 4.1653 | 0 | N/A | 0 | 0
2020-11-21 19:30 | 4.2473 | 0 | N/A | 0 | 0
2020-11-21 20:00 | 4.3557 | 0 | N/A | 0 | 0
2020-11-21 20:30 | 4.2195 | 0 | N/A | 0 | 0
2020-11-21 21:00 | 4.1517 | 0 | N/A | 0 | 0
2020-11-21 21:30 | 3.9949 | 0 | N/A | 0 | 0
2020-11-21 22:00 | 3.6236 | 0 | N/A | 0 | 0
2020-11-21 22:30 | 3.9755 | 0 | N/A | 0 | 0
2020-11-21 23:00 | 4.1734 | 0 | N/A | 0 | 0
2020-11-21 23:30 | 3.9355 | 0 | N/A | 0 | 0
2020-11-22 | 4.0138 | 0 | N/A | 0 | 0
2020-11-22 00:30 | 4.3504 | 0 | N/A | 0 | 0
2020-11-22 01:00 | 4.6451 | 0 | N/A | 0 | 0
2020-11-22 01:30 | 3.7302 | 0 | N/A | 0 | 0
2020-11-22 02:00 | 2.9267 | 0 | N/A | 0 | 0
2020-11-22 02:30 | 2.9542 | 0 | N/A | 0 | 0
2020-11-22 03:00 | 2.6149 | 0 | N/A | 0 | 0
2020-11-22 03:30 | 2.2686 | 0 | N/A | 0 | 0
2020-11-22 04:00 | 2.1035 | 0 | N/A | 0 | 0
2020-11-22 04:30 | 2.0367 | 0 | N/A | 0 | 0
2020-11-22 05:00 | 1.9312 | 0 | N/A | 0 | 0
2020-11-22 05:30 | 2.005 | 0 | N/A | 0 | 0
2020-11-22 06:00 | 2.1444 | 0 | N/A | 0 | 0
2020-11-22 06:30 | 2.2073 | 0 | N/A | 0 | 0
2020-11-22 07:00 | 2.3071 | 0 | N/A | 0 | 0
2020-11-22 07:30 | 2.5194 | 0 | N/A | 0 | 0
2020-11-22 08:00 | 2.7415 | 0 | N/A | 0 | 0
2020-11-22 08:30 | 2.4092 | 0 | N/A | 0 | 0
2020-11-22 09:00 | 2.5009 | 0 | N/A | 0 | 0
2020-11-22 09:30 | 3.2763 | 0 | N/A | 0 | 0
2020-11-22 10:00 | 3.6484 | 0 | N/A | 0 | 0
2020-11-22 10:30 | 3.6823 | 0 | N/A | 0 | 0
2020-11-22 11:00 | 3.0948 | 0 | N/A | 0 | 0
2020-11-22 11:30 | 2.5282 | 0 | N/A | 0 | 0
2020-11-22 12:00 | 0.84869 | 0 | N/A | 0 | 0
2020-11-22 12:30 | 1.2814 | 0 | N/A | 0 | 0
2020-11-22 13:00 | -0.053748 | 0 | N/A | 0 | 0
2020-11-22 13:30 | -0.22669 | 0 | N/A | 0 | 0
2020-11-22 14:00 | 1.5364 | 0 | N/A | 0 | 0
2020-11-22 14:30 | 3.4976 | 0 | N/A | 0 | 0
2020-11-22 15:00 | 1.7113 | 0 | N/A | 0 | 0
2020-11-22 15:30 | 1.9499 | 0 | N/A | 0 | 0
2020-11-22 16:00 | 3.2375 | 0 | N/A | 0 | 0
2020-11-22 16:30 | 3.5965 | 0 | N/A | 0 | 0
2020-11-22 17:00 | 4.5878 | 0 | N/A | 0 | 0
2020-11-22 17:30 | 5.3207 | 0 | N/A | 0 | 0
2020-11-22 18:00 | 5.5108 | 0 | N/A | 0 | 0
2020-11-22 18:30 | 4.6464 | 0 | N/A | 0 | 0
2020-11-22 19:00 | 4.3876 | 0 | N/A | 0 | 0
2020-11-22 19:30 | 4.3552 | 0 | N/A | 0 | 0
2020-11-22 20:00 | 4.2887 | 0 | N/A | 0 | 0
2020-11-22 20:30 | 4.1726 | 0 | N/A | 0 | 0
2020-11-22 21:00 | 4.0227 | 0 | N/A | 0 | 0
2020-11-22 21:30 | 3.775 | 0 | N/A | 0 | 0
2020-11-22 22:00 | 3.4912 | 0 | N/A | 0 | 0
2020-11-22 22:30 | 3.8832 | 0 | N/A | 0 | 0
2020-11-22 23:00 | 4.0887 | 0 | N/A | 0 | 0
2020-11-22 23:30 | 3.8158 | 0 | N/A | 0 | 0
2020-11-23 | 3.8775 | 0 | N/A | 0 | 0
2020-11-23 00:30 | 4.2408 | 0 | N/A | 0 | 0
2020-11-23 01:00 | 4.7424 | 0 | N/A | 0 | 0
2020-11-23 01:30 | 3.8398 | 0 | N/A | 0 | 0
2020-11-23 02:00 | 3.0391 | 0 | N/A | 0 | 0
2020-11-23 02:30 | 2.9987 | 0 | N/A | 0 | 0
2020-11-23 03:00 | 2.7268 | 0 | N/A | 0 | 0
2020-11-23 03:30 | 2.339 | 0 | N/A | 0 | 0
2020-11-23 04:00 | 2.1552 | 0 | N/A | 0 | 0
2020-11-23 04:30 | 2.1168 | 0 | N/A | 0 | 0
2020-11-23 05:00 | 2.0836 | 0 | N/A | 0 | 0
2020-11-23 05:30 | 2.3882 | 0 | N/A | 0 | 0
2020-11-23 06:00 | 2.7132 | 0 | N/A | 0 | 0
2020-11-23 06:30 | 3.1696 | 0 | N/A | 0 | 0
2020-11-23 07:00 | 3.5425 | 0 | N/A | 0 | 0
2020-11-23 07:30 | 3.9443 | 0 | N/A | 0 | 0
2020-11-23 08:00 | 4.3353 | 0 | N/A | 0 | 0
2020-11-23 08:30 | 3.611 | 0 | N/A | 0 | 0
2020-11-23 09:00 | 3.6982 | 0 | N/A | 0 | 0
2020-11-23 09:30 | 3.8028 | 0 | N/A | 0 | 0
2020-11-23 10:00 | 3.6556 | 0 | N/A | 0 | 0
2020-11-23 10:30 | 3.7944 | 0 | N/A | 0 | 0
2020-11-23 11:00 | 3.8885 | 0 | N/A | 0 | 0
2020-11-23 11:30 | 3.94 | 0 | N/A | 0 | 0
2020-11-23 12:00 | 3.5934 | 0 | N/A | 0 | 0
2020-11-23 12:30 | 2.9505 | 0 | N/A | 0 | 0
2020-11-23 13:00 | 2.9654 | 0 | N/A | 0 | 0
2020-11-23 13:30 | 2.6351 | 0 | N/A | 0 | 0
2020-11-23 14:00 | 2.42 | 0 | N/A | 0 | 0
2020-11-23 14:30 | 2.1541 | 0 | N/A | 0 | 0
2020-11-23 15:00 | 2.0034 | 0 | N/A | 0 | 0
2020-11-23 15:30 | 2.3278 | 0 | N/A | 0 | 0
2020-11-23 16:00 | 2.6153 | 0 | N/A | 0 | 0
2020-11-23 16:30 | 2.5181 | 0 | N/A | 0 | 0
2020-11-23 17:00 | 3.0067 | 0 | N/A | 0 | 0
2020-11-23 17:30 | 3.9718 | 0 | N/A | 0 | 0
2020-11-23 18:00 | 4.3699 | 0 | N/A | 0 | 0
2020-11-23 18:30 | 4.6905 | 0 | N/A | 0 | 0
2020-11-23 19:00 | 4.6888 | 0 | N/A | 0 | 0
2020-11-23 19:30 | 4.7179 | 0 | N/A | 0 | 0
2020-11-23 20:00 | 4.8289 | 0 | N/A | 0 | 0
2020-11-23 20:30 | 4.8731 | 0 | N/A | 0 | 0
2020-11-23 21:00 | 4.8416 | 0 | N/A | 0 | 0
2020-11-23 21:30 | 4.5265 | 0 | N/A | 0 | 0
2020-11-23 22:00 | 4.1869 | 0 | N/A | 0 | 0
2020-11-23 22:30 | 4.4868 | 0 | N/A | 0 | 0
2020-11-23 23:00 | 4.58 | 0 | N/A | 0 | 0
2020-11-23 23:30 | 4.2056 | 0 | N/A | 0 | 0
2020-11-24 | 4.2735 | 0 | N/A | 0 | 0
2020-11-24 00:30 | 4.8837 | 0 | N/A | 0 | 0
2020-11-24 01:00 | 5.2077 | 0 | N/A | 0 | 0
2020-11-24 01:30 | 4.2599 | 0 | N/A | 0 | 0
2020-11-24 02:00 | 3.4612 | 0 | N/A | 0 | 0
2020-11-24 02:30 | 3.3948 | 0 | N/A | 0 | 0
2020-11-24 03:00 | 2.9897 | 0 | N/A | 0 | 0
2020-11-24 03:30 | 2.6776 | 0 | N/A | 0 | 0
2020-11-24 04:00 | 2.446 | 0 | N/A | 0 | 0
2020-11-24 04:30 | 2.3691 | 0 | N/A | 0 | 0
2020-11-24 05:00 | 2.4096 | 0 | N/A | 0 | 0
2020-11-24 05:30 | 2.6584 | 0 | N/A | 0 | 0
2020-11-24 06:00 | 2.8548 | 0 | N/A | 0 | 0
2020-11-24 06:30 | 3.4535 | 0 | N/A | 0 | 0
2020-11-24 07:00 | 3.8797 | 0 | N/A | 0 | 0
2020-11-24 07:30 | 4.6749 | 0 | N/A | 0 | 0
2020-11-24 08:00 | 4.9334 | 0 | N/A | 0 | 0
2020-11-24 08:30 | 4.3133 | 0 | N/A | 0 | 0
2020-11-24 09:00 | 4.2939 | 0 | N/A | 0 | 0
2020-11-24 09:30 | 4.1714 | 0 | N/A | 0 | 0
2020-11-24 10:00 | 3.5776 | 0 | N/A | 0 | 0
2020-11-24 10:30 | 3.1557 | 0 | N/A | 0 | 0
2020-11-24 11:00 | 2.5602 | 0 | N/A | 0 | 0
2020-11-24 11:30 | 2.3452 | 0 | N/A | 0 | 0
2020-11-24 12:00 | 2.5533 | 0 | N/A | 0 | 0
2020-11-24 12:30 | 2.3286 | 0 | N/A | 0 | 0
2020-11-24 13:00 | 2.51 | 0 | N/A | 0 | 0
2020-11-24 13:30 | 1.6872 | 0 | N/A | 0 | 0
2020-11-24 14:00 | 1.1801 | 0 | N/A | 0 | 0
2020-11-24 14:30 | 0.26742 | 0 | N/A | 0 | 0
2020-11-24 15:00 | 1.3633 | 0 | N/A | 0 | 0
2020-11-24 15:30 | 1.9568 | 0 | N/A | 0 | 0
2020-11-24 16:00 | 2.586 | 0 | N/A | 0 | 0
2020-11-24 16:30 | 2.6542 | 0 | N/A | 0 | 0
2020-11-24 17:00 | 2.8404 | 0 | N/A | 0 | 0
2020-11-24 17:30 | 3.6166 | 0 | N/A | 0 | 0
2020-11-24 18:00 | 4.6077 | 0 | N/A | 0 | 0
2020-11-24 18:30 | 4.7568 | 0 | N/A | 0 | 0
2020-11-24 19:00 | 4.7166 | 0 | N/A | 0 | 0
2020-11-24 19:30 | 4.4933 | 0 | N/A | 0 | 0
2020-11-24 20:00 | 4.4861 | 0 | N/A | 0 | 0
2020-11-24 20:30 | 4.5814 | 0 | N/A | 0 | 0
2020-11-24 21:00 | 4.4676 | 0 | N/A | 0 | 0
2020-11-24 21:30 | 4.2543 | 0 | N/A | 0 | 0
2020-11-24 22:00 | 4.1689 | 0 | N/A | 0 | 0
2020-11-24 22:30 | 5.5342 | 0 | N/A | 0 | 0
2020-11-24 23:00 | 5.7231 | 0 | N/A | 0 | 0
2020-11-24 23:30 | 5.1802 | 0 | N/A | 0 | 0
2020-11-25 | 4.0291 | 0 | N/A | 0 | 0
2020-11-25 00:30 | 4.5513 | 0 | N/A | 0 | 0
2020-11-25 01:00 | 4.7649 | 0 | N/A | 0 | 0
2020-11-25 01:30 | 3.929 | 0 | N/A | 0 | 0
2020-11-25 02:00 | 3.1309 | 0 | N/A | 0 | 0
2020-11-25 02:30 | 3.0915 | 0 | N/A | 0 | 0
2020-11-25 03:00 | 2.7008 | 0 | N/A | 0 | 0
2020-11-25 03:30 | 2.3439 | 0 | N/A | 0 | 0
2020-11-25 04:00 | 2.2222 | 0 | N/A | 0 | 0
2020-11-25 04:30 | 2.2052 | 0 | N/A | 0 | 0
2020-11-25 05:00 | 2.1609 | 0 | N/A | 0 | 0
2020-11-25 05:30 | 2.3214 | 0 | N/A | 0 | 0
2020-11-25 06:00 | 2.6458 | 0 | N/A | 0 | 0
2020-11-25 06:30 | 3.2093 | 0 | N/A | 0 | 0
2020-11-25 07:00 | 3.567 | 0 | N/A | 0 | 0
2020-11-25 07:30 | 4.092 | 0 | N/A | 0 | 0
2020-11-25 08:00 | 3.7113 | 0 | N/A | 0 | 0
2020-11-25 08:30 | 2.6248 | 0 | N/A | 0 | 0
2020-11-25 09:00 | 1.87 | 0 | N/A | 0 | 0
2020-11-25 09:30 | 1.22 | 0 | N/A | 0 | 0
2020-11-25 10:00 | 0.57333 | 0 | N/A | 0 | 0
2020-11-25 10:30 | 0.18248 | 0 | N/A | 0 | 0
2020-11-25 11:00 | -0.14885 | 0 | N/A | 0 | 0
2020-11-25 11:30 | -0.26874 | 0 | N/A | 0 | 0
2020-11-25 12:00 | -0.44274 | 0 | N/A | 0 | 0
2020-11-25 12:30 | -0.45436 | 0 | N/A | 0 | 0
2020-11-25 13:00 | -0.5051 | 0 | N/A | 0 | 0
2020-11-25 13:30 | -0.5696 | 0 | N/A | 0 | 0
2020-11-25 14:00 | -0.44402 | 0 | N/A | 0 | 0
2020-11-25 14:30 | 0.93291 | 0 | N/A | 0 | 0
2020-11-25 15:00 | 1.1178 | 0 | N/A | 0 | 0
2020-11-25 15:30 | 1.209 | 0 | N/A | 0 | 0
2020-11-25 16:00 | 1.2381 | 0 | N/A | 0 | 0
2020-11-25 16:30 | 0.58257 | 0 | N/A | 0 | 0
2020-11-25 17:00 | 1.3074 | 0 | N/A | 0 | 0
2020-11-25 17:30 | 2.2333 | 0 | N/A | 0 | 0
2020-11-25 18:00 | 3.3136 | 0 | N/A | 0 | 0
2020-11-25 18:30 | 3.9967 | 0 | N/A | 0 | 0
2020-11-25 19:00 | 4.43 | 0 | N/A | 0 | 0
2020-11-25 19:30 | 4.6333 | 0 | N/A | 0 | 0
2020-11-25 20:00 | 4.6939 | 0 | N/A | 0 | 0
2020-11-25 20:30 | 4.6213 | 0 | N/A | 0 | 0
2020-11-25 21:00 | 4.5052 | 0 | N/A | 0 | 0
2020-11-25 21:30 | 4.224 | 0 | N/A | 0 | 0
2020-11-25 22:00 | 3.9016 | 0 | N/A | 0 | 0
2020-11-25 22:30 | 4.2357 | 0 | N/A | 0 | 0
2020-11-25 23:00 | 4.2423 | 0 | N/A | 0 | 0
2020-11-25 23:30 | 3.8402 | 0 | N/A | 0 | 0
2020-11-26 | 3.8924 | 0 | N/A | 0 | 0
2020-11-26 00:30 | 4.2716 | 0 | N/A | 0 | 0
2020-11-26 01:00 | 4.6874 | 0 | N/A | 0 | 0
2020-11-26 01:30 | 3.6341 | 0 | N/A | 0 | 0
2020-11-26 02:00 | 2.8503 | 0 | N/A | 0 | 0
2020-11-26 02:30 | 2.8408 | 0 | N/A | 0 | 0
2020-11-26 03:00 | 2.6002 | 0 | N/A | 0 | 0
2020-11-26 03:30 | 2.3414 | 0 | N/A | 0 | 0
2020-11-26 04:00 | 2.2124 | 0 | N/A | 0 | 0
2020-11-26 04:30 | 2.1123 | 0 | N/A | 0 | 0
2020-11-26 05:00 | 2.1874 | 0 | N/A | 0 | 0
2020-11-26 05:30 | 2.3562 | 0 | N/A | 0 | 0
2020-11-26 06:00 | 2.5264 | 0 | N/A | 0 | 0
2020-11-26 06:30 | 2.9895 | 0 | N/A | 0 | 0
2020-11-26 07:00 | 3.3217 | 0 | N/A | 0 | 0
2020-11-26 07:30 | 3.8397 | 0 | N/A | 0 | 0
2020-11-26 08:00 | 3.8852 | 0 | N/A | 0 | 0
2020-11-26 08:30 | 3.2576 | 0 | N/A | 0 | 0
2020-11-26 09:00 | 2.7136 | 0 | N/A | 0 | 0
2020-11-26 09:30 | 2.9807 | 0 | N/A | 0 | 0
2020-11-26 10:00 | 2.8445 | 0 | N/A | 0 | 0
2020-11-26 10:30 | 2.3734 | 0 | N/A | 0 | 0
2020-11-26 11:00 | 1.7273 | 0 | N/A | 0 | 0
2020-11-26 11:30 | 0.73686 | 0 | N/A | 0 | 0
2020-11-26 12:00 | 0.17308 | 0 | N/A | 0 | 0
2020-11-26 12:30 | -0.16398 | 0 | N/A | 0 | 0
2020-11-26 13:00 | -0.23646 | 0 | N/A | 0 | 0
2020-11-26 13:30 | -0.27346 | 0 | N/A | 0 | 0
2020-11-26 14:00 | -0.52664 | 0 | N/A | 0 | 0
2020-11-26 14:30 | -0.63052 | 0 | N/A | 0 | 0
2020-11-26 15:00 | -0.38737 | 0 | N/A | 0 | 0
2020-11-26 15:30 | -0.31098 | 0 | N/A | 0 | 0
2020-11-26 16:00 | -0.20989 | 0 | N/A | 0 | 0
2020-11-26 16:30 | 0.09 | 0 | N/A | 0 | 0
2020-11-26 17:00 | 0.60466 | 0 | N/A | 0 | 0
2020-11-26 17:30 | 1.4046 | 0 | N/A | 0 | 0
2020-11-26 18:00 | 2.293 | 0 | N/A | 0 | 0
2020-11-26 18:30 | 3.1108 | 0 | N/A | 0 | 0
2020-11-26 19:00 | 3.6413 | 0 | N/A | 0 | 0
2020-11-26 19:30 | 3.8918 | 0 | N/A | 0 | 0
2020-11-26 20:00 | 4.1089 | 0 | N/A | 0 | 0
2020-11-26 20:30 | 4.2244 | 0 | N/A | 0 | 0
2020-11-26 21:00 | 4.2773 | 0 | N/A | 0 | 0
2020-11-26 21:30 | 4.1596 | 0 | N/A | 0 | 0
2020-11-26 22:00 | 3.9612 | 0 | N/A | 0 | 0
2020-11-26 22:30 | 4.1974 | 0 | N/A | 0 | 0
2020-11-26 23:00 | 4.2661 | 0 | N/A | 0 | 0
2020-11-26 23:30 | 4.0376 | 0 | N/A | 0 | 0
2020-11-27 | 4.057 | 0 | N/A | 0 | 0
2020-11-27 00:30 | 4.4996 | 0 | N/A | 0 | 0
2020-11-27 01:00 | 4.8295 | 0 | N/A | 0 | 0
2020-11-27 01:30 | 3.9727 | 0 | N/A | 0 | 0
2020-11-27 02:00 | 3.1922 | 0 | N/A | 0 | 0
2020-11-27 02:30 | 3.1654 | 0 | N/A | 0 | 0
2020-11-27 03:00 | 2.8354 | 0 | N/A | 0 | 0
2020-11-27 03:30 | 2.5421 | 0 | N/A | 0 | 0
2020-11-27 04:00 | 2.3796 | 0 | N/A | 0 | 0
2020-11-27 04:30 | 2.2836 | 0 | N/A | 0 | 0
2020-11-27 05:00 | 2.3326 | 0 | N/A | 0 | 0
2020-11-27 05:30 | 2.4579 | 0 | N/A | 0 | 0
2020-11-27 06:00 | 2.7126 | 0 | N/A | 0 | 0
2020-11-27 06:30 | 3.2236 | 0 | N/A | 0 | 0
2020-11-27 07:00 | 3.5231 | 0 | N/A | 0 | 0
2020-11-27 07:30 | 3.9649 | 0 | N/A | 0 | 0
2020-11-27 08:00 | 3.5403 | 0 | N/A | 0 | 0
2020-11-27 08:30 | 2.469 | 0 | N/A | 0 | 0
2020-11-27 09:00 | 1.8433 | 0 | N/A | 0 | 0
2020-11-27 09:30 | 1.18 | 0 | N/A | 0 | 0
2020-11-27 10:00 | 0.57001 | 0 | N/A | 0 | 0
2020-11-27 10:30 | 0.013333 | 0 | N/A | 0 | 0
2020-11-27 11:00 | -0.15811 | 0 | N/A | 0 | 0
2020-11-27 11:30 | -0.33042 | 0 | N/A | 0 | 0
2020-11-27 12:00 | -0.41189 | 0 | N/A | 0 | 0
2020-11-27 12:30 | -0.50695 | 0 | N/A | 0 | 0
2020-11-27 13:00 | -0.4911 | 0 | N/A | 0 | 0
2020-11-27 13:30 | -0.34649 | 0 | N/A | 0 | 0
2020-11-27 14:00 | -0.31064 | 0 | N/A | 0 | 0
2020-11-27 14:30 | 0.379 | 0 | N/A | 0 | 0
2020-11-27 15:00 | 0.73619 | 0 | N/A | 0 | 0
2020-11-27 15:30 | 0.77167 | 0 | N/A | 0 | 0
2020-11-27 16:00 | 1.3676 | 0 | N/A | 0 | 0
2020-11-27 16:30 | 2.3696 | 0 | N/A | 0 | 0
2020-11-27 17:00 | 3.3281 | 0 | N/A | 0 | 0
2020-11-27 17:30 | 3.6106 | 0 | N/A | 0 | 0
2020-11-27 18:00 | 4.473 | 0 | N/A | 0 | 0
2020-11-27 18:30 | 5.5016 | 0 | N/A | 0 | 0
2020-11-27 19:00 | 5.6589 | 0 | N/A | 0 | 0
2020-11-27 19:30 | 5.5685 | 0 | N/A | 0 | 0
2020-11-27 20:00 | 5.4367 | 0 | N/A | 0 | 0
2020-11-27 20:30 | 5.2501 | 0 | N/A | 0 | 0
2020-11-27 21:00 | 5.0967 | 0 | N/A | 0 | 0
2020-11-27 21:30 | 4.7234 | 0 | N/A | 0 | 0
2020-11-27 22:00 | 4.3472 | 0 | N/A | 0 | 0
2020-11-27 22:30 | 4.5738 | 0 | N/A | 0 | 0
2020-11-27 23:00 | 4.6007 | 0 | N/A | 0 | 0
2020-11-27 23:30 | 4.1934 | 0 | N/A | 0 | 0
2020-11-28 | 4.1637 | 0 | N/A | 0 | 0
2020-11-28 00:30 | 4.6052 | 0 | N/A | 0 | 0
2020-11-28 01:00 | 4.7765 | 0 | N/A | 0 | 0
2020-11-28 01:30 | 3.7267 | 0 | N/A | 0 | 0
2020-11-28 02:00 | 3.0167 | 0 | N/A | 0 | 0
2020-11-28 02:30 | 3.0349 | 0 | N/A | 0 | 0
2020-11-28 03:00 | 2.7238 | 0 | N/A | 0 | 0
2020-11-28 03:30 | 2.3924 | 0 | N/A | 0 | 0
2020-11-28 04:00 | 2.3298 | 0 | N/A | 0 | 0
2020-11-28 04:30 | 2.2184 | 0 | N/A | 0 | 0
2020-11-28 05:00 | 2.1489 | 0 | N/A | 0 | 0
2020-11-28 05:30 | 2.1854 | 0 | N/A | 0 | 0
2020-11-28 06:00 | 2.2763 | 0 | N/A | 0 | 0
2020-11-28 06:30 | 2.3971 | 0 | N/A | 0 | 0
2020-11-28 07:00 | 2.4675 | 0 | N/A | 0 | 0
2020-11-28 07:30 | 2.5621 | 0 | N/A | 0 | 0
2020-11-28 08:00 | 2.4757 | 0 | N/A | 0 | 0
2020-11-28 08:30 | 2.1621 | 0 | N/A | 0 | 0
2020-11-28 09:00 | 2.7702 | 0 | N/A | 0 | 0
2020-11-28 09:30 | 2.6736 | 0 | N/A | 0 | 0
2020-11-28 10:00 | 2.7836 | 0 | N/A | 0 | 0
2020-11-28 10:30 | 2.6071 | 0 | N/A | 0 | 0
2020-11-28 11:00 | 2.7895 | 0 | N/A | 0 | 0
2020-11-28 11:30 | 2.5993 | 0 | N/A | 0 | 0
2020-11-28 12:00 | 2.5646 | 0 | N/A | 0 | 0
2020-11-28 12:30 | 2.7311 | 0 | N/A | 0 | 0
2020-11-28 13:00 | 2.9759 | 0 | N/A | 0 | 0
2020-11-28 13:30 | 3.0111 | 0 | N/A | 0 | 0
2020-11-28 14:00 | 2.5367 | 0 | N/A | 0 | 0
2020-11-28 14:30 | 2.6229 | 0 | N/A | 0 | 0
2020-11-28 15:00 | 2.744 | 0 | N/A | 0 | 0
2020-11-28 15:30 | 2.8639 | 0 | N/A | 0 | 0
2020-11-28 16:00 | 2.8938 | 0 | N/A | 0 | 0
2020-11-28 16:30 | 3.0252 | 0 | N/A | 0 | 0
2020-11-28 17:00 | 2.5452 | 0 | N/A | 0 | 0
2020-11-28 17:30 | 3.2138 | 0 | N/A | 0 | 0
2020-11-28 18:00 | 3.5321 | 0 | N/A | 0 | 0
2020-11-28 18:30 | 3.8571 | 0 | N/A | 0 | 0
2020-11-28 19:00 | 3.9792 | 0 | N/A | 0 | 0
2020-11-28 19:30 | 4.1195 | 0 | N/A | 0 | 0
2020-11-28 20:00 | 4.0551 | 0 | N/A | 0 | 0
2020-11-28 20:30 | 3.9242 | 0 | N/A | 0 | 0
2020-11-28 21:00 | 3.8707 | 0 | N/A | 0 | 0
2020-11-28 21:30 | 3.6544 | 0 | N/A | 0 | 0
2020-11-28 22:00 | 3.399 | 0 | N/A | 0 | 0
2020-11-28 22:30 | 3.8217 | 0 | N/A | 0 | 0
2020-11-28 23:00 | 4.1051 | 0 | N/A | 0 | 0
2020-11-28 23:30 | 3.7453 | 0 | N/A | 0 | 0
2020-11-29 | 3.8184 | 0 | N/A | 0 | 0
2020-11-29 00:30 | 4.2418 | 0 | N/A | 0 | 0
2020-11-29 01:00 | 4.744 | 0 | N/A | 0 | 0
2020-11-29 01:30 | 3.8567 | 0 | N/A | 0 | 0
2020-11-29 02:00 | 4.2694 | 0 | N/A | 0 | 0
2020-11-29 02:30 | 3.9034 | 0 | N/A | 0 | 0
2020-11-29 03:00 | 2.6603 | 0 | N/A | 0 | 0
2020-11-29 03:30 | 2.6956 | 0 | N/A | 0 | 0
2020-11-29 04:00 | 2.6553 | 0 | N/A | 0 | 0
2020-11-29 04:30 | 2.4091 | 0 | N/A | 0 | 0
2020-11-29 05:00 | 2.409 | 0 | N/A | 0 | 0
2020-11-29 05:30 | 2.5741 | 0 | N/A | 0 | 0
2020-11-29 06:00 | 2.619 | 0 | N/A | 0 | 0
2020-11-29 06:30 | 2.7251 | 0 | N/A | 0 | 0
2020-11-29 07:00 | 2.9522 | 0 | N/A | 0 | 0
2020-11-29 07:30 | 3.0357 | 0 | N/A | 0 | 0
2020-11-29 08:00 | 3.1845 | 0 | N/A | 0 | 0
2020-11-29 08:30 | 2.9656 | 0 | N/A | 0 | 0
2020-11-29 09:00 | 3.4887 | 0 | N/A | 0 | 0
2020-11-29 09:30 | 3.4954 | 0 | N/A | 0 | 0
2020-11-29 10:00 | 3.1501 | 0 | N/A | 0 | 0
2020-11-29 10:30 | 3.4254 | 0 | N/A | 0 | 0
2020-11-29 11:00 | 2.358 | 0 | N/A | 0 | 0
2020-11-29 11:30 | 1.6781 | 0 | N/A | 0 | 0
2020-11-29 12:00 | 1.1827 | 0 | N/A | 0 | 0
2020-11-29 12:30 | 2.0156 | 0 | N/A | 0 | 0
2020-11-29 13:00 | 1.5534 | 0 | N/A | 0 | 0
2020-11-29 13:30 | 1.3458 | 0 | N/A | 0 | 0
2020-11-29 14:00 | 1.6853 | 0 | N/A | 0 | 0
2020-11-29 14:30 | 1.2482 | 0 | N/A | 0 | 0
2020-11-29 15:00 | 1.9765 | 0 | N/A | 0 | 0
2020-11-29 15:30 | 1.9905 | 0 | N/A | 0 | 0
2020-11-29 16:00 | 1.5132 | 0 | N/A | 0 | 0
2020-11-29 16:30 | 2.5334 | 0 | N/A | 0 | 0
2020-11-29 17:00 | 2.3576 | 0 | N/A | 0 | 0
2020-11-29 17:30 | 3.5087 | 0 | N/A | 0 | 0
2020-11-29 18:00 | 3.5832 | 0 | N/A | 0 | 0
2020-11-29 18:30 | 3.984 | 0 | N/A | 0 | 0
2020-11-29 19:00 | 4.1261 | 0 | N/A | 0 | 0
2020-11-29 19:30 | 4.6451 | 0 | N/A | 0 | 0
2020-11-29 20:00 | 4.6703 | 0 | N/A | 0 | 0
2020-11-29 20:30 | 4.6538 | 0 | N/A | 0 | 0
2020-11-29 21:00 | 4.5625 | 0 | N/A | 0 | 0
2020-11-29 21:30 | 4.4053 | 0 | N/A | 0 | 0
2020-11-29 22:00 | 4.0541 | 0 | N/A | 0 | 0
2020-11-29 22:30 | 4.3817 | 0 | N/A | 0 | 0
2020-11-29 23:00 | 4.5319 | 0 | N/A | 0 | 0
2020-11-29 23:30 | 4.2441 | 0 | N/A | 0 | 0
2020-11-30 | 4.3416 | 0 | N/A | 0 | 0
2020-11-30 00:30 | 4.5712 | 0 | N/A | 0 | 0
2020-11-30 01:00 | 5.0265 | 0 | N/A | 0 | 0
2020-11-30 01:30 | 4.1973 | 0 | N/A | 0 | 0
2020-11-30 02:00 | 3.5929 | 0 | N/A | 0 | 0
2020-11-30 02:30 | 3.536 | 0 | N/A | 0 | 0
2020-11-30 03:00 | 3.2211 | 0 | N/A | 0 | 0
2020-11-30 03:30 | 2.7359 | 0 | N/A | 0 | 0
2020-11-30 04:00 | 2.4763 | 0 | N/A | 0 | 0
2020-11-30 04:30 | 2.3413 | 0 | N/A | 0 | 0
2020-11-30 05:00 | 2.3331 | 0 | N/A | 0 | 0
2020-11-30 05:30 | 2.5246 | 0 | N/A | 0 | 0
2020-11-30 06:00 | 2.7967 | 0 | N/A | 0 | 0
2020-11-30 06:30 | 3.3139 | 0 | N/A | 0 | 0
2020-11-30 07:00 | 3.5087 | 0 | N/A | 0 | 0
2020-11-30 07:30 | 4.0684 | 0 | N/A | 0 | 0
2020-11-30 08:00 | 3.9097 | 0 | N/A | 0 | 0
2020-11-30 08:30 | 2.594 | 0 | N/A | 0 | 0
2020-11-30 09:00 | 2.0534 | 0 | N/A | 0 | 0
2020-11-30 09:30 | 1.3933 | 0 | N/A | 0 | 0
2020-11-30 10:00 | 0.75334 | 0 | N/A | 0 | 0
2020-11-30 10:30 | 0.51334 | 0 | N/A | 0 | 0
2020-11-30 11:00 | 0.10382 | 0 | N/A | 0 | 0
2020-11-30 11:30 | -0.11081 | 0 | N/A | 0 | 0
2020-11-30 12:00 | -0.16347 | 0 | N/A | 0 | 0
2020-11-30 12:30 | -0.32085 | 0 | N/A | 0 | 0
2020-11-30 13:00 | -0.40139 | 0 | N/A | 0 | 0
2020-11-30 13:30 | -0.52325 | 0 | N/A | 0 | 0
2020-11-30 14:00 | -0.57281 | 0 | N/A | 0 | 0
2020-11-30 14:30 | -0.60285 | 0 | N/A | 0 | 0
2020-11-30 15:00 | -0.47867 | 0 | N/A | 0 | 0
2020-11-30 15:30 | -0.26843 | 0 | N/A | 0 | 0
2020-11-30 16:00 | -0.13149 | 0 | N/A | 0 | 0
2020-11-30 16:30 | 0.36303 | 0 | N/A | 0 | 0
2020-11-30 17:00 | 1.3533 | 0 | N/A | 0 | 0
2020-11-30 17:30 | 2.36 | 0 | N/A | 0 | 0
2020-11-30 18:00 | 3.1567 | 0 | N/A | 0 | 0
2020-11-30 18:30 | 3.9833 | 0 | N/A | 0 | 0
2020-11-30 19:00 | 4.2601 | 0 | N/A | 0 | 0
2020-11-30 19:30 | 4.3341 | 0 | N/A | 0 | 0
2020-11-30 20:00 | 4.4958 | 0 | N/A | 0 | 0
2020-11-30 20:30 | 4.5158 | 0 | N/A | 0 | 0
2020-11-30 21:00 | 4.4708 | 0 | N/A | 0 | 0
2020-11-30 21:30 | 4.2519 | 0 | N/A | 0 | 0
2020-11-30 22:00 | 3.9065 | 0 | N/A | 0 | 0
2020-11-30 22:30 | 4.1025 | 0 | N/A | 0 | 0
2020-11-30 23:00 | 4.2395 | 0 | N/A | 0 | 0
2020-11-30 23:30 | 3.8631 | 0 | N/A | 0 | 0
2020-12-01 | 4.0257 | 0 | N/A | 0 | 0
2020-12-01 00:30 | 4.4281 | 0 | N/A | 0 | 0
2020-12-01 01:00 | 4.6165 | 0 | N/A | 0 | 0
2020-12-01 01:30 | 3.6624 | 0 | N/A | 0 | 0
2020-12-01 02:00 | 2.9521 | 0 | N/A | 0 | 0
2020-12-01 02:30 | 2.8514 | 0 | N/A | 0 | 0
2020-12-01 03:00 | 2.5739 | 0 | N/A | 0 | 0
2020-12-01 03:30 | 2.3034 | 0 | N/A | 0 | 0
2020-12-01 04:00 | 2.1756 | 0 | N/A | 0 | 0
2020-12-01 04:30 | 2.144 | 0 | N/A | 0 | 0
2020-12-01 05:00 | 2.1691 | 0 | N/A | 0 | 0
2020-12-01 05:30 | 2.3284 | 0 | N/A | 0 | 0
2020-12-01 06:00 | 2.5698 | 0 | N/A | 0 | 0
2020-12-01 06:30 | 2.8825 | 0 | N/A | 0 | 0
2020-12-01 07:00 | 3.1638 | 0 | N/A | 0 | 0
2020-12-01 07:30 | 3.7556 | 0 | N/A | 0 | 0
2020-12-01 08:00 | 4.3835 | 0 | N/A | 0 | 0
2020-12-01 08:30 | 3.4398 | 0 | N/A | 0 | 0
2020-12-01 09:00 | 3.1897 | 0 | N/A | 0 | 0
2020-12-01 09:30 | 3.6703 | 0 | N/A | 0 | 0
2020-12-01 10:00 | 3.6226 | 0 | N/A | 0 | 0
2020-12-01 10:30 | 3.4024 | 0 | N/A | 0 | 0
2020-12-01 11:00 | 3.451 | 0 | N/A | 0 | 0
2020-12-01 11:30 | 3.44 | 0 | N/A | 0 | 0
2020-12-01 12:00 | 3.2313 | 0 | N/A | 0 | 0
2020-12-01 12:30 | 3.4207 | 0 | N/A | 0 | 0
2020-12-01 13:00 | 4.0275 | 0 | N/A | 0 | 0
2020-12-01 13:30 | 2.7691 | 0 | N/A | 0 | 0
2020-12-01 14:00 | 1.2835 | 0 | N/A | 0 | 0
2020-12-01 14:30 | 1.6197 | 0 | N/A | 0 | 0
2020-12-01 15:00 | 1.5042 | 0 | N/A | 0 | 0
2020-12-01 15:30 | 0.89122 | 0 | N/A | 0 | 0
2020-12-01 16:00 | 0.81011 | 0 | N/A | 0 | 0
2020-12-01 16:30 | 0.87699 | 0 | N/A | 0 | 0
2020-12-01 17:00 | 0.96128 | 0 | N/A | 0 | 0
2020-12-01 17:30 | 1.6614 | 0 | N/A | 0 | 0
2020-12-01 18:00 | 2.433 | 0 | N/A | 0 | 0
2020-12-01 18:30 | 3.1855 | 0 | N/A | 0 | 0
2020-12-01 19:00 | 3.7883 | 0 | N/A | 0 | 0
2020-12-01 19:30 | 4.1219 | 0 | N/A | 0 | 0
2020-12-01 20:00 | 4.3787 | 0 | N/A | 0 | 0
2020-12-01 20:30 | 4.4793 | 0 | N/A | 0 | 0
2020-12-01 21:00 | 4.5093 | 0 | N/A | 0 | 0
2020-12-01 21:30 | 4.4879 | 0 | N/A | 0 | 0
2020-12-01 22:00 | 4.1787 | 0 | N/A | 0 | 0
2020-12-01 22:30 | 4.5049 | 0 | N/A | 0 | 0
2020-12-01 23:00 | 4.7244 | 0 | N/A | 0 | 0
2020-12-01 23:30 | 4.4149 | 0 | N/A | 0 | 0
2020-12-02 | 4.4045 | 0 | N/A | 0 | 0
2020-12-02 00:30 | 4.8122 | 0 | N/A | 0 | 0
2020-12-02 01:00 | 5.1849 | 0 | N/A | 0 | 0
2020-12-02 01:30 | 4.2403 | 0 | N/A | 0 | 0
2020-12-02 02:00 | 3.5184 | 0 | N/A | 0 | 0
2020-12-02 02:30 | 3.4257 | 0 | N/A | 0 | 0
2020-12-02 03:00 | 3.0667 | 0 | N/A | 0 | 0
2020-12-02 03:30 | 2.7102 | 0 | N/A | 0 | 0
2020-12-02 04:00 | 2.5714 | 0 | N/A | 0 | 0
2020-12-02 04:30 | 2.5508 | 0 | N/A | 0 | 0
2020-12-02 05:00 | 2.5418 | 0 | N/A | 0 | 0
2020-12-02 05:30 | 2.7497 | 0 | N/A | 0 | 0
2020-12-02 06:00 | 3.0126 | 0 | N/A | 0 | 0
2020-12-02 06:30 | 3.6656 | 0 | N/A | 0 | 0
2020-12-02 07:00 | 3.9757 | 0 | N/A | 0 | 0
2020-12-02 07:30 | 4.6883 | 0 | N/A | 0 | 0
2020-12-02 08:00 | 4.2822 | 0 | N/A | 0 | 0
2020-12-02 08:30 | 3.1084 | 0 | N/A | 0 | 0
2020-12-02 09:00 | 3.1579 | 0 | N/A | 0 | 0
2020-12-02 09:30 | 3.0648 | 0 | N/A | 0 | 0
2020-12-02 10:00 | 1.8317 | 0 | N/A | 0 | 0
2020-12-02 10:30 | 1.7809 | 0 | N/A | 0 | 0
2020-12-02 11:00 | 1.6416 | 0 | N/A | 0 | 0
2020-12-02 11:30 | 1.6667 | 0 | N/A | 0 | 0
2020-12-02 12:00 | 1.3033 | 0 | N/A | 0 | 0
2020-12-02 12:30 | 0.98 | 0 | N/A | 0 | 0
2020-12-02 13:00 | 0.73333 | 0 | N/A | 0 | 0
2020-12-02 13:30 | 1.05 | 0 | N/A | 0 | 0
2020-12-02 14:00 | 0.96703 | 0 | N/A | 0 | 0
2020-12-02 14:30 | 0.85667 | 0 | N/A | 0 | 0
2020-12-02 15:00 | 0.80667 | 0 | N/A | 0 | 0
2020-12-02 15:30 | 0.33682 | 0 | N/A | 0 | 0
2020-12-02 16:00 | 0.3549 | 0 | N/A | 0 | 0
2020-12-02 16:30 | 1.0809 | 0 | N/A | 0 | 0
2020-12-02 17:00 | 1.1222 | 0 | N/A | 0 | 0
2020-12-02 17:30 | 1.8883 | 0 | N/A | 0 | 0
2020-12-02 18:00 | 2.3482 | 0 | N/A | 0 | 0
2020-12-02 18:30 | 3.0817 | 0 | N/A | 0 | 0
2020-12-02 19:00 | 3.5447 | 0 | N/A | 0 | 0
2020-12-02 19:30 | 4.0941 | 0 | N/A | 0 | 0
2020-12-02 20:00 | 4.3188 | 0 | N/A | 0 | 0
2020-12-02 20:30 | 4.493 | 0 | N/A | 0 | 0
2020-12-02 21:00 | 4.5914 | 0 | N/A | 0 | 0
2020-12-02 21:30 | 4.5567 | 0 | N/A | 0 | 0
2020-12-02 22:00 | 4.2711 | 0 | N/A | 0 | 0
2020-12-02 22:30 | 4.621 | 0 | N/A | 0 | 0
2020-12-02 23:00 | 4.7925 | 0 | N/A | 0 | 0
2020-12-02 23:30 | 4.4419 | 0 | N/A | 0 | 0
2020-12-03 | 4.4832 | 0 | N/A | 0 | 0
2020-12-03 00:30 | 4.9319 | 0 | N/A | 0 | 0
2020-12-03 01:00 | 5.2466 | 0 | N/A | 0 | 0
2020-12-03 01:30 | 4.3074 | 0 | N/A | 0 | 0
2020-12-03 02:00 | 3.5134 | 0 | N/A | 0 | 0
2020-12-03 02:30 | 3.4952 | 0 | N/A | 0 | 0
2020-12-03 03:00 | 3.1432 | 0 | N/A | 0 | 0
2020-12-03 03:30 | 2.8231 | 0 | N/A | 0 | 0
2020-12-03 04:00 | 2.6943 | 0 | N/A | 0 | 0
2020-12-03 04:30 | 2.5769 | 0 | N/A | 0 | 0
2020-12-03 05:00 | 2.6292 | 0 | N/A | 0 | 0
2020-12-03 05:30 | 2.8466 | 0 | N/A | 0 | 0
2020-12-03 06:00 | 3.1003 | 0 | N/A | 0 | 0
2020-12-03 06:30 | 3.6613 | 0 | N/A | 0 | 0
2020-12-03 07:00 | 4.1722 | 0 | N/A | 0 | 0
2020-12-03 07:30 | 4.7519 | 0 | N/A | 0 | 0
2020-12-03 08:00 | 4.3981 | 0 | N/A | 0 | 0
2020-12-03 08:30 | 3.0734 | 0 | N/A | 0 | 0
2020-12-03 09:00 | 2.2333 | 0 | N/A | 0 | 0
2020-12-03 09:30 | 1.4462 | 0 | N/A | 0 | 0
2020-12-03 10:00 | 0.93638 | 0 | N/A | 0 | 0
2020-12-03 10:30 | 0.59908 | 0 | N/A | 0 | 0
2020-12-03 11:00 | 0.44912 | 0 | N/A | 0 | 0
2020-12-03 11:30 | 0.51908 | 0 | N/A | 0 | 0
2020-12-03 12:00 | -0.59742 | 0 | N/A | 0 | 0
2020-12-03 12:30 | -0.5815 | 0 | N/A | 0 | 0
2020-12-03 13:00 | -0.51599 | 0 | N/A | 0 | 0
2020-12-03 13:30 | -0.44468 | 0 | N/A | 0 | 0
2020-12-03 14:00 | -0.49801 | 0 | N/A | 0 | 0
2020-12-03 14:30 | -0.55201 | 0 | N/A | 0 | 0
2020-12-03 15:00 | -0.50706 | 0 | N/A | 0 | 0
2020-12-03 15:30 | -0.43712 | 0 | N/A | 0 | 0
2020-12-03 16:00 | -0.2816 | 0 | N/A | 0 | 0
2020-12-03 16:30 | 0.12333 | 0 | N/A | 0 | 0
2020-12-03 17:00 | 0.45338 | 0 | N/A | 0 | 0
2020-12-03 17:30 | 1.2087 | 0 | N/A | 0 | 0
2020-12-03 18:00 | 2.1127 | 0 | N/A | 0 | 0
2020-12-03 18:30 | 2.8619 | 0 | N/A | 0 | 0
2020-12-03 19:00 | 3.5942 | 0 | N/A | 0 | 0
2020-12-03 19:30 | 3.9417 | 0 | N/A | 0 | 0
2020-12-03 20:00 | 4.0377 | 0 | N/A | 0 | 0
2020-12-03 20:30 | 4.0685 | 0 | N/A | 0 | 0
2020-12-03 21:00 | 4.2066 | 0 | N/A | 0 | 0
2020-12-03 21:30 | 4.1537 | 0 | N/A | 0 | 0
2020-12-03 22:00 | 3.8942 | 0 | N/A | 0 | 0
2020-12-03 22:30 | 4.2708 | 0 | N/A | 0 | 0
2020-12-03 23:00 | 4.3455 | 0 | N/A | 0 | 0
2020-12-03 23:30 | 3.9905 | 0 | N/A | 0 | 0
2020-12-04 | 4.0065 | 0 | N/A | 0 | 0
2020-12-04 00:30 | 4.457 | 0 | N/A | 0 | 0
2020-12-04 01:00 | 4.8553 | 0 | N/A | 0 | 0
2020-12-04 01:30 | 3.9587 | 0 | N/A | 0 | 0
2020-12-04 02:00 | 3.255 | 0 | N/A | 0 | 0
2020-12-04 02:30 | 3.2334 | 0 | N/A | 0 | 0
2020-12-04 03:00 | 2.8336 | 0 | N/A | 0 | 0
2020-12-04 03:30 | 2.5559 | 0 | N/A | 0 | 0
2020-12-04 04:00 | 2.4385 | 0 | N/A | 0 | 0
2020-12-04 04:30 | 2.3225 | 0 | N/A | 0 | 0
2020-12-04 05:00 | 2.3644 | 0 | N/A | 0 | 0
2020-12-04 05:30 | 2.5014 | 0 | N/A | 0 | 0
2020-12-04 06:00 | 2.8067 | 0 | N/A | 0 | 0
2020-12-04 06:30 | 3.2535 | 0 | N/A | 0 | 0
2020-12-04 07:00 | 3.6624 | 0 | N/A | 0 | 0
2020-12-04 07:30 | 4.3341 | 0 | N/A | 0 | 0
2020-12-04 08:00 | 4.0154 | 0 | N/A | 0 | 0
2020-12-04 08:30 | 2.9433 | 0 | N/A | 0 | 0
2020-12-04 09:00 | 2.2934 | 0 | N/A | 0 | 0
2020-12-04 09:30 | 1.879 | 0 | N/A | 0 | 0
2020-12-04 10:00 | 1.33 | 0 | N/A | 0 | 0
2020-12-04 10:30 | 0.66152 | 0 | N/A | 0 | 0
2020-12-04 11:00 | 0.37006 | 0 | N/A | 0 | 0
2020-12-04 11:30 | -0.17295 | 0 | N/A | 0 | 0
2020-12-04 12:00 | -0.3061 | 0 | N/A | 0 | 0
2020-12-04 12:30 | -0.44338 | 0 | N/A | 0 | 0
2020-12-04 13:00 | -0.77377 | 0 | N/A | 0 | 0
2020-12-04 13:30 | -0.89062 | 0 | N/A | 0 | 0
2020-12-04 14:00 | -0.89333 | 0 | N/A | 0 | 0
2020-12-04 14:30 | -0.97703 | 0 | N/A | 0 | 0
2020-12-04 15:00 | -0.85667 | 0 | N/A | 0 | 0
2020-12-04 15:30 | -0.82 | 0 | N/A | 0 | 0
2020-12-04 16:00 | -0.58676 | 0 | N/A | 0 | 0
2020-12-04 16:30 | -0.23118 | 0 | N/A | 0 | 0
2020-12-04 17:00 | 0.29242 | 0 | N/A | 0 | 0
2020-12-04 17:30 | 1.0231 | 0 | N/A | 0 | 0
2020-12-04 18:00 | 1.7904 | 0 | N/A | 0 | 0
2020-12-04 18:30 | 2.4977 | 0 | N/A | 0 | 0
2020-12-04 19:00 | 2.9988 | 0 | N/A | 0 | 0
2020-12-04 19:30 | 3.4709 | 0 | N/A | 0 | 0
2020-12-04 20:00 | 3.7961 | 0 | N/A | 0 | 0
2020-12-04 20:30 | 3.7562 | 0 | N/A | 0 | 0
2020-12-04 21:00 | 3.8474 | 0 | N/A | 0 | 0
2020-12-04 21:30 | 3.7793 | 0 | N/A | 0 | 0
2020-12-04 22:00 | 3.6832 | 0 | N/A | 0 | 0
2020-12-04 22:30 | 4.0324 | 0 | N/A | 0 | 0
2020-12-04 23:00 | 4.2635 | 0 | N/A | 0 | 0
2020-12-04 23:30 | 3.9768 | 0 | N/A | 0 | 0
2020-12-05 | 4.0282 | 0 | N/A | 0 | 0
2020-12-05 00:30 | 4.4389 | 0 | N/A | 0 | 0
2020-12-05 01:00 | 4.7506 | 0 | N/A | 0 | 0
2020-12-05 01:30 | 3.8499 | 0 | N/A | 0 | 0
2020-12-05 02:00 | 3.1695 | 0 | N/A | 0 | 0
2020-12-05 02:30 | 3.0896 | 0 | N/A | 0 | 0
2020-12-05 03:00 | 2.7625 | 0 | N/A | 0 | 0
2020-12-05 03:30 | 2.3978 | 0 | N/A | 0 | 0
2020-12-05 04:00 | 2.2147 | 0 | N/A | 0 | 0
2020-12-05 04:30 | 2.1295 | 0 | N/A | 0 | 0
2020-12-05 05:00 | 2.1342 | 0 | N/A | 0 | 0
2020-12-05 05:30 | 2.0932 | 0 | N/A | 0 | 0
2020-12-05 06:00 | 2.1989 | 0 | N/A | 0 | 0
2020-12-05 06:30 | 2.2843 | 0 | N/A | 0 | 0
2020-12-05 07:00 | 2.4014 | 0 | N/A | 0 | 0
2020-12-05 07:30 | 2.6816 | 0 | N/A | 0 | 0
2020-12-05 08:00 | 2.7602 | 0 | N/A | 0 | 0
2020-12-05 08:30 | 2.7038 | 0 | N/A | 0 | 0
2020-12-05 09:00 | 2.5654 | 0 | N/A | 0 | 0
2020-12-05 09:30 | 2.7824 | 0 | N/A | 0 | 0
2020-12-05 10:00 | 2.8984 | 0 | N/A | 0 | 0
2020-12-05 10:30 | 2.7107 | 0 | N/A | 0 | 0
2020-12-05 11:00 | 2.6118 | 0 | N/A | 0 | 0
2020-12-05 11:30 | 2.0533 | 0 | N/A | 0 | 0
2020-12-05 12:00 | 2.1815 | 0 | N/A | 0 | 0
2020-12-05 12:30 | 2.1222 | 0 | N/A | 0 | 0
2020-12-05 13:00 | 1.8605 | 0 | N/A | 0 | 0
2020-12-05 13:30 | 2.6808 | 0 | N/A | 0 | 0
2020-12-05 14:00 | 2.9376 | 0 | N/A | 0 | 0
2020-12-05 14:30 | 2.7275 | 0 | N/A | 0 | 0
2020-12-05 15:00 | 2.8529 | 0 | N/A | 0 | 0
2020-12-05 15:30 | 3.0377 | 0 | N/A | 0 | 0
2020-12-05 16:00 | 3.8467 | 0 | N/A | 0 | 0
2020-12-05 16:30 | 3.6807 | 0 | N/A | 0 | 0
2020-12-05 17:00 | 2.7274 | 0 | N/A | 0 | 0
2020-12-05 17:30 | 2.1773 | 0 | N/A | 0 | 0
2020-12-05 18:00 | 2.7713 | 0 | N/A | 0 | 0
2020-12-05 18:30 | 2.9307 | 0 | N/A | 0 | 0
2020-12-05 19:00 | 3.2366 | 0 | N/A | 0 | 0
2020-12-05 19:30 | 4.8267 | 0 | N/A | 0 | 0
2020-12-05 20:00 | 5.4668 | 0 | N/A | 0 | 0
2020-12-05 20:30 | 5.6565 | 0 | N/A | 0 | 0
2020-12-05 21:00 | 5.6015 | 0 | N/A | 0 | 0
2020-12-05 21:30 | 5.2639 | 0 | N/A | 0 | 0
2020-12-05 22:00 | 3.9991 | 0 | N/A | 0 | 0
2020-12-05 22:30 | 4.1565 | 0 | N/A | 0 | 0
2020-12-05 23:00 | 4.4207 | 0 | N/A | 0 | 0
2020-12-05 23:30 | 4.1653 | 0 | N/A | 0 | 0
2020-12-06 | 4.3295 | 0 | N/A | 0 | 0
2020-12-06 00:30 | 4.6203 | 0 | N/A | 0 | 0
2020-12-06 01:00 | 4.9076 | 0 | N/A | 0 | 0
2020-12-06 01:30 | 4.1461 | 0 | N/A | 0 | 0
2020-12-06 02:00 | 3.3935 | 0 | N/A | 0 | 0
2020-12-06 02:30 | 3.3034 | 0 | N/A | 0 | 0
2020-12-06 03:00 | 2.9857 | 0 | N/A | 0 | 0
2020-12-06 03:30 | 2.5944 | 0 | N/A | 0 | 0
2020-12-06 04:00 | 2.3222 | 0 | N/A | 0 | 0
2020-12-06 04:30 | 2.2364 | 0 | N/A | 0 | 0
2020-12-06 05:00 | 2.2225 | 0 | N/A | 0 | 0
2020-12-06 05:30 | 2.1719 | 0 | N/A | 0 | 0
2020-12-06 06:00 | 2.2645 | 0 | N/A | 0 | 0
2020-12-06 06:30 | 2.3222 | 0 | N/A | 0 | 0
2020-12-06 07:00 | 2.4814 | 0 | N/A | 0 | 0
2020-12-06 07:30 | 2.5552 | 0 | N/A | 0 | 0
2020-12-06 08:00 | 2.8774 | 0 | N/A | 0 | 0
2020-12-06 08:30 | 2.2454 | 0 | N/A | 0 | 0
2020-12-06 09:00 | 2.0104 | 0 | N/A | 0 | 0
2020-12-06 09:30 | 2.4335 | 0 | N/A | 0 | 0
2020-12-06 10:00 | 2.438 | 0 | N/A | 0 | 0
2020-12-06 10:30 | 2.5802 | 0 | N/A | 0 | 0
2020-12-06 11:00 | 1.0995 | 0 | N/A | 0 | 0
2020-12-06 11:30 | 0.84146 | 0 | N/A | 0 | 0
2020-12-06 12:00 | 1.9396 | 0 | N/A | 0 | 0
2020-12-06 12:30 | 1.6129 | 0 | N/A | 0 | 0
2020-12-06 13:00 | 1.1349 | 0 | N/A | 0 | 0
2020-12-06 13:30 | 1.0321 | 0 | N/A | 0 | 0
2020-12-06 14:00 | 0.43012 | 0 | N/A | 0 | 0
2020-12-06 14:30 | 1.4391 | 0 | N/A | 0 | 0
2020-12-06 15:00 | -0.41293 | 0 | N/A | 0 | 0
2020-12-06 15:30 | 1.3725 | 0 | N/A | 0 | 0
2020-12-06 16:00 | 1.9905 | 0 | N/A | 0 | 0
2020-12-06 16:30 | 0.78768 | 0 | N/A | 0 | 0
2020-12-06 17:00 | 2.6815 | 0 | N/A | 0 | 0
2020-12-06 17:30 | 2.8217 | 0 | N/A | 0 | 0
2020-12-06 18:00 | 3.0025 | 0 | N/A | 0 | 0
2020-12-06 18:30 | 4.1858 | 0 | N/A | 0 | 0
2020-12-06 19:00 | 4.7076 | 0 | N/A | 0 | 0
2020-12-06 19:30 | 4.5755 | 0 | N/A | 0 | 0
2020-12-06 20:00 | 4.6502 | 0 | N/A | 0 | 0
2020-12-06 20:30 | 4.6675 | 0 | N/A | 0 | 0
2020-12-06 21:00 | 4.889 | 0 | N/A | 0 | 0
2020-12-06 21:30 | 4.8485 | 0 | N/A | 0 | 0
2020-12-06 22:00 | 4.3871 | 0 | N/A | 0 | 0
2020-12-06 22:30 | 4.6683 | 0 | N/A | 0 | 0
2020-12-06 23:00 | 4.7784 | 0 | N/A | 0 | 0
2020-12-06 23:30 | 4.4385 | 0 | N/A | 0 | 0
2020-12-07 | 4.4658 | 0 | N/A | 0 | 0
2020-12-07 00:30 | 4.7427 | 0 | N/A | 0 | 0
2020-12-07 01:00 | 5.3417 | 0 | N/A | 0 | 0
2020-12-07 01:30 | 4.5456 | 0 | N/A | 0 | 0
2020-12-07 02:00 | 3.7675 | 0 | N/A | 0 | 0
2020-12-07 02:30 | 3.6696 | 0 | N/A | 0 | 0
2020-12-07 03:00 | 3.3315 | 0 | N/A | 0 | 0
2020-12-07 03:30 | 2.9193 | 0 | N/A | 0 | 0
2020-12-07 04:00 | 2.6813 | 0 | N/A | 0 | 0
2020-12-07 04:30 | 2.5756 | 0 | N/A | 0 | 0
2020-12-07 05:00 | 2.5536 | 0 | N/A | 0 | 0
2020-12-07 05:30 | 2.695 | 0 | N/A | 0 | 0
2020-12-07 06:00 | 2.9412 | 0 | N/A | 0 | 0
2020-12-07 06:30 | 3.5701 | 0 | N/A | 0 | 0
2020-12-07 07:00 | 4.1422 | 0 | N/A | 0 | 0
2020-12-07 07:30 | 4.7555 | 0 | N/A | 0 | 0
2020-12-07 08:00 | 4.5147 | 0 | N/A | 0 | 0
2020-12-07 08:30 | 3.5949 | 0 | N/A | 0 | 0
2020-12-07 09:00 | 3.2052 | 0 | N/A | 0 | 0
2020-12-07 09:30 | 3.0975 | 0 | N/A | 0 | 0
2020-12-07 10:00 | 3.0807 | 0 | N/A | 0 | 0
2020-12-07 10:30 | 2.6612 | 0 | N/A | 0 | 0
2020-12-07 11:00 | 3.1348 | 0 | N/A | 0 | 0
2020-12-07 11:30 | 2.1274 | 0 | N/A | 0 | 0
2020-12-07 12:00 | 2.6512 | 0 | N/A | 0 | 0
2020-12-07 12:30 | 3.3887 | 0 | N/A | 0 | 0
2020-12-07 13:00 | 1.5232 | 0 | N/A | 0 | 0
2020-12-07 13:30 | 2.65 | 0 | N/A | 0 | 0
2020-12-07 14:00 | 0.80456 | 0 | N/A | 0 | 0
2020-12-07 14:30 | 2.3734 | 0 | N/A | 0 | 0
2020-12-07 15:00 | 3.2667 | 0 | N/A | 0 | 0
2020-12-07 15:30 | 3.2467 | 0 | N/A | 0 | 0
2020-12-07 16:00 | 3.3941 | 0 | N/A | 0 | 0
2020-12-07 16:30 | 3.2411 | 0 | N/A | 0 | 0
2020-12-07 17:00 | 2.2293 | 0 | N/A | 0 | 0
2020-12-07 17:30 | 2.4927 | 0 | N/A | 0 | 0
2020-12-07 18:00 | 4.131 | 0 | N/A | 0 | 0
2020-12-07 18:30 | 4.2312 | 0 | N/A | 0 | 0
2020-12-07 19:00 | 4.8358 | 0 | N/A | 0 | 0
2020-12-07 19:30 | 5.0262 | 0 | N/A | 0 | 0
2020-12-07 20:00 | 5.2023 | 0 | N/A | 0 | 0
2020-12-07 20:30 | 5.4291 | 0 | N/A | 0 | 0
2020-12-07 21:00 | 5.507 | 0 | N/A | 0 | 0
2020-12-07 21:30 | 5.3803 | 0 | N/A | 0 | 0
2020-12-07 22:00 | 5.0295 | 0 | N/A | 0 | 0
2020-12-07 22:30 | 5.1904 | 0 | N/A | 0 | 0
2020-12-07 23:00 | 5.2779 | 0 | N/A | 0 | 0
2020-12-07 23:30 | 4.8748 | 0 | N/A | 0 | 0
2020-12-08 | 4.8061 | 0 | N/A | 0 | 0
2020-12-08 00:30 | 5.2124 | 0 | N/A | 0 | 0
2020-12-08 01:00 | 5.6227 | 0 | N/A | 0 | 0
2020-12-08 01:30 | 4.7935 | 0 | N/A | 0 | 0
2020-12-08 02:00 | 4.0493 | 0 | N/A | 0 | 0
2020-12-08 02:30 | 3.9242 | 0 | N/A | 0 | 0
2020-12-08 03:00 | 3.6326 | 0 | N/A | 0 | 0
2020-12-08 03:30 | 3.1889 | 0 | N/A | 0 | 0
2020-12-08 04:00 | 2.905 | 0 | N/A | 0 | 0
2020-12-08 04:30 | 2.8225 | 0 | N/A | 0 | 0
2020-12-08 05:00 | 2.8627 | 0 | N/A | 0 | 0
2020-12-08 05:30 | 3.1228 | 0 | N/A | 0 | 0
2020-12-08 06:00 | 3.3516 | 0 | N/A | 0 | 0
2020-12-08 06:30 | 3.8717 | 0 | N/A | 0 | 0
2020-12-08 07:00 | 4.1639 | 0 | N/A | 0 | 0
2020-12-08 07:30 | 5.2983 | 0 | N/A | 0 | 0
2020-12-08 08:00 | 5.39 | 0 | N/A | 0 | 0
2020-12-08 08:30 | 5.0579 | 0 | N/A | 0 | 0
2020-12-08 09:00 | 4.4615 | 0 | N/A | 0 | 0
2020-12-08 09:30 | 4.3663 | 0 | N/A | 0 | 0
2020-12-08 10:00 | 4.3509 | 0 | N/A | 0 | 0
2020-12-08 10:30 | 3.0344 | 0 | N/A | 0 | 0
2020-12-08 11:00 | 3.0242 | 0 | N/A | 0 | 0
2020-12-08 11:30 | 4.0358 | 0 | N/A | 0 | 0
2020-12-08 12:00 | 3.6005 | 0 | N/A | 0 | 0
2020-12-08 12:30 | 3.0673 | 0 | N/A | 0 | 0
2020-12-08 13:00 | 3.7302 | 0 | N/A | 0 | 0
2020-12-08 13:30 | 3.5289 | 0 | N/A | 0 | 0
2020-12-08 14:00 | 3.419 | 0 | N/A | 0 | 0
2020-12-08 14:30 | 3.1751 | 0 | N/A | 0 | 0
2020-12-08 15:00 | 3.1595 | 0 | N/A | 0 | 0
2020-12-08 15:30 | 3.0004 | 0 | N/A | 0 | 0
2020-12-08 16:00 | 2.7927 | 0 | N/A | 0 | 0
2020-12-08 16:30 | 3.2451 | 0 | N/A | 0 | 0
2020-12-08 17:00 | 3.6512 | 0 | N/A | 0 | 0
2020-12-08 17:30 | 4.1877 | 0 | N/A | 0 | 0
2020-12-08 18:00 | 4.8111 | 0 | N/A | 0 | 0
2020-12-08 18:30 | 4.9501 | 0 | N/A | 0 | 0
2020-12-08 19:00 | 5.2417 | 0 | N/A | 0 | 0
2020-12-08 19:30 | 5.4377 | 0 | N/A | 0 | 0
2020-12-08 20:00 | 5.6091 | 0 | N/A | 0 | 0
2020-12-08 20:30 | 5.6068 | 0 | N/A | 0 | 0
2020-12-08 21:00 | 5.4899 | 0 | N/A | 0 | 0
2020-12-08 21:30 | 5.2007 | 0 | N/A | 0 | 0
2020-12-08 22:00 | 4.8161 | 0 | N/A | 0 | 0
2020-12-08 22:30 | 5.0353 | 0 | N/A | 0 | 0
2020-12-08 23:00 | 5.1214 | 0 | N/A | 0 | 0
2020-12-08 23:30 | 4.7066 | 0 | N/A | 0 | 0
2020-12-09 | 4.5571 | 0 | N/A | 0 | 0
2020-12-09 00:30 | 4.9652 | 0 | N/A | 0 | 0
2020-12-09 01:00 | 5.3759 | 0 | N/A | 0 | 0
2020-12-09 01:30 | 4.5729 | 0 | N/A | 0 | 0
2020-12-09 02:00 | 3.7748 | 0 | N/A | 0 | 0
2020-12-09 02:30 | 3.7497 | 0 | N/A | 0 | 0
2020-12-09 03:00 | 3.3647 | 0 | N/A | 0 | 0
2020-12-09 03:30 | 2.9414 | 0 | N/A | 0 | 0
2020-12-09 04:00 | 2.661 | 0 | N/A | 0 | 0
2020-12-09 04:30 | 2.6312 | 0 | N/A | 0 | 0
2020-12-09 05:00 | 2.6481 | 0 | N/A | 0 | 0
2020-12-09 05:30 | 2.8151 | 0 | N/A | 0 | 0
2020-12-09 06:00 | 3.1239 | 0 | N/A | 0 | 0
2020-12-09 06:30 | 3.6904 | 0 | N/A | 0 | 0
2020-12-09 07:00 | 4.3524 | 0 | N/A | 0 | 0
2020-12-09 07:30 | 4.8751 | 0 | N/A | 0 | 0
2020-12-09 08:00 | 4.5534 | 0 | N/A | 0 | 0
2020-12-09 08:30 | 3.5638 | 0 | N/A | 0 | 0
2020-12-09 09:00 | 2.5802 | 0 | N/A | 0 | 0
2020-12-09 09:30 | 1.5709 | 0 | N/A | 0 | 0
2020-12-09 10:00 | 0.94362 | 0 | N/A | 0 | 0
2020-12-09 10:30 | 0.49374 | 0 | N/A | 0 | 0
2020-12-09 11:00 | 0.16014 | 0 | N/A | 0 | 0
2020-12-09 11:30 | 0.046308 | 0 | N/A | 0 | 0
2020-12-09 12:00 | -0.16997 | 0 | N/A | 0 | 0
2020-12-09 12:30 | -0.2377 | 0 | N/A | 0 | 0
2020-12-09 13:00 | -0.29031 | 0 | N/A | 0 | 0
2020-12-09 13:30 | -0.34335 | 0 | N/A | 0 | 0
2020-12-09 14:00 | -0.44385 | 0 | N/A | 0 | 0
2020-12-09 14:30 | -0.41987 | 0 | N/A | 0 | 0
2020-12-09 15:00 | -0.36301 | 0 | N/A | 0 | 0
2020-12-09 15:30 | -0.38159 | 0 | N/A | 0 | 0
2020-12-09 16:00 | 0.22455 | 0 | N/A | 0 | 0
2020-12-09 16:30 | 0.32113 | 0 | N/A | 0 | 0
2020-12-09 17:00 | 0.7134 | 0 | N/A | 0 | 0
2020-12-09 17:30 | 1.5549 | 0 | N/A | 0 | 0
2020-12-09 18:00 | 2.321 | 0 | N/A | 0 | 0
2020-12-09 18:30 | 3.0451 | 0 | N/A | 0 | 0
2020-12-09 19:00 | 3.649 | 0 | N/A | 0 | 0
2020-12-09 19:30 | 3.9701 | 0 | N/A | 0 | 0
2020-12-09 20:00 | 4.0463 | 0 | N/A | 0 | 0
2020-12-09 20:30 | 4.0806 | 0 | N/A | 0 | 0
2020-12-09 21:00 | 4.1438 | 0 | N/A | 0 | 0
2020-12-09 21:30 | 4.1092 | 0 | N/A | 0 | 0
2020-12-09 22:00 | 3.8762 | 0 | N/A | 0 | 0
2020-12-09 22:30 | 4.1602 | 0 | N/A | 0 | 0
2020-12-09 23:00 | 4.4346 | 0 | N/A | 0 | 0
2020-12-09 23:30 | 4.1508 | 0 | N/A | 0 | 0
2020-12-10 | 4.1328 | 0 | N/A | 0 | 0
2020-12-10 00:30 | 4.5508 | 0 | N/A | 0 | 0
2020-12-10 01:00 | 4.9462 | 0 | N/A | 0 | 0
2020-12-10 01:30 | 4.0334 | 0 | N/A | 0 | 0
2020-12-10 02:00 | 3.1916 | 0 | N/A | 0 | 0
2020-12-10 02:30 | 3.19 | 0 | N/A | 0 | 0
2020-12-10 03:00 | 2.8587 | 0 | N/A | 0 | 0
2020-12-10 03:30 | 2.5833 | 0 | N/A | 0 | 0
2020-12-10 04:00 | 2.4549 | 0 | N/A | 0 | 0
2020-12-10 04:30 | 2.389 | 0 | N/A | 0 | 0
2020-12-10 05:00 | 2.4128 | 0 | N/A | 0 | 0
2020-12-10 05:30 | 2.5361 | 0 | N/A | 0 | 0
2020-12-10 06:00 | 2.8054 | 0 | N/A | 0 | 0
2020-12-10 06:30 | 3.3033 | 0 | N/A | 0 | 0
2020-12-10 07:00 | 3.7796 | 0 | N/A | 0 | 0
2020-12-10 07:30 | 4.3892 | 0 | N/A | 0 | 0
2020-12-10 08:00 | 4.7977 | 0 | N/A | 0 | 0
2020-12-10 08:30 | 3.9837 | 0 | N/A | 0 | 0
2020-12-10 09:00 | 3.3234 | 0 | N/A | 0 | 0
2020-12-10 09:30 | 2.7733 | 0 | N/A | 0 | 0
2020-12-10 10:00 | 2.0743 | 0 | N/A | 0 | 0
2020-12-10 10:30 | 1.799 | 0 | N/A | 0 | 0
2020-12-10 11:00 | 1.0334 | 0 | N/A | 0 | 0
2020-12-10 11:30 | 0.50535 | 0 | N/A | 0 | 0
2020-12-10 12:00 | 0.7398 | 0 | N/A | 0 | 0
2020-12-10 12:30 | 0.23113 | 0 | N/A | 0 | 0
2020-12-10 13:00 | -0.13828 | 0 | N/A | 0 | 0
2020-12-10 13:30 | -0.33652 | 0 | N/A | 0 | 0
2020-12-10 14:00 | -0.38942 | 0 | N/A | 0 | 0
2020-12-10 14:30 | -0.60019 | 0 | N/A | 0 | 0
2020-12-10 15:00 | -0.69362 | 0 | N/A | 0 | 0
2020-12-10 15:30 | -0.72729 | 0 | N/A | 0 | 0
2020-12-10 16:00 | -0.47984 | 0 | N/A | 0 | 0
2020-12-10 16:30 | -0.17337 | 0 | N/A | 0 | 0
2020-12-10 17:00 | 0.4174 | 0 | N/A | 0 | 0
2020-12-10 17:30 | 0.88769 | 0 | N/A | 0 | 0
2020-12-10 18:00 | 1.71 | 0 | N/A | 0 | 0
2020-12-10 18:30 | 2.5286 | 0 | N/A | 0 | 0
2020-12-10 19:00 | 3.3344 | 0 | N/A | 0 | 0
2020-12-10 19:30 | 3.7728 | 0 | N/A | 0 | 0
2020-12-10 20:00 | 4.182 | 0 | N/A | 0 | 0
2020-12-10 20:30 | 4.4883 | 0 | N/A | 0 | 0
2020-12-10 21:00 | 4.8462 | 0 | N/A | 0 | 0
2020-12-10 21:30 | 4.9681 | 0 | N/A | 0 | 0
2020-12-10 22:00 | 4.7242 | 0 | N/A | 0 | 0
2020-12-10 22:30 | 4.9921 | 0 | N/A | 0 | 0
2020-12-10 23:00 | 5.141 | 0 | N/A | 0 | 0
2020-12-10 23:30 | 4.7313 | 0 | N/A | 0 | 0
2020-12-11 | 4.7237 | 0 | N/A | 0 | 0
2020-12-11 00:30 | 4.9854 | 0 | N/A | 0 | 0
2020-12-11 01:00 | 5.3531 | 0 | N/A | 0 | 0
2020-12-11 01:30 | 4.5005 | 0 | N/A | 0 | 0
2020-12-11 02:00 | 3.7961 | 0 | N/A | 0 | 0
2020-12-11 02:30 | 3.6373 | 0 | N/A | 0 | 0
2020-12-11 03:00 | 3.206 | 0 | N/A | 0 | 0
2020-12-11 03:30 | 2.8523 | 0 | N/A | 0 | 0
2020-12-11 04:00 | 2.7218 | 0 | N/A | 0 | 0
2020-12-11 04:30 | 2.6063 | 0 | N/A | 0 | 0
2020-12-11 05:00 | 2.6242 | 0 | N/A | 0 | 0
2020-12-11 05:30 | 2.7974 | 0 | N/A | 0 | 0
2020-12-11 06:00 | 3.0871 | 0 | N/A | 0 | 0
2020-12-11 06:30 | 3.6773 | 0 | N/A | 0 | 0
2020-12-11 07:00 | 4.0183 | 0 | N/A | 0 | 0
2020-12-11 07:30 | 4.5202 | 0 | N/A | 0 | 0
2020-12-11 08:00 | 4.3464 | 0 | N/A | 0 | 0
2020-12-11 08:30 | 3.1715 | 0 | N/A | 0 | 0
2020-12-11 09:00 | 2.538 | 0 | N/A | 0 | 0
2020-12-11 09:30 | 2.2743 | 0 | N/A | 0 | 0
2020-12-11 10:00 | 0.85053 | 0 | N/A | 0 | 0
2020-12-11 10:30 | 0.14472 | 0 | N/A | 0 | 0
2020-12-11 11:00 | -0.20025 | 0 | N/A | 0 | 0
2020-12-11 11:30 | -0.48695 | 0 | N/A | 0 | 0
2020-12-11 12:00 | -0.73003 | 0 | N/A | 0 | 0
2020-12-11 12:30 | -0.99941 | 0 | N/A | 0 | 0
2020-12-11 13:00 | -1.0143 | 0 | N/A | 0 | 0
2020-12-11 13:30 | -1.0505 | 0 | N/A | 0 | 0
2020-12-11 14:00 | -1.1268 | 0 | N/A | 0 | 0
2020-12-11 14:30 | -1.1067 | 0 | N/A | 0 | 0
2020-12-11 15:00 | -1.0033 | 0 | N/A | 0 | 0
2020-12-11 15:30 | -0.98299 | 0 | N/A | 0 | 0
2020-12-11 16:00 | -0.86744 | 0 | N/A | 0 | 0
2020-12-11 16:30 | -0.43701 | 0 | N/A | 0 | 0
2020-12-11 17:00 | 0.21095 | 0 | N/A | 0 | 0
2020-12-11 17:30 | 0.69192 | 0 | N/A | 0 | 0
2020-12-11 18:00 | 1.4028 | 0 | N/A | 0 | 0
2020-12-11 18:30 | 2.139 | 0 | N/A | 0 | 0
2020-12-11 19:00 | 2.8483 | 0 | N/A | 0 | 0
2020-12-11 19:30 | 3.2941 | 0 | N/A | 0 | 0
2020-12-11 20:00 | 3.5676 | 0 | N/A | 0 | 0
2020-12-11 20:30 | 3.8778 | 0 | N/A | 0 | 0
2020-12-11 21:00 | 4.031 | 0 | N/A | 0 | 0
2020-12-11 21:30 | 4.0994 | 0 | N/A | 0 | 0
2020-12-11 22:00 | 3.9593 | 0 | N/A | 0 | 0
2020-12-11 22:30 | 4.3176 | 0 | N/A | 0 | 0
2020-12-11 23:00 | 4.6359 | 0 | N/A | 0 | 0
2020-12-11 23:30 | 4.3011 | 0 | N/A | 0 | 0
2020-12-12 | 4.3322 | 0 | N/A | 0 | 0
2020-12-12 00:30 | 4.7249 | 0 | N/A | 0 | 0
2020-12-12 01:00 | 4.9574 | 0 | N/A | 0 | 0
2020-12-12 01:30 | 3.9956 | 0 | N/A | 0 | 0
2020-12-12 02:00 | 3.357 | 0 | N/A | 0 | 0
2020-12-12 02:30 | 3.3832 | 0 | N/A | 0 | 0
2020-12-12 03:00 | 3.006 | 0 | N/A | 0 | 0
2020-12-12 03:30 | 2.6905 | 0 | N/A | 0 | 0
2020-12-12 04:00 | 2.4584 | 0 | N/A | 0 | 0
2020-12-12 04:30 | 2.4234 | 0 | N/A | 0 | 0
2020-12-12 05:00 | 0.4075 | 0 | N/A | 0 | 0
2020-12-12 05:30 | 3.9917 | 0 | N/A | 0 | 0
2020-12-12 06:00 | 3.453 | 0 | N/A | 0 | 0
2020-12-12 06:30 | 2.5362 | 0 | N/A | 0 | 0
2020-12-12 07:00 | 2.4901 | 0 | N/A | 0 | 0
2020-12-12 07:30 | 2.493 | 0 | N/A | 0 | 0
2020-12-12 08:00 | 2.3214 | 0 | N/A | 0 | 0
2020-12-12 08:30 | 1.678 | 0 | N/A | 0 | 0
2020-12-12 09:00 | 1.1583 | 0 | N/A | 0 | 0
2020-12-12 09:30 | 0.78032 | 0 | N/A | 0 | 0
2020-12-12 10:00 | 0.49554 | 0 | N/A | 0 | 0
2020-12-12 10:30 | -0.36284 | 0 | N/A | 0 | 0
2020-12-12 11:00 | -0.69769 | 0 | N/A | 0 | 0
2020-12-12 11:30 | -0.91279 | 0 | N/A | 0 | 0
2020-12-12 12:00 | -1.0701 | 0 | N/A | 0 | 0
2020-12-12 12:30 | -1.0196 | 0 | N/A | 0 | 0
2020-12-12 13:00 | -0.96713 | 0 | N/A | 0 | 0
2020-12-12 13:30 | -1.0134 | 0 | N/A | 0 | 0
2020-12-12 14:00 | -1.0035 | 0 | N/A | 0 | 0
2020-12-12 14:30 | -0.88334 | 0 | N/A | 0 | 0
2020-12-12 15:00 | -0.64337 | 0 | N/A | 0 | 0
2020-12-12 15:30 | -0.31378 | 0 | N/A | 0 | 0
2020-12-12 16:00 | -0.056667 | 0 | N/A | 0 | 0
2020-12-12 16:30 | 0.19082 | 0 | N/A | 0 | 0
2020-12-12 17:00 | 0.83931 | 0 | N/A | 0 | 0
2020-12-12 17:30 | 1.7899 | 0 | N/A | 0 | 0
2020-12-12 18:00 | 2.4172 | 0 | N/A | 0 | 0
2020-12-12 18:30 | 2.4273 | 0 | N/A | 0 | 0
2020-12-12 19:00 | 2.9202 | 0 | N/A | 0 | 0
2020-12-12 19:30 | 3.4278 | 0 | N/A | 0 | 0
2020-12-12 20:00 | 3.5421 | 0 | N/A | 0 | 0
2020-12-12 20:30 | 3.5921 | 0 | N/A | 0 | 0
2020-12-12 21:00 | 3.7099 | 0 | N/A | 0 | 0
2020-12-12 21:30 | 3.5092 | 0 | N/A | 0 | 0
2020-12-12 22:00 | 3.2406 | 0 | N/A | 0 | 0
2020-12-12 22:30 | 3.75 | 0 | N/A | 0 | 0
2020-12-12 23:00 | 3.9646 | 0 | N/A | 0 | 0
2020-12-12 23:30 | 3.7374 | 0 | N/A | 0 | 0
2020-12-13 | 3.875 | 0 | N/A | 0 | 0
2020-12-13 00:30 | 4.2896 | 0 | N/A | 0 | 0
2020-12-13 01:00 | 4.4856 | 0 | N/A | 0 | 0
2020-12-13 01:30 | 3.5713 | 0 | N/A | 0 | 0
2020-12-13 02:00 | 2.8877 | 0 | N/A | 0 | 0
2020-12-13 02:30 | 2.8774 | 0 | N/A | 0 | 0
2020-12-13 03:00 | 2.6089 | 0 | N/A | 0 | 0
2020-12-13 03:30 | 2.2369 | 0 | N/A | 0 | 0
2020-12-13 04:00 | 1.9878 | 0 | N/A | 0 | 0
2020-12-13 04:30 | 1.9257 | 0 | N/A | 0 | 0
2020-12-13 05:00 | 1.9085 | 0 | N/A | 0 | 0
2020-12-13 05:30 | 1.911 | 0 | N/A | 0 | 0
2020-12-13 06:00 | 1.9777 | 0 | N/A | 0 | 0
2020-12-13 06:30 | 2.106 | 0 | N/A | 0 | 0
2020-12-13 07:00 | 2.0782 | 0 | N/A | 0 | 0
2020-12-13 07:30 | 2.1165 | 0 | N/A | 0 | 0
2020-12-13 08:00 | 1.8913 | 0 | N/A | 0 | 0
2020-12-13 08:30 | 1.3372 | 0 | N/A | 0 | 0
2020-12-13 09:00 | 1.0577 | 0 | N/A | 0 | 0
2020-12-13 09:30 | 0.6747 | 0 | N/A | 0 | 0
2020-12-13 10:00 | 0.39623 | 0 | N/A | 0 | 0
2020-12-13 10:30 | -0.31903 | 0 | N/A | 0 | 0
2020-12-13 11:00 | -0.31116 | 0 | N/A | 0 | 0
2020-12-13 11:30 | -0.50191 | 0 | N/A | 0 | 0
2020-12-13 12:00 | -0.27546 | 0 | N/A | 0 | 0
2020-12-13 12:30 | -0.32258 | 0 | N/A | 0 | 0
2020-12-13 13:00 | -0.68219 | 0 | N/A | 0 | 0
2020-12-13 13:30 | -0.61233 | 0 | N/A | 0 | 0
2020-12-13 14:00 | -0.56887 | 0 | N/A | 0 | 0
2020-12-13 14:30 | 0.12824 | 0 | N/A | 0 | 0
2020-12-13 15:00 | 0.11552 | 0 | N/A | 0 | 0
2020-12-13 15:30 | 0.5206 | 0 | N/A | 0 | 0
2020-12-13 16:00 | 0.48195 | 0 | N/A | 0 | 0
2020-12-13 16:30 | 0.66435 | 0 | N/A | 0 | 0
2020-12-13 17:00 | 1.657 | 0 | N/A | 0 | 0
2020-12-13 17:30 | 2.7283 | 0 | N/A | 0 | 0
2020-12-13 18:00 | 2.5378 | 0 | N/A | 0 | 0
2020-12-13 18:30 | 3.4369 | 0 | N/A | 0 | 0
2020-12-13 19:00 | 4.3602 | 0 | N/A | 0 | 0
2020-12-13 19:30 | 4.3218 | 0 | N/A | 0 | 0
2020-12-13 20:00 | 4.0743 | 0 | N/A | 0 | 0
2020-12-13 20:30 | 4.3501 | 0 | N/A | 0 | 0
2020-12-13 21:00 | 4.3375 | 0 | N/A | 0 | 0
2020-12-13 21:30 | 4.1535 | 0 | N/A | 0 | 0
2020-12-13 22:00 | 3.765 | 0 | N/A | 0 | 0
2020-12-13 22:30 | 4.0632 | 0 | N/A | 0 | 0
2020-12-13 23:00 | 4.153 | 0 | N/A | 0 | 0
2020-12-13 23:30 | 3.7968 | 0 | N/A | 0 | 0
2020-12-14 | 3.9489 | 0 | N/A | 0 | 0
2020-12-14 00:30 | 4.2591 | 0 | N/A | 0 | 0
2020-12-14 01:00 | 4.5005 | 0 | N/A | 0 | 0
2020-12-14 01:30 | 3.6466 | 0 | N/A | 0 | 0
2020-12-14 02:00 | 2.8792 | 0 | N/A | 0 | 0
2020-12-14 02:30 | 2.9288 | 0 | N/A | 0 | 0
2020-12-14 03:00 | 2.5986 | 0 | N/A | 0 | 0
2020-12-14 03:30 | 2.255 | 0 | N/A | 0 | 0
2020-12-14 04:00 | 2.0355 | 0 | N/A | 0 | 0
2020-12-14 04:30 | 1.9272 | 0 | N/A | 0 | 0
2020-12-14 05:00 | 1.9785 | 0 | N/A | 0 | 0
2020-12-14 05:30 | 2.189 | 0 | N/A | 0 | 0
2020-12-14 06:00 | 2.4642 | 0 | N/A | 0 | 0
2020-12-14 06:30 | 2.8993 | 0 | N/A | 0 | 0
2020-12-14 07:00 | 3.0639 | 0 | N/A | 0 | 0
2020-12-14 07:30 | 3.422 | 0 | N/A | 0 | 0
2020-12-14 08:00 | 3.6945 | 0 | N/A | 0 | 0
2020-12-14 08:30 | 3.7202 | 0 | N/A | 0 | 0
2020-12-14 09:00 | 3.0993 | 0 | N/A | 0 | 0
2020-12-14 09:30 | 2.5221 | 0 | N/A | 0 | 0
2020-12-14 10:00 | 1.85 | 0 | N/A | 0 | 0
2020-12-14 10:30 | 0.93881 | 0 | N/A | 0 | 0
2020-12-14 11:00 | 0.71802 | 0 | N/A | 0 | 0
2020-12-14 11:30 | 0.52521 | 0 | N/A | 0 | 0
2020-12-14 12:00 | 0.54187 | 0 | N/A | 0 | 0
2020-12-14 12:30 | 0.56844 | 0 | N/A | 0 | 0
2020-12-14 13:00 | 0.61465 | 0 | N/A | 0 | 0
2020-12-14 13:30 | 0.87578 | 0 | N/A | 0 | 0
2020-12-14 14:00 | 0.55017 | 0 | N/A | 0 | 0
2020-12-14 14:30 | 0.62106 | 0 | N/A | 0 | 0
2020-12-14 15:00 | 0.87413 | 0 | N/A | 0 | 0
2020-12-14 15:30 | 1.1354 | 0 | N/A | 0 | 0
2020-12-14 16:00 | 1.5064 | 0 | N/A | 0 | 0
2020-12-14 16:30 | 2.0784 | 0 | N/A | 0 | 0
2020-12-14 17:00 | 2.8784 | 0 | N/A | 0 | 0
2020-12-14 17:30 | 3.9133 | 0 | N/A | 0 | 0
2020-12-14 18:00 | 4.9734 | 0 | N/A | 0 | 0
2020-12-14 18:30 | 5.7002 | 0 | N/A | 0 | 0
2020-12-14 19:00 | 6.3318 | 0 | N/A | 0 | 0
2020-12-14 19:30 | 6.6326 | 0 | N/A | 0 | 0
2020-12-14 20:00 | 6.5608 | 0 | N/A | 0 | 0
2020-12-14 20:30 | 6.2829 | 0 | N/A | 0 | 0
2020-12-14 21:00 | 5.8688 | 0 | N/A | 0 | 0
2020-12-14 21:30 | 5.3834 | 0 | N/A | 0 | 0
2020-12-14 22:00 | 4.92 | 0 | N/A | 0 | 0
2020-12-14 22:30 | 5.0833 | 0 | N/A | 0 | 0
2020-12-14 23:00 | 4.8773 | 0 | N/A | 0 | 0
2020-12-14 23:30 | 4.2272 | 0 | N/A | 0 | 0
2020-12-15 | 4.1797 | 0 | N/A | 0 | 0
2020-12-15 00:30 | 4.6191 | 0 | N/A | 0 | 0
2020-12-15 01:00 | 4.7737 | 0 | N/A | 0 | 0
2020-12-15 01:30 | 3.7121 | 0 | N/A | 0 | 0
2020-12-15 02:00 | 3.0879 | 0 | N/A | 0 | 0
2020-12-15 02:30 | 3.02 | 0 | N/A | 0 | 0
2020-12-15 03:00 | 2.6547 | 0 | N/A | 0 | 0
2020-12-15 03:30 | 2.4058 | 0 | N/A | 0 | 0
2020-12-15 04:00 | 2.258 | 0 | N/A | 0 | 0
2020-12-15 04:30 | 2.2322 | 0 | N/A | 0 | 0
2020-12-15 05:00 | 2.313 | 0 | N/A | 0 | 0
2020-12-15 05:30 | 2.4247 | 0 | N/A | 0 | 0
2020-12-15 06:00 | 2.5688 | 0 | N/A | 0 | 0
2020-12-15 06:30 | 2.9553 | 0 | N/A | 0 | 0
2020-12-15 07:00 | 3.1377 | 0 | N/A | 0 | 0
2020-12-15 07:30 | 3.4841 | 0 | N/A | 0 | 0
2020-12-15 08:00 | 3.3146 | 0 | N/A | 0 | 0
2020-12-15 08:30 | 2.6 | 0 | N/A | 0 | 0
2020-12-15 09:00 | 2.2211 | 0 | N/A | 0 | 0
2020-12-15 09:30 | 2.1045 | 0 | N/A | 0 | 0
2020-12-15 10:00 | 2.4145 | 0 | N/A | 0 | 0
2020-12-15 10:30 | 1.7968 | 0 | N/A | 0 | 0
2020-12-15 11:00 | 1.9246 | 0 | N/A | 0 | 0
2020-12-15 11:30 | 2.2573 | 0 | N/A | 0 | 0
2020-12-15 12:00 | 2.5797 | 0 | N/A | 0 | 0
2020-12-15 12:30 | 2.9939 | 0 | N/A | 0 | 0
2020-12-15 13:00 | 2.6063 | 0 | N/A | 0 | 0
2020-12-15 13:30 | 2.8726 | 0 | N/A | 0 | 0
2020-12-15 14:00 | 2.4609 | 0 | N/A | 0 | 0
2020-12-15 14:30 | 2.1053 | 0 | N/A | 0 | 0
2020-12-15 15:00 | 2.239 | 0 | N/A | 0 | 0
2020-12-15 15:30 | 2.7164 | 0 | N/A | 0 | 0
2020-12-15 16:00 | 3.0387 | 0 | N/A | 0 | 0
2020-12-15 16:30 | 3.8195 | 0 | N/A | 0 | 0
2020-12-15 17:00 | 4.1925 | 0 | N/A | 0 | 0
2020-12-15 17:30 | 4.2436 | 0 | N/A | 0 | 0
2020-12-15 18:00 | 5.1998 | 0 | N/A | 0 | 0
2020-12-15 18:30 | 5.5448 | 0 | N/A | 0 | 0
2020-12-15 19:00 | 5.8204 | 0 | N/A | 0 | 0
2020-12-15 19:30 | 5.7421 | 0 | N/A | 0 | 0
2020-12-15 20:00 | 5.461 | 0 | N/A | 0 | 0
2020-12-15 20:30 | 5.1035 | 0 | N/A | 0 | 0
2020-12-15 21:00 | 4.8311 | 0 | N/A | 0 | 0
2020-12-15 21:30 | 4.4316 | 0 | N/A | 0 | 0
2020-12-15 22:00 | 4.0552 | 0 | N/A | 0 | 0
2020-12-15 22:30 | 4.2503 | 0 | N/A | 0 | 0
2020-12-15 23:00 | 4.3068 | 0 | N/A | 0 | 0
2020-12-15 23:30 | 3.9156 | 0 | N/A | 0 | 0
2020-12-16 | 3.8832 | 0 | N/A | 0 | 0
2020-12-16 00:30 | 4.4074 | 0 | N/A | 0 | 0
2020-12-16 01:00 | 4.5564 | 0 | N/A | 0 | 0
2020-12-16 01:30 | 3.5794 | 0 | N/A | 0 | 0
2020-12-16 02:00 | 2.835 | 0 | N/A | 0 | 0
2020-12-16 02:30 | 2.8019 | 0 | N/A | 0 | 0
2020-12-16 03:00 | 2.4868 | 0 | N/A | 0 | 0
2020-12-16 03:30 | 2.252 | 0 | N/A | 0 | 0
2020-12-16 04:00 | 2.0976 | 0 | N/A | 0 | 0
2020-12-16 04:30 | 2.1054 | 0 | N/A | 0 | 0
2020-12-16 05:00 | 2.0843 | 0 | N/A | 0 | 0
2020-12-16 05:30 | 2.3003 | 0 | N/A | 0 | 0
2020-12-16 06:00 | 2.5282 | 0 | N/A | 0 | 0
2020-12-16 06:30 | 2.928 | 0 | N/A | 0 | 0
2020-12-16 07:00 | 3.1 | 0 | N/A | 0 | 0
2020-12-16 07:30 | 3.4871 | 0 | N/A | 0 | 0
2020-12-16 08:00 | 3.2638 | 0 | N/A | 0 | 0
2020-12-16 08:30 | 2.3687 | 0 | N/A | 0 | 0
2020-12-16 09:00 | 1.7249 | 0 | N/A | 0 | 0
2020-12-16 09:30 | 1.3622 | 0 | N/A | 0 | 0
2020-12-16 10:00 | 0.80417 | 0 | N/A | 0 | 0
2020-12-16 10:30 | 0.16125 | 0 | N/A | 0 | 0
2020-12-16 11:00 | -0.082798 | 0 | N/A | 0 | 0
2020-12-16 11:30 | -0.21082 | 0 | N/A | 0 | 0
2020-12-16 12:00 | -0.34437 | 0 | N/A | 0 | 0
2020-12-16 12:30 | -0.32912 | 0 | N/A | 0 | 0
2020-12-16 13:00 | -0.34854 | 0 | N/A | 0 | 0
2020-12-16 13:30 | 0.23949 | 0 | N/A | 0 | 0
2020-12-16 14:00 | 0.27849 | 0 | N/A | 0 | 0
2020-12-16 14:30 | -0.21708 | 0 | N/A | 0 | 0
2020-12-16 15:00 | 0.44315 | 0 | N/A | 0 | 0
2020-12-16 15:30 | 0.42908 | 0 | N/A | 0 | 0
2020-12-16 16:00 | 0.79367 | 0 | N/A | 0 | 0
2020-12-16 16:30 | 1.6501 | 0 | N/A | 0 | 0
2020-12-16 17:00 | 1.7467 | 0 | N/A | 0 | 0
2020-12-16 17:30 | 3.1607 | 0 | N/A | 0 | 0
2020-12-16 18:00 | 4.0721 | 0 | N/A | 0 | 0
2020-12-16 18:30 | 4.473 | 0 | N/A | 0 | 0
2020-12-16 19:00 | 4.663 | 0 | N/A | 0 | 0
2020-12-16 19:30 | 4.5534 | 0 | N/A | 0 | 0
2020-12-16 20:00 | 4.4525 | 0 | N/A | 0 | 0
2020-12-16 20:30 | 4.2774 | 0 | N/A | 0 | 0
2020-12-16 21:00 | 4.1703 | 0 | N/A | 0 | 0
2020-12-16 21:30 | 3.8719 | 0 | N/A | 0 | 0
2020-12-16 22:00 | 3.5865 | 0 | N/A | 0 | 0
2020-12-16 22:30 | 3.9229 | 0 | N/A | 0 | 0
2020-12-16 23:00 | 4.1387 | 0 | N/A | 0 | 0
2020-12-16 23:30 | 3.7475 | 0 | N/A | 0 | 0
2020-12-17 | 3.8269 | 0 | N/A | 0 | 0
2020-12-17 00:30 | 4.3474 | 0 | N/A | 0 | 0
2020-12-17 01:00 | 4.4737 | 0 | N/A | 0 | 0
2020-12-17 01:30 | 3.4728 | 0 | N/A | 0 | 0
2020-12-17 02:00 | 2.7431 | 0 | N/A | 0 | 0
2020-12-17 02:30 | 2.7471 | 0 | N/A | 0 | 0
2020-12-17 03:00 | 2.4334 | 0 | N/A | 0 | 0
2020-12-17 03:30 | 2.1744 | 0 | N/A | 0 | 0
2020-12-17 04:00 | 2.0589 | 0 | N/A | 0 | 0
2020-12-17 04:30 | 2.0221 | 0 | N/A | 0 | 0
2020-12-17 05:00 | 2.0357 | 0 | N/A | 0 | 0
2020-12-17 05:30 | 2.2092 | 0 | N/A | 0 | 0
2020-12-17 06:00 | 2.4441 | 0 | N/A | 0 | 0
2020-12-17 06:30 | 2.784 | 0 | N/A | 0 | 0
2020-12-17 07:00 | 2.8547 | 0 | N/A | 0 | 0
2020-12-17 07:30 | 3.1852 | 0 | N/A | 0 | 0
2020-12-17 08:00 | 3.0396 | 0 | N/A | 0 | 0
2020-12-17 08:30 | 2.2856 | 0 | N/A | 0 | 0
2020-12-17 09:00 | 1.7485 | 0 | N/A | 0 | 0
2020-12-17 09:30 | 1.14 | 0 | N/A | 0 | 0
2020-12-17 10:00 | 0.85548 | 0 | N/A | 0 | 0
2020-12-17 10:30 | 0.91244 | 0 | N/A | 0 | 0
2020-12-17 11:00 | 1.2343 | 0 | N/A | 0 | 0
2020-12-17 11:30 | 1.4475 | 0 | N/A | 0 | 0
2020-12-17 12:00 | 1.1934 | 0 | N/A | 0 | 0
2020-12-17 12:30 | 1.1505 | 0 | N/A | 0 | 0
2020-12-17 13:00 | 2.4178 | 0 | N/A | 0 | 0
2020-12-17 13:30 | 1.6324 | 0 | N/A | 0 | 0
2020-12-17 14:00 | 1.2474 | 0 | N/A | 0 | 0
2020-12-17 14:30 | 1.6241 | 0 | N/A | 0 | 0
2020-12-17 15:00 | 1.3262 | 0 | N/A | 0 | 0
2020-12-17 15:30 | 1.2083 | 0 | N/A | 0 | 0
2020-12-17 16:00 | 1.4525 | 0 | N/A | 0 | 0
2020-12-17 16:30 | 1.8208 | 0 | N/A | 0 | 0
2020-12-17 17:00 | 1.8838 | 0 | N/A | 0 | 0
2020-12-17 17:30 | 2.6619 | 0 | N/A | 0 | 0
2020-12-17 18:00 | 3.1468 | 0 | N/A | 0 | 0
2020-12-17 18:30 | 3.8267 | 0 | N/A | 0 | 0
2020-12-17 19:00 | 4.1203 | 0 | N/A | 0 | 0
2020-12-17 19:30 | 4.031 | 0 | N/A | 0 | 0
2020-12-17 20:00 | 4.1191 | 0 | N/A | 0 | 0
2020-12-17 20:30 | 4.0493 | 0 | N/A | 0 | 0
2020-12-17 21:00 | 3.9634 | 0 | N/A | 0 | 0
2020-12-17 21:30 | 3.8661 | 0 | N/A | 0 | 0
2020-12-17 22:00 | 3.597 | 0 | N/A | 0 | 0
2020-12-17 22:30 | 3.9952 | 0 | N/A | 0 | 0
2020-12-17 23:00 | 4.1126 | 0 | N/A | 0 | 0
2020-12-17 23:30 | 3.8095 | 0 | N/A | 0 | 0
2020-12-18 | 3.7781 | 0 | N/A | 0 | 0
2020-12-18 00:30 | 4.2803 | 0 | N/A | 0 | 0
2020-12-18 01:00 | 4.5299 | 0 | N/A | 0 | 0
2020-12-18 01:30 | 3.4881 | 0 | N/A | 0 | 0
2020-12-18 02:00 | 2.7702 | 0 | N/A | 0 | 0
2020-12-18 02:30 | 2.7558 | 0 | N/A | 0 | 0
2020-12-18 03:00 | 2.4533 | 0 | N/A | 0 | 0
2020-12-18 03:30 | 2.2248 | 0 | N/A | 0 | 0
2020-12-18 04:00 | 2.0978 | 0 | N/A | 0 | 0
2020-12-18 04:30 | 2.0613 | 0 | N/A | 0 | 0
2020-12-18 05:00 | 2.1482 | 0 | N/A | 0 | 0
2020-12-18 05:30 | 2.2834 | 0 | N/A | 0 | 0
2020-12-18 06:00 | 2.4125 | 0 | N/A | 0 | 0
2020-12-18 06:30 | 2.9364 | 0 | N/A | 0 | 0
2020-12-18 07:00 | 3.127 | 0 | N/A | 0 | 0
2020-12-18 07:30 | 3.5017 | 0 | N/A | 0 | 0
2020-12-18 08:00 | 3.619 | 0 | N/A | 0 | 0
2020-12-18 08:30 | 3.1681 | 0 | N/A | 0 | 0
2020-12-18 09:00 | 2.906 | 0 | N/A | 0 | 0
2020-12-18 09:30 | 2.995 | 0 | N/A | 0 | 0
2020-12-18 10:00 | 2.9878 | 0 | N/A | 0 | 0
2020-12-18 10:30 | 2.2207 | 0 | N/A | 0 | 0
2020-12-18 11:00 | 2.8359 | 0 | N/A | 0 | 0
2020-12-18 11:30 | 3.4282 | 0 | N/A | 0 | 0
2020-12-18 12:00 | 2.7293 | 0 | N/A | 0 | 0
2020-12-18 12:30 | 1.2133 | 0 | N/A | 0 | 0
2020-12-18 13:00 | 1.1998 | 0 | N/A | 0 | 0
2020-12-18 13:30 | 0.82152 | 0 | N/A | 0 | 0
2020-12-18 14:00 | 1.4121 | 0 | N/A | 0 | 0
2020-12-18 14:30 | 0.84286 | 0 | N/A | 0 | 0
2020-12-18 15:00 | 1.3396 | 0 | N/A | 0 | 0
2020-12-18 15:30 | 1.5063 | 0 | N/A | 0 | 0
2020-12-18 16:00 | 1.2207 | 0 | N/A | 0 | 0
2020-12-18 16:30 | 0.44578 | 0 | N/A | 0 | 0
2020-12-18 17:00 | 0.4139 | 0 | N/A | 0 | 0
2020-12-18 17:30 | 0.55626 | 0 | N/A | 0 | 0
2020-12-18 18:00 | 1.2645 | 0 | N/A | 0 | 0
2020-12-18 18:30 | 1.8829 | 0 | N/A | 0 | 0
2020-12-18 19:00 | 2.4881 | 0 | N/A | 0 | 0
2020-12-18 19:30 | 3.048 | 0 | N/A | 0 | 0
2020-12-18 20:00 | 3.3938 | 0 | N/A | 0 | 0
2020-12-18 20:30 | 3.6937 | 0 | N/A | 0 | 0
2020-12-18 21:00 | 3.9061 | 0 | N/A | 0 | 0
2020-12-18 21:30 | 3.984 | 0 | N/A | 0 | 0
2020-12-18 22:00 | 3.8997 | 0 | N/A | 0 | 0
2020-12-18 22:30 | 4.4384 | 0 | N/A | 0 | 0
2020-12-18 23:00 | 4.6532 | 0 | N/A | 0 | 0
2020-12-18 23:30 | 4.3925 | 0 | N/A | 0 | 0
2020-12-19 | 4.4398 | 0 | N/A | 0 | 0
2020-12-19 00:30 | 4.8312 | 0 | N/A | 0 | 0
2020-12-19 01:00 | 5.1172 | 0 | N/A | 0 | 0
2020-12-19 01:30 | 4.2054 | 0 | N/A | 0 | 0
2020-12-19 02:00 | 3.3915 | 0 | N/A | 0 | 0
2020-12-19 02:30 | 3.2815 | 0 | N/A | 0 | 0
2020-12-19 03:00 | 2.9712 | 0 | N/A | 0 | 0
2020-12-19 03:30 | 2.5906 | 0 | N/A | 0 | 0
2020-12-19 04:00 | 2.4642 | 0 | N/A | 0 | 0
2020-12-19 04:30 | 2.3266 | 0 | N/A | 0 | 0
2020-12-19 05:00 | 2.3064 | 0 | N/A | 0 | 0
2020-12-19 05:30 | 2.3233 | 0 | N/A | 0 | 0
2020-12-19 06:00 | 2.4987 | 0 | N/A | 0 | 0
2020-12-19 06:30 | 2.6786 | 0 | N/A | 0 | 0
2020-12-19 07:00 | 2.7034 | 0 | N/A | 0 | 0
2020-12-19 07:30 | 2.8611 | 0 | N/A | 0 | 0
2020-12-19 08:00 | 2.7768 | 0 | N/A | 0 | 0
2020-12-19 08:30 | 2.0594 | 0 | N/A | 0 | 0
2020-12-19 09:00 | 1.6492 | 0 | N/A | 0 | 0
2020-12-19 09:30 | 1.2354 | 0 | N/A | 0 | 0
2020-12-19 10:00 | 1.0699 | 0 | N/A | 0 | 0
2020-12-19 10:30 | 0.86349 | 0 | N/A | 0 | 0
2020-12-19 11:00 | 0.75036 | 0 | N/A | 0 | 0
2020-12-19 11:30 | 0.68471 | 0 | N/A | 0 | 0
2020-12-19 12:00 | 1.1217 | 0 | N/A | 0 | 0
2020-12-19 12:30 | 0.79747 | 0 | N/A | 0 | 0
2020-12-19 13:00 | 0.50576 | 0 | N/A | 0 | 0
2020-12-19 13:30 | 0.30113 | 0 | N/A | 0 | 0
2020-12-19 14:00 | -0.24342 | 0 | N/A | 0 | 0
2020-12-19 14:30 | 0.37631 | 0 | N/A | 0 | 0
2020-12-19 15:00 | 0.48472 | 0 | N/A | 0 | 0
2020-12-19 15:30 | 0.66675 | 0 | N/A | 0 | 0
2020-12-19 16:00 | 0.79259 | 0 | N/A | 0 | 0
2020-12-19 16:30 | 1.0133 | 0 | N/A | 0 | 0
2020-12-19 17:00 | 1.2575 | 0 | N/A | 0 | 0
2020-12-19 17:30 | 1.555 | 0 | N/A | 0 | 0
2020-12-19 18:00 | 2.1161 | 0 | N/A | 0 | 0
2020-12-19 18:30 | 2.6025 | 0 | N/A | 0 | 0
2020-12-19 19:00 | 2.7033 | 0 | N/A | 0 | 0
2020-12-19 19:30 | 3.1121 | 0 | N/A | 0 | 0
2020-12-19 20:00 | 3.3215 | 0 | N/A | 0 | 0
2020-12-19 20:30 | 3.6674 | 0 | N/A | 0 | 0
2020-12-19 21:00 | 3.8707 | 0 | N/A | 0 | 0
2020-12-19 21:30 | 4.0568 | 0 | N/A | 0 | 0
2020-12-19 22:00 | 3.8976 | 0 | N/A | 0 | 0
2020-12-19 22:30 | 4.1649 | 0 | N/A | 0 | 0
2020-12-19 23:00 | 4.3149 | 0 | N/A | 0 | 0
2020-12-19 23:30 | 4.1239 | 0 | N/A | 0 | 0
2020-12-20 | 4.2007 | 0 | N/A | 0 | 0
2020-12-20 00:30 | 4.5808 | 0 | N/A | 0 | 0
2020-12-20 01:00 | 4.8466 | 0 | N/A | 0 | 0
2020-12-20 01:30 | 4.0789 | 0 | N/A | 0 | 0
2020-12-20 02:00 | 3.3641 | 0 | N/A | 0 | 0
2020-12-20 02:30 | 3.3406 | 0 | N/A | 0 | 0
2020-12-20 03:00 | 3.1123 | 0 | N/A | 0 | 0
2020-12-20 03:30 | 2.6698 | 0 | N/A | 0 | 0
2020-12-20 04:00 | 2.3594 | 0 | N/A | 0 | 0
2020-12-20 04:30 | 2.1673 | 0 | N/A | 0 | 0
2020-12-20 05:00 | 2.1107 | 0 | N/A | 0 | 0
2020-12-20 05:30 | 2.1486 | 0 | N/A | 0 | 0
2020-12-20 06:00 | 2.2769 | 0 | N/A | 0 | 0
2020-12-20 06:30 | 2.4593 | 0 | N/A | 0 | 0
2020-12-20 07:00 | 2.4586 | 0 | N/A | 0 | 0
2020-12-20 07:30 | 2.6258 | 0 | N/A | 0 | 0
2020-12-20 08:00 | 2.3949 | 0 | N/A | 0 | 0
2020-12-20 08:30 | 1.9933 | 0 | N/A | 0 | 0
2020-12-20 09:00 | 1.845 | 0 | N/A | 0 | 0
2020-12-20 09:30 | 1.6503 | 0 | N/A | 0 | 0
2020-12-20 10:00 | 1.1464 | 0 | N/A | 0 | 0
2020-12-20 10:30 | 0.86163 | 0 | N/A | 0 | 0
2020-12-20 11:00 | 0.47527 | 0 | N/A | 0 | 0
2020-12-20 11:30 | -0.31127 | 0 | N/A | 0 | 0
2020-12-20 12:00 | -0.796 | 0 | N/A | 0 | 0
2020-12-20 12:30 | -0.84987 | 0 | N/A | 0 | 0
2020-12-20 13:00 | -1.2489 | 0 | N/A | 0 | 0
2020-12-20 13:30 | -1.352 | 0 | N/A | 0 | 0
2020-12-20 14:00 | -1.3021 | 0 | N/A | 0 | 0
2020-12-20 14:30 | -1.4274 | 0 | N/A | 0 | 0
2020-12-20 15:00 | -1.3562 | 0 | N/A | 0 | 0
2020-12-20 15:30 | -1.295 | 0 | N/A | 0 | 0
2020-12-20 16:00 | -1.1349 | 0 | N/A | 0 | 0
2020-12-20 16:30 | -0.63141 | 0 | N/A | 0 | 0
2020-12-20 17:00 | -0.29769 | 0 | N/A | 0 | 0
2020-12-20 17:30 | 0.54456 | 0 | N/A | 0 | 0
2020-12-20 18:00 | 1.41 | 0 | N/A | 0 | 0
2020-12-20 18:30 | 2.0684 | 0 | N/A | 0 | 0
2020-12-20 19:00 | 2.671 | 0 | N/A | 0 | 0
2020-12-20 19:30 | 3.192 | 0 | N/A | 0 | 0
2020-12-20 20:00 | 3.5021 | 0 | N/A | 0 | 0
2020-12-20 20:30 | 3.754 | 0 | N/A | 0 | 0
2020-12-20 21:00 | 3.8872 | 0 | N/A | 0 | 0
2020-12-20 21:30 | 3.9057 | 0 | N/A | 0 | 0
2020-12-20 22:00 | 3.8099 | 0 | N/A | 0 | 0
2020-12-20 22:30 | 4.0184 | 0 | N/A | 0 | 0
2020-12-20 23:00 | 4.1028 | 0 | N/A | 0 | 0
2020-12-20 23:30 | 3.7934 | 0 | N/A | 0 | 0
2020-12-21 | 3.8975 | 0 | N/A | 0 | 0
2020-12-21 00:30 | 4.2785 | 0 | N/A | 0 | 0
2020-12-21 01:00 | 4.6592 | 0 | N/A | 0 | 0
2020-12-21 01:30 | 3.9525 | 0 | N/A | 0 | 0
2020-12-21 02:00 | 3.3315 | 0 | N/A | 0 | 0
2020-12-21 02:30 | 3.2931 | 0 | N/A | 0 | 0
2020-12-21 03:00 | 2.9177 | 0 | N/A | 0 | 0
2020-12-21 03:30 | 2.4954 | 0 | N/A | 0 | 0
2020-12-21 04:00 | 2.24 | 0 | N/A | 0 | 0
2020-12-21 04:30 | 2.1968 | 0 | N/A | 0 | 0
2020-12-21 05:00 | 2.1032 | 0 | N/A | 0 | 0
2020-12-21 05:30 | 2.1778 | 0 | N/A | 0 | 0
2020-12-21 06:00 | 2.4377 | 0 | N/A | 0 | 0
2020-12-21 06:30 | 2.8692 | 0 | N/A | 0 | 0
2020-12-21 07:00 | 2.9981 | 0 | N/A | 0 | 0
2020-12-21 07:30 | 3.5092 | 0 | N/A | 0 | 0
2020-12-21 08:00 | 3.8763 | 0 | N/A | 0 | 0
2020-12-21 08:30 | 3.5513 | 0 | N/A | 0 | 0
2020-12-21 09:00 | 3.2002 | 0 | N/A | 0 | 0
2020-12-21 09:30 | 2.7492 | 0 | N/A | 0 | 0
2020-12-21 10:00 | 2.8539 | 0 | N/A | 0 | 0
2020-12-21 10:30 | 2.9237 | 0 | N/A | 0 | 0
2020-12-21 11:00 | 1.752 | 0 | N/A | 0 | 0
2020-12-21 11:30 | 1.3395 | 0 | N/A | 0 | 0
2020-12-21 12:00 | 2.5812 | 0 | N/A | 0 | 0
2020-12-21 12:30 | 2.682 | 0 | N/A | 0 | 0
2020-12-21 13:00 | 1.8305 | 0 | N/A | 0 | 0
2020-12-21 13:30 | 1.1767 | 0 | N/A | 0 | 0
2020-12-21 14:00 | 2.2401 | 0 | N/A | 0 | 0
2020-12-21 14:30 | 2.71 | 0 | N/A | 0 | 0
2020-12-21 15:00 | 2.9444 | 0 | N/A | 0 | 0
2020-12-21 15:30 | 2.968 | 0 | N/A | 0 | 0
2020-12-21 16:00 | 3.465 | 0 | N/A | 0 | 0
2020-12-21 16:30 | 2.8709 | 0 | N/A | 0 | 0
2020-12-21 17:00 | 3.2777 | 0 | N/A | 0 | 0
2020-12-21 17:30 | 3.913 | 0 | N/A | 0 | 0
2020-12-21 18:00 | 4.644 | 0 | N/A | 0 | 0
2020-12-21 18:30 | 4.8723 | 0 | N/A | 0 | 0
2020-12-21 19:00 | 4.8404 | 0 | N/A | 0 | 0
2020-12-21 19:30 | 4.9141 | 0 | N/A | 0 | 0
2020-12-21 20:00 | 4.9559 | 0 | N/A | 0 | 0
2020-12-21 20:30 | 4.8961 | 0 | N/A | 0 | 0
2020-12-21 21:00 | 4.7336 | 0 | N/A | 0 | 0
2020-12-21 21:30 | 4.6389 | 0 | N/A | 0 | 0
2020-12-21 22:00 | 4.2395 | 0 | N/A | 0 | 0
2020-12-21 22:30 | 4.5322 | 0 | N/A | 0 | 0
2020-12-21 23:00 | 4.6382 | 0 | N/A | 0 | 0
2020-12-21 23:30 | 4.2973 | 0 | N/A | 0 | 0
2020-12-22 | 4.3058 | 0 | N/A | 0 | 0
2020-12-22 00:30 | 4.6602 | 0 | N/A | 0 | 0
2020-12-22 01:00 | 4.9729 | 0 | N/A | 0 | 0
2020-12-22 01:30 | 4.0717 | 0 | N/A | 0 | 0
2020-12-22 02:00 | 3.222 | 0 | N/A | 0 | 0
2020-12-22 02:30 | 3.251 | 0 | N/A | 0 | 0
2020-12-22 03:00 | 2.86 | 0 | N/A | 0 | 0
2020-12-22 03:30 | 2.4929 | 0 | N/A | 0 | 0
2020-12-22 04:00 | 2.2294 | 0 | N/A | 0 | 0
2020-12-22 04:30 | 2.2115 | 0 | N/A | 0 | 0
2020-12-22 05:00 | 2.2074 | 0 | N/A | 0 | 0
2020-12-22 05:30 | 2.4986 | 0 | N/A | 0 | 0
2020-12-22 06:00 | 2.7029 | 0 | N/A | 0 | 0
2020-12-22 06:30 | 3.1026 | 0 | N/A | 0 | 0
2020-12-22 07:00 | 3.3649 | 0 | N/A | 0 | 0
2020-12-22 07:30 | 3.9027 | 0 | N/A | 0 | 0
2020-12-22 08:00 | 3.9749 | 0 | N/A | 0 | 0
2020-12-22 08:30 | 3.9719 | 0 | N/A | 0 | 0
2020-12-22 09:00 | 4.0561 | 0 | N/A | 0 | 0
2020-12-22 09:30 | 4.0104 | 0 | N/A | 0 | 0
2020-12-22 10:00 | 3.7666 | 0 | N/A | 0 | 0
2020-12-22 10:30 | 3.2902 | 0 | N/A | 0 | 0
2020-12-22 11:00 | 2.9851 | 0 | N/A | 0 | 0
2020-12-22 11:30 | 3.6896 | 0 | N/A | 0 | 0
2020-12-22 12:00 | 4.4367 | 0 | N/A | 0 | 0
2020-12-22 12:30 | 4.386 | 0 | N/A | 0 | 0
2020-12-22 13:00 | 4.2967 | 0 | N/A | 0 | 0
2020-12-22 13:30 | 4.7798 | 0 | N/A | 0 | 0
2020-12-22 14:00 | 5.2396 | 0 | N/A | 0 | 0
2020-12-22 14:30 | 5.4753 | 0 | N/A | 0 | 0
2020-12-22 15:00 | 5.6378 | 0 | N/A | 0 | 0
2020-12-22 15:30 | 5.7841 | 0 | N/A | 0 | 0
2020-12-22 16:00 | 5.7939 | 0 | N/A | 0 | 0
2020-12-22 16:30 | 5.6859 | 0 | N/A | 0 | 0
2020-12-22 17:00 | 6.1365 | 0 | N/A | 0 | 0
2020-12-22 17:30 | 6.3403 | 0 | N/A | 0 | 0
2020-12-22 18:00 | 5.9654 | 0 | N/A | 0 | 0
2020-12-22 18:30 | 6.018 | 0 | N/A | 0 | 0
2020-12-22 19:00 | 6.0691 | 0 | N/A | 0 | 0
2020-12-22 19:30 | 5.5196 | 0 | N/A | 0 | 0
2020-12-22 20:00 | 5.405 | 0 | N/A | 0 | 0
2020-12-22 20:30 | 5.4273 | 0 | N/A | 0 | 0
2020-12-22 21:00 | 5.4999 | 0 | N/A | 0 | 0
2020-12-22 21:30 | 5.3296 | 0 | N/A | 0 | 0
2020-12-22 22:00 | 5.0342 | 0 | N/A | 0 | 0
2020-12-22 22:30 | 5.2806 | 0 | N/A | 0 | 0
2020-12-22 23:00 | 5.3249 | 0 | N/A | 0 | 0
2020-12-22 23:30 | 4.9189 | 0 | N/A | 0 | 0
2020-12-23 | 4.7839 | 0 | N/A | 0 | 0
2020-12-23 00:30 | 5.1719 | 0 | N/A | 0 | 0
2020-12-23 01:00 | 5.5375 | 0 | N/A | 0 | 0
2020-12-23 01:30 | 4.6468 | 0 | N/A | 0 | 0
2020-12-23 02:00 | 3.7884 | 0 | N/A | 0 | 0
2020-12-23 02:30 | 3.6924 | 0 | N/A | 0 | 0
2020-12-23 03:00 | 3.2987 | 0 | N/A | 0 | 0
2020-12-23 03:30 | 2.8353 | 0 | N/A | 0 | 0
2020-12-23 04:00 | 2.6572 | 0 | N/A | 0 | 0
2020-12-23 04:30 | 2.5 | 0 | N/A | 0 | 0
2020-12-23 05:00 | 2.5801 | 0 | N/A | 0 | 0
2020-12-23 05:30 | 2.8288 | 0 | N/A | 0 | 0
2020-12-23 06:00 | 3.0783 | 0 | N/A | 0 | 0
2020-12-23 06:30 | 3.5113 | 0 | N/A | 0 | 0
2020-12-23 07:00 | 3.7304 | 0 | N/A | 0 | 0
2020-12-23 07:30 | 4.1957 | 0 | N/A | 0 | 0
2020-12-23 08:00 | 4.1743 | 0 | N/A | 0 | 0
2020-12-23 08:30 | 3.538 | 0 | N/A | 0 | 0
2020-12-23 09:00 | 3.5992 | 0 | N/A | 0 | 0
2020-12-23 09:30 | 2.8432 | 0 | N/A | 0 | 0
2020-12-23 10:00 | 2.5547 | 0 | N/A | 0 | 0
2020-12-23 10:30 | 2.7499 | 0 | N/A | 0 | 0
2020-12-23 11:00 | 2.7027 | 0 | N/A | 0 | 0
2020-12-23 11:30 | 2.5404 | 0 | N/A | 0 | 0
2020-12-23 12:00 | 2.1766 | 0 | N/A | 0 | 0
2020-12-23 12:30 | 1.7885 | 0 | N/A | 0 | 0
2020-12-23 13:00 | 1.3749 | 0 | N/A | 0 | 0
2020-12-23 13:30 | 1.1529 | 0 | N/A | 0 | 0
2020-12-23 14:00 | 1.7317 | 0 | N/A | 0 | 0
2020-12-23 14:30 | 1.9783 | 0 | N/A | 0 | 0
2020-12-23 15:00 | 1.5441 | 0 | N/A | 0 | 0
2020-12-23 15:30 | 1.25 | 0 | N/A | 0 | 0
2020-12-23 16:00 | 1.1175 | 0 | N/A | 0 | 0
2020-12-23 16:30 | 1.4952 | 0 | N/A | 0 | 0
2020-12-23 17:00 | 1.9648 | 0 | N/A | 0 | 0
2020-12-23 17:30 | 2.8427 | 0 | N/A | 0 | 0
2020-12-23 18:00 | 3.4205 | 0 | N/A | 0 | 0
2020-12-23 18:30 | 3.9592 | 0 | N/A | 0 | 0
2020-12-23 19:00 | 4.277 | 0 | N/A | 0 | 0
2020-12-23 19:30 | 4.3657 | 0 | N/A | 0 | 0
2020-12-23 20:00 | 4.4817 | 0 | N/A | 0 | 0
2020-12-23 20:30 | 4.5785 | 0 | N/A | 0 | 0
2020-12-23 21:00 | 4.6909 | 0 | N/A | 0 | 0
2020-12-23 21:30 | 4.5856 | 0 | N/A | 0 | 0
2020-12-23 22:00 | 4.2965 | 0 | N/A | 0 | 0
2020-12-23 22:30 | 4.6923 | 0 | N/A | 0 | 0
2020-12-23 23:00 | 4.8323 | 0 | N/A | 0 | 0
2020-12-23 23:30 | 4.4519 | 0 | N/A | 0 | 0
2020-12-24 | 4.5568 | 0 | N/A | 0 | 0
2020-12-24 00:30 | 4.9749 | 0 | N/A | 0 | 0
2020-12-24 01:00 | 5.1856 | 0 | N/A | 0 | 0
2020-12-24 01:30 | 4.3693 | 0 | N/A | 0 | 0
2020-12-24 02:00 | 3.676 | 0 | N/A | 0 | 0
2020-12-24 02:30 | 3.5236 | 0 | N/A | 0 | 0
2020-12-24 03:00 | 3.166 | 0 | N/A | 0 | 0
2020-12-24 03:30 | 2.6901 | 0 | N/A | 0 | 0
2020-12-24 04:00 | 2.3535 | 0 | N/A | 0 | 0
2020-12-24 04:30 | 2.3096 | 0 | N/A | 0 | 0
2020-12-24 05:00 | 2.2477 | 0 | N/A | 0 | 0
2020-12-24 05:30 | 2.4505 | 0 | N/A | 0 | 0
2020-12-24 06:00 | 2.6423 | 0 | N/A | 0 | 0
2020-12-24 06:30 | 2.9212 | 0 | N/A | 0 | 0
2020-12-24 07:00 | 3.0536 | 0 | N/A | 0 | 0
2020-12-24 07:30 | 3.3236 | 0 | N/A | 0 | 0
2020-12-24 08:00 | 3.0484 | 0 | N/A | 0 | 0
2020-12-24 08:30 | 2.8189 | 0 | N/A | 0 | 0
2020-12-24 09:00 | 2.7412 | 0 | N/A | 0 | 0
2020-12-24 09:30 | 3.031 | 0 | N/A | 0 | 0
2020-12-24 10:00 | 2.7306 | 0 | N/A | 0 | 0
2020-12-24 10:30 | 2.2953 | 0 | N/A | 0 | 0
2020-12-24 11:00 | 1.8129 | 0 | N/A | 0 | 0
2020-12-24 11:30 | 1.8056 | 0 | N/A | 0 | 0
2020-12-24 12:00 | 1.3083 | 0 | N/A | 0 | 0
2020-12-24 12:30 | 0.84698 | 0 | N/A | 0 | 0
2020-12-24 13:00 | 0.88944 | 0 | N/A | 0 | 0
2020-12-24 13:30 | 0.67915 | 0 | N/A | 0 | 0
2020-12-24 14:00 | 0.42335 | 0 | N/A | 0 | 0
2020-12-24 14:30 | 0.62891 | 0 | N/A | 0 | 0
2020-12-24 15:00 | 0.60278 | 0 | N/A | 0 | 0
2020-12-24 15:30 | 0.67805 | 0 | N/A | 0 | 0
2020-12-24 16:00 | 0.35335 | 0 | N/A | 0 | 0
2020-12-24 16:30 | 0.44258 | 0 | N/A | 0 | 0
2020-12-24 17:00 | 0.74863 | 0 | N/A | 0 | 0
2020-12-24 17:30 | 0.70919 | 0 | N/A | 0 | 0
2020-12-24 18:00 | 1.6736 | 0 | N/A | 0 | 0
2020-12-24 18:30 | 2.7596 | 0 | N/A | 0 | 0
2020-12-24 19:00 | 3.1807 | 0 | N/A | 0 | 0
2020-12-24 19:30 | 3.7982 | 0 | N/A | 0 | 0
2020-12-24 20:00 | 3.9414 | 0 | N/A | 0 | 0
2020-12-24 20:30 | 4.0981 | 0 | N/A | 0 | 0
2020-12-24 21:00 | 4.1541 | 0 | N/A | 0 | 0
2020-12-24 21:30 | 4.3158 | 0 | N/A | 0 | 0
2020-12-24 22:00 | 4.2903 | 0 | N/A | 0 | 0
2020-12-24 22:30 | 4.7347 | 0 | N/A | 0 | 0
2020-12-24 23:00 | 5.0058 | 0 | N/A | 0 | 0
2020-12-24 23:30 | 4.7636 | 0 | N/A | 0 | 0
2020-12-25 | 4.756 | 0 | N/A | 0 | 0
2020-12-25 00:30 | 5.0249 | 0 | N/A | 0 | 0
2020-12-25 01:00 | 5.4151 | 0 | N/A | 0 | 0
2020-12-25 01:30 | 4.7475 | 0 | N/A | 0 | 0
2020-12-25 02:00 | 4.6852 | 0 | N/A | 0 | 0
2020-12-25 02:30 | 4.5233 | 0 | N/A | 0 | 0
2020-12-25 03:00 | 4.1013 | 0 | N/A | 0 | 0
2020-12-25 03:30 | 3.6334 | 0 | N/A | 0 | 0
2020-12-25 04:00 | 3.2948 | 0 | N/A | 0 | 0
2020-12-25 04:30 | 3.1958 | 0 | N/A | 0 | 0
2020-12-25 05:00 | 3.0496 | 0 | N/A | 0 | 0
2020-12-25 05:30 | 2.9436 | 0 | N/A | 0 | 0
2020-12-25 06:00 | 3.0228 | 0 | N/A | 0 | 0
2020-12-25 06:30 | 3.3585 | 0 | N/A | 0 | 0
2020-12-25 07:00 | 3.5458 | 0 | N/A | 0 | 0
2020-12-25 07:30 | 3.8357 | 0 | N/A | 0 | 0
2020-12-25 08:00 | 3.9144 | 0 | N/A | 0 | 0
2020-12-25 08:30 | 3.5669 | 0 | N/A | 0 | 0
2020-12-25 09:00 | 3.1359 | 0 | N/A | 0 | 0
2020-12-25 09:30 | 3.2204 | 0 | N/A | 0 | 0
2020-12-25 10:00 | 2.9573 | 0 | N/A | 0 | 0
2020-12-25 10:30 | 1.9468 | 0 | N/A | 0 | 0
2020-12-25 11:00 | 2.4606 | 0 | N/A | 0 | 0
2020-12-25 11:30 | 1.2395 | 0 | N/A | 0 | 0
2020-12-25 12:00 | 0.75175 | 0 | N/A | 0 | 0
2020-12-25 12:30 | 0.68577 | 0 | N/A | 0 | 0
2020-12-25 13:00 | -0.38159 | 0 | N/A | 0 | 0
2020-12-25 13:30 | -0.51602 | 0 | N/A | 0 | 0
2020-12-25 14:00 | -0.78927 | 0 | N/A | 0 | 0
2020-12-25 14:30 | -1.2717 | 0 | N/A | 0 | 0
2020-12-25 15:00 | -0.84223 | 0 | N/A | 0 | 0
2020-12-25 15:30 | -0.76837 | 0 | N/A | 0 | 0
2020-12-25 16:00 | -1.3441 | 0 | N/A | 0 | 0
2020-12-25 16:30 | -1.2734 | 0 | N/A | 0 | 0
2020-12-25 17:00 | -0.62526 | 0 | N/A | 0 | 0
2020-12-25 17:30 | 0.49782 | 0 | N/A | 0 | 0
2020-12-25 18:00 | 0.57256 | 0 | N/A | 0 | 0
2020-12-25 18:30 | 0.96619 | 0 | N/A | 0 | 0
2020-12-25 19:00 | 1.6261 | 0 | N/A | 0 | 0
2020-12-25 19:30 | 2.3254 | 0 | N/A | 0 | 0
2020-12-25 20:00 | 2.5977 | 0 | N/A | 0 | 0
2020-12-25 20:30 | 2.9268 | 0 | N/A | 0 | 0
2020-12-25 21:00 | 3.2758 | 0 | N/A | 0 | 0
2020-12-25 21:30 | 3.5067 | 0 | N/A | 0 | 0
2020-12-25 22:00 | 3.602 | 0 | N/A | 0 | 0
2020-12-25 22:30 | 4.0762 | 0 | N/A | 0 | 0
2020-12-25 23:00 | 4.348 | 0 | N/A | 0 | 0
2020-12-25 23:30 | 4.1668 | 0 | N/A | 0 | 0
2020-12-26 | 4.304 | 0 | N/A | 0 | 0
2020-12-26 00:30 | 4.5343 | 0 | N/A | 0 | 0
2020-12-26 01:00 | 4.9164 | 0 | N/A | 0 | 0
2020-12-26 01:30 | 4.236 | 0 | N/A | 0 | 0
2020-12-26 02:00 | 3.6225 | 0 | N/A | 0 | 0
2020-12-26 02:30 | 3.5711 | 0 | N/A | 0 | 0
2020-12-26 03:00 | 3.223 | 0 | N/A | 0 | 0
2020-12-26 03:30 | 2.7529 | 0 | N/A | 0 | 0
2020-12-26 04:00 | 2.4773 | 0 | N/A | 0 | 0
2020-12-26 04:30 | 2.2844 | 0 | N/A | 0 | 0
2020-12-26 05:00 | 2.2484 | 0 | N/A | 0 | 0
2020-12-26 05:30 | 2.2242 | 0 | N/A | 0 | 0
2020-12-26 06:00 | 2.2275 | 0 | N/A | 0 | 0
2020-12-26 06:30 | 2.4497 | 0 | N/A | 0 | 0
2020-12-26 07:00 | 2.4779 | 0 | N/A | 0 | 0
2020-12-26 07:30 | 2.511 | 0 | N/A | 0 | 0
2020-12-26 08:00 | 2.255 | 0 | N/A | 0 | 0
2020-12-26 08:30 | 1.6932 | 0 | N/A | 0 | 0
2020-12-26 09:00 | 1.2977 | 0 | N/A | 0 | 0
2020-12-26 09:30 | 0.85506 | 0 | N/A | 0 | 0
2020-12-26 10:00 | 0.51461 | 0 | N/A | 0 | 0
2020-12-26 10:30 | -0.33948 | 0 | N/A | 0 | 0
2020-12-26 11:00 | -0.51451 | 0 | N/A | 0 | 0
2020-12-26 11:30 | -0.79651 | 0 | N/A | 0 | 0
2020-12-26 12:00 | -0.97673 | 0 | N/A | 0 | 0
2020-12-26 12:30 | -1.195 | 0 | N/A | 0 | 0
2020-12-26 13:00 | -1.3572 | 0 | N/A | 0 | 0
2020-12-26 13:30 | -1.4279 | 0 | N/A | 0 | 0
2020-12-26 14:00 | -1.5062 | 0 | N/A | 0 | 0
2020-12-26 14:30 | -1.5138 | 0 | N/A | 0 | 0
2020-12-26 15:00 | -1.3603 | 0 | N/A | 0 | 0
2020-12-26 15:30 | -1.3021 | 0 | N/A | 0 | 0
2020-12-26 16:00 | -1.0559 | 0 | N/A | 0 | 0
2020-12-26 16:30 | -0.67133 | 0 | N/A | 0 | 0
2020-12-26 17:00 | -0.1675 | 0 | N/A | 0 | 0
2020-12-26 17:30 | 0.45966 | 0 | N/A | 0 | 0
2020-12-26 18:00 | 1.2682 | 0 | N/A | 0 | 0
2020-12-26 18:30 | 2.1015 | 0 | N/A | 0 | 0
2020-12-26 19:00 | 2.9271 | 0 | N/A | 0 | 0
2020-12-26 19:30 | 3.2236 | 0 | N/A | 0 | 0
2020-12-26 20:00 | 3.5398 | 0 | N/A | 0 | 0
2020-12-26 20:30 | 3.6953 | 0 | N/A | 0 | 0
2020-12-26 21:00 | 3.5904 | 0 | N/A | 0 | 0
2020-12-26 21:30 | 3.607 | 0 | N/A | 0 | 0
2020-12-26 22:00 | 3.4186 | 0 | N/A | 0 | 0
2020-12-26 22:30 | 3.6343 | 0 | N/A | 0 | 0
2020-12-26 23:00 | 3.8414 | 0 | N/A | 0 | 0
2020-12-26 23:30 | 3.6115 | 0 | N/A | 0 | 0
2020-12-27 | 3.6925 | 0 | N/A | 0 | 0
2020-12-27 00:30 | 3.9755 | 0 | N/A | 0 | 0
2020-12-27 01:00 | 4.2184 | 0 | N/A | 0 | 0
2020-12-27 01:30 | 3.4776 | 0 | N/A | 0 | 0
2020-12-27 02:00 | 2.8955 | 0 | N/A | 0 | 0
2020-12-27 02:30 | 2.7733 | 0 | N/A | 0 | 0
2020-12-27 03:00 | 2.5596 | 0 | N/A | 0 | 0
2020-12-27 03:30 | 2.1733 | 0 | N/A | 0 | 0
2020-12-27 04:00 | 1.9322 | 0 | N/A | 0 | 0
2020-12-27 04:30 | 1.8033 | 0 | N/A | 0 | 0
2020-12-27 05:00 | 1.6966 | 0 | N/A | 0 | 0
2020-12-27 05:30 | 1.7251 | 0 | N/A | 0 | 0
2020-12-27 06:00 | 1.8223 | 0 | N/A | 0 | 0
2020-12-27 06:30 | 1.9213 | 0 | N/A | 0 | 0
2020-12-27 07:00 | 1.9096 | 0 | N/A | 0 | 0
2020-12-27 07:30 | 1.9065 | 0 | N/A | 0 | 0
2020-12-27 08:00 | 2.1937 | 0 | N/A | 0 | 0
2020-12-27 08:30 | 1.847 | 0 | N/A | 0 | 0
2020-12-27 09:00 | 1.5035 | 0 | N/A | 0 | 0
2020-12-27 09:30 | 1.6118 | 0 | N/A | 0 | 0
2020-12-27 10:00 | 1.6067 | 0 | N/A | 0 | 0
2020-12-27 10:30 | 0.9054 | 0 | N/A | 0 | 0
2020-12-27 11:00 | 0.43461 | 0 | N/A | 0 | 0
2020-12-27 11:30 | 0.74017 | 0 | N/A | 0 | 0
2020-12-27 12:00 | 2.317 | 0 | N/A | 0 | 0
2020-12-27 12:30 | 1.7783 | 0 | N/A | 0 | 0
2020-12-27 13:00 | 1.35 | 0 | N/A | 0 | 0
2020-12-27 13:30 | 1.9197 | 0 | N/A | 0 | 0
2020-12-27 14:00 | 2.5039 | 0 | N/A | 0 | 0
2020-12-27 14:30 | 2.4956 | 0 | N/A | 0 | 0
2020-12-27 15:00 | 2.5037 | 0 | N/A | 0 | 0
2020-12-27 15:30 | 2.2948 | 0 | N/A | 0 | 0
2020-12-27 16:00 | 2.2319 | 0 | N/A | 0 | 0
2020-12-27 16:30 | 2.2096 | 0 | N/A | 0 | 0
2020-12-27 17:00 | 2.5028 | 0 | N/A | 0 | 0
2020-12-27 17:30 | 4.4519 | 0 | N/A | 0 | 0
2020-12-27 18:00 | 5.381 | 0 | N/A | 0 | 0
2020-12-27 18:30 | 5.6362 | 0 | N/A | 0 | 0
2020-12-27 19:00 | 5.6439 | 0 | N/A | 0 | 0
2020-12-27 19:30 | 5.6218 | 0 | N/A | 0 | 0
2020-12-27 20:00 | 5.3819 | 0 | N/A | 0 | 0
2020-12-27 20:30 | 5.3088 | 0 | N/A | 0 | 0
2020-12-27 21:00 | 5.2879 | 0 | N/A | 0 | 0
2020-12-27 21:30 | 5.2988 | 0 | N/A | 0 | 0
2020-12-27 22:00 | 5.1304 | 0 | N/A | 0 | 0
2020-12-27 22:30 | 5.5067 | 0 | N/A | 0 | 0
2020-12-27 23:00 | 4.4043 | 0 | N/A | 0 | 0
2020-12-27 23:30 | 3.9086 | 0 | N/A | 0 | 0
2020-12-28 | 4.0019 | 0 | N/A | 0 | 0
2020-12-28 00:30 | 4.419 | 0 | N/A | 0 | 0
2020-12-28 01:00 | 4.765 | 0 | N/A | 0 | 0
2020-12-28 01:30 | 3.985 | 0 | N/A | 0 | 0
2020-12-28 02:00 | 3.3043 | 0 | N/A | 0 | 0
2020-12-28 02:30 | 3.2178 | 0 | N/A | 0 | 0
2020-12-28 03:00 | 2.8474 | 0 | N/A | 0 | 0
2020-12-28 03:30 | 2.4546 | 0 | N/A | 0 | 0
2020-12-28 04:00 | 2.2443 | 0 | N/A | 0 | 0
2020-12-28 04:30 | 2.1462 | 0 | N/A | 0 | 0
2020-12-28 05:00 | 2.0606 | 0 | N/A | 0 | 0
2020-12-28 05:30 | 2.1195 | 0 | N/A | 0 | 0
2020-12-28 06:00 | 2.3059 | 0 | N/A | 0 | 0
2020-12-28 06:30 | 2.4824 | 0 | N/A | 0 | 0
2020-12-28 07:00 | 2.4965 | 0 | N/A | 0 | 0
2020-12-28 07:30 | 2.6314 | 0 | N/A | 0 | 0
2020-12-28 08:00 | 2.5773 | 0 | N/A | 0 | 0
2020-12-28 08:30 | 1.7205 | 0 | N/A | 0 | 0
2020-12-28 09:00 | 1.4083 | 0 | N/A | 0 | 0
2020-12-28 09:30 | 1.2343 | 0 | N/A | 0 | 0
2020-12-28 10:00 | 1.0205 | 0 | N/A | 0 | 0
2020-12-28 10:30 | 0.6996 | 0 | N/A | 0 | 0
2020-12-28 11:00 | 0.65097 | 0 | N/A | 0 | 0
2020-12-28 11:30 | 0.50618 | 0 | N/A | 0 | 0
2020-12-28 12:00 | 0.938 | 0 | N/A | 0 | 0
2020-12-28 12:30 | 0.73182 | 0 | N/A | 0 | 0
2020-12-28 13:00 | 0.3533 | 0 | N/A | 0 | 0
2020-12-28 13:30 | -0.32338 | 0 | N/A | 0 | 0
2020-12-28 14:00 | -0.29614 | 0 | N/A | 0 | 0
2020-12-28 14:30 | -0.54422 | 0 | N/A | 0 | 0
2020-12-28 15:00 | -0.60237 | 0 | N/A | 0 | 0
2020-12-28 15:30 | -0.81693 | 0 | N/A | 0 | 0
2020-12-28 16:00 | -0.55415 | 0 | N/A | 0 | 0
2020-12-28 16:30 | 0.49859 | 0 | N/A | 0 | 0
2020-12-28 17:00 | 0.74748 | 0 | N/A | 0 | 0
2020-12-28 17:30 | 1.9082 | 0 | N/A | 0 | 0
2020-12-28 18:00 | 2.5933 | 0 | N/A | 0 | 0
2020-12-28 18:30 | 2.6693 | 0 | N/A | 0 | 0
2020-12-28 19:00 | 2.8542 | 0 | N/A | 0 | 0
2020-12-28 19:30 | 3.2757 | 0 | N/A | 0 | 0
2020-12-28 20:00 | 3.6289 | 0 | N/A | 0 | 0
2020-12-28 20:30 | 3.631 | 0 | N/A | 0 | 0
2020-12-28 21:00 | 3.841 | 0 | N/A | 0 | 0
2020-12-28 21:30 | 3.9179 | 0 | N/A | 0 | 0
2020-12-28 22:00 | 3.8072 | 0 | N/A | 0 | 0
2020-12-28 22:30 | 4.2093 | 0 | N/A | 0 | 0
2020-12-28 23:00 | 4.3193 | 0 | N/A | 0 | 0
2020-12-28 23:30 | 4.0725 | 0 | N/A | 0 | 0
2020-12-29 | 4.2111 | 0 | N/A | 0 | 0
2020-12-29 00:30 | 4.6021 | 0 | N/A | 0 | 0
2020-12-29 01:00 | 4.8745 | 0 | N/A | 0 | 0
2020-12-29 01:30 | 4.1122 | 0 | N/A | 0 | 0
2020-12-29 02:00 | 3.5441 | 0 | N/A | 0 | 0
2020-12-29 02:30 | 3.5826 | 0 | N/A | 0 | 0
2020-12-29 03:00 | 3.1451 | 0 | N/A | 0 | 0
2020-12-29 03:30 | 2.6915 | 0 | N/A | 0 | 0
2020-12-29 04:00 | 2.4613 | 0 | N/A | 0 | 0
2020-12-29 04:30 | 2.4128 | 0 | N/A | 0 | 0
2020-12-29 05:00 | 2.3854 | 0 | N/A | 0 | 0
2020-12-29 05:30 | 2.394 | 0 | N/A | 0 | 0
2020-12-29 06:00 | 2.5869 | 0 | N/A | 0 | 0
2020-12-29 06:30 | 2.8852 | 0 | N/A | 0 | 0
2020-12-29 07:00 | 2.8695 | 0 | N/A | 0 | 0
2020-12-29 07:30 | 2.9645 | 0 | N/A | 0 | 0
2020-12-29 08:00 | 2.7568 | 0 | N/A | 0 | 0
2020-12-29 08:30 | 2.0704 | 0 | N/A | 0 | 0
2020-12-29 09:00 | 1.5673 | 0 | N/A | 0 | 0
2020-12-29 09:30 | 1.0234 | 0 | N/A | 0 | 0
2020-12-29 10:00 | 0.51317 | 0 | N/A | 0 | 0
2020-12-29 10:30 | -0.45212 | 0 | N/A | 0 | 0
2020-12-29 11:00 | -0.59945 | 0 | N/A | 0 | 0
2020-12-29 11:30 | -0.77107 | 0 | N/A | 0 | 0
2020-12-29 12:00 | -0.5631 | 0 | N/A | 0 | 0
2020-12-29 12:30 | -0.65206 | 0 | N/A | 0 | 0
2020-12-29 13:00 | -0.63217 | 0 | N/A | 0 | 0
2020-12-29 13:30 | -0.73049 | 0 | N/A | 0 | 0
2020-12-29 14:00 | -0.65403 | 0 | N/A | 0 | 0
2020-12-29 14:30 | -0.565 | 0 | N/A | 0 | 0
2020-12-29 15:00 | -0.43533 | 0 | N/A | 0 | 0
2020-12-29 15:30 | -0.35158 | 0 | N/A | 0 | 0
2020-12-29 16:00 | 0.74905 | 0 | N/A | 0 | 0
2020-12-29 16:30 | 1.4073 | 0 | N/A | 0 | 0
2020-12-29 17:00 | 1.4178 | 0 | N/A | 0 | 0
2020-12-29 17:30 | 1.75 | 0 | N/A | 0 | 0
2020-12-29 18:00 | 2.2261 | 0 | N/A | 0 | 0
2020-12-29 18:30 | 2.2776 | 0 | N/A | 0 | 0
2020-12-29 19:00 | 2.7924 | 0 | N/A | 0 | 0
2020-12-29 19:30 | 3.1624 | 0 | N/A | 0 | 0
2020-12-29 20:00 | 3.3884 | 0 | N/A | 0 | 0
2020-12-29 20:30 | 3.5346 | 0 | N/A | 0 | 0
2020-12-29 21:00 | 3.6491 | 0 | N/A | 0 | 0
2020-12-29 21:30 | 3.6497 | 0 | N/A | 0 | 0
2020-12-29 22:00 | 3.4995 | 0 | N/A | 0 | 0
2020-12-29 22:30 | 3.9031 | 0 | N/A | 0 | 0
2020-12-29 23:00 | 4.0748 | 0 | N/A | 0 | 0
2020-12-29 23:30 | 3.7946 | 0 | N/A | 0 | 0
2020-12-30 | 3.8618 | 0 | N/A | 0 | 0
2020-12-30 00:30 | 4.245 | 0 | N/A | 0 | 0
2020-12-30 01:00 | 4.4956 | 0 | N/A | 0 | 0
2020-12-30 01:30 | 3.7423 | 0 | N/A | 0 | 0
2020-12-30 02:00 | 3.1641 | 0 | N/A | 0 | 0
2020-12-30 02:30 | 3.0717 | 0 | N/A | 0 | 0
2020-12-30 03:00 | 2.7892 | 0 | N/A | 0 | 0
2020-12-30 03:30 | 2.3951 | 0 | N/A | 0 | 0
2020-12-30 04:00 | 2.1841 | 0 | N/A | 0 | 0
2020-12-30 04:30 | 2.0685 | 0 | N/A | 0 | 0
2020-12-30 05:00 | 2.0171 | 0 | N/A | 0 | 0
2020-12-30 05:30 | 2.0624 | 0 | N/A | 0 | 0
2020-12-30 06:00 | 2.2368 | 0 | N/A | 0 | 0
2020-12-30 06:30 | 2.4571 | 0 | N/A | 0 | 0
2020-12-30 07:00 | 2.4701 | 0 | N/A | 0 | 0
2020-12-30 07:30 | 2.7113 | 0 | N/A | 0 | 0
2020-12-30 08:00 | 2.8668 | 0 | N/A | 0 | 0
2020-12-30 08:30 | 3.2207 | 0 | N/A | 0 | 0
2020-12-30 09:00 | 3.2598 | 0 | N/A | 0 | 0
2020-12-30 09:30 | 3.1183 | 0 | N/A | 0 | 0
2020-12-30 10:00 | 2.9283 | 0 | N/A | 0 | 0
2020-12-30 10:30 | 2.7787 | 0 | N/A | 0 | 0
2020-12-30 11:00 | 2.2912 | 0 | N/A | 0 | 0
2020-12-30 11:30 | 1.0595 | 0 | N/A | 0 | 0
2020-12-30 12:00 | 0.46077 | 0 | N/A | 0 | 0
2020-12-30 12:30 | -0.5886 | 0 | N/A | 0 | 0
2020-12-30 13:00 | -0.54818 | 0 | N/A | 0 | 0
2020-12-30 13:30 | -1.2047 | 0 | N/A | 0 | 0
2020-12-30 14:00 | -1.0356 | 0 | N/A | 0 | 0
2020-12-30 14:30 | -1.0349 | 0 | N/A | 0 | 0
2020-12-30 15:00 | -1.0379 | 0 | N/A | 0 | 0
2020-12-30 15:30 | -1.333 | 0 | N/A | 0 | 0
2020-12-30 16:00 | -1.0089 | 0 | N/A | 0 | 0
2020-12-30 16:30 | -0.37277 | 0 | N/A | 0 | 0
2020-12-30 17:00 | -0.20069 | 0 | N/A | 0 | 0
2020-12-30 17:30 | 0.77302 | 0 | N/A | 0 | 0
2020-12-30 18:00 | 1.1132 | 0 | N/A | 0 | 0
2020-12-30 18:30 | 2.1229 | 0 | N/A | 0 | 0
2020-12-30 19:00 | 2.5412 | 0 | N/A | 0 | 0
2020-12-30 19:30 | 2.8573 | 0 | N/A | 0 | 0
2020-12-30 20:00 | 3.0673 | 0 | N/A | 0 | 0
2020-12-30 20:30 | 3.3199 | 0 | N/A | 0 | 0
2020-12-30 21:00 | 3.476 | 0 | N/A | 0 | 0
2020-12-30 21:30 | 3.5009 | 0 | N/A | 0 | 0
2020-12-30 22:00 | 3.6223 | 0 | N/A | 0 | 0
2020-12-30 22:30 | 4.1773 | 0 | N/A | 0 | 0
2020-12-30 23:00 | 4.3286 | 0 | N/A | 0 | 0
2020-12-30 23:30 | 4.1097 | 0 | N/A | 0 | 0
2020-12-31 | 4.2356 | 0 | N/A | 0 | 0
2020-12-31 00:30 | 4.601 | 0 | N/A | 0 | 0
2020-12-31 01:00 | 4.7479 | 0 | N/A | 0 | 0
2020-12-31 01:30 | 3.679 | 0 | N/A | 0 | 0
2020-12-31 02:00 | 3.0259 | 0 | N/A | 0 | 0
2020-12-31 02:30 | 3.0023 | 0 | N/A | 0 | 0
2020-12-31 03:00 | 2.7447 | 0 | N/A | 0 | 0
2020-12-31 03:30 | 2.3668 | 0 | N/A | 0 | 0
2020-12-31 04:00 | 2.1368 | 0 | N/A | 0 | 0
2020-12-31 04:30 | 2.0237 | 0 | N/A | 0 | 0
2020-12-31 05:00 | 1.9885 | 0 | N/A | 0 | 0
2020-12-31 05:30 | 2.0642 | 0 | N/A | 0 | 0
2020-12-31 06:00 | 2.1474 | 0 | N/A | 0 | 0
2020-12-31 06:30 | 2.3212 | 0 | N/A | 0 | 0
2020-12-31 07:00 | 2.3686 | 0 | N/A | 0 | 0
2020-12-31 07:30 | 2.6863 | 0 | N/A | 0 | 0
2020-12-31 08:00 | 2.7353 | 0 | N/A | 0 | 0
2020-12-31 08:30 | 2.5086 | 0 | N/A | 0 | 0
2020-12-31 09:00 | 2.7103 | 0 | N/A | 0 | 0
2020-12-31 09:30 | 2.5322 | 0 | N/A | 0 | 0
2020-12-31 10:00 | 2.2742 | 0 | N/A | 0 | 0
2020-12-31 10:30 | 1.8577 | 0 | N/A | 0 | 0
2020-12-31 11:00 | 1.7634 | 0 | N/A | 0 | 0
2020-12-31 11:30 | 1.2903 | 0 | N/A | 0 | 0
2020-12-31 12:00 | 0.69437 | 0 | N/A | 0 | 0
2020-12-31 12:30 | 0.37642 | 0 | N/A | 0 | 0
2020-12-31 13:00 | -0.37845 | 0 | N/A | 0 | 0
2020-12-31 13:30 | -0.43672 | 0 | N/A | 0 | 0
2020-12-31 14:00 | -0.60359 | 0 | N/A | 0 | 0
2020-12-31 14:30 | -0.68134 | 0 | N/A | 0 | 0
2020-12-31 15:00 | -0.93417 | 0 | N/A | 0 | 0
2020-12-31 15:30 | -1.2926 | 0 | N/A | 0 | 0
2020-12-31 16:00 | -1.2319 | 0 | N/A | 0 | 0
2020-12-31 16:30 | -0.81274 | 0 | N/A | 0 | 0
2020-12-31 17:00 | -0.43976 | 0 | N/A | 0 | 0
2020-12-31 17:30 | 0.3769 | 0 | N/A | 0 | 0
2020-12-31 18:00 | 1.3727 | 0 | N/A | 0 | 0
2020-12-31 18:30 | 2.1528 | 0 | N/A | 0 | 0
2020-12-31 19:00 | 2.4456 | 0 | N/A | 0 | 0
2020-12-31 19:30 | 2.8102 | 0 | N/A | 0 | 0
2020-12-31 20:00 | 3.1252 | 0 | N/A | 0 | 0
2020-12-31 20:30 | 3.2261 | 0 | N/A | 0 | 0
2020-12-31 21:00 | 3.252 | 0 | N/A | 0 | 0
2020-12-31 21:30 | 3.2416 | 0 | N/A | 0 | 0
2020-12-31 22:00 | 3.1368 | 0 | N/A | 0 | 0
2020-12-31 22:30 | 3.685 | 0 | N/A | 0 | 0
2020-12-31 23:00 | 3.9542 | 0 | N/A | 0 | 0
2020-12-31 23:30 | 3.7777 | 0 | N/A | 0 | 0
2021-01-01 | 3.9354 | 0 | N/A | 0 | 0
2021-01-01 00:30 | 4.4119 | 0 | N/A | 0 | 0
2021-01-01 01:00 | 4.6724 | 0 | N/A | 0 | 0
2021-01-01 01:30 | 3.7386 | 0 | N/A | 0 | 0
2021-01-01 02:00 | 3.0307 | 0 | N/A | 0 | 0
2021-01-01 02:30 | 2.963 | 0 | N/A | 0 | 0
2021-01-01 03:00 | 2.7107 | 0 | N/A | 0 | 0
2021-01-01 03:30 | 2.2633 | 0 | N/A | 0 | 0
2021-01-01 04:00 | 2.0317 | 0 | N/A | 0 | 0
2021-01-01 04:30 | 1.8761 | 0 | N/A | 0 | 0
2021-01-01 05:00 | 1.818 | 0 | N/A | 0 | 0
2021-01-01 05:30 | 1.8186 | 0 | N/A | 0 | 0
2021-01-01 06:00 | 1.8663 | 0 | N/A | 0 | 0
2021-01-01 06:30 | 2.0077 | 0 | N/A | 0 | 0
2021-01-01 07:00 | 1.8831 | 0 | N/A | 0 | 0
2021-01-01 07:30 | 1.828 | 0 | N/A | 0 | 0
2021-01-01 08:00 | 1.5503 | 0 | N/A | 0 | 0
2021-01-01 08:30 | 1.1664 | 0 | N/A | 0 | 0
2021-01-01 09:00 | 0.93889 | 0 | N/A | 0 | 0
2021-01-01 09:30 | 0.52926 | 0 | N/A | 0 | 0
2021-01-01 10:00 | -0.40613 | 0 | N/A | 0 | 0
2021-01-01 10:30 | -0.51343 | 0 | N/A | 0 | 0
2021-01-01 11:00 | -0.58371 | 0 | N/A | 0 | 0
2021-01-01 11:30 | -0.6741 | 0 | N/A | 0 | 0
2021-01-01 12:00 | -0.27335 | 0 | N/A | 0 | 0
2021-01-01 12:30 | 0.64334 | 0 | N/A | 0 | 0
2021-01-01 13:00 | 0.485 | 0 | N/A | 0 | 0
2021-01-01 13:30 | -0.72241 | 0 | N/A | 0 | 0
2021-01-01 14:00 | -1.1335 | 0 | N/A | 0 | 0
2021-01-01 14:30 | -1.014 | 0 | N/A | 0 | 0
2021-01-01 15:00 | -0.20699 | 0 | N/A | 0 | 0
2021-01-01 15:30 | -0.62057 | 0 | N/A | 0 | 0
2021-01-01 16:00 | -0.30554 | 0 | N/A | 0 | 0
2021-01-01 16:30 | 1.5781 | 0 | N/A | 0 | 0
2021-01-01 17:00 | 2.4557 | 0 | N/A | 0 | 0
2021-01-01 17:30 | 3.0955 | 0 | N/A | 0 | 0
2021-01-01 18:00 | 3.7377 | 0 | N/A | 0 | 0
2021-01-01 18:30 | 4.1781 | 0 | N/A | 0 | 0
2021-01-01 19:00 | 4.3319 | 0 | N/A | 0 | 0
2021-01-01 19:30 | 4.1808 | 0 | N/A | 0 | 0
2021-01-01 20:00 | 3.9409 | 0 | N/A | 0 | 0
2021-01-01 20:30 | 3.7543 | 0 | N/A | 0 | 0
2021-01-01 21:00 | 3.6551 | 0 | N/A | 0 | 0
2021-01-01 21:30 | 3.5697 | 0 | N/A | 0 | 0
2021-01-01 22:00 | 3.3248 | 0 | N/A | 0 | 0
2021-01-01 22:30 | 3.7012 | 0 | N/A | 0 | 0
2021-01-01 23:00 | 3.817 | 0 | N/A | 0 | 0
2021-01-01 23:30 | 3.5653 | 0 | N/A | 0 | 0
2021-01-02 | 3.64 | 0 | N/A | 0 | 0
2021-01-02 00:30 | 4.0967 | 0 | N/A | 0 | 0
2021-01-02 01:00 | 4.2476 | 0 | N/A | 0 | 0
2021-01-02 01:30 | 3.2974 | 0 | N/A | 0 | 0
2021-01-02 02:00 | 2.6817 | 0 | N/A | 0 | 0
2021-01-02 02:30 | 2.6755 | 0 | N/A | 0 | 0
2021-01-02 03:00 | 2.3632 | 0 | N/A | 0 | 0
2021-01-02 03:30 | 1.9888 | 0 | N/A | 0 | 0
2021-01-02 04:00 | 1.9237 | 0 | N/A | 0 | 0
2021-01-02 04:30 | 1.7385 | 0 | N/A | 0 | 0
2021-01-02 05:00 | 1.742 | 0 | N/A | 0 | 0
2021-01-02 05:30 | 1.7387 | 0 | N/A | 0 | 0
2021-01-02 06:00 | 1.8732 | 0 | N/A | 0 | 0
2021-01-02 06:30 | 1.9863 | 0 | N/A | 0 | 0
2021-01-02 07:00 | 1.948 | 0 | N/A | 0 | 0
2021-01-02 07:30 | 2.1199 | 0 | N/A | 0 | 0
2021-01-02 08:00 | 2.1856 | 0 | N/A | 0 | 0
2021-01-02 08:30 | 2.0802 | 0 | N/A | 0 | 0
2021-01-02 09:00 | 1.9355 | 0 | N/A | 0 | 0
2021-01-02 09:30 | 1.2719 | 0 | N/A | 0 | 0
2021-01-02 10:00 | 0.50364 | 0 | N/A | 0 | 0
2021-01-02 10:30 | 1.0106 | 0 | N/A | 0 | 0
2021-01-02 11:00 | 1.5683 | 0 | N/A | 0 | 0
2021-01-02 11:30 | 2.0991 | 0 | N/A | 0 | 0
2021-01-02 12:00 | 2.4537 | 0 | N/A | 0 | 0
2021-01-02 12:30 | 2.1906 | 0 | N/A | 0 | 0
2021-01-02 13:00 | 1.7677 | 0 | N/A | 0 | 0
2021-01-02 13:30 | 1.3645 | 0 | N/A | 0 | 0
2021-01-02 14:00 | 1.1016 | 0 | N/A | 0 | 0
2021-01-02 14:30 | 0.66188 | 0 | N/A | 0 | 0
2021-01-02 15:00 | -0.29153 | 0 | N/A | 0 | 0
2021-01-02 15:30 | 0.52499 | 0 | N/A | 0 | 0
2021-01-02 16:00 | 0.82026 | 0 | N/A | 0 | 0
2021-01-02 16:30 | -0.16465 | 0 | N/A | 0 | 0
2021-01-02 17:00 | 0.70334 | 0 | N/A | 0 | 0
2021-01-02 17:30 | 0.83931 | 0 | N/A | 0 | 0
2021-01-02 18:00 | 2.8788 | 0 | N/A | 0 | 0
2021-01-02 18:30 | 4.1288 | 0 | N/A | 0 | 0
2021-01-02 19:00 | 4.3633 | 0 | N/A | 0 | 0
2021-01-02 19:30 | 4.338 | 0 | N/A | 0 | 0
2021-01-02 20:00 | 4.1232 | 0 | N/A | 0 | 0
2021-01-02 20:30 | 3.8927 | 0 | N/A | 0 | 0
2021-01-02 21:00 | 3.6737 | 0 | N/A | 0 | 0
2021-01-02 21:30 | 3.4724 | 0 | N/A | 0 | 0
2021-01-02 22:00 | 3.2759 | 0 | N/A | 0 | 0
2021-01-02 22:30 | 3.7885 | 0 | N/A | 0 | 0
2021-01-02 23:00 | 4.0601 | 0 | N/A | 0 | 0
2021-01-02 23:30 | 3.8026 | 0 | N/A | 0 | 0
2021-01-03 | 3.7402 | 0 | N/A | 0 | 0
2021-01-03 00:30 | 4.322 | 0 | N/A | 0 | 0
2021-01-03 01:00 | 4.5123 | 0 | N/A | 0 | 0
2021-01-03 01:30 | 3.579 | 0 | N/A | 0 | 0
2021-01-03 02:00 | 2.7865 | 0 | N/A | 0 | 0
2021-01-03 02:30 | 2.7814 | 0 | N/A | 0 | 0
2021-01-03 03:00 | 2.3794 | 0 | N/A | 0 | 0
2021-01-03 03:30 | 2.0221 | 0 | N/A | 0 | 0
2021-01-03 04:00 | 1.847 | 0 | N/A | 0 | 0
2021-01-03 04:30 | 1.7818 | 0 | N/A | 0 | 0
2021-01-03 05:00 | 1.7338 | 0 | N/A | 0 | 0
2021-01-03 05:30 | 1.7821 | 0 | N/A | 0 | 0
2021-01-03 06:00 | 1.8106 | 0 | N/A | 0 | 0
2021-01-03 06:30 | 2.0609 | 0 | N/A | 0 | 0
2021-01-03 07:00 | 2.0314 | 0 | N/A | 0 | 0
2021-01-03 07:30 | 2.2922 | 0 | N/A | 0 | 0
2021-01-03 08:00 | 2.3467 | 0 | N/A | 0 | 0
2021-01-03 08:30 | 1.918 | 0 | N/A | 0 | 0
2021-01-03 09:00 | 1.6484 | 0 | N/A | 0 | 0
2021-01-03 09:30 | 1.0742 | 0 | N/A | 0 | 0
2021-01-03 10:00 | 1.2579 | 0 | N/A | 0 | 0
2021-01-03 10:30 | 0.98387 | 0 | N/A | 0 | 0
2021-01-03 11:00 | 1.1957 | 0 | N/A | 0 | 0
2021-01-03 11:30 | 0.60745 | 0 | N/A | 0 | 0
2021-01-03 12:00 | 0.28302 | 0 | N/A | 0 | 0
2021-01-03 12:30 | -0.3662 | 0 | N/A | 0 | 0
2021-01-03 13:00 | 0.20069 | 0 | N/A | 0 | 0
2021-01-03 13:30 | 0.19925 | 0 | N/A | 0 | 0
2021-01-03 14:00 | 0.20734 | 0 | N/A | 0 | 0
2021-01-03 14:30 | 0.324 | 0 | N/A | 0 | 0
2021-01-03 15:00 | 0.27643 | 0 | N/A | 0 | 0
2021-01-03 15:30 | 0.31934 | 0 | N/A | 0 | 0
2021-01-03 16:00 | 0.51343 | 0 | N/A | 0 | 0
2021-01-03 16:30 | 0.63956 | 0 | N/A | 0 | 0
2021-01-03 17:00 | 0.71779 | 0 | N/A | 0 | 0
2021-01-03 17:30 | 1.2983 | 0 | N/A | 0 | 0
2021-01-03 18:00 | 2.0743 | 0 | N/A | 0 | 0
2021-01-03 18:30 | 2.7986 | 0 | N/A | 0 | 0
2021-01-03 19:00 | 3.0563 | 0 | N/A | 0 | 0
2021-01-03 19:30 | 3.5098 | 0 | N/A | 0 | 0
2021-01-03 20:00 | 3.4904 | 0 | N/A | 0 | 0
2021-01-03 20:30 | 3.4086 | 0 | N/A | 0 | 0
2021-01-03 21:00 | 3.4245 | 0 | N/A | 0 | 0
2021-01-03 21:30 | 3.3587 | 0 | N/A | 0 | 0
2021-01-03 22:00 | 3.2 | 0 | N/A | 0 | 0
2021-01-03 22:30 | 3.6547 | 0 | N/A | 0 | 0
2021-01-03 23:00 | 3.8887 | 0 | N/A | 0 | 0
2021-01-03 23:30 | 3.6392 | 0 | N/A | 0 | 0
2021-01-04 | 3.7319 | 0 | N/A | 0 | 0
2021-01-04 00:30 | 3.9905 | 0 | N/A | 0 | 0
2021-01-04 01:00 | 4.3363 | 0 | N/A | 0 | 0
2021-01-04 01:30 | 3.614 | 0 | N/A | 0 | 0
2021-01-04 02:00 | 2.9275 | 0 | N/A | 0 | 0
2021-01-04 02:30 | 2.8426 | 0 | N/A | 0 | 0
2021-01-04 03:00 | 2.4194 | 0 | N/A | 0 | 0
2021-01-04 03:30 | 2.0799 | 0 | N/A | 0 | 0
2021-01-04 04:00 | 1.8675 | 0 | N/A | 0 | 0
2021-01-04 04:30 | 1.7893 | 0 | N/A | 0 | 0
2021-01-04 05:00 | 1.8077 | 0 | N/A | 0 | 0
2021-01-04 05:30 | 1.9591 | 0 | N/A | 0 | 0
2021-01-04 06:00 | 2.0517 | 0 | N/A | 0 | 0
2021-01-04 06:30 | 2.3458 | 0 | N/A | 0 | 0
2021-01-04 07:00 | 2.5078 | 0 | N/A | 0 | 0
2021-01-04 07:30 | 2.942 | 0 | N/A | 0 | 0
2021-01-04 08:00 | 2.9197 | 0 | N/A | 0 | 0
2021-01-04 08:30 | 2.4972 | 0 | N/A | 0 | 0
2021-01-04 09:00 | 2.5649 | 0 | N/A | 0 | 0
2021-01-04 09:30 | 2.6641 | 0 | N/A | 0 | 0
2021-01-04 10:00 | 2.4567 | 0 | N/A | 0 | 0
2021-01-04 10:30 | 2.0903 | 0 | N/A | 0 | 0
2021-01-04 11:00 | 2.217 | 0 | N/A | 0 | 0
2021-01-04 11:30 | 2.1087 | 0 | N/A | 0 | 0
2021-01-04 12:00 | 2.5602 | 0 | N/A | 0 | 0
2021-01-04 12:30 | 1.8802 | 0 | N/A | 0 | 0
2021-01-04 13:00 | 1.718 | 0 | N/A | 0 | 0
2021-01-04 13:30 | 1.267 | 0 | N/A | 0 | 0
2021-01-04 14:00 | 1.2267 | 0 | N/A | 0 | 0
2021-01-04 14:30 | 0.95949 | 0 | N/A | 0 | 0
2021-01-04 15:00 | 1.5693 | 0 | N/A | 0 | 0
2021-01-04 15:30 | 1.7269 | 0 | N/A | 0 | 0
2021-01-04 16:00 | 2.1115 | 0 | N/A | 0 | 0
2021-01-04 16:30 | 2.7228 | 0 | N/A | 0 | 0
2021-01-04 17:00 | 3.1642 | 0 | N/A | 0 | 0
2021-01-04 17:30 | 3.4922 | 0 | N/A | 0 | 0
2021-01-04 18:00 | 4.1549 | 0 | N/A | 0 | 0
2021-01-04 18:30 | 4.4568 | 0 | N/A | 0 | 0
2021-01-04 19:00 | 4.4714 | 0 | N/A | 0 | 0
2021-01-04 19:30 | 4.1829 | 0 | N/A | 0 | 0
2021-01-04 20:00 | 4.256 | 0 | N/A | 0 | 0
2021-01-04 20:30 | 4.3193 | 0 | N/A | 0 | 0
2021-01-04 21:00 | 4.4268 | 0 | N/A | 0 | 0
2021-01-04 21:30 | 4.218 | 0 | N/A | 0 | 0
2021-01-04 22:00 | 3.9852 | 0 | N/A | 0 | 0
2021-01-04 22:30 | 4.224 | 0 | N/A | 0 | 0
2021-01-04 23:00 | 4.4326 | 0 | N/A | 0 | 0
2021-01-04 23:30 | 4.1165 | 0 | N/A | 0 | 0
2021-01-05 | 4.1644 | 0 | N/A | 0 | 0
2021-01-05 00:30 | 4.4541 | 0 | N/A | 0 | 0
2021-01-05 01:00 | 4.7795 | 0 | N/A | 0 | 0
2021-01-05 01:30 | 3.9053 | 0 | N/A | 0 | 0
2021-01-05 02:00 | 3.1523 | 0 | N/A | 0 | 0
2021-01-05 02:30 | 3.0511 | 0 | N/A | 0 | 0
2021-01-05 03:00 | 2.7043 | 0 | N/A | 0 | 0
2021-01-05 03:30 | 2.3319 | 0 | N/A | 0 | 0
2021-01-05 04:00 | 2.1451 | 0 | N/A | 0 | 0
2021-01-05 04:30 | 2.03 | 0 | N/A | 0 | 0
2021-01-05 05:00 | 2.0482 | 0 | N/A | 0 | 0
2021-01-05 05:30 | 2.1432 | 0 | N/A | 0 | 0
2021-01-05 06:00 | 2.3446 | 0 | N/A | 0 | 0
2021-01-05 06:30 | 2.6122 | 0 | N/A | 0 | 0
2021-01-05 07:00 | 2.766 | 0 | N/A | 0 | 0
2021-01-05 07:30 | 3.096 | 0 | N/A | 0 | 0
2021-01-05 08:00 | 3.1954 | 0 | N/A | 0 | 0
2021-01-05 08:30 | 3.2406 | 0 | N/A | 0 | 0
2021-01-05 09:00 | 3.1364 | 0 | N/A | 0 | 0
2021-01-05 09:30 | 3.1576 | 0 | N/A | 0 | 0
2021-01-05 10:00 | 3.1315 | 0 | N/A | 0 | 0
2021-01-05 10:30 | 2.985 | 0 | N/A | 0 | 0
2021-01-05 11:00 | 2.6221 | 0 | N/A | 0 | 0
2021-01-05 11:30 | 2.6347 | 0 | N/A | 0 | 0
2021-01-05 12:00 | 2.5664 | 0 | N/A | 0 | 0
2021-01-05 12:30 | 2.3725 | 0 | N/A | 0 | 0
2021-01-05 13:00 | 1.9555 | 0 | N/A | 0 | 0
2021-01-05 13:30 | 1.7781 | 0 | N/A | 0 | 0
2021-01-05 14:00 | 1.6199 | 0 | N/A | 0 | 0
2021-01-05 14:30 | 1.6235 | 0 | N/A | 0 | 0
2021-01-05 15:00 | 1.6472 | 0 | N/A | 0 | 0
2021-01-05 15:30 | 2.0103 | 0 | N/A | 0 | 0
2021-01-05 16:00 | 2.1623 | 0 | N/A | 0 | 0
2021-01-05 16:30 | 2.2506 | 0 | N/A | 0 | 0
2021-01-05 17:00 | 2.5857 | 0 | N/A | 0 | 0
2021-01-05 17:30 | 2.9656 | 0 | N/A | 0 | 0
2021-01-05 18:00 | 3.315 | 0 | N/A | 0 | 0
2021-01-05 18:30 | 4.1849 | 0 | N/A | 0 | 0
2021-01-05 19:00 | 4.2492 | 0 | N/A | 0 | 0
2021-01-05 19:30 | 4.1593 | 0 | N/A | 0 | 0
2021-01-05 20:00 | 4.2527 | 0 | N/A | 0 | 0
2021-01-05 20:30 | 4.2443 | 0 | N/A | 0 | 0
2021-01-05 21:00 | 4.2509 | 0 | N/A | 0 | 0
2021-01-05 21:30 | 4.1494 | 0 | N/A | 0 | 0
2021-01-05 22:00 | 3.9174 | 0 | N/A | 0 | 0
2021-01-05 22:30 | 4.2321 | 0 | N/A | 0 | 0
2021-01-05 23:00 | 4.438 | 0 | N/A | 0 | 0
2021-01-05 23:30 | 3.9966 | 0 | N/A | 0 | 0
2021-01-06 | 4.0428 | 0 | N/A | 0 | 0
2021-01-06 00:30 | 4.4909 | 0 | N/A | 0 | 0
2021-01-06 01:00 | 4.8568 | 0 | N/A | 0 | 0
2021-01-06 01:30 | 3.9882 | 0 | N/A | 0 | 0
2021-01-06 02:00 | 3.1655 | 0 | N/A | 0 | 0
2021-01-06 02:30 | 3.0455 | 0 | N/A | 0 | 0
2021-01-06 03:00 | 2.6452 | 0 | N/A | 0 | 0
2021-01-06 03:30 | 2.316 | 0 | N/A | 0 | 0
2021-01-06 04:00 | 2.0935 | 0 | N/A | 0 | 0
2021-01-06 04:30 | 2.0142 | 0 | N/A | 0 | 0
2021-01-06 05:00 | 2.0136 | 0 | N/A | 0 | 0
2021-01-06 05:30 | 2.1321 | 0 | N/A | 0 | 0
2021-01-06 06:00 | 2.3445 | 0 | N/A | 0 | 0
2021-01-06 06:30 | 2.6681 | 0 | N/A | 0 | 0
2021-01-06 07:00 | 2.7991 | 0 | N/A | 0 | 0
2021-01-06 07:30 | 3.215 | 0 | N/A | 0 | 0
2021-01-06 08:00 | 3.3672 | 0 | N/A | 0 | 0
2021-01-06 08:30 | 2.9654 | 0 | N/A | 0 | 0
2021-01-06 09:00 | 2.6691 | 0 | N/A | 0 | 0
2021-01-06 09:30 | 2.3179 | 0 | N/A | 0 | 0
2021-01-06 10:00 | 2.1814 | 0 | N/A | 0 | 0
2021-01-06 10:30 | 1.9476 | 0 | N/A | 0 | 0
2021-01-06 11:00 | 1.6628 | 0 | N/A | 0 | 0
2021-01-06 11:30 | 1.4451 | 0 | N/A | 0 | 0
2021-01-06 12:00 | 1.2944 | 0 | N/A | 0 | 0
2021-01-06 12:30 | 1.5031 | 0 | N/A | 0 | 0
2021-01-06 13:00 | 1.243 | 0 | N/A | 0 | 0
2021-01-06 13:30 | 1.435 | 0 | N/A | 0 | 0
2021-01-06 14:00 | 1.2079 | 0 | N/A | 0 | 0
2021-01-06 14:30 | 0.47479 | 0 | N/A | 0 | 0
2021-01-06 15:00 | 0.4285 | 0 | N/A | 0 | 0
2021-01-06 15:30 | 0.63716 | 0 | N/A | 0 | 0
2021-01-06 16:00 | 0.82492 | 0 | N/A | 0 | 0
2021-01-06 16:30 | 1.3673 | 0 | N/A | 0 | 0
2021-01-06 17:00 | 1.6172 | 0 | N/A | 0 | 0
2021-01-06 17:30 | 2.2999 | 0 | N/A | 0 | 0
2021-01-06 18:00 | 2.629 | 0 | N/A | 0 | 0
2021-01-06 18:30 | 3.0096 | 0 | N/A | 0 | 0
2021-01-06 19:00 | 3.5318 | 0 | N/A | 0 | 0
2021-01-06 19:30 | 3.6572 | 0 | N/A | 0 | 0
2021-01-06 20:00 | 3.8841 | 0 | N/A | 0 | 0
2021-01-06 20:30 | 3.9854 | 0 | N/A | 0 | 0
2021-01-06 21:00 | 4.0994 | 0 | N/A | 0 | 0
2021-01-06 21:30 | 4.0792 | 0 | N/A | 0 | 0
2021-01-06 22:00 | 3.9528 | 0 | N/A | 0 | 0
2021-01-06 22:30 | 4.2804 | 0 | N/A | 0 | 0
2021-01-06 23:00 | 4.3389 | 0 | N/A | 0 | 0
2021-01-06 23:30 | 3.9327 | 0 | N/A | 0 | 0
2021-01-07 | 4.0024 | 0 | N/A | 0 | 0
2021-01-07 00:30 | 4.4823 | 0 | N/A | 0 | 0
2021-01-07 01:00 | 4.7508 | 0 | N/A | 0 | 0
2021-01-07 01:30 | 3.8968 | 0 | N/A | 0 | 0
2021-01-07 02:00 | 3.1694 | 0 | N/A | 0 | 0
2021-01-07 02:30 | 3.1394 | 0 | N/A | 0 | 0
2021-01-07 03:00 | 2.8207 | 0 | N/A | 0 | 0
2021-01-07 03:30 | 2.3887 | 0 | N/A | 0 | 0
2021-01-07 04:00 | 2.0649 | 0 | N/A | 0 | 0
2021-01-07 04:30 | 1.9988 | 0 | N/A | 0 | 0
2021-01-07 05:00 | 2.0247 | 0 | N/A | 0 | 0
2021-01-07 05:30 | 2.1532 | 0 | N/A | 0 | 0
2021-01-07 06:00 | 2.3313 | 0 | N/A | 0 | 0
2021-01-07 06:30 | 2.621 | 0 | N/A | 0 | 0
2021-01-07 07:00 | 2.8111 | 0 | N/A | 0 | 0
2021-01-07 07:30 | 3.2935 | 0 | N/A | 0 | 0
2021-01-07 08:00 | 3.2748 | 0 | N/A | 0 | 0
2021-01-07 08:30 | 2.9466 | 0 | N/A | 0 | 0
2021-01-07 09:00 | 2.6798 | 0 | N/A | 0 | 0
2021-01-07 09:30 | 2.2083 | 0 | N/A | 0 | 0
2021-01-07 10:00 | 1.5281 | 0 | N/A | 0 | 0
2021-01-07 10:30 | 0.76205 | 0 | N/A | 0 | 0
2021-01-07 11:00 | 0.42544 | 0 | N/A | 0 | 0
2021-01-07 11:30 | -0.23835 | 0 | N/A | 0 | 0
2021-01-07 12:00 | -0.64339 | 0 | N/A | 0 | 0
2021-01-07 12:30 | -0.84554 | 0 | N/A | 0 | 0
2021-01-07 13:00 | -1.0445 | 0 | N/A | 0 | 0
2021-01-07 13:30 | -1.0933 | 0 | N/A | 0 | 0
2021-01-07 14:00 | -1.15 | 0 | N/A | 0 | 0
2021-01-07 14:30 | -1.1045 | 0 | N/A | 0 | 0
2021-01-07 15:00 | -0.99792 | 0 | N/A | 0 | 0
2021-01-07 15:30 | -0.40399 | 0 | N/A | 0 | 0
2021-01-07 16:00 | -0.42628 | 0 | N/A | 0 | 0
2021-01-07 16:30 | -0.19351 | 0 | N/A | 0 | 0
2021-01-07 17:00 | 0.36076 | 0 | N/A | 0 | 0
2021-01-07 17:30 | 0.97097 | 0 | N/A | 0 | 0
2021-01-07 18:00 | 1.6977 | 0 | N/A | 0 | 0
2021-01-07 18:30 | 2.5395 | 0 | N/A | 0 | 0
2021-01-07 19:00 | 3.0971 | 0 | N/A | 0 | 0
2021-01-07 19:30 | 3.1957 | 0 | N/A | 0 | 0
2021-01-07 20:00 | 3.4361 | 0 | N/A | 0 | 0
2021-01-07 20:30 | 3.6067 | 0 | N/A | 0 | 0
2021-01-07 21:00 | 3.6408 | 0 | N/A | 0 | 0
2021-01-07 21:30 | 3.6256 | 0 | N/A | 0 | 0
2021-01-07 22:00 | 3.6233 | 0 | N/A | 0 | 0
2021-01-07 22:30 | 3.9354 | 0 | N/A | 0 | 0
2021-01-07 23:00 | 4.0833 | 0 | N/A | 0 | 0
2021-01-07 23:30 | 3.6922 | 0 | N/A | 0 | 0
2021-01-08 | 3.7835 | 0 | N/A | 0 | 0
2021-01-08 00:30 | 4.1768 | 0 | N/A | 0 | 0
2021-01-08 01:00 | 4.4661 | 0 | N/A | 0 | 0
2021-01-08 01:30 | 3.6294 | 0 | N/A | 0 | 0
2021-01-08 02:00 | 2.893 | 0 | N/A | 0 | 0
2021-01-08 02:30 | 2.8892 | 0 | N/A | 0 | 0
2021-01-08 03:00 | 2.5294 | 0 | N/A | 0 | 0
2021-01-08 03:30 | 2.2117 | 0 | N/A | 0 | 0
2021-01-08 04:00 | 1.9616 | 0 | N/A | 0 | 0
2021-01-08 04:30 | 1.8868 | 0 | N/A | 0 | 0
2021-01-08 05:00 | 1.8682 | 0 | N/A | 0 | 0
2021-01-08 05:30 | 2.0642 | 0 | N/A | 0 | 0
2021-01-08 06:00 | 2.2241 | 0 | N/A | 0 | 0
2021-01-08 06:30 | 2.3914 | 0 | N/A | 0 | 0
2021-01-08 07:00 | 2.5083 | 0 | N/A | 0 | 0
2021-01-08 07:30 | 2.8245 | 0 | N/A | 0 | 0
2021-01-08 08:00 | 2.6549 | 0 | N/A | 0 | 0
2021-01-08 08:30 | 2.0543 | 0 | N/A | 0 | 0
2021-01-08 09:00 | 2.8875 | 0 | N/A | 0 | 0
2021-01-08 09:30 | 2.2037 | 0 | N/A | 0 | 0
2021-01-08 10:00 | 0.60296 | 0 | N/A | 0 | 0
2021-01-08 10:30 | -0.24608 | 0 | N/A | 0 | 0
2021-01-08 11:00 | -0.47118 | 0 | N/A | 0 | 0
2021-01-08 11:30 | -0.65575 | 0 | N/A | 0 | 0
2021-01-08 12:00 | -0.83323 | 0 | N/A | 0 | 0
2021-01-08 12:30 | -0.98478 | 0 | N/A | 0 | 0
2021-01-08 13:00 | -1.116 | 0 | N/A | 0 | 0
2021-01-08 13:30 | -1.1113 | 0 | N/A | 0 | 0
2021-01-08 14:00 | -1.1767 | 0 | N/A | 0 | 0
2021-01-08 14:30 | -1.1267 | 0 | N/A | 0 | 0
2021-01-08 15:00 | -1.0067 | 0 | N/A | 0 | 0
2021-01-08 15:30 | -0.86001 | 0 | N/A | 0 | 0
2021-01-08 16:00 | -0.61341 | 0 | N/A | 0 | 0
2021-01-08 16:30 | -0.26213 | 0 | N/A | 0 | 0
2021-01-08 17:00 | 0.19128 | 0 | N/A | 0 | 0
2021-01-08 17:30 | 0.83353 | 0 | N/A | 0 | 0
2021-01-08 18:00 | 1.6337 | 0 | N/A | 0 | 0
2021-01-08 18:30 | 2.4469 | 0 | N/A | 0 | 0
2021-01-08 19:00 | 3.0495 | 0 | N/A | 0 | 0
2021-01-08 19:30 | 3.4668 | 0 | N/A | 0 | 0
2021-01-08 20:00 | 3.6699 | 0 | N/A | 0 | 0
2021-01-08 20:30 | 3.7105 | 0 | N/A | 0 | 0
2021-01-08 21:00 | 3.6912 | 0 | N/A | 0 | 0
2021-01-08 21:30 | 3.7006 | 0 | N/A | 0 | 0
2021-01-08 22:00 | 3.5257 | 0 | N/A | 0 | 0
2021-01-08 22:30 | 3.951 | 0 | N/A | 0 | 0
2021-01-08 23:00 | 4.09 | 0 | N/A | 0 | 0
2021-01-08 23:30 | 3.6526 | 0 | N/A | 0 | 0
2021-01-09 | 3.7844 | 0 | N/A | 0 | 0
2021-01-09 00:30 | 4.2205 | 0 | N/A | 0 | 0
2021-01-09 01:00 | 4.3334 | 0 | N/A | 0 | 0
2021-01-09 01:30 | 3.4447 | 0 | N/A | 0 | 0
2021-01-09 02:00 | 2.7821 | 0 | N/A | 0 | 0
2021-01-09 02:30 | 2.7463 | 0 | N/A | 0 | 0
2021-01-09 03:00 | 2.3879 | 0 | N/A | 0 | 0
2021-01-09 03:30 | 2.0777 | 0 | N/A | 0 | 0
2021-01-09 04:00 | 1.9239 | 0 | N/A | 0 | 0
2021-01-09 04:30 | 1.7875 | 0 | N/A | 0 | 0
2021-01-09 05:00 | 1.7696 | 0 | N/A | 0 | 0
2021-01-09 05:30 | 1.8024 | 0 | N/A | 0 | 0
2021-01-09 06:00 | 1.9244 | 0 | N/A | 0 | 0
2021-01-09 06:30 | 2.1835 | 0 | N/A | 0 | 0
2021-01-09 07:00 | 2.1095 | 0 | N/A | 0 | 0
2021-01-09 07:30 | 2.2015 | 0 | N/A | 0 | 0
2021-01-09 08:00 | 2.0663 | 0 | N/A | 0 | 0
2021-01-09 08:30 | 1.5793 | 0 | N/A | 0 | 0
2021-01-09 09:00 | 1.2202 | 0 | N/A | 0 | 0
2021-01-09 09:30 | 0.81118 | 0 | N/A | 0 | 0
2021-01-09 10:00 | 0.34209 | 0 | N/A | 0 | 0
2021-01-09 10:30 | -0.22191 | 0 | N/A | 0 | 0
2021-01-09 11:00 | -0.39419 | 0 | N/A | 0 | 0
2021-01-09 11:30 | -0.64438 | 0 | N/A | 0 | 0
2021-01-09 12:00 | -0.7334 | 0 | N/A | 0 | 0
2021-01-09 12:30 | -0.78333 | 0 | N/A | 0 | 0
2021-01-09 13:00 | -0.81333 | 0 | N/A | 0 | 0
2021-01-09 13:30 | -0.58333 | 0 | N/A | 0 | 0
2021-01-09 14:00 | -0.58368 | 0 | N/A | 0 | 0
2021-01-09 14:30 | -0.45079 | 0 | N/A | 0 | 0
2021-01-09 15:00 | -0.20177 | 0 | N/A | 0 | 0
2021-01-09 15:30 | 0.078031 | 0 | N/A | 0 | 0
2021-01-09 16:00 | 0.43345 | 0 | N/A | 0 | 0
2021-01-09 16:30 | 0.98009 | 0 | N/A | 0 | 0
2021-01-09 17:00 | 1.7675 | 0 | N/A | 0 | 0
2021-01-09 17:30 | 2.6748 | 0 | N/A | 0 | 0
2021-01-09 18:00 | 3.5942 | 0 | N/A | 0 | 0
2021-01-09 18:30 | 4.3755 | 0 | N/A | 0 | 0
2021-01-09 19:00 | 4.9678 | 0 | N/A | 0 | 0
2021-01-09 19:30 | 5.2768 | 0 | N/A | 0 | 0
2021-01-09 20:00 | 5.4467 | 0 | N/A | 0 | 0
2021-01-09 20:30 | 5.0667 | 0 | N/A | 0 | 0
2021-01-09 21:00 | 4.6768 | 0 | N/A | 0 | 0
2021-01-09 21:30 | 4.4111 | 0 | N/A | 0 | 0
2021-01-09 22:00 | 4.0204 | 0 | N/A | 0 | 0
2021-01-09 22:30 | 4.3095 | 0 | N/A | 0 | 0
2021-01-09 23:00 | 4.3559 | 0 | N/A | 0 | 0
2021-01-09 23:30 | 3.8987 | 0 | N/A | 0 | 0
2021-01-10 | 3.9564 | 0 | N/A | 0 | 0
2021-01-10 00:30 | 4.2661 | 0 | N/A | 0 | 0
2021-01-10 01:00 | 4.4604 | 0 | N/A | 0 | 0
2021-01-10 01:30 | 3.4611 | 0 | N/A | 0 | 0
2021-01-10 02:00 | 2.7757 | 0 | N/A | 0 | 0
2021-01-10 02:30 | 2.7758 | 0 | N/A | 0 | 0
2021-01-10 03:00 | 2.4618 | 0 | N/A | 0 | 0
2021-01-10 03:30 | 2.0584 | 0 | N/A | 0 | 0
2021-01-10 04:00 | 1.9058 | 0 | N/A | 0 | 0
2021-01-10 04:30 | 1.8177 | 0 | N/A | 0 | 0
2021-01-10 05:00 | 1.8043 | 0 | N/A | 0 | 0
2021-01-10 05:30 | 1.7604 | 0 | N/A | 0 | 0
2021-01-10 06:00 | 1.8489 | 0 | N/A | 0 | 0
2021-01-10 06:30 | 1.9472 | 0 | N/A | 0 | 0
2021-01-10 07:00 | 1.9945 | 0 | N/A | 0 | 0
2021-01-10 07:30 | 2.0864 | 0 | N/A | 0 | 0
2021-01-10 08:00 | 1.8947 | 0 | N/A | 0 | 0
2021-01-10 08:30 | 1.477 | 0 | N/A | 0 | 0
2021-01-10 09:00 | 1.1554 | 0 | N/A | 0 | 0
2021-01-10 09:30 | 0.80217 | 0 | N/A | 0 | 0
2021-01-10 10:00 | 0.49334 | 0 | N/A | 0 | 0
2021-01-10 10:30 | 0.31077 | 0 | N/A | 0 | 0
2021-01-10 11:00 | 0.14621 | 0 | N/A | 0 | 0
2021-01-10 11:30 | 0.14333 | 0 | N/A | 0 | 0
2021-01-10 12:00 | 0.19667 | 0 | N/A | 0 | 0
2021-01-10 12:30 | 0.36818 | 0 | N/A | 0 | 0
2021-01-10 13:00 | 0.50148 | 0 | N/A | 0 | 0
2021-01-10 13:30 | 0.77274 | 0 | N/A | 0 | 0
2021-01-10 14:00 | 1.5292 | 0 | N/A | 0 | 0
2021-01-10 14:30 | 1.9281 | 0 | N/A | 0 | 0
2021-01-10 15:00 | 2.0441 | 0 | N/A | 0 | 0
2021-01-10 15:30 | 2.6353 | 0 | N/A | 0 | 0
2021-01-10 16:00 | 3.001 | 0 | N/A | 0 | 0
2021-01-10 16:30 | 4.1371 | 0 | N/A | 0 | 0
2021-01-10 17:00 | 4.6798 | 0 | N/A | 0 | 0
2021-01-10 17:30 | 5.2753 | 0 | N/A | 0 | 0
2021-01-10 18:00 | 5.5355 | 0 | N/A | 0 | 0
2021-01-10 18:30 | 6.3909 | 0 | N/A | 0 | 0
2021-01-10 19:00 | 7.2989 | 0 | N/A | 0 | 0
2021-01-10 19:30 | 6.9802 | 0 | N/A | 0 | 0
2021-01-10 20:00 | 6.6353 | 0 | N/A | 0 | 0
2021-01-10 20:30 | 6.1634 | 0 | N/A | 0 | 0
2021-01-10 21:00 | 5.6667 | 0 | N/A | 0 | 0
2021-01-10 21:30 | 5.1167 | 0 | N/A | 0 | 0
2021-01-10 22:00 | 4.6803 | 0 | N/A | 0 | 0
2021-01-10 22:30 | 4.8183 | 0 | N/A | 0 | 0
2021-01-10 23:00 | 4.7325 | 0 | N/A | 0 | 0
2021-01-10 23:30 | 4.2822 | 0 | N/A | 0 | 0
2021-01-11 | 4.2222 | 0 | N/A | 0 | 0
2021-01-11 00:30 | 4.5245 | 0 | N/A | 0 | 0
2021-01-11 01:00 | 4.6254 | 0 | N/A | 0 | 0
2021-01-11 01:30 | 3.6103 | 0 | N/A | 0 | 0
2021-01-11 02:00 | 2.9645 | 0 | N/A | 0 | 0
2021-01-11 02:30 | 2.9571 | 0 | N/A | 0 | 0
2021-01-11 03:00 | 2.5721 | 0 | N/A | 0 | 0
2021-01-11 03:30 | 2.2381 | 0 | N/A | 0 | 0
2021-01-11 04:00 | 2.1182 | 0 | N/A | 0 | 0
2021-01-11 04:30 | 2.0179 | 0 | N/A | 0 | 0
2021-01-11 05:00 | 2.0665 | 0 | N/A | 0 | 0
2021-01-11 05:30 | 2.1906 | 0 | N/A | 0 | 0
2021-01-11 06:00 | 2.4108 | 0 | N/A | 0 | 0
2021-01-11 06:30 | 2.7431 | 0 | N/A | 0 | 0
2021-01-11 07:00 | 2.8884 | 0 | N/A | 0 | 0
2021-01-11 07:30 | 3.1493 | 0 | N/A | 0 | 0
2021-01-11 08:00 | 3.0717 | 0 | N/A | 0 | 0
2021-01-11 08:30 | 2.6223 | 0 | N/A | 0 | 0
2021-01-11 09:00 | 2.3735 | 0 | N/A | 0 | 0
2021-01-11 09:30 | 2.2453 | 0 | N/A | 0 | 0
2021-01-11 10:00 | 2.0686 | 0 | N/A | 0 | 0
2021-01-11 10:30 | 1.65 | 0 | N/A | 0 | 0
2021-01-11 11:00 | 1.8743 | 0 | N/A | 0 | 0
2021-01-11 11:30 | 2.0724 | 0 | N/A | 0 | 0
2021-01-11 12:00 | 3.1117 | 0 | N/A | 0 | 0
2021-01-11 12:30 | 3.1183 | 0 | N/A | 0 | 0
2021-01-11 13:00 | 3.608 | 0 | N/A | 0 | 0
2021-01-11 13:30 | 3.2787 | 0 | N/A | 0 | 0
2021-01-11 14:00 | 3.1581 | 0 | N/A | 0 | 0
2021-01-11 14:30 | 3.5846 | 0 | N/A | 0 | 0
2021-01-11 15:00 | 3.7596 | 0 | N/A | 0 | 0
2021-01-11 15:30 | 3.7742 | 0 | N/A | 0 | 0
2021-01-11 16:00 | 4.0589 | 0 | N/A | 0 | 0
2021-01-11 16:30 | 4.696 | 0 | N/A | 0 | 0
2021-01-11 17:00 | 5.4747 | 0 | N/A | 0 | 0
2021-01-11 17:30 | 6.4391 | 0 | N/A | 0 | 0
2021-01-11 18:00 | 7.273 | 0 | N/A | 0 | 0
2021-01-11 18:30 | 7.0203 | 0 | N/A | 0 | 0
2021-01-11 19:00 | 7.4998 | 0 | N/A | 0 | 0
2021-01-11 19:30 | 7.5007 | 0 | N/A | 0 | 0
2021-01-11 20:00 | 7.172 | 0 | N/A | 0 | 0
2021-01-11 20:30 | 6.786 | 0 | N/A | 0 | 0
2021-01-11 21:00 | 6.3482 | 0 | N/A | 0 | 0
2021-01-11 21:30 | 5.6136 | 0 | N/A | 0 | 0
2021-01-11 22:00 | 4.8867 | 0 | N/A | 0 | 0
2021-01-11 22:30 | 4.9274 | 0 | N/A | 0 | 0
2021-01-11 23:00 | 4.8079 | 0 | N/A | 0 | 0
2021-01-11 23:30 | 4.2863 | 0 | N/A | 0 | 0
2021-01-12 | 4.1951 | 0 | N/A | 0 | 0
2021-01-12 00:30 | 4.577 | 0 | N/A | 0 | 0
2021-01-12 01:00 | 4.6549 | 0 | N/A | 0 | 0
2021-01-12 01:30 | 3.515 | 0 | N/A | 0 | 0
2021-01-12 02:00 | 2.7353 | 0 | N/A | 0 | 0
2021-01-12 02:30 | 2.7904 | 0 | N/A | 0 | 0
2021-01-12 03:00 | 2.4436 | 0 | N/A | 0 | 0
2021-01-12 03:30 | 2.1667 | 0 | N/A | 0 | 0
2021-01-12 04:00 | 2.0737 | 0 | N/A | 0 | 0
2021-01-12 04:30 | 1.994 | 0 | N/A | 0 | 0
2021-01-12 05:00 | 2.0587 | 0 | N/A | 0 | 0
2021-01-12 05:30 | 2.1804 | 0 | N/A | 0 | 0
2021-01-12 06:00 | 2.3227 | 0 | N/A | 0 | 0
2021-01-12 06:30 | 2.7584 | 0 | N/A | 0 | 0
2021-01-12 07:00 | 2.8359 | 0 | N/A | 0 | 0
2021-01-12 07:30 | 3.0234 | 0 | N/A | 0 | 0
2021-01-12 08:00 | 2.7748 | 0 | N/A | 0 | 0
2021-01-12 08:30 | 2.351 | 0 | N/A | 0 | 0
2021-01-12 09:00 | 2.1719 | 0 | N/A | 0 | 0
2021-01-12 09:30 | 1.6337 | 0 | N/A | 0 | 0
2021-01-12 10:00 | 1.1577 | 0 | N/A | 0 | 0
2021-01-12 10:30 | 0.52693 | 0 | N/A | 0 | 0
2021-01-12 11:00 | -0.066999 | 0 | N/A | 0 | 0
2021-01-12 11:30 | -0.21982 | 0 | N/A | 0 | 0
2021-01-12 12:00 | -0.35901 | 0 | N/A | 0 | 0
2021-01-12 12:30 | -0.44944 | 0 | N/A | 0 | 0
2021-01-12 13:00 | -0.4672 | 0 | N/A | 0 | 0
2021-01-12 13:30 | -0.5308 | 0 | N/A | 0 | 0
2021-01-12 14:00 | -0.53344 | 0 | N/A | 0 | 0
2021-01-12 14:30 | -0.56964 | 0 | N/A | 0 | 0
2021-01-12 15:00 | -0.49875 | 0 | N/A | 0 | 0
2021-01-12 15:30 | -0.33119 | 0 | N/A | 0 | 0
2021-01-12 16:00 | -0.28097 | 0 | N/A | 0 | 0
2021-01-12 16:30 | 0.15442 | 0 | N/A | 0 | 0
2021-01-12 17:00 | 0.4691 | 0 | N/A | 0 | 0
2021-01-12 17:30 | 1.16 | 0 | N/A | 0 | 0
2021-01-12 18:00 | 2.0733 | 0 | N/A | 0 | 0
2021-01-12 18:30 | 2.7511 | 0 | N/A | 0 | 0
2021-01-12 19:00 | 3.3654 | 0 | N/A | 0 | 0
2021-01-12 19:30 | 3.7072 | 0 | N/A | 0 | 0
2021-01-12 20:00 | 3.8689 | 0 | N/A | 0 | 0
2021-01-12 20:30 | 3.8759 | 0 | N/A | 0 | 0
2021-01-12 21:00 | 3.8556 | 0 | N/A | 0 | 0
2021-01-12 21:30 | 3.7437 | 0 | N/A | 0 | 0
2021-01-12 22:00 | 3.5592 | 0 | N/A | 0 | 0
2021-01-12 22:30 | 3.9006 | 0 | N/A | 0 | 0
2021-01-12 23:00 | 4.0167 | 0 | N/A | 0 | 0
2021-01-12 23:30 | 3.6421 | 0 | N/A | 0 | 0
2021-01-13 | 3.7105 | 0 | N/A | 0 | 0
2021-01-13 00:30 | 4.1374 | 0 | N/A | 0 | 0
2021-01-13 01:00 | 4.2288 | 0 | N/A | 0 | 0
2021-01-13 01:30 | 3.2093 | 0 | N/A | 0 | 0
2021-01-13 02:00 | 2.5224 | 0 | N/A | 0 | 0
2021-01-13 02:30 | 2.5655 | 0 | N/A | 0 | 0
2021-01-13 03:00 | 2.3134 | 0 | N/A | 0 | 0
2021-01-13 03:30 | 2.0282 | 0 | N/A | 0 | 0
2021-01-13 04:00 | 1.9289 | 0 | N/A | 0 | 0
2021-01-13 04:30 | 1.9141 | 0 | N/A | 0 | 0
2021-01-13 05:00 | 1.8385 | 0 | N/A | 0 | 0
2021-01-13 05:30 | 2.1021 | 0 | N/A | 0 | 0
2021-01-13 06:00 | 2.2963 | 0 | N/A | 0 | 0
2021-01-13 06:30 | 2.6578 | 0 | N/A | 0 | 0
2021-01-13 07:00 | 2.847 | 0 | N/A | 0 | 0
2021-01-13 07:30 | 3.1444 | 0 | N/A | 0 | 0
2021-01-13 08:00 | 3.0595 | 0 | N/A | 0 | 0
2021-01-13 08:30 | 2.1312 | 0 | N/A | 0 | 0
2021-01-13 09:00 | 1.6825 | 0 | N/A | 0 | 0
2021-01-13 09:30 | 1.0817 | 0 | N/A | 0 | 0
2021-01-13 10:00 | 0.46174 | 0 | N/A | 0 | 0
2021-01-13 10:30 | 0.22251 | 0 | N/A | 0 | 0
2021-01-13 11:00 | 0.76012 | 0 | N/A | 0 | 0
2021-01-13 11:30 | 1.2863 | 0 | N/A | 0 | 0
2021-01-13 12:00 | 0.43391 | 0 | N/A | 0 | 0
2021-01-13 12:30 | 0.98284 | 0 | N/A | 0 | 0
2021-01-13 13:00 | -0.42038 | 0 | N/A | 0 | 0
2021-01-13 13:30 | 0.57513 | 0 | N/A | 0 | 0
2021-01-13 14:00 | 1.659 | 0 | N/A | 0 | 0
2021-01-13 14:30 | 0.78894 | 0 | N/A | 0 | 0
2021-01-13 15:00 | 1.0325 | 0 | N/A | 0 | 0
2021-01-13 15:30 | 2.0574 | 0 | N/A | 0 | 0
2021-01-13 16:00 | 2.6103 | 0 | N/A | 0 | 0
2021-01-13 16:30 | 3.7105 | 0 | N/A | 0 | 0
2021-01-13 17:00 | 4.1818 | 0 | N/A | 0 | 0
2021-01-13 17:30 | 4.7579 | 0 | N/A | 0 | 0
2021-01-13 18:00 | 4.8639 | 0 | N/A | 0 | 0
2021-01-13 18:30 | 4.5768 | 0 | N/A | 0 | 0
2021-01-13 19:00 | 3.7233 | 0 | N/A | 0 | 0
2021-01-13 19:30 | 3.9536 | 0 | N/A | 0 | 0
2021-01-13 20:00 | 4.294 | 0 | N/A | 0 | 0
2021-01-13 20:30 | 4.3122 | 0 | N/A | 0 | 0
2021-01-13 21:00 | 4.211 | 0 | N/A | 0 | 0
2021-01-13 21:30 | 4.0401 | 0 | N/A | 0 | 0
2021-01-13 22:00 | 3.7404 | 0 | N/A | 0 | 0
2021-01-13 22:30 | 3.9662 | 0 | N/A | 0 | 0
2021-01-13 23:00 | 4.0227 | 0 | N/A | 0 | 0
2021-01-13 23:30 | 3.6653 | 0 | N/A | 0 | 0
2021-01-14 | 3.6299 | 0 | N/A | 0 | 0
2021-01-14 00:30 | 4.1027 | 0 | N/A | 0 | 0
2021-01-14 01:00 | 4.2546 | 0 | N/A | 0 | 0
2021-01-14 01:30 | 3.2491 | 0 | N/A | 0 | 0
2021-01-14 02:00 | 2.6109 | 0 | N/A | 0 | 0
2021-01-14 02:30 | 2.5494 | 0 | N/A | 0 | 0
2021-01-14 03:00 | 2.2711 | 0 | N/A | 0 | 0
2021-01-14 03:30 | 1.9944 | 0 | N/A | 0 | 0
2021-01-14 04:00 | 1.8696 | 0 | N/A | 0 | 0
2021-01-14 04:30 | 1.8316 | 0 | N/A | 0 | 0
2021-01-14 05:00 | 1.8861 | 0 | N/A | 0 | 0
2021-01-14 05:30 | 2.0528 | 0 | N/A | 0 | 0
2021-01-14 06:00 | 2.2244 | 0 | N/A | 0 | 0
2021-01-14 06:30 | 2.6609 | 0 | N/A | 0 | 0
2021-01-14 07:00 | 2.9395 | 0 | N/A | 0 | 0
2021-01-14 07:30 | 3.4179 | 0 | N/A | 0 | 0
2021-01-14 08:00 | 3.2077 | 0 | N/A | 0 | 0
2021-01-14 08:30 | 3.0107 | 0 | N/A | 0 | 0
2021-01-14 09:00 | 2.9002 | 0 | N/A | 0 | 0
2021-01-14 09:30 | 2.4972 | 0 | N/A | 0 | 0
2021-01-14 10:00 | 1.9851 | 0 | N/A | 0 | 0
2021-01-14 10:30 | 2.0067 | 0 | N/A | 0 | 0
2021-01-14 11:00 | 1.9767 | 0 | N/A | 0 | 0
2021-01-14 11:30 | 1.7646 | 0 | N/A | 0 | 0
2021-01-14 12:00 | 1.7737 | 0 | N/A | 0 | 0
2021-01-14 12:30 | 1.6467 | 0 | N/A | 0 | 0
2021-01-14 13:00 | 1.1367 | 0 | N/A | 0 | 0
2021-01-14 13:30 | 0.90437 | 0 | N/A | 0 | 0
2021-01-14 14:00 | 1.174 | 0 | N/A | 0 | 0
2021-01-14 14:30 | 0.70995 | 0 | N/A | 0 | 0
2021-01-14 15:00 | 1.0237 | 0 | N/A | 0 | 0
2021-01-14 15:30 | 1.0982 | 0 | N/A | 0 | 0
2021-01-14 16:00 | 1.2301 | 0 | N/A | 0 | 0
2021-01-14 16:30 | 1.0343 | 0 | N/A | 0 | 0
2021-01-14 17:00 | 1.0215 | 0 | N/A | 0 | 0
2021-01-14 17:30 | 1.6347 | 0 | N/A | 0 | 0
2021-01-14 18:00 | 1.9588 | 0 | N/A | 0 | 0
2021-01-14 18:30 | 2.3002 | 0 | N/A | 0 | 0
2021-01-14 19:00 | 2.7789 | 0 | N/A | 0 | 0
2021-01-14 19:30 | 3.1628 | 0 | N/A | 0 | 0
2021-01-14 20:00 | 3.3809 | 0 | N/A | 0 | 0
2021-01-14 20:30 | 3.631 | 0 | N/A | 0 | 0
2021-01-14 21:00 | 3.7495 | 0 | N/A | 0 | 0
2021-01-14 21:30 | 3.7328 | 0 | N/A | 0 | 0
2021-01-14 22:00 | 3.6178 | 0 | N/A | 0 | 0
2021-01-14 22:30 | 4.0431 | 0 | N/A | 0 | 0
2021-01-14 23:00 | 4.1143 | 0 | N/A | 0 | 0
2021-01-14 23:30 | 3.712 | 0 | N/A | 0 | 0
2021-01-15 | 3.7576 | 0 | N/A | 0 | 0
2021-01-15 00:30 | 4.2726 | 0 | N/A | 0 | 0
2021-01-15 01:00 | 4.44 | 0 | N/A | 0 | 0
2021-01-15 01:30 | 3.491 | 0 | N/A | 0 | 0
2021-01-15 02:00 | 2.8466 | 0 | N/A | 0 | 0
2021-01-15 02:30 | 2.8879 | 0 | N/A | 0 | 0
2021-01-15 03:00 | 2.5119 | 0 | N/A | 0 | 0
2021-01-15 03:30 | 2.2285 | 0 | N/A | 0 | 0
2021-01-15 04:00 | 2.0311 | 0 | N/A | 0 | 0
2021-01-15 04:30 | 1.981 | 0 | N/A | 0 | 0
2021-01-15 05:00 | 2.038 | 0 | N/A | 0 | 0
2021-01-15 05:30 | 2.1524 | 0 | N/A | 0 | 0
2021-01-15 06:00 | 2.3803 | 0 | N/A | 0 | 0
2021-01-15 06:30 | 2.8033 | 0 | N/A | 0 | 0
2021-01-15 07:00 | 3.0918 | 0 | N/A | 0 | 0
2021-01-15 07:30 | 3.3733 | 0 | N/A | 0 | 0
2021-01-15 08:00 | 3.6982 | 0 | N/A | 0 | 0
2021-01-15 08:30 | 3.6189 | 0 | N/A | 0 | 0
2021-01-15 09:00 | 3.9237 | 0 | N/A | 0 | 0
2021-01-15 09:30 | 3.4305 | 0 | N/A | 0 | 0
2021-01-15 10:00 | 2.7392 | 0 | N/A | 0 | 0
2021-01-15 10:30 | 2.7169 | 0 | N/A | 0 | 0
2021-01-15 11:00 | 1.3675 | 0 | N/A | 0 | 0
2021-01-15 11:30 | 1.3062 | 0 | N/A | 0 | 0
2021-01-15 12:00 | 1.2346 | 0 | N/A | 0 | 0
2021-01-15 12:30 | 1.3753 | 0 | N/A | 0 | 0
2021-01-15 13:00 | 0.35971 | 0 | N/A | 0 | 0
2021-01-15 13:30 | 0.99712 | 0 | N/A | 0 | 0
2021-01-15 14:00 | 1.9333 | 0 | N/A | 0 | 0
2021-01-15 14:30 | 2.6034 | 0 | N/A | 0 | 0
2021-01-15 15:00 | 0.87397 | 0 | N/A | 0 | 0
2021-01-15 15:30 | 0.58701 | 0 | N/A | 0 | 0
2021-01-15 16:00 | 0.49442 | 0 | N/A | 0 | 0
2021-01-15 16:30 | 2.4254 | 0 | N/A | 0 | 0
2021-01-15 17:00 | 1.9631 | 0 | N/A | 0 | 0
2021-01-15 17:30 | 1.1027 | 0 | N/A | 0 | 0
2021-01-15 18:00 | 2.5659 | 0 | N/A | 0 | 0
2021-01-15 18:30 | 2.9736 | 0 | N/A | 0 | 0
2021-01-15 19:00 | 3.7955 | 0 | N/A | 0 | 0
2021-01-15 19:30 | 5.1032 | 0 | N/A | 0 | 0
2021-01-15 20:00 | 5.8719 | 0 | N/A | 0 | 0
2021-01-15 20:30 | 6.1044 | 0 | N/A | 0 | 0
2021-01-15 21:00 | 6.2561 | 0 | N/A | 0 | 0
2021-01-15 21:30 | 6.1573 | 0 | N/A | 0 | 0
2021-01-15 22:00 | 5.4798 | 0 | N/A | 0 | 0
2021-01-15 22:30 | 5.7265 | 0 | N/A | 0 | 0
2021-01-15 23:00 | 5.9078 | 0 | N/A | 0 | 0
2021-01-15 23:30 | 5.4424 | 0 | N/A | 0 | 0
2021-01-16 | 5.3247 | 0 | N/A | 0 | 0
2021-01-16 00:30 | 5.7935 | 0 | N/A | 0 | 0
2021-01-16 01:00 | 6.1448 | 0 | N/A | 0 | 0
2021-01-16 01:30 | 5.0723 | 0 | N/A | 0 | 0
2021-01-16 02:00 | 4.322 | 0 | N/A | 0 | 0
2021-01-16 02:30 | 3.6569 | 0 | N/A | 0 | 0
2021-01-16 03:00 | 3.297 | 0 | N/A | 0 | 0
2021-01-16 03:30 | 2.9856 | 0 | N/A | 0 | 0
2021-01-16 04:00 | 2.7729 | 0 | N/A | 0 | 0
2021-01-16 04:30 | 2.6321 | 0 | N/A | 0 | 0
2021-01-16 05:00 | 2.624 | 0 | N/A | 0 | 0
2021-01-16 05:30 | 2.6485 | 0 | N/A | 0 | 0
2021-01-16 06:00 | 2.7857 | 0 | N/A | 0 | 0
2021-01-16 06:30 | 2.9064 | 0 | N/A | 0 | 0
2021-01-16 07:00 | 3.056 | 0 | N/A | 0 | 0
2021-01-16 07:30 | 3.3157 | 0 | N/A | 0 | 0
2021-01-16 08:00 | 3.474 | 0 | N/A | 0 | 0
2021-01-16 08:30 | 3.1692 | 0 | N/A | 0 | 0
2021-01-16 09:00 | 3.3074 | 0 | N/A | 0 | 0
2021-01-16 09:30 | 3.1627 | 0 | N/A | 0 | 0
2021-01-16 10:00 | 3.3418 | 0 | N/A | 0 | 0
2021-01-16 10:30 | 3.4153 | 0 | N/A | 0 | 0
2021-01-16 11:00 | 3.4875 | 0 | N/A | 0 | 0
2021-01-16 11:30 | 3.0458 | 0 | N/A | 0 | 0
2021-01-16 12:00 | 2.9261 | 0 | N/A | 0 | 0
2021-01-16 12:30 | 2.8808 | 0 | N/A | 0 | 0
2021-01-16 13:00 | 1.6571 | 0 | N/A | 0 | 0
2021-01-16 13:30 | 1.5685 | 0 | N/A | 0 | 0
2021-01-16 14:00 | 1.7917 | 0 | N/A | 0 | 0
2021-01-16 14:30 | 1.362 | 0 | N/A | 0 | 0
2021-01-16 15:00 | 1.7988 | 0 | N/A | 0 | 0
2021-01-16 15:30 | 1.4744 | 0 | N/A | 0 | 0
2021-01-16 16:00 | 1.1105 | 0 | N/A | 0 | 0
2021-01-16 16:30 | 1.3132 | 0 | N/A | 0 | 0
2021-01-16 17:00 | 2.0407 | 0 | N/A | 0 | 0
2021-01-16 17:30 | 2.9779 | 0 | N/A | 0 | 0
2021-01-16 18:00 | 3.084 | 0 | N/A | 0 | 0
2021-01-16 18:30 | 3.8013 | 0 | N/A | 0 | 0
2021-01-16 19:00 | 4.1263 | 0 | N/A | 0 | 0
2021-01-16 19:30 | 4.167 | 0 | N/A | 0 | 0
2021-01-16 20:00 | 4.2114 | 0 | N/A | 0 | 0
2021-01-16 20:30 | 4.2627 | 0 | N/A | 0 | 0
2021-01-16 21:00 | 4.2462 | 0 | N/A | 0 | 0
2021-01-16 21:30 | 4.1771 | 0 | N/A | 0 | 0
2021-01-16 22:00 | 3.9493 | 0 | N/A | 0 | 0
2021-01-16 22:30 | 4.3135 | 0 | N/A | 0 | 0
2021-01-16 23:00 | 4.6341 | 0 | N/A | 0 | 0
2021-01-16 23:30 | 4.3425 | 0 | N/A | 0 | 0
2021-01-17 | 4.3224 | 0 | N/A | 0 | 0
2021-01-17 00:30 | 4.7134 | 0 | N/A | 0 | 0
2021-01-17 01:00 | 5.1364 | 0 | N/A | 0 | 0
2021-01-17 01:30 | 4.2945 | 0 | N/A | 0 | 0
2021-01-17 02:00 | 3.4928 | 0 | N/A | 0 | 0
2021-01-17 02:30 | 3.4393 | 0 | N/A | 0 | 0
2021-01-17 03:00 | 3.0215 | 0 | N/A | 0 | 0
2021-01-17 03:30 | 2.5847 | 0 | N/A | 0 | 0
2021-01-17 04:00 | 2.3799 | 0 | N/A | 0 | 0
2021-01-17 04:30 | 2.2443 | 0 | N/A | 0 | 0
2021-01-17 05:00 | 2.157 | 0 | N/A | 0 | 0
2021-01-17 05:30 | 2.159 | 0 | N/A | 0 | 0
2021-01-17 06:00 | 2.2105 | 0 | N/A | 0 | 0
2021-01-17 06:30 | 2.3699 | 0 | N/A | 0 | 0
2021-01-17 07:00 | 2.4972 | 0 | N/A | 0 | 0
2021-01-17 07:30 | 2.5678 | 0 | N/A | 0 | 0
2021-01-17 08:00 | 2.636 | 0 | N/A | 0 | 0
2021-01-17 08:30 | 2.0357 | 0 | N/A | 0 | 0
2021-01-17 09:00 | 1.6669 | 0 | N/A | 0 | 0
2021-01-17 09:30 | 1.4466 | 0 | N/A | 0 | 0
2021-01-17 10:00 | 1.6417 | 0 | N/A | 0 | 0
2021-01-17 10:30 | 1.2146 | 0 | N/A | 0 | 0
2021-01-17 11:00 | 0.61951 | 0 | N/A | 0 | 0
2021-01-17 11:30 | -0.39672 | 0 | N/A | 0 | 0
2021-01-17 12:00 | -0.56253 | 0 | N/A | 0 | 0
2021-01-17 12:30 | -0.79744 | 0 | N/A | 0 | 0
2021-01-17 13:00 | -1.1147 | 0 | N/A | 0 | 0
2021-01-17 13:30 | -1.2958 | 0 | N/A | 0 | 0
2021-01-17 14:00 | -1.4019 | 0 | N/A | 0 | 0
2021-01-17 14:30 | -1.3733 | 0 | N/A | 0 | 0
2021-01-17 15:00 | -1.4654 | 0 | N/A | 0 | 0
2021-01-17 15:30 | -1.3513 | 0 | N/A | 0 | 0
2021-01-17 16:00 | -1.1996 | 0 | N/A | 0 | 0
2021-01-17 16:30 | -0.87068 | 0 | N/A | 0 | 0
2021-01-17 17:00 | -0.46606 | 0 | N/A | 0 | 0
2021-01-17 17:30 | 0.45934 | 0 | N/A | 0 | 0
2021-01-17 18:00 | 1.2091 | 0 | N/A | 0 | 0
2021-01-17 18:30 | 2.0599 | 0 | N/A | 0 | 0
2021-01-17 19:00 | 2.6414 | 0 | N/A | 0 | 0
2021-01-17 19:30 | 3.1157 | 0 | N/A | 0 | 0
2021-01-17 20:00 | 3.3577 | 0 | N/A | 0 | 0
2021-01-17 20:30 | 3.5286 | 0 | N/A | 0 | 0
2021-01-17 21:00 | 3.5358 | 0 | N/A | 0 | 0
2021-01-17 21:30 | 3.6228 | 0 | N/A | 0 | 0
2021-01-17 22:00 | 3.4902 | 0 | N/A | 0 | 0
2021-01-17 22:30 | 3.8823 | 0 | N/A | 0 | 0
2021-01-17 23:00 | 4.0349 | 0 | N/A | 0 | 0
2021-01-17 23:30 | 3.8142 | 0 | N/A | 0 | 0
2021-01-18 | 3.9289 | 0 | N/A | 0 | 0
2021-01-18 00:30 | 4.2408 | 0 | N/A | 0 | 0
2021-01-18 01:00 | 4.5163 | 0 | N/A | 0 | 0
2021-01-18 01:30 | 3.7071 | 0 | N/A | 0 | 0
2021-01-18 02:00 | 3.0037 | 0 | N/A | 0 | 0
2021-01-18 02:30 | 3.0869 | 0 | N/A | 0 | 0
2021-01-18 03:00 | 2.7949 | 0 | N/A | 0 | 0
2021-01-18 03:30 | 2.3448 | 0 | N/A | 0 | 0
2021-01-18 04:00 | 2.1062 | 0 | N/A | 0 | 0
2021-01-18 04:30 | 1.9702 | 0 | N/A | 0 | 0
2021-01-18 05:00 | 1.9845 | 0 | N/A | 0 | 0
2021-01-18 05:30 | 2.2134 | 0 | N/A | 0 | 0
2021-01-18 06:00 | 2.3949 | 0 | N/A | 0 | 0
2021-01-18 06:30 | 2.9656 | 0 | N/A | 0 | 0
2021-01-18 07:00 | 3.4319 | 0 | N/A | 0 | 0
2021-01-18 07:30 | 3.8336 | 0 | N/A | 0 | 0
2021-01-18 08:00 | 4.011 | 0 | N/A | 0 | 0
2021-01-18 08:30 | 3.71 | 0 | N/A | 0 | 0
2021-01-18 09:00 | 3.4233 | 0 | N/A | 0 | 0
2021-01-18 09:30 | 3.1167 | 0 | N/A | 0 | 0
2021-01-18 10:00 | 2.8334 | 0 | N/A | 0 | 0
2021-01-18 10:30 | 2.7601 | 0 | N/A | 0 | 0
2021-01-18 11:00 | 2.4655 | 0 | N/A | 0 | 0
2021-01-18 11:30 | 1.9674 | 0 | N/A | 0 | 0
2021-01-18 12:00 | 1.3706 | 0 | N/A | 0 | 0
2021-01-18 12:30 | 0.85652 | 0 | N/A | 0 | 0
2021-01-18 13:00 | 0.35443 | 0 | N/A | 0 | 0
2021-01-18 13:30 | 0.27352 | 0 | N/A | 0 | 0
2021-01-18 14:00 | -0.35258 | 0 | N/A | 0 | 0
2021-01-18 14:30 | -0.45158 | 0 | N/A | 0 | 0
2021-01-18 15:00 | -0.48231 | 0 | N/A | 0 | 0
2021-01-18 15:30 | -0.53679 | 0 | N/A | 0 | 0
2021-01-18 16:00 | -0.52799 | 0 | N/A | 0 | 0
2021-01-18 16:30 | -0.068394 | 0 | N/A | 0 | 0
2021-01-18 17:00 | 0.6531 | 0 | N/A | 0 | 0
2021-01-18 17:30 | 1.7877 | 0 | N/A | 0 | 0
2021-01-18 18:00 | 2.5142 | 0 | N/A | 0 | 0
2021-01-18 18:30 | 2.6076 | 0 | N/A | 0 | 0
2021-01-18 19:00 | 2.895 | 0 | N/A | 0 | 0
2021-01-18 19:30 | 3.5019 | 0 | N/A | 0 | 0
2021-01-18 20:00 | 3.9295 | 0 | N/A | 0 | 0
2021-01-18 20:30 | 3.9816 | 0 | N/A | 0 | 0
2021-01-18 21:00 | 4.0349 | 0 | N/A | 0 | 0
2021-01-18 21:30 | 3.9844 | 0 | N/A | 0 | 0
2021-01-18 22:00 | 3.7442 | 0 | N/A | 0 | 0
2021-01-18 22:30 | 4.0981 | 0 | N/A | 0 | 0
2021-01-18 23:00 | 4.0635 | 0 | N/A | 0 | 0
2021-01-18 23:30 | 3.7878 | 0 | N/A | 0 | 0
2021-01-19 | 3.8805 | 0 | N/A | 0 | 0
2021-01-19 00:30 | 4.2431 | 0 | N/A | 0 | 0
2021-01-19 01:00 | 4.5397 | 0 | N/A | 0 | 0
2021-01-19 01:30 | 3.7407 | 0 | N/A | 0 | 0
2021-01-19 02:00 | 3.0945 | 0 | N/A | 0 | 0
2021-01-19 02:30 | 3.0266 | 0 | N/A | 0 | 0
2021-01-19 03:00 | 2.5449 | 0 | N/A | 0 | 0
2021-01-19 03:30 | 2.2858 | 0 | N/A | 0 | 0
2021-01-19 04:00 | 2.024 | 0 | N/A | 0 | 0
2021-01-19 04:30 | 1.9797 | 0 | N/A | 0 | 0
2021-01-19 05:00 | 2.0427 | 0 | N/A | 0 | 0
2021-01-19 05:30 | 2.2562 | 0 | N/A | 0 | 0
2021-01-19 06:00 | 3.826 | 0 | N/A | 0 | 0
2021-01-19 06:30 | 4.4458 | 0 | N/A | 0 | 0
2021-01-19 07:00 | 4.92 | 0 | N/A | 0 | 0
2021-01-19 07:30 | 5.3324 | 0 | N/A | 0 | 0
2021-01-19 08:00 | 5.38 | 0 | N/A | 0 | 0
2021-01-19 08:30 | 4.6902 | 0 | N/A | 0 | 0
2021-01-19 09:00 | 4.2934 | 0 | N/A | 0 | 0
2021-01-19 09:30 | 3.7871 | 0 | N/A | 0 | 0
2021-01-19 10:00 | 2.9205 | 0 | N/A | 0 | 0
2021-01-19 10:30 | 2.7367 | 0 | N/A | 0 | 0
2021-01-19 11:00 | 2.5175 | 0 | N/A | 0 | 0
2021-01-19 11:30 | 0.83789 | 0 | N/A | 0 | 0
2021-01-19 12:00 | -0.38759 | 0 | N/A | 0 | 0
2021-01-19 12:30 | -0.43433 | 0 | N/A | 0 | 0
2021-01-19 13:00 | -0.55683 | 0 | N/A | 0 | 0
2021-01-19 13:30 | -0.67383 | 0 | N/A | 0 | 0
2021-01-19 14:00 | -0.688 | 0 | N/A | 0 | 0
2021-01-19 14:30 | -0.69061 | 0 | N/A | 0 | 0
2021-01-19 15:00 | -0.74536 | 0 | N/A | 0 | 0
2021-01-19 15:30 | -0.83915 | 0 | N/A | 0 | 0
2021-01-19 16:00 | -0.69321 | 0 | N/A | 0 | 0
2021-01-19 16:30 | -0.49667 | 0 | N/A | 0 | 0
2021-01-19 17:00 | -0.23068 | 0 | N/A | 0 | 0
2021-01-19 17:30 | 0.48252 | 0 | N/A | 0 | 0
2021-01-19 18:00 | 1.2491 | 0 | N/A | 0 | 0
2021-01-19 18:30 | 2.0698 | 0 | N/A | 0 | 0
2021-01-19 19:00 | 2.6314 | 0 | N/A | 0 | 0
2021-01-19 19:30 | 3.1143 | 0 | N/A | 0 | 0
2021-01-19 20:00 | 3.4319 | 0 | N/A | 0 | 0
2021-01-19 20:30 | 3.7454 | 0 | N/A | 0 | 0
2021-01-19 21:00 | 3.9631 | 0 | N/A | 0 | 0
2021-01-19 21:30 | 4.0244 | 0 | N/A | 0 | 0
2021-01-19 22:00 | 3.8476 | 0 | N/A | 0 | 0
2021-01-19 22:30 | 4.0509 | 0 | N/A | 0 | 0
2021-01-19 23:00 | 4.187 | 0 | N/A | 0 | 0
2021-01-19 23:30 | 3.857 | 0 | N/A | 0 | 0
2021-01-20 | 3.954 | 0 | N/A | 0 | 0
2021-01-20 00:30 | 4.2829 | 0 | N/A | 0 | 0
2021-01-20 01:00 | 4.4993 | 0 | N/A | 0 | 0
2021-01-20 01:30 | 3.7748 | 0 | N/A | 0 | 0
2021-01-20 02:00 | 3.0419 | 0 | N/A | 0 | 0
2021-01-20 02:30 | 3.0157 | 0 | N/A | 0 | 0
2021-01-20 03:00 | 2.6947 | 0 | N/A | 0 | 0
2021-01-20 03:30 | 2.3691 | 0 | N/A | 0 | 0
2021-01-20 04:00 | 2.097 | 0 | N/A | 0 | 0
2021-01-20 04:30 | 2.0378 | 0 | N/A | 0 | 0
2021-01-20 05:00 | 2.0383 | 0 | N/A | 0 | 0
2021-01-20 05:30 | 2.2979 | 0 | N/A | 0 | 0
2021-01-20 06:00 | 2.5344 | 0 | N/A | 0 | 0
2021-01-20 06:30 | 3.027 | 0 | N/A | 0 | 0
2021-01-20 07:00 | 3.5199 | 0 | N/A | 0 | 0
2021-01-20 07:30 | 4.014 | 0 | N/A | 0 | 0
2021-01-20 08:00 | 4.7168 | 0 | N/A | 0 | 0
2021-01-20 08:30 | 4.8669 | 0 | N/A | 0 | 0
2021-01-20 09:00 | 4.2434 | 0 | N/A | 0 | 0
2021-01-20 09:30 | 3.57 | 0 | N/A | 0 | 0
2021-01-20 10:00 | 2.8803 | 0 | N/A | 0 | 0
2021-01-20 10:30 | 1.1386 | 0 | N/A | 0 | 0
2021-01-20 11:00 | 0.50078 | 0 | N/A | 0 | 0
2021-01-20 11:30 | 0.44746 | 0 | N/A | 0 | 0
2021-01-20 12:00 | -0.23469 | 0 | N/A | 0 | 0
2021-01-20 12:30 | -0.33007 | 0 | N/A | 0 | 0
2021-01-20 13:00 | -0.36667 | 0 | N/A | 0 | 0
2021-01-20 13:30 | -0.54781 | 0 | N/A | 0 | 0
2021-01-20 14:00 | -0.62626 | 0 | N/A | 0 | 0
2021-01-20 14:30 | -0.57319 | 0 | N/A | 0 | 0
2021-01-20 15:00 | -0.5318 | 0 | N/A | 0 | 0
2021-01-20 15:30 | -0.52693 | 0 | N/A | 0 | 0
2021-01-20 16:00 | -0.44011 | 0 | N/A | 0 | 0
2021-01-20 16:30 | -0.13437 | 0 | N/A | 0 | 0
2021-01-20 17:00 | 0.27685 | 0 | N/A | 0 | 0
2021-01-20 17:30 | 1 | 0 | N/A | 0 | 0
2021-01-20 18:00 | 1.9567 | 0 | N/A | 0 | 0
2021-01-20 18:30 | 2.7367 | 0 | N/A | 0 | 0
2021-01-20 19:00 | 3.4307 | 0 | N/A | 0 | 0
2021-01-20 19:30 | 3.7656 | 0 | N/A | 0 | 0
2021-01-20 20:00 | 3.8783 | 0 | N/A | 0 | 0
2021-01-20 20:30 | 3.8443 | 0 | N/A | 0 | 0
2021-01-20 21:00 | 3.8907 | 0 | N/A | 0 | 0
2021-01-20 21:30 | 3.8926 | 0 | N/A | 0 | 0
2021-01-20 22:00 | 3.6197 | 0 | N/A | 0 | 0
2021-01-20 22:30 | 3.8928 | 0 | N/A | 0 | 0
2021-01-20 23:00 | 3.9547 | 0 | N/A | 0 | 0
2021-01-20 23:30 | 3.5884 | 0 | N/A | 0 | 0
2021-01-21 | 3.7229 | 0 | N/A | 0 | 0
2021-01-21 00:30 | 4.0249 | 0 | N/A | 0 | 0
2021-01-21 01:00 | 4.2251 | 0 | N/A | 0 | 0
2021-01-21 01:30 | 3.4525 | 0 | N/A | 0 | 0
2021-01-21 02:00 | 2.813 | 0 | N/A | 0 | 0
2021-01-21 02:30 | 2.7707 | 0 | N/A | 0 | 0
2021-01-21 03:00 | 2.4046 | 0 | N/A | 0 | 0
2021-01-21 03:30 | 2.0999 | 0 | N/A | 0 | 0
2021-01-21 04:00 | 1.8918 | 0 | N/A | 0 | 0
2021-01-21 04:30 | 1.8372 | 0 | N/A | 0 | 0
2021-01-21 05:00 | 1.8898 | 0 | N/A | 0 | 0
2021-01-21 05:30 | 2.0927 | 0 | N/A | 0 | 0
2021-01-21 06:00 | 2.3266 | 0 | N/A | 0 | 0
2021-01-21 06:30 | 2.6927 | 0 | N/A | 0 | 0
2021-01-21 07:00 | 3.2934 | 0 | N/A | 0 | 0
2021-01-21 07:30 | 3.6893 | 0 | N/A | 0 | 0
2021-01-21 08:00 | 3.73 | 0 | N/A | 0 | 0
2021-01-21 08:30 | 2.9933 | 0 | N/A | 0 | 0
2021-01-21 09:00 | 2.712 | 0 | N/A | 0 | 0
2021-01-21 09:30 | 2.1619 | 0 | N/A | 0 | 0
2021-01-21 10:00 | 1.0135 | 0 | N/A | 0 | 0
2021-01-21 10:30 | 0.75333 | 0 | N/A | 0 | 0
2021-01-21 11:00 | 0.33428 | 0 | N/A | 0 | 0
2021-01-21 11:30 | 0.21738 | 0 | N/A | 0 | 0
2021-01-21 12:00 | -0.22023 | 0 | N/A | 0 | 0
2021-01-21 12:30 | -0.23823 | 0 | N/A | 0 | 0
2021-01-21 13:00 | -0.26918 | 0 | N/A | 0 | 0
2021-01-21 13:30 | 0.34041 | 0 | N/A | 0 | 0
2021-01-21 14:00 | 0.44578 | 0 | N/A | 0 | 0
2021-01-21 14:30 | 0.46098 | 0 | N/A | 0 | 0
2021-01-21 15:00 | 0.55227 | 0 | N/A | 0 | 0
2021-01-21 15:30 | 0.93041 | 0 | N/A | 0 | 0
2021-01-21 16:00 | 1.2544 | 0 | N/A | 0 | 0
2021-01-21 16:30 | 1.7221 | 0 | N/A | 0 | 0
2021-01-21 17:00 | 2.4609 | 0 | N/A | 0 | 0
2021-01-21 17:30 | 3.3111 | 0 | N/A | 0 | 0
2021-01-21 18:00 | 4.1949 | 0 | N/A | 0 | 0
2021-01-21 18:30 | 5.3891 | 0 | N/A | 0 | 0
2021-01-21 19:00 | 5.9617 | 0 | N/A | 0 | 0
2021-01-21 19:30 | 6.0246 | 0 | N/A | 0 | 0
2021-01-21 20:00 | 5.8304 | 0 | N/A | 0 | 0
2021-01-21 20:30 | 5.4555 | 0 | N/A | 0 | 0
2021-01-21 21:00 | 5.3435 | 0 | N/A | 0 | 0
2021-01-21 21:30 | 5.0333 | 0 | N/A | 0 | 0
2021-01-21 22:00 | 4.6267 | 0 | N/A | 0 | 0
2021-01-21 22:30 | 4.5572 | 0 | N/A | 0 | 0
2021-01-21 23:00 | 4.4402 | 0 | N/A | 0 | 0
2021-01-21 23:30 | 3.9248 | 0 | N/A | 0 | 0
2021-01-22 | 3.8564 | 0 | N/A | 0 | 0
2021-01-22 00:30 | 4.3843 | 0 | N/A | 0 | 0
2021-01-22 01:00 | 4.4203 | 0 | N/A | 0 | 0
2021-01-22 01:30 | 3.4777 | 0 | N/A | 0 | 0
2021-01-22 02:00 | 2.6562 | 0 | N/A | 0 | 0
2021-01-22 02:30 | 2.6911 | 0 | N/A | 0 | 0
2021-01-22 03:00 | 2.4175 | 0 | N/A | 0 | 0
2021-01-22 03:30 | 2.1396 | 0 | N/A | 0 | 0
2021-01-22 04:00 | 2.0348 | 0 | N/A | 0 | 0
2021-01-22 04:30 | 1.9776 | 0 | N/A | 0 | 0
2021-01-22 05:00 | 2.0565 | 0 | N/A | 0 | 0
2021-01-22 05:30 | 2.1852 | 0 | N/A | 0 | 0
2021-01-22 06:00 | 2.2978 | 0 | N/A | 0 | 0
2021-01-22 06:30 | 2.9115 | 0 | N/A | 0 | 0
2021-01-22 07:00 | 3.3534 | 0 | N/A | 0 | 0
2021-01-22 07:30 | 3.6692 | 0 | N/A | 0 | 0
2021-01-22 08:00 | 3.5935 | 0 | N/A | 0 | 0
2021-01-22 08:30 | 2.9168 | 0 | N/A | 0 | 0
2021-01-22 09:00 | 2.4557 | 0 | N/A | 0 | 0
2021-01-22 09:30 | 1.9834 | 0 | N/A | 0 | 0
2021-01-22 10:00 | 1.26 | 0 | N/A | 0 | 0
2021-01-22 10:30 | 0.97402 | 0 | N/A | 0 | 0
2021-01-22 11:00 | 1.1497 | 0 | N/A | 0 | 0
2021-01-22 11:30 | 0.77003 | 0 | N/A | 0 | 0
2021-01-22 12:00 | 0.58459 | 0 | N/A | 0 | 0
2021-01-22 12:30 | 0.5069 | 0 | N/A | 0 | 0
2021-01-22 13:00 | -0.5 | 0 | N/A | 0 | 0
2021-01-22 13:30 | 0.51001 | 0 | N/A | 0 | 0
2021-01-22 14:00 | 0.764 | 0 | N/A | 0 | 0
2021-01-22 14:30 | 0.79433 | 0 | N/A | 0 | 0
2021-01-22 15:00 | 0.72223 | 0 | N/A | 0 | 0
2021-01-22 15:30 | 0.64667 | 0 | N/A | 0 | 0
2021-01-22 16:00 | 0.58245 | 0 | N/A | 0 | 0
2021-01-22 16:30 | 0.85255 | 0 | N/A | 0 | 0
2021-01-22 17:00 | 1.3053 | 0 | N/A | 0 | 0
2021-01-22 17:30 | 1.9279 | 0 | N/A | 0 | 0
2021-01-22 18:00 | 2.8782 | 0 | N/A | 0 | 0
2021-01-22 18:30 | 3.6671 | 0 | N/A | 0 | 0
2021-01-22 19:00 | 4.1267 | 0 | N/A | 0 | 0
2021-01-22 19:30 | 4.33 | 0 | N/A | 0 | 0
2021-01-22 20:00 | 4.3937 | 0 | N/A | 0 | 0
2021-01-22 20:30 | 4.2779 | 0 | N/A | 0 | 0
2021-01-22 21:00 | 4.1176 | 0 | N/A | 0 | 0
2021-01-22 21:30 | 3.9203 | 0 | N/A | 0 | 0
2021-01-22 22:00 | 3.7686 | 0 | N/A | 0 | 0
2021-01-22 22:30 | 4.034 | 0 | N/A | 0 | 0
2021-01-22 23:00 | 4.1029 | 0 | N/A | 0 | 0
2021-01-22 23:30 | 3.6712 | 0 | N/A | 0 | 0
2021-01-23 | 3.6826 | 0 | N/A | 0 | 0
2021-01-23 00:30 | 4.248 | 0 | N/A | 0 | 0
2021-01-23 01:00 | 4.3771 | 0 | N/A | 0 | 0
2021-01-23 01:30 | 3.4076 | 0 | N/A | 0 | 0
2021-01-23 02:00 | 2.6326 | 0 | N/A | 0 | 0
2021-01-23 02:30 | 2.6424 | 0 | N/A | 0 | 0
2021-01-23 03:00 | 2.2725 | 0 | N/A | 0 | 0
2021-01-23 03:30 | 2.0462 | 0 | N/A | 0 | 0
2021-01-23 04:00 | 1.8987 | 0 | N/A | 0 | 0
2021-01-23 04:30 | 1.7971 | 0 | N/A | 0 | 0
2021-01-23 05:00 | 1.7839 | 0 | N/A | 0 | 0
2021-01-23 05:30 | 1.8026 | 0 | N/A | 0 | 0
2021-01-23 06:00 | 2.0069 | 0 | N/A | 0 | 0
2021-01-23 06:30 | 2.2062 | 0 | N/A | 0 | 0
2021-01-23 07:00 | 2.302 | 0 | N/A | 0 | 0
2021-01-23 07:30 | 2.3594 | 0 | N/A | 0 | 0
2021-01-23 08:00 | 2.339 | 0 | N/A | 0 | 0
2021-01-23 08:30 | 1.8515 | 0 | N/A | 0 | 0
2021-01-23 09:00 | 1.5098 | 0 | N/A | 0 | 0
2021-01-23 09:30 | 0.965 | 0 | N/A | 0 | 0
2021-01-23 10:00 | 0.49989 | 0 | N/A | 0 | 0
2021-01-23 10:30 | 0.20811 | 0 | N/A | 0 | 0
2021-01-23 11:00 | -0.14067 | 0 | N/A | 0 | 0
2021-01-23 11:30 | -0.33869 | 0 | N/A | 0 | 0
2021-01-23 12:00 | -0.33 | 0 | N/A | 0 | 0
2021-01-23 12:30 | -0.32728 | 0 | N/A | 0 | 0
2021-01-23 13:00 | -0.36372 | 0 | N/A | 0 | 0
2021-01-23 13:30 | -0.25044 | 0 | N/A | 0 | 0
2021-01-23 14:00 | -0.17448 | 0 | N/A | 0 | 0
2021-01-23 14:30 | -0.17346 | 0 | N/A | 0 | 0
2021-01-23 15:00 | 0.34209 | 0 | N/A | 0 | 0
2021-01-23 15:30 | 0.69687 | 0 | N/A | 0 | 0
2021-01-23 16:00 | 1.1253 | 0 | N/A | 0 | 0
2021-01-23 16:30 | 1.8638 | 0 | N/A | 0 | 0
2021-01-23 17:00 | 2.6603 | 0 | N/A | 0 | 0
2021-01-23 17:30 | 3.4491 | 0 | N/A | 0 | 0
2021-01-23 18:00 | 4.3313 | 0 | N/A | 0 | 0
2021-01-23 18:30 | 5.1427 | 0 | N/A | 0 | 0
2021-01-23 19:00 | 5.9081 | 0 | N/A | 0 | 0
2021-01-23 19:30 | 6.1901 | 0 | N/A | 0 | 0
2021-01-23 20:00 | 6.1211 | 0 | N/A | 0 | 0
2021-01-23 20:30 | 5.6201 | 0 | N/A | 0 | 0
2021-01-23 21:00 | 5.1433 | 0 | N/A | 0 | 0
2021-01-23 21:30 | 4.7033 | 0 | N/A | 0 | 0
2021-01-23 22:00 | 4.2571 | 0 | N/A | 0 | 0
2021-01-23 22:30 | 4.5217 | 0 | N/A | 0 | 0
2021-01-23 23:00 | 4.4887 | 0 | N/A | 0 | 0
2021-01-23 23:30 | 3.9284 | 0 | N/A | 0 | 0
2021-01-24 | 3.8777 | 0 | N/A | 0 | 0
2021-01-24 00:30 | 4.3253 | 0 | N/A | 0 | 0
2021-01-24 01:00 | 4.4233 | 0 | N/A | 0 | 0
2021-01-24 01:30 | 3.411 | 0 | N/A | 0 | 0
2021-01-24 02:00 | 2.7364 | 0 | N/A | 0 | 0
2021-01-24 02:30 | 2.6634 | 0 | N/A | 0 | 0
2021-01-24 03:00 | 2.3731 | 0 | N/A | 0 | 0
2021-01-24 03:30 | 2.1459 | 0 | N/A | 0 | 0
2021-01-24 04:00 | 1.9856 | 0 | N/A | 0 | 0
2021-01-24 04:30 | 1.8458 | 0 | N/A | 0 | 0
2021-01-24 05:00 | 1.8155 | 0 | N/A | 0 | 0
2021-01-24 05:30 | 1.8386 | 0 | N/A | 0 | 0
2021-01-24 06:00 | 1.8953 | 0 | N/A | 0 | 0
2021-01-24 06:30 | 2.0486 | 0 | N/A | 0 | 0
2021-01-24 07:00 | 2.0295 | 0 | N/A | 0 | 0
2021-01-24 07:30 | 2.1357 | 0 | N/A | 0 | 0
2021-01-24 08:00 | 2.1878 | 0 | N/A | 0 | 0
2021-01-24 08:30 | 1.7066 | 0 | N/A | 0 | 0
2021-01-24 09:00 | 1.4391 | 0 | N/A | 0 | 0
2021-01-24 09:30 | 1.2078 | 0 | N/A | 0 | 0
2021-01-24 10:00 | 1.1606 | 0 | N/A | 0 | 0
2021-01-24 10:30 | 1.7976 | 0 | N/A | 0 | 0
2021-01-24 11:00 | 1.2941 | 0 | N/A | 0 | 0
2021-01-24 11:30 | 0.86719 | 0 | N/A | 0 | 0
2021-01-24 12:00 | 1.4436 | 0 | N/A | 0 | 0
2021-01-24 12:30 | 1.8533 | 0 | N/A | 0 | 0
2021-01-24 13:00 | 2.5694 | 0 | N/A | 0 | 0
2021-01-24 13:30 | 3.7361 | 0 | N/A | 0 | 0
2021-01-24 14:00 | 3.5078 | 0 | N/A | 0 | 0
2021-01-24 14:30 | 3.8577 | 0 | N/A | 0 | 0
2021-01-24 15:00 | 3.8972 | 0 | N/A | 0 | 0
2021-01-24 15:30 | 4.2896 | 0 | N/A | 0 | 0
2021-01-24 16:00 | 4.1387 | 0 | N/A | 0 | 0
2021-01-24 16:30 | 4.161 | 0 | N/A | 0 | 0
2021-01-24 17:00 | 4.8063 | 0 | N/A | 0 | 0
2021-01-24 17:30 | 5.6851 | 0 | N/A | 0 | 0
2021-01-24 18:00 | 6.6203 | 0 | N/A | 0 | 0
2021-01-24 18:30 | 7.4489 | 0 | N/A | 0 | 0
2021-01-24 19:00 | 8.2772 | 0 | N/A | 0 | 0
2021-01-24 19:30 | 8.6417 | 0 | N/A | 0 | 0
2021-01-24 20:00 | 8.6599 | 0 | N/A | 0 | 0
2021-01-24 20:30 | 8.2804 | 0 | N/A | 0 | 0
2021-01-24 21:00 | 7.4891 | 0 | N/A | 0 | 0
2021-01-24 21:30 | 6.8257 | 0 | N/A | 0 | 0
2021-01-24 22:00 | 5.8717 | 0 | N/A | 0 | 0
2021-01-24 22:30 | 5.77 | 0 | N/A | 0 | 0
2021-01-24 23:00 | 5.5233 | 0 | N/A | 0 | 0
2021-01-24 23:30 | 4.9168 | 0 | N/A | 0 | 0
2021-01-25 | 4.7542 | 0 | N/A | 0 | 0
2021-01-25 00:30 | 5.1045 | 0 | N/A | 0 | 0
2021-01-25 01:00 | 5.0675 | 0 | N/A | 0 | 0
2021-01-25 01:30 | 3.8933 | 0 | N/A | 0 | 0
2021-01-25 02:00 | 3.2588 | 0 | N/A | 0 | 0
2021-01-25 02:30 | 3.2415 | 0 | N/A | 0 | 0
2021-01-25 03:00 | 2.9271 | 0 | N/A | 0 | 0
2021-01-25 03:30 | 2.6165 | 0 | N/A | 0 | 0
2021-01-25 04:00 | 2.5738 | 0 | N/A | 0 | 0
2021-01-25 04:30 | 2.4499 | 0 | N/A | 0 | 0
2021-01-25 05:00 | 2.4512 | 0 | N/A | 0 | 0
2021-01-25 05:30 | 2.5824 | 0 | N/A | 0 | 0
2021-01-25 06:00 | 2.7305 | 0 | N/A | 0 | 0
2021-01-25 06:30 | 2.9699 | 0 | N/A | 0 | 0
2021-01-25 07:00 | 3.3844 | 0 | N/A | 0 | 0
2021-01-25 07:30 | 3.8167 | 0 | N/A | 0 | 0
2021-01-25 08:00 | 3.7134 | 0 | N/A | 0 | 0
2021-01-25 08:30 | 3.7618 | 0 | N/A | 0 | 0
2021-01-25 09:00 | 3.5354 | 0 | N/A | 0 | 0
2021-01-25 09:30 | 3.7562 | 0 | N/A | 0 | 0
2021-01-25 10:00 | 2.9297 | 0 | N/A | 0 | 0
2021-01-25 10:30 | 3.8262 | 0 | N/A | 0 | 0
2021-01-25 11:00 | 4.4963 | 0 | N/A | 0 | 0
2021-01-25 11:30 | 4.4218 | 0 | N/A | 0 | 0
2021-01-25 12:00 | 5.7468 | 0 | N/A | 0 | 0
2021-01-25 12:30 | 5.903 | 0 | N/A | 0 | 0
2021-01-25 13:00 | 5.5348 | 0 | N/A | 0 | 0
2021-01-25 13:30 | 5.3113 | 0 | N/A | 0 | 0
2021-01-25 14:00 | 5.5084 | 0 | N/A | 0 | 0
2021-01-25 14:30 | 6.1278 | 0 | N/A | 0 | 0
2021-01-25 15:00 | 6.5669 | 0 | N/A | 0 | 0
2021-01-25 15:30 | 6.6894 | 0 | N/A | 0 | 0
2021-01-25 16:00 | 5.8103 | 0 | N/A | 0 | 0
2021-01-25 16:30 | 5.2943 | 0 | N/A | 0 | 0
2021-01-25 17:00 | 5.6278 | 0 | N/A | 0 | 0
2021-01-25 17:30 | 5.6499 | 0 | N/A | 0 | 0
2021-01-25 18:00 | 5.7812 | 0 | N/A | 0 | 0
2021-01-25 18:30 | 5.7096 | 0 | N/A | 0 | 0
2021-01-25 19:00 | 5.7636 | 0 | N/A | 0 | 0
2021-01-25 19:30 | 5.66 | 0 | N/A | 0 | 0
2021-01-25 20:00 | 5.35 | 0 | N/A | 0 | 0
2021-01-25 20:30 | 4.9967 | 0 | N/A | 0 | 0
2021-01-25 21:00 | 4.76 | 0 | N/A | 0 | 0
2021-01-25 21:30 | 4.4275 | 0 | N/A | 0 | 0
2021-01-25 22:00 | 4.1095 | 0 | N/A | 0 | 0
2021-01-25 22:30 | 3.977 | 0 | N/A | 0 | 0
2021-01-25 23:00 | 3.7957 | 0 | N/A | 0 | 0
2021-01-25 23:30 | 3.3879 | 0 | N/A | 0 | 0
2021-01-26 | 3.3498 | 0 | N/A | 0 | 0
2021-01-26 00:30 | 3.8284 | 0 | N/A | 0 | 0
2021-01-26 01:00 | 3.8351 | 0 | N/A | 0 | 0
2021-01-26 01:30 | 2.9143 | 0 | N/A | 0 | 0
2021-01-26 02:00 | 2.3817 | 0 | N/A | 0 | 0
2021-01-26 02:30 | 2.3038 | 0 | N/A | 0 | 0
2021-01-26 03:00 | 2.1404 | 0 | N/A | 0 | 0
2021-01-26 03:30 | 1.9893 | 0 | N/A | 0 | 0
2021-01-26 04:00 | 1.8287 | 0 | N/A | 0 | 0
2021-01-26 04:30 | 1.7167 | 0 | N/A | 0 | 0
2021-01-26 05:00 | 1.7591 | 0 | N/A | 0 | 0
2021-01-26 05:30 | 1.9263 | 0 | N/A | 0 | 0
2021-01-26 06:00 | 2.2605 | 0 | N/A | 0 | 0
2021-01-26 06:30 | 2.477 | 0 | N/A | 0 | 0
2021-01-26 07:00 | 2.4478 | 0 | N/A | 0 | 0
2021-01-26 07:30 | 2.5849 | 0 | N/A | 0 | 0
2021-01-26 08:00 | 2.6666 | 0 | N/A | 0 | 0
2021-01-26 08:30 | 2.5033 | 0 | N/A | 0 | 0
2021-01-26 09:00 | 2.42 | 0 | N/A | 0 | 0
2021-01-26 09:30 | 2.3784 | 0 | N/A | 0 | 0
2021-01-26 10:00 | 2.2069 | 0 | N/A | 0 | 0
2021-01-26 10:30 | 2.0413 | 0 | N/A | 0 | 0
2021-01-26 11:00 | 2.11 | 0 | N/A | 0 | 0
2021-01-26 11:30 | 2.2136 | 0 | N/A | 0 | 0
2021-01-26 12:00 | 2.3044 | 0 | N/A | 0 | 0
2021-01-26 12:30 | 1.6794 | 0 | N/A | 0 | 0
2021-01-26 13:00 | 2.2907 | 0 | N/A | 0 | 0
2021-01-26 13:30 | 1.7705 | 0 | N/A | 0 | 0
2021-01-26 14:00 | 1.3751 | 0 | N/A | 0 | 0
2021-01-26 14:30 | 1.5997 | 0 | N/A | 0 | 0
2021-01-26 15:00 | 0.45197 | 0 | N/A | 0 | 0
2021-01-26 15:30 | 0.22373 | 0 | N/A | 0 | 0
2021-01-26 16:00 | 0.2361 | 0 | N/A | 0 | 0
2021-01-26 16:30 | 0.86436 | 0 | N/A | 0 | 0
2021-01-26 17:00 | 1.1917 | 0 | N/A | 0 | 0
2021-01-26 17:30 | 1.619 | 0 | N/A | 0 | 0
2021-01-26 18:00 | 2.8793 | 0 | N/A | 0 | 0
2021-01-26 18:30 | 2.9996 | 0 | N/A | 0 | 0
2021-01-26 19:00 | 3.0308 | 0 | N/A | 0 | 0
2021-01-26 19:30 | 3.2581 | 0 | N/A | 0 | 0
2021-01-26 20:00 | 3.4079 | 0 | N/A | 0 | 0
2021-01-26 20:30 | 3.6218 | 0 | N/A | 0 | 0
2021-01-26 21:00 | 3.6293 | 0 | N/A | 0 | 0
2021-01-26 21:30 | 3.602 | 0 | N/A | 0 | 0
2021-01-26 22:00 | 3.3425 | 0 | N/A | 0 | 0
2021-01-26 22:30 | 3.6908 | 0 | N/A | 0 | 0
2021-01-26 23:00 | 3.8549 | 0 | N/A | 0 | 0
2021-01-26 23:30 | 3.6192 | 0 | N/A | 0 | 0
2021-01-27 | 3.7682 | 0 | N/A | 0 | 0
2021-01-27 00:30 | 4.1547 | 0 | N/A | 0 | 0
2021-01-27 01:00 | 4.5328 | 0 | N/A | 0 | 0
2021-01-27 01:30 | 3.71 | 0 | N/A | 0 | 0
2021-01-27 02:00 | 2.9857 | 0 | N/A | 0 | 0
2021-01-27 02:30 | 2.8943 | 0 | N/A | 0 | 0
2021-01-27 03:00 | 2.4434 | 0 | N/A | 0 | 0
2021-01-27 03:30 | 2.1474 | 0 | N/A | 0 | 0
2021-01-27 04:00 | 1.9882 | 0 | N/A | 0 | 0
2021-01-27 04:30 | 1.9141 | 0 | N/A | 0 | 0
2021-01-27 05:00 | 1.9465 | 0 | N/A | 0 | 0
2021-01-27 05:30 | 2.1243 | 0 | N/A | 0 | 0
2021-01-27 06:00 | 2.4693 | 0 | N/A | 0 | 0
2021-01-27 06:30 | 3.0363 | 0 | N/A | 0 | 0
2021-01-27 07:00 | 3.6408 | 0 | N/A | 0 | 0
2021-01-27 07:30 | 4.0751 | 0 | N/A | 0 | 0
2021-01-27 08:00 | 4.2235 | 0 | N/A | 0 | 0
2021-01-27 08:30 | 3.75 | 0 | N/A | 0 | 0
2021-01-27 09:00 | 3.3233 | 0 | N/A | 0 | 0
2021-01-27 09:30 | 3.0314 | 0 | N/A | 0 | 0
2021-01-27 10:00 | 2.1651 | 0 | N/A | 0 | 0
2021-01-27 10:30 | 1.0896 | 0 | N/A | 0 | 0
2021-01-27 11:00 | 1.8705 | 0 | N/A | 0 | 0
2021-01-27 11:30 | 1.5503 | 0 | N/A | 0 | 0
2021-01-27 12:00 | 1.2899 | 0 | N/A | 0 | 0
2021-01-27 12:30 | 0.57644 | 0 | N/A | 0 | 0
2021-01-27 13:00 | 0.426 | 0 | N/A | 0 | 0
2021-01-27 13:30 | 0.29898 | 0 | N/A | 0 | 0
2021-01-27 14:00 | 0.31002 | 0 | N/A | 0 | 0
2021-01-27 14:30 | -0.27586 | 0 | N/A | 0 | 0
2021-01-27 15:00 | -0.2546 | 0 | N/A | 0 | 0
2021-01-27 15:30 | -0.73104 | 0 | N/A | 0 | 0
2021-01-27 16:00 | -0.67538 | 0 | N/A | 0 | 0
2021-01-27 16:30 | -0.64 | 0 | N/A | 0 | 0
2021-01-27 17:00 | -0.35631 | 0 | N/A | 0 | 0
2021-01-27 17:30 | 0.46934 | 0 | N/A | 0 | 0
2021-01-27 18:00 | 1.2888 | 0 | N/A | 0 | 0
2021-01-27 18:30 | 2.1502 | 0 | N/A | 0 | 0
2021-01-27 19:00 | 2.7423 | 0 | N/A | 0 | 0
2021-01-27 19:30 | 3.2942 | 0 | N/A | 0 | 0
2021-01-27 20:00 | 3.5427 | 0 | N/A | 0 | 0
2021-01-27 20:30 | 3.7236 | 0 | N/A | 0 | 0
2021-01-27 21:00 | 3.8066 | 0 | N/A | 0 | 0
2021-01-27 21:30 | 3.7809 | 0 | N/A | 0 | 0
2021-01-27 22:00 | 3.564 | 0 | N/A | 0 | 0
2021-01-27 22:30 | 3.9034 | 0 | N/A | 0 | 0
2021-01-27 23:00 | 3.9563 | 0 | N/A | 0 | 0
2021-01-27 23:30 | 3.6242 | 0 | N/A | 0 | 0
2021-01-28 | 3.7209 | 0 | N/A | 0 | 0
2021-01-28 00:30 | 4.1999 | 0 | N/A | 0 | 0
2021-01-28 01:00 | 4.3573 | 0 | N/A | 0 | 0
2021-01-28 01:30 | 3.4903 | 0 | N/A | 0 | 0
2021-01-28 02:00 | 2.7586 | 0 | N/A | 0 | 0
2021-01-28 02:30 | 2.7265 | 0 | N/A | 0 | 0
2021-01-28 03:00 | 2.4706 | 0 | N/A | 0 | 0
2021-01-28 03:30 | 2.1241 | 0 | N/A | 0 | 0
2021-01-28 04:00 | 1.9055 | 0 | N/A | 0 | 0
2021-01-28 04:30 | 1.8378 | 0 | N/A | 0 | 0
2021-01-28 05:00 | 1.9035 | 0 | N/A | 0 | 0
2021-01-28 05:30 | 2.0644 | 0 | N/A | 0 | 0
2021-01-28 06:00 | 2.2721 | 0 | N/A | 0 | 0
2021-01-28 06:30 | 2.8238 | 0 | N/A | 0 | 0
2021-01-28 07:00 | 3.406 | 0 | N/A | 0 | 0
2021-01-28 07:30 | 3.848 | 0 | N/A | 0 | 0
2021-01-28 08:00 | 4.02 | 0 | N/A | 0 | 0
2021-01-28 08:30 | 3.2834 | 0 | N/A | 0 | 0
2021-01-28 09:00 | 3.1267 | 0 | N/A | 0 | 0
2021-01-28 09:30 | 2.94 | 0 | N/A | 0 | 0
2021-01-28 10:00 | 2.5069 | 0 | N/A | 0 | 0
2021-01-28 10:30 | 2.3473 | 0 | N/A | 0 | 0
2021-01-28 11:00 | 1.8539 | 0 | N/A | 0 | 0
2021-01-28 11:30 | 1.5579 | 0 | N/A | 0 | 0
2021-01-28 12:00 | 2.2159 | 0 | N/A | 0 | 0
2021-01-28 12:30 | 2.1092 | 0 | N/A | 0 | 0
2021-01-28 13:00 | 1.5541 | 0 | N/A | 0 | 0
2021-01-28 13:30 | 0.82738 | 0 | N/A | 0 | 0
2021-01-28 14:00 | 1.9226 | 0 | N/A | 0 | 0
2021-01-28 14:30 | 2.1701 | 0 | N/A | 0 | 0
2021-01-28 15:00 | 2.3459 | 0 | N/A | 0 | 0
2021-01-28 15:30 | 1.6121 | 0 | N/A | 0 | 0
2021-01-28 16:00 | 1.633 | 0 | N/A | 0 | 0
2021-01-28 16:30 | 2.9871 | 0 | N/A | 0 | 0
2021-01-28 17:00 | 2.963 | 0 | N/A | 0 | 0
2021-01-28 17:30 | 2.8623 | 0 | N/A | 0 | 0
2021-01-28 18:00 | 3.0366 | 0 | N/A | 0 | 0
2021-01-28 18:30 | 3.6291 | 0 | N/A | 0 | 0
2021-01-28 19:00 | 4.0427 | 0 | N/A | 0 | 0
2021-01-28 19:30 | 4.0371 | 0 | N/A | 0 | 0
2021-01-28 20:00 | 3.9528 | 0 | N/A | 0 | 0
2021-01-28 20:30 | 4.0081 | 0 | N/A | 0 | 0
2021-01-28 21:00 | 4.0748 | 0 | N/A | 0 | 0
2021-01-28 21:30 | 3.9148 | 0 | N/A | 0 | 0
2021-01-28 22:00 | 3.6079 | 0 | N/A | 0 | 0
2021-01-28 22:30 | 3.9855 | 0 | N/A | 0 | 0
2021-01-28 23:00 | 3.9952 | 0 | N/A | 0 | 0
2021-01-28 23:30 | 3.6883 | 0 | N/A | 0 | 0
2021-01-29 | 3.7568 | 0 | N/A | 0 | 0
2021-01-29 00:30 | 4.202 | 0 | N/A | 0 | 0
2021-01-29 01:00 | 4.3499 | 0 | N/A | 0 | 0
2021-01-29 01:30 | 3.4145 | 0 | N/A | 0 | 0
2021-01-29 02:00 | 2.7556 | 0 | N/A | 0 | 0
2021-01-29 02:30 | 2.6972 | 0 | N/A | 0 | 0
2021-01-29 03:00 | 2.3301 | 0 | N/A | 0 | 0
2021-01-29 03:30 | 2.0147 | 0 | N/A | 0 | 0
2021-01-29 04:00 | 1.8816 | 0 | N/A | 0 | 0
2021-01-29 04:30 | 1.9064 | 0 | N/A | 0 | 0
2021-01-29 05:00 | 1.9801 | 0 | N/A | 0 | 0
2021-01-29 05:30 | 2.0692 | 0 | N/A | 0 | 0
2021-01-29 06:00 | 2.4137 | 0 | N/A | 0 | 0
2021-01-29 06:30 | 2.877 | 0 | N/A | 0 | 0
2021-01-29 07:00 | 3.2744 | 0 | N/A | 0 | 0
2021-01-29 07:30 | 3.9528 | 0 | N/A | 0 | 0
2021-01-29 08:00 | 4.311 | 0 | N/A | 0 | 0
2021-01-29 08:30 | 4.3206 | 0 | N/A | 0 | 0
2021-01-29 09:00 | 4.2127 | 0 | N/A | 0 | 0
2021-01-29 09:30 | 4.1484 | 0 | N/A | 0 | 0
2021-01-29 10:00 | 3.9601 | 0 | N/A | 0 | 0
2021-01-29 10:30 | 4.2506 | 0 | N/A | 0 | 0
2021-01-29 11:00 | 4.1273 | 0 | N/A | 0 | 0
2021-01-29 11:30 | 3.8702 | 0 | N/A | 0 | 0
2021-01-29 12:00 | 3.38 | 0 | N/A | 0 | 0
2021-01-29 12:30 | 3.6517 | 0 | N/A | 0 | 0
2021-01-29 13:00 | 4.036 | 0 | N/A | 0 | 0
2021-01-29 13:30 | 3.4738 | 0 | N/A | 0 | 0
2021-01-29 14:00 | 2.8219 | 0 | N/A | 0 | 0
2021-01-29 14:30 | 3.111 | 0 | N/A | 0 | 0
2021-01-29 15:00 | 2.7414 | 0 | N/A | 0 | 0
2021-01-29 15:30 | 2.4783 | 0 | N/A | 0 | 0
2021-01-29 16:00 | 2.1759 | 0 | N/A | 0 | 0
2021-01-29 16:30 | 3.1237 | 0 | N/A | 0 | 0
2021-01-29 17:00 | 2.981 | 0 | N/A | 0 | 0
2021-01-29 17:30 | 2.7051 | 0 | N/A | 0 | 0
2021-01-29 18:00 | 3.2261 | 0 | N/A | 0 | 0
2021-01-29 18:30 | 3.144 | 0 | N/A | 0 | 0
2021-01-29 19:00 | 3.6532 | 0 | N/A | 0 | 0
2021-01-29 19:30 | 3.9652 | 0 | N/A | 0 | 0
2021-01-29 20:00 | 4.1116 | 0 | N/A | 0 | 0
2021-01-29 20:30 | 4.0256 | 0 | N/A | 0 | 0
2021-01-29 21:00 | 4.0479 | 0 | N/A | 0 | 0
2021-01-29 21:30 | 3.9533 | 0 | N/A | 0 | 0
2021-01-29 22:00 | 3.6932 | 0 | N/A | 0 | 0
2021-01-29 22:30 | 4.0657 | 0 | N/A | 0 | 0
2021-01-29 23:00 | 4.2137 | 0 | N/A | 0 | 0
2021-01-29 23:30 | 3.9435 | 0 | N/A | 0 | 0
2021-01-30 | 3.8352 | 0 | N/A | 0 | 0
2021-01-30 00:30 | 4.4847 | 0 | N/A | 0 | 0
2021-01-30 01:00 | 4.5613 | 0 | N/A | 0 | 0
2021-01-30 01:30 | 3.5255 | 0 | N/A | 0 | 0
2021-01-30 02:00 | 2.7236 | 0 | N/A | 0 | 0
2021-01-30 02:30 | 2.6601 | 0 | N/A | 0 | 0
2021-01-30 03:00 | 2.3359 | 0 | N/A | 0 | 0
2021-01-30 03:30 | 2.0186 | 0 | N/A | 0 | 0
2021-01-30 04:00 | 1.9343 | 0 | N/A | 0 | 0
2021-01-30 04:30 | 1.839 | 0 | N/A | 0 | 0
2021-01-30 05:00 | 1.8585 | 0 | N/A | 0 | 0
2021-01-30 05:30 | 1.7908 | 0 | N/A | 0 | 0
2021-01-30 06:00 | 2.0194 | 0 | N/A | 0 | 0
2021-01-30 06:30 | 2.2231 | 0 | N/A | 0 | 0
2021-01-30 07:00 | 2.2929 | 0 | N/A | 0 | 0
2021-01-30 07:30 | 2.5329 | 0 | N/A | 0 | 0
2021-01-30 08:00 | 2.7392 | 0 | N/A | 0 | 0
2021-01-30 08:30 | 2.8064 | 0 | N/A | 0 | 0
2021-01-30 09:00 | 2.9058 | 0 | N/A | 0 | 0
2021-01-30 09:30 | 2.8827 | 0 | N/A | 0 | 0
2021-01-30 10:00 | 2.5739 | 0 | N/A | 0 | 0
2021-01-30 10:30 | 2.4305 | 0 | N/A | 0 | 0
2021-01-30 11:00 | 1.5048 | 0 | N/A | 0 | 0
2021-01-30 11:30 | 1.2752 | 0 | N/A | 0 | 0
2021-01-30 12:00 | 0.8676 | 0 | N/A | 0 | 0
2021-01-30 12:30 | 0.53971 | 0 | N/A | 0 | 0
2021-01-30 13:00 | 0.27358 | 0 | N/A | 0 | 0
2021-01-30 13:30 | -0.2275 | 0 | N/A | 0 | 0
2021-01-30 14:00 | -0.39436 | 0 | N/A | 0 | 0
2021-01-30 14:30 | 0.15293 | 0 | N/A | 0 | 0
2021-01-30 15:00 | 0.16282 | 0 | N/A | 0 | 0
2021-01-30 15:30 | -0.39939 | 0 | N/A | 0 | 0
2021-01-30 16:00 | -0.19894 | 0 | N/A | 0 | 0
2021-01-30 16:30 | 0.324 | 0 | N/A | 0 | 0
2021-01-30 17:00 | 0.87363 | 0 | N/A | 0 | 0
2021-01-30 17:30 | 1.6744 | 0 | N/A | 0 | 0
2021-01-30 18:00 | 2.7059 | 0 | N/A | 0 | 0
2021-01-30 18:30 | 3.3003 | 0 | N/A | 0 | 0
2021-01-30 19:00 | 3.6003 | 0 | N/A | 0 | 0
2021-01-30 19:30 | 3.8343 | 0 | N/A | 0 | 0
2021-01-30 20:00 | 3.7488 | 0 | N/A | 0 | 0
2021-01-30 20:30 | 3.651 | 0 | N/A | 0 | 0
2021-01-30 21:00 | 3.5787 | 0 | N/A | 0 | 0
2021-01-30 21:30 | 3.5333 | 0 | N/A | 0 | 0
2021-01-30 22:00 | 3.3411 | 0 | N/A | 0 | 0
2021-01-30 22:30 | 3.7611 | 0 | N/A | 0 | 0
2021-01-30 23:00 | 4.0735 | 0 | N/A | 0 | 0
2021-01-30 23:30 | 3.8335 | 0 | N/A | 0 | 0
2021-01-31 | 3.8993 | 0 | N/A | 0 | 0
2021-01-31 00:30 | 4.3359 | 0 | N/A | 0 | 0
2021-01-31 01:00 | 4.5547 | 0 | N/A | 0 | 0
2021-01-31 01:30 | 3.748 | 0 | N/A | 0 | 0
2021-01-31 02:00 | 2.9556 | 0 | N/A | 0 | 0
2021-01-31 02:30 | 2.8617 | 0 | N/A | 0 | 0
2021-01-31 03:00 | 2.6024 | 0 | N/A | 0 | 0
2021-01-31 03:30 | 2.2091 | 0 | N/A | 0 | 0
2021-01-31 04:00 | 2.043 | 0 | N/A | 0 | 0
2021-01-31 04:30 | 1.9531 | 0 | N/A | 0 | 0
2021-01-31 05:00 | 1.8582 | 0 | N/A | 0 | 0
2021-01-31 05:30 | 1.8873 | 0 | N/A | 0 | 0
2021-01-31 06:00 | 1.9251 | 0 | N/A | 0 | 0
2021-01-31 06:30 | 2.1735 | 0 | N/A | 0 | 0
2021-01-31 07:00 | 2.2749 | 0 | N/A | 0 | 0
2021-01-31 07:30 | 2.3823 | 0 | N/A | 0 | 0
2021-01-31 08:00 | 2.2568 | 0 | N/A | 0 | 0
2021-01-31 08:30 | 1.9459 | 0 | N/A | 0 | 0
2021-01-31 09:00 | 1.8366 | 0 | N/A | 0 | 0
2021-01-31 09:30 | 1.4875 | 0 | N/A | 0 | 0
2021-01-31 10:00 | 0.98018 | 0 | N/A | 0 | 0
2021-01-31 10:30 | 0.68827 | 0 | N/A | 0 | 0
2021-01-31 11:00 | -0.34527 | 0 | N/A | 0 | 0
2021-01-31 11:30 | -0.57969 | 0 | N/A | 0 | 0
2021-01-31 12:00 | -0.74739 | 0 | N/A | 0 | 0
2021-01-31 12:30 | -0.70017 | 0 | N/A | 0 | 0
2021-01-31 13:00 | -0.94136 | 0 | N/A | 0 | 0
2021-01-31 13:30 | -1.0912 | 0 | N/A | 0 | 0
2021-01-31 14:00 | -1.2144 | 0 | N/A | 0 | 0
2021-01-31 14:30 | -1.3451 | 0 | N/A | 0 | 0
2021-01-31 15:00 | -1.2853 | 0 | N/A | 0 | 0
2021-01-31 15:30 | -1.1752 | 0 | N/A | 0 | 0
2021-01-31 16:00 | -0.9485 | 0 | N/A | 0 | 0
2021-01-31 16:30 | -0.61119 | 0 | N/A | 0 | 0
2021-01-31 17:00 | -0.20467 | 0 | N/A | 0 | 0
2021-01-31 17:30 | 0.71006 | 0 | N/A | 0 | 0
2021-01-31 18:00 | 1.6572 | 0 | N/A | 0 | 0
2021-01-31 18:30 | 2.4053 | 0 | N/A | 0 | 0
2021-01-31 19:00 | 3.0402 | 0 | N/A | 0 | 0
2021-01-31 19:30 | 3.4998 | 0 | N/A | 0 | 0
2021-01-31 20:00 | 3.6275 | 0 | N/A | 0 | 0
2021-01-31 20:30 | 3.6168 | 0 | N/A | 0 | 0
2021-01-31 21:00 | 3.6354 | 0 | N/A | 0 | 0
2021-01-31 21:30 | 3.6973 | 0 | N/A | 0 | 0
2021-01-31 22:00 | 3.4712 | 0 | N/A | 0 | 0
2021-01-31 22:30 | 3.7578 | 0 | N/A | 0 | 0
2021-01-31 23:00 | 3.982 | 0 | N/A | 0 | 0
2021-01-31 23:30 | 3.6623 | 0 | N/A | 0 | 0
2021-02-01 | 3.7856 | 0 | N/A | 0 | 0
2021-02-01 00:30 | 4.0909 | 0 | N/A | 0 | 0
2021-02-01 01:00 | 4.639 | 0 | N/A | 0 | 0
2021-02-01 01:30 | 3.8289 | 0 | N/A | 0 | 0
2021-02-01 02:00 | 3.0531 | 0 | N/A | 0 | 0
2021-02-01 02:30 | 2.9235 | 0 | N/A | 0 | 0
2021-02-01 03:00 | 2.6602 | 0 | N/A | 0 | 0
2021-02-01 03:30 | 2.3455 | 0 | N/A | 0 | 0
2021-02-01 04:00 | 2.1068 | 0 | N/A | 0 | 0
2021-02-01 04:30 | 1.9907 | 0 | N/A | 0 | 0
2021-02-01 05:00 | 1.9714 | 0 | N/A | 0 | 0
2021-02-01 05:30 | 2.1465 | 0 | N/A | 0 | 0
2021-02-01 06:00 | 2.4338 | 0 | N/A | 0 | 0
2021-02-01 06:30 | 2.9553 | 0 | N/A | 0 | 0
2021-02-01 07:00 | 3.4698 | 0 | N/A | 0 | 0
2021-02-01 07:30 | 4.2465 | 0 | N/A | 0 | 0
2021-02-01 08:00 | 4.3606 | 0 | N/A | 0 | 0
2021-02-01 08:30 | 3.5567 | 0 | N/A | 0 | 0
2021-02-01 09:00 | 3.2233 | 0 | N/A | 0 | 0
2021-02-01 09:30 | 3.25 | 0 | N/A | 0 | 0
2021-02-01 10:00 | 3.0167 | 0 | N/A | 0 | 0
2021-02-01 10:30 | 2.88 | 0 | N/A | 0 | 0
2021-02-01 11:00 | 2.7434 | 0 | N/A | 0 | 0
2021-02-01 11:30 | 2.9034 | 0 | N/A | 0 | 0
2021-02-01 12:00 | 2.0416 | 0 | N/A | 0 | 0
2021-02-01 12:30 | 1.8811 | 0 | N/A | 0 | 0
2021-02-01 13:00 | 1.6101 | 0 | N/A | 0 | 0
2021-02-01 13:30 | 1.4471 | 0 | N/A | 0 | 0
2021-02-01 14:00 | 1.6405 | 0 | N/A | 0 | 0
2021-02-01 14:30 | 1.9513 | 0 | N/A | 0 | 0
2021-02-01 15:00 | 1.864 | 0 | N/A | 0 | 0
2021-02-01 15:30 | 1.5734 | 0 | N/A | 0 | 0
2021-02-01 16:00 | 1.3334 | 0 | N/A | 0 | 0
2021-02-01 16:30 | 1.161 | 0 | N/A | 0 | 0
2021-02-01 17:00 | 0.85615 | 0 | N/A | 0 | 0
2021-02-01 17:30 | 1.5328 | 0 | N/A | 0 | 0
2021-02-01 18:00 | 2.5865 | 0 | N/A | 0 | 0
2021-02-01 18:30 | 3.4576 | 0 | N/A | 0 | 0
2021-02-01 19:00 | 3.7039 | 0 | N/A | 0 | 0
2021-02-01 19:30 | 3.6318 | 0 | N/A | 0 | 0
2021-02-01 20:00 | 3.7964 | 0 | N/A | 0 | 0
2021-02-01 20:30 | 3.9993 | 0 | N/A | 0 | 0
2021-02-01 21:00 | 4.0235 | 0 | N/A | 0 | 0
2021-02-01 21:30 | 3.9055 | 0 | N/A | 0 | 0
2021-02-01 22:00 | 3.7397 | 0 | N/A | 0 | 0
2021-02-01 22:30 | 3.9739 | 0 | N/A | 0 | 0
2021-02-01 23:00 | 4.1216 | 0 | N/A | 0 | 0
2021-02-01 23:30 | 3.7661 | 0 | N/A | 0 | 0
2021-02-02 | 3.7028 | 0 | N/A | 0 | 0
2021-02-02 00:30 | 4.3198 | 0 | N/A | 0 | 0
2021-02-02 01:00 | 4.5932 | 0 | N/A | 0 | 0
2021-02-02 01:30 | 3.6821 | 0 | N/A | 0 | 0
2021-02-02 02:00 | 2.9973 | 0 | N/A | 0 | 0
2021-02-02 02:30 | 2.7407 | 0 | N/A | 0 | 0
2021-02-02 03:00 | 2.4393 | 0 | N/A | 0 | 0
2021-02-02 03:30 | 2.2158 | 0 | N/A | 0 | 0
2021-02-02 04:00 | 2.0761 | 0 | N/A | 0 | 0
2021-02-02 04:30 | 1.956 | 0 | N/A | 0 | 0
2021-02-02 05:00 | 2.0147 | 0 | N/A | 0 | 0
2021-02-02 05:30 | 2.2203 | 0 | N/A | 0 | 0
2021-02-02 06:00 | 2.5121 | 0 | N/A | 0 | 0
2021-02-02 06:30 | 3.1094 | 0 | N/A | 0 | 0
2021-02-02 07:00 | 4.0426 | 0 | N/A | 0 | 0
2021-02-02 07:30 | 4.8805 | 0 | N/A | 0 | 0
2021-02-02 08:00 | 4.6637 | 0 | N/A | 0 | 0
2021-02-02 08:30 | 3.6967 | 0 | N/A | 0 | 0
2021-02-02 09:00 | 3.0633 | 0 | N/A | 0 | 0
2021-02-02 09:30 | 2.89 | 0 | N/A | 0 | 0
2021-02-02 10:00 | 2.64 | 0 | N/A | 0 | 0
2021-02-02 10:30 | 2.0243 | 0 | N/A | 0 | 0
2021-02-02 11:00 | 1.828 | 0 | N/A | 0 | 0
2021-02-02 11:30 | 1.451 | 0 | N/A | 0 | 0
2021-02-02 12:00 | 1.1073 | 0 | N/A | 0 | 0
2021-02-02 12:30 | 0.87689 | 0 | N/A | 0 | 0
2021-02-02 13:00 | 0.46545 | 0 | N/A | 0 | 0
2021-02-02 13:30 | 0.57419 | 0 | N/A | 0 | 0
2021-02-02 14:00 | 0.27657 | 0 | N/A | 0 | 0
2021-02-02 14:30 | 0.33213 | 0 | N/A | 0 | 0
2021-02-02 15:00 | -0.36857 | 0 | N/A | 0 | 0
2021-02-02 15:30 | -0.32648 | 0 | N/A | 0 | 0
2021-02-02 16:00 | -0.095452 | 0 | N/A | 0 | 0
2021-02-02 16:30 | 0.44045 | 0 | N/A | 0 | 0
2021-02-02 17:00 | 0.5492 | 0 | N/A | 0 | 0
2021-02-02 17:30 | 1.1453 | 0 | N/A | 0 | 0
2021-02-02 18:00 | 2.3345 | 0 | N/A | 0 | 0
2021-02-02 18:30 | 3.3199 | 0 | N/A | 0 | 0
2021-02-02 19:00 | 3.6425 | 0 | N/A | 0 | 0
2021-02-02 19:30 | 3.8649 | 0 | N/A | 0 | 0
2021-02-02 20:00 | 3.9612 | 0 | N/A | 0 | 0
2021-02-02 20:30 | 4.0819 | 0 | N/A | 0 | 0
2021-02-02 21:00 | 4.168 | 0 | N/A | 0 | 0
2021-02-02 21:30 | 4.0394 | 0 | N/A | 0 | 0
2021-02-02 22:00 | 3.7392 | 0 | N/A | 0 | 0
2021-02-02 22:30 | 3.9839 | 0 | N/A | 0 | 0
2021-02-02 23:00 | 4.1257 | 0 | N/A | 0 | 0
2021-02-02 23:30 | 3.7412 | 0 | N/A | 0 | 0
2021-02-03 | 3.88 | 0 | N/A | 0 | 0
2021-02-03 00:30 | 4.2799 | 0 | N/A | 0 | 0
2021-02-03 01:00 | 4.536 | 0 | N/A | 0 | 0
2021-02-03 01:30 | 3.6803 | 0 | N/A | 0 | 0
2021-02-03 02:00 | 2.9001 | 0 | N/A | 0 | 0
2021-02-03 02:30 | 2.8474 | 0 | N/A | 0 | 0
2021-02-03 03:00 | 2.4945 | 0 | N/A | 0 | 0
2021-02-03 03:30 | 2.1894 | 0 | N/A | 0 | 0
2021-02-03 04:00 | 1.9928 | 0 | N/A | 0 | 0
2021-02-03 04:30 | 1.9814 | 0 | N/A | 0 | 0
2021-02-03 05:00 | 2.0377 | 0 | N/A | 0 | 0
2021-02-03 05:30 | 2.208 | 0 | N/A | 0 | 0
2021-02-03 06:00 | 2.4897 | 0 | N/A | 0 | 0
2021-02-03 06:30 | 3.1612 | 0 | N/A | 0 | 0
2021-02-03 07:00 | 3.8295 | 0 | N/A | 0 | 0
2021-02-03 07:30 | 4.7154 | 0 | N/A | 0 | 0
2021-02-03 08:00 | 4.8667 | 0 | N/A | 0 | 0
2021-02-03 08:30 | 4.19 | 0 | N/A | 0 | 0
2021-02-03 09:00 | 3.6467 | 0 | N/A | 0 | 0
2021-02-03 09:30 | 3.6802 | 0 | N/A | 0 | 0
2021-02-03 10:00 | 3.0533 | 0 | N/A | 0 | 0
2021-02-03 10:30 | 2.8435 | 0 | N/A | 0 | 0
2021-02-03 11:00 | 2.6241 | 0 | N/A | 0 | 0
2021-02-03 11:30 | 2.3172 | 0 | N/A | 0 | 0
2021-02-03 12:00 | 1.4626 | 0 | N/A | 0 | 0
2021-02-03 12:30 | 0.37631 | 0 | N/A | 0 | 0
2021-02-03 13:00 | -0.31314 | 0 | N/A | 0 | 0
2021-02-03 13:30 | -0.51161 | 0 | N/A | 0 | 0
2021-02-03 14:00 | -0.65021 | 0 | N/A | 0 | 0
2021-02-03 14:30 | -0.68007 | 0 | N/A | 0 | 0
2021-02-03 15:00 | -0.65456 | 0 | N/A | 0 | 0
2021-02-03 15:30 | -0.6389 | 0 | N/A | 0 | 0
2021-02-03 16:00 | -0.46482 | 0 | N/A | 0 | 0
2021-02-03 16:30 | -0.20301 | 0 | N/A | 0 | 0
2021-02-03 17:00 | 0.22204 | 0 | N/A | 0 | 0
2021-02-03 17:30 | 0.83683 | 0 | N/A | 0 | 0
2021-02-03 18:00 | 1.745 | 0 | N/A | 0 | 0
2021-02-03 18:30 | 2.4574 | 0 | N/A | 0 | 0
2021-02-03 19:00 | 3.0969 | 0 | N/A | 0 | 0
2021-02-03 19:30 | 3.4213 | 0 | N/A | 0 | 0
2021-02-03 20:00 | 3.6668 | 0 | N/A | 0 | 0
2021-02-03 20:30 | 3.8336 | 0 | N/A | 0 | 0
2021-02-03 21:00 | 3.9484 | 0 | N/A | 0 | 0
2021-02-03 21:30 | 3.8578 | 0 | N/A | 0 | 0
2021-02-03 22:00 | 3.6557 | 0 | N/A | 0 | 0
2021-02-03 22:30 | 3.9096 | 0 | N/A | 0 | 0
2021-02-03 23:00 | 4.0402 | 0 | N/A | 0 | 0
2021-02-03 23:30 | 3.628 | 0 | N/A | 0 | 0
2021-02-04 | 3.6355 | 0 | N/A | 0 | 0
2021-02-04 00:30 | 4.168 | 0 | N/A | 0 | 0
2021-02-04 01:00 | 4.4067 | 0 | N/A | 0 | 0
2021-02-04 01:30 | 3.4612 | 0 | N/A | 0 | 0
2021-02-04 02:00 | 2.6865 | 0 | N/A | 0 | 0
2021-02-04 02:30 | 2.6404 | 0 | N/A | 0 | 0
2021-02-04 03:00 | 2.316 | 0 | N/A | 0 | 0
2021-02-04 03:30 | 2.0586 | 0 | N/A | 0 | 0
2021-02-04 04:00 | 1.8991 | 0 | N/A | 0 | 0
2021-02-04 04:30 | 1.8496 | 0 | N/A | 0 | 0
2021-02-04 05:00 | 1.8879 | 0 | N/A | 0 | 0
2021-02-04 05:30 | 2.1001 | 0 | N/A | 0 | 0
2021-02-04 06:00 | 2.363 | 0 | N/A | 0 | 0
2021-02-04 06:30 | 2.8613 | 0 | N/A | 0 | 0
2021-02-04 07:00 | 3.3543 | 0 | N/A | 0 | 0
2021-02-04 07:30 | 4.0025 | 0 | N/A | 0 | 0
2021-02-04 08:00 | 3.9018 | 0 | N/A | 0 | 0
2021-02-04 08:30 | 3.3458 | 0 | N/A | 0 | 0
2021-02-04 09:00 | 2.78 | 0 | N/A | 0 | 0
2021-02-04 09:30 | 2.2918 | 0 | N/A | 0 | 0
2021-02-04 10:00 | 2.5182 | 0 | N/A | 0 | 0
2021-02-04 10:30 | 2.5547 | 0 | N/A | 0 | 0
2021-02-04 11:00 | 2.3509 | 0 | N/A | 0 | 0
2021-02-04 11:30 | 2.27 | 0 | N/A | 0 | 0
2021-02-04 12:00 | 1.9737 | 0 | N/A | 0 | 0
2021-02-04 12:30 | 1.6467 | 0 | N/A | 0 | 0
2021-02-04 13:00 | 1.5033 | 0 | N/A | 0 | 0
2021-02-04 13:30 | 0.67212 | 0 | N/A | 0 | 0
2021-02-04 14:00 | 0.60665 | 0 | N/A | 0 | 0
2021-02-04 14:30 | 1.3841 | 0 | N/A | 0 | 0
2021-02-04 15:00 | 1.5915 | 0 | N/A | 0 | 0
2021-02-04 15:30 | 1.8004 | 0 | N/A | 0 | 0
2021-02-04 16:00 | 1.8202 | 0 | N/A | 0 | 0
2021-02-04 16:30 | 2.1329 | 0 | N/A | 0 | 0
2021-02-04 17:00 | 2.7556 | 0 | N/A | 0 | 0
2021-02-04 17:30 | 3.1739 | 0 | N/A | 0 | 0
2021-02-04 18:00 | 3.9371 | 0 | N/A | 0 | 0
2021-02-04 18:30 | 3.764 | 0 | N/A | 0 | 0
2021-02-04 19:00 | 3.8179 | 0 | N/A | 0 | 0
2021-02-04 19:30 | 3.7714 | 0 | N/A | 0 | 0
2021-02-04 20:00 | 3.8584 | 0 | N/A | 0 | 0
2021-02-04 20:30 | 4.0114 | 0 | N/A | 0 | 0
2021-02-04 21:00 | 3.9299 | 0 | N/A | 0 | 0
2021-02-04 21:30 | 3.8568 | 0 | N/A | 0 | 0
2021-02-04 22:00 | 3.5323 | 0 | N/A | 0 | 0
2021-02-04 22:30 | 3.805 | 0 | N/A | 0 | 0
2021-02-04 23:00 | 3.9292 | 0 | N/A | 0 | 0
2021-02-04 23:30 | 3.6435 | 0 | N/A | 0 | 0
2021-02-05 | 3.512 | 0 | N/A | 0 | 0
2021-02-05 00:30 | 4.0094 | 0 | N/A | 0 | 0
2021-02-05 01:00 | 4.4666 | 0 | N/A | 0 | 0
2021-02-05 01:30 | 3.4692 | 0 | N/A | 0 | 0
2021-02-05 02:00 | 2.7681 | 0 | N/A | 0 | 0
2021-02-05 02:30 | 2.7045 | 0 | N/A | 0 | 0
2021-02-05 03:00 | 2.4011 | 0 | N/A | 0 | 0
2021-02-05 03:30 | 2.0437 | 0 | N/A | 0 | 0
2021-02-05 04:00 | 1.9319 | 0 | N/A | 0 | 0
2021-02-05 04:30 | 1.8636 | 0 | N/A | 0 | 0
2021-02-05 05:00 | 1.9978 | 0 | N/A | 0 | 0
2021-02-05 05:30 | 2.0819 | 0 | N/A | 0 | 0
2021-02-05 06:00 | 2.3737 | 0 | N/A | 0 | 0
2021-02-05 06:30 | 2.9068 | 0 | N/A | 0 | 0
2021-02-05 07:00 | 3.4517 | 0 | N/A | 0 | 0
2021-02-05 07:30 | 3.7809 | 0 | N/A | 0 | 0
2021-02-05 08:00 | 3.7934 | 0 | N/A | 0 | 0
2021-02-05 08:30 | 2.861 | 0 | N/A | 0 | 0
2021-02-05 09:00 | 2.0726 | 0 | N/A | 0 | 0
2021-02-05 09:30 | 2.0474 | 0 | N/A | 0 | 0
2021-02-05 10:00 | 1.3252 | 0 | N/A | 0 | 0
2021-02-05 10:30 | 1.8077 | 0 | N/A | 0 | 0
2021-02-05 11:00 | 3.37 | 0 | N/A | 0 | 0
2021-02-05 11:30 | 2.7033 | 0 | N/A | 0 | 0
2021-02-05 12:00 | 3.2401 | 0 | N/A | 0 | 0
2021-02-05 12:30 | 3.0141 | 0 | N/A | 0 | 0
2021-02-05 13:00 | 2.5643 | 0 | N/A | 0 | 0
2021-02-05 13:30 | 2.3283 | 0 | N/A | 0 | 0
2021-02-05 14:00 | 0.58682 | 0 | N/A | 0 | 0
2021-02-05 14:30 | 0.41034 | 0 | N/A | 0 | 0
2021-02-05 15:00 | 0.13667 | 0 | N/A | 0 | 0
2021-02-05 15:30 | -0.65697 | 0 | N/A | 0 | 0
2021-02-05 16:00 | -0.55989 | 0 | N/A | 0 | 0
2021-02-05 16:30 | -0.23106 | 0 | N/A | 0 | 0
2021-02-05 17:00 | 0.7433 | 0 | N/A | 0 | 0
2021-02-05 17:30 | 1.0978 | 0 | N/A | 0 | 0
2021-02-05 18:00 | 1.9644 | 0 | N/A | 0 | 0
2021-02-05 18:30 | 2.456 | 0 | N/A | 0 | 0
2021-02-05 19:00 | 3.1331 | 0 | N/A | 0 | 0
2021-02-05 19:30 | 3.3212 | 0 | N/A | 0 | 0
2021-02-05 20:00 | 3.4926 | 0 | N/A | 0 | 0
2021-02-05 20:30 | 3.6054 | 0 | N/A | 0 | 0
2021-02-05 21:00 | 3.7208 | 0 | N/A | 0 | 0
2021-02-05 21:30 | 3.6366 | 0 | N/A | 0 | 0
2021-02-05 22:00 | 3.4663 | 0 | N/A | 0 | 0
2021-02-05 22:30 | 3.8444 | 0 | N/A | 0 | 0
2021-02-05 23:00 | 4.018 | 0 | N/A | 0 | 0
2021-02-05 23:30 | 3.7156 | 0 | N/A | 0 | 0
2021-02-06 | 3.6816 | 0 | N/A | 0 | 0
2021-02-06 00:30 | 4.1758 | 0 | N/A | 0 | 0
2021-02-06 01:00 | 4.3434 | 0 | N/A | 0 | 0
2021-02-06 01:30 | 3.3319 | 0 | N/A | 0 | 0
2021-02-06 02:00 | 2.571 | 0 | N/A | 0 | 0
2021-02-06 02:30 | 2.6261 | 0 | N/A | 0 | 0
2021-02-06 03:00 | 2.2745 | 0 | N/A | 0 | 0
2021-02-06 03:30 | 2.0077 | 0 | N/A | 0 | 0
2021-02-06 04:00 | 1.9153 | 0 | N/A | 0 | 0
2021-02-06 04:30 | 1.8496 | 0 | N/A | 0 | 0
2021-02-06 05:00 | 1.82 | 0 | N/A | 0 | 0
2021-02-06 05:30 | 1.8644 | 0 | N/A | 0 | 0
2021-02-06 06:00 | 1.9956 | 0 | N/A | 0 | 0
2021-02-06 06:30 | 2.2888 | 0 | N/A | 0 | 0
2021-02-06 07:00 | 2.4233 | 0 | N/A | 0 | 0
2021-02-06 07:30 | 2.7456 | 0 | N/A | 0 | 0
2021-02-06 08:00 | 2.8402 | 0 | N/A | 0 | 0
2021-02-06 08:30 | 2.7469 | 0 | N/A | 0 | 0
2021-02-06 09:00 | 2.779 | 0 | N/A | 0 | 0
2021-02-06 09:30 | 2.7244 | 0 | N/A | 0 | 0
2021-02-06 10:00 | 2.6946 | 0 | N/A | 0 | 0
2021-02-06 10:30 | 2.4859 | 0 | N/A | 0 | 0
2021-02-06 11:00 | 1.769 | 0 | N/A | 0 | 0
2021-02-06 11:30 | 1.4827 | 0 | N/A | 0 | 0
2021-02-06 12:00 | 0.81275 | 0 | N/A | 0 | 0
2021-02-06 12:30 | 0.72014 | 0 | N/A | 0 | 0
2021-02-06 13:00 | 0.73424 | 0 | N/A | 0 | 0
2021-02-06 13:30 | 0.6744 | 0 | N/A | 0 | 0
2021-02-06 14:00 | 0.49872 | 0 | N/A | 0 | 0
2021-02-06 14:30 | 0.37538 | 0 | N/A | 0 | 0
2021-02-06 15:00 | -0.4714 | 0 | N/A | 0 | 0
2021-02-06 15:30 | -0.52062 | 0 | N/A | 0 | 0
2021-02-06 16:00 | -0.48268 | 0 | N/A | 0 | 0
2021-02-06 16:30 | 0.29002 | 0 | N/A | 0 | 0
2021-02-06 17:00 | 0.3769 | 0 | N/A | 0 | 0
2021-02-06 17:30 | 0.74232 | 0 | N/A | 0 | 0
2021-02-06 18:00 | 1.5948 | 0 | N/A | 0 | 0
2021-02-06 18:30 | 2.2753 | 0 | N/A | 0 | 0
2021-02-06 19:00 | 2.9958 | 0 | N/A | 0 | 0
2021-02-06 19:30 | 3.3116 | 0 | N/A | 0 | 0
2021-02-06 20:00 | 3.5106 | 0 | N/A | 0 | 0
2021-02-06 20:30 | 3.4288 | 0 | N/A | 0 | 0
2021-02-06 21:00 | 3.3924 | 0 | N/A | 0 | 0
2021-02-06 21:30 | 3.3481 | 0 | N/A | 0 | 0
2021-02-06 22:00 | 3.2278 | 0 | N/A | 0 | 0
2021-02-06 22:30 | 3.6911 | 0 | N/A | 0 | 0
2021-02-06 23:00 | 3.8977 | 0 | N/A | 0 | 0
2021-02-06 23:30 | 3.5724 | 0 | N/A | 0 | 0
2021-02-07 | 3.7548 | 0 | N/A | 0 | 0
2021-02-07 00:30 | 4.3053 | 0 | N/A | 0 | 0
2021-02-07 01:00 | 4.5708 | 0 | N/A | 0 | 0
2021-02-07 01:30 | 3.715 | 0 | N/A | 0 | 0
2021-02-07 02:00 | 2.9655 | 0 | N/A | 0 | 0
2021-02-07 02:30 | 2.8158 | 0 | N/A | 0 | 0
2021-02-07 03:00 | 2.5444 | 0 | N/A | 0 | 0
2021-02-07 03:30 | 2.1525 | 0 | N/A | 0 | 0
2021-02-07 04:00 | 1.9531 | 0 | N/A | 0 | 0
2021-02-07 04:30 | 1.9028 | 0 | N/A | 0 | 0
2021-02-07 05:00 | 1.8619 | 0 | N/A | 0 | 0
2021-02-07 05:30 | 1.8867 | 0 | N/A | 0 | 0
2021-02-07 06:00 | 1.9426 | 0 | N/A | 0 | 0
2021-02-07 06:30 | 2.1775 | 0 | N/A | 0 | 0
2021-02-07 07:00 | 2.2484 | 0 | N/A | 0 | 0
2021-02-07 07:30 | 2.4743 | 0 | N/A | 0 | 0
2021-02-07 08:00 | 2.5057 | 0 | N/A | 0 | 0
2021-02-07 08:30 | 2.3612 | 0 | N/A | 0 | 0
2021-02-07 09:00 | 2.3439 | 0 | N/A | 0 | 0
2021-02-07 09:30 | 2.5041 | 0 | N/A | 0 | 0
2021-02-07 10:00 | 2.7351 | 0 | N/A | 0 | 0
2021-02-07 10:30 | 2.6939 | 0 | N/A | 0 | 0
2021-02-07 11:00 | 2.6646 | 0 | N/A | 0 | 0
2021-02-07 11:30 | 2.5495 | 0 | N/A | 0 | 0
2021-02-07 12:00 | 2.6497 | 0 | N/A | 0 | 0
2021-02-07 12:30 | 2.3993 | 0 | N/A | 0 | 0
2021-02-07 13:00 | 2.3469 | 0 | N/A | 0 | 0
2021-02-07 13:30 | 2.5011 | 0 | N/A | 0 | 0
2021-02-07 14:00 | 1.7369 | 0 | N/A | 0 | 0
2021-02-07 14:30 | 1.8132 | 0 | N/A | 0 | 0
2021-02-07 15:00 | 1.6119 | 0 | N/A | 0 | 0
2021-02-07 15:30 | 1.4473 | 0 | N/A | 0 | 0
2021-02-07 16:00 | 1.4188 | 0 | N/A | 0 | 0
2021-02-07 16:30 | 1.3935 | 0 | N/A | 0 | 0
2021-02-07 17:00 | 1.2227 | 0 | N/A | 0 | 0
2021-02-07 17:30 | 1.325 | 0 | N/A | 0 | 0
2021-02-07 18:00 | 2.2312 | 0 | N/A | 0 | 0
2021-02-07 18:30 | 2.8234 | 0 | N/A | 0 | 0
2021-02-07 19:00 | 3.3423 | 0 | N/A | 0 | 0
2021-02-07 19:30 | 3.7887 | 0 | N/A | 0 | 0
2021-02-07 20:00 | 3.9706 | 0 | N/A | 0 | 0
2021-02-07 20:30 | 4.0921 | 0 | N/A | 0 | 0
2021-02-07 21:00 | 4.1479 | 0 | N/A | 0 | 0
2021-02-07 21:30 | 4.0032 | 0 | N/A | 0 | 0
2021-02-07 22:00 | 3.7006 | 0 | N/A | 0 | 0
2021-02-07 22:30 | 4.0148 | 0 | N/A | 0 | 0
2021-02-07 23:00 | 4.1504 | 0 | N/A | 0 | 0
2021-02-07 23:30 | 3.8942 | 0 | N/A | 0 | 0
2021-02-08 | 4.083 | 0 | N/A | 0 | 0
2021-02-08 00:30 | 4.4422 | 0 | N/A | 0 | 0
2021-02-08 01:00 | 4.7759 | 0 | N/A | 0 | 0
2021-02-08 01:30 | 4.0533 | 0 | N/A | 0 | 0
2021-02-08 02:00 | 3.284 | 0 | N/A | 0 | 0
2021-02-08 02:30 | 3.2757 | 0 | N/A | 0 | 0
2021-02-08 03:00 | 2.9769 | 0 | N/A | 0 | 0
2021-02-08 03:30 | 2.4581 | 0 | N/A | 0 | 0
2021-02-08 04:00 | 2.2505 | 0 | N/A | 0 | 0
2021-02-08 04:30 | 2.0986 | 0 | N/A | 0 | 0
2021-02-08 05:00 | 2.1041 | 0 | N/A | 0 | 0
2021-02-08 05:30 | 2.2927 | 0 | N/A | 0 | 0
2021-02-08 06:00 | 2.5734 | 0 | N/A | 0 | 0
2021-02-08 06:30 | 3.0573 | 0 | N/A | 0 | 0
2021-02-08 07:00 | 3.6552 | 0 | N/A | 0 | 0
2021-02-08 07:30 | 4.5591 | 0 | N/A | 0 | 0
2021-02-08 08:00 | 4.6838 | 0 | N/A | 0 | 0
2021-02-08 08:30 | 4.1069 | 0 | N/A | 0 | 0
2021-02-08 09:00 | 3.987 | 0 | N/A | 0 | 0
2021-02-08 09:30 | 3.8283 | 0 | N/A | 0 | 0
2021-02-08 10:00 | 3.1937 | 0 | N/A | 0 | 0
2021-02-08 10:30 | 2.6965 | 0 | N/A | 0 | 0
2021-02-08 11:00 | 1.9466 | 0 | N/A | 0 | 0
2021-02-08 11:30 | 1.5347 | 0 | N/A | 0 | 0
2021-02-08 12:00 | 0.88336 | 0 | N/A | 0 | 0
2021-02-08 12:30 | 0.16667 | 0 | N/A | 0 | 0
2021-02-08 13:00 | 0.24748 | 0 | N/A | 0 | 0
2021-02-08 13:30 | 0.17346 | 0 | N/A | 0 | 0
2021-02-08 14:00 | 0.070079 | 0 | N/A | 0 | 0
2021-02-08 14:30 | -0.13068 | 0 | N/A | 0 | 0
2021-02-08 15:00 | -0.11045 | 0 | N/A | 0 | 0
2021-02-08 15:30 | -0.2169 | 0 | N/A | 0 | 0
2021-02-08 16:00 | -0.34745 | 0 | N/A | 0 | 0
2021-02-08 16:30 | -0.14682 | 0 | N/A | 0 | 0
2021-02-08 17:00 | 0.95249 | 0 | N/A | 0 | 0
2021-02-08 17:30 | 1.182 | 0 | N/A | 0 | 0
2021-02-08 18:00 | 2.3255 | 0 | N/A | 0 | 0
2021-02-08 18:30 | 3.0203 | 0 | N/A | 0 | 0
2021-02-08 19:00 | 3.6678 | 0 | N/A | 0 | 0
2021-02-08 19:30 | 3.9257 | 0 | N/A | 0 | 0
2021-02-08 20:00 | 4.0365 | 0 | N/A | 0 | 0
2021-02-08 20:30 | 4.1965 | 0 | N/A | 0 | 0
2021-02-08 21:00 | 4.3267 | 0 | N/A | 0 | 0
2021-02-08 21:30 | 4.2181 | 0 | N/A | 0 | 0
2021-02-08 22:00 | 3.8344 | 0 | N/A | 0 | 0
2021-02-08 22:30 | 4.0057 | 0 | N/A | 0 | 0
2021-02-08 23:00 | 4.1503 | 0 | N/A | 0 | 0
2021-02-08 23:30 | 3.7347 | 0 | N/A | 0 | 0
2021-02-09 | 3.7818 | 0 | N/A | 0 | 0
2021-02-09 00:30 | 4.2794 | 0 | N/A | 0 | 0
2021-02-09 01:00 | 4.6286 | 0 | N/A | 0 | 0
2021-02-09 01:30 | 3.7518 | 0 | N/A | 0 | 0
2021-02-09 02:00 | 3.0024 | 0 | N/A | 0 | 0
2021-02-09 02:30 | 2.9283 | 0 | N/A | 0 | 0
2021-02-09 03:00 | 2.6122 | 0 | N/A | 0 | 0
2021-02-09 03:30 | 2.2168 | 0 | N/A | 0 | 0
2021-02-09 04:00 | 2.0264 | 0 | N/A | 0 | 0
2021-02-09 04:30 | 1.9513 | 0 | N/A | 0 | 0
2021-02-09 05:00 | 2.086 | 0 | N/A | 0 | 0
2021-02-09 05:30 | 2.2511 | 0 | N/A | 0 | 0
2021-02-09 06:00 | 2.5887 | 0 | N/A | 0 | 0
2021-02-09 06:30 | 3.1013 | 0 | N/A | 0 | 0
2021-02-09 07:00 | 3.635 | 0 | N/A | 0 | 0
2021-02-09 07:30 | 4.4366 | 0 | N/A | 0 | 0
2021-02-09 08:00 | 4.4171 | 0 | N/A | 0 | 0
2021-02-09 08:30 | 3.549 | 0 | N/A | 0 | 0
2021-02-09 09:00 | 2.7917 | 0 | N/A | 0 | 0
2021-02-09 09:30 | 1.9814 | 0 | N/A | 0 | 0
2021-02-09 10:00 | 1.2814 | 0 | N/A | 0 | 0
2021-02-09 10:30 | 0.65436 | 0 | N/A | 0 | 0
2021-02-09 11:00 | 0.27107 | 0 | N/A | 0 | 0
2021-02-09 11:30 | 0.068718 | 0 | N/A | 0 | 0
2021-02-09 12:00 | -0.21554 | 0 | N/A | 0 | 0
2021-02-09 12:30 | -0.27841 | 0 | N/A | 0 | 0
2021-02-09 13:00 | -0.39801 | 0 | N/A | 0 | 0
2021-02-09 13:30 | -0.48718 | 0 | N/A | 0 | 0
2021-02-09 14:00 | -0.5226 | 0 | N/A | 0 | 0
2021-02-09 14:30 | -0.4831 | 0 | N/A | 0 | 0
2021-02-09 15:00 | -0.37668 | 0 | N/A | 0 | 0
2021-02-09 15:30 | -0.39138 | 0 | N/A | 0 | 0
2021-02-09 16:00 | -0.28492 | 0 | N/A | 0 | 0
2021-02-09 16:30 | 0.10462 | 0 | N/A | 0 | 0
2021-02-09 17:00 | 0.38672 | 0 | N/A | 0 | 0
2021-02-09 17:30 | 1.1768 | 0 | N/A | 0 | 0
2021-02-09 18:00 | 2.0919 | 0 | N/A | 0 | 0
2021-02-09 18:30 | 2.8586 | 0 | N/A | 0 | 0
2021-02-09 19:00 | 3.5255 | 0 | N/A | 0 | 0
2021-02-09 19:30 | 3.8386 | 0 | N/A | 0 | 0
2021-02-09 20:00 | 3.9422 | 0 | N/A | 0 | 0
2021-02-09 20:30 | 4.1066 | 0 | N/A | 0 | 0
2021-02-09 21:00 | 4.149 | 0 | N/A | 0 | 0
2021-02-09 21:30 | 3.9233 | 0 | N/A | 0 | 0
2021-02-09 22:00 | 3.6079 | 0 | N/A | 0 | 0
2021-02-09 22:30 | 3.9146 | 0 | N/A | 0 | 0
2021-02-09 23:00 | 3.9166 | 0 | N/A | 0 | 0
2021-02-09 23:30 | 3.5605 | 0 | N/A | 0 | 0
2021-02-10 | 3.6661 | 0 | N/A | 0 | 0
2021-02-10 00:30 | 4.0638 | 0 | N/A | 0 | 0
2021-02-10 01:00 | 4.2772 | 0 | N/A | 0 | 0
2021-02-10 01:30 | 3.3998 | 0 | N/A | 0 | 0
2021-02-10 02:00 | 2.7183 | 0 | N/A | 0 | 0
2021-02-10 02:30 | 2.6315 | 0 | N/A | 0 | 0
2021-02-10 03:00 | 2.3251 | 0 | N/A | 0 | 0
2021-02-10 03:30 | 2.0682 | 0 | N/A | 0 | 0
2021-02-10 04:00 | 1.9165 | 0 | N/A | 0 | 0
2021-02-10 04:30 | 1.8712 | 0 | N/A | 0 | 0
2021-02-10 05:00 | 1.9133 | 0 | N/A | 0 | 0
2021-02-10 05:30 | 2.0975 | 0 | N/A | 0 | 0
2021-02-10 06:00 | 2.4194 | 0 | N/A | 0 | 0
2021-02-10 06:30 | 3.0418 | 0 | N/A | 0 | 0
2021-02-10 07:00 | 3.4858 | 0 | N/A | 0 | 0
2021-02-10 07:30 | 4.2341 | 0 | N/A | 0 | 0
2021-02-10 08:00 | 4.1784 | 0 | N/A | 0 | 0
2021-02-10 08:30 | 3.4929 | 0 | N/A | 0 | 0
2021-02-10 09:00 | 3.3328 | 0 | N/A | 0 | 0
2021-02-10 09:30 | 2.7602 | 0 | N/A | 0 | 0
2021-02-10 10:00 | 2.1233 | 0 | N/A | 0 | 0
2021-02-10 10:30 | 1.5333 | 0 | N/A | 0 | 0
2021-02-10 11:00 | 1.1551 | 0 | N/A | 0 | 0
2021-02-10 11:30 | 0.90151 | 0 | N/A | 0 | 0
2021-02-10 12:00 | 0.78775 | 0 | N/A | 0 | 0
2021-02-10 12:30 | 0.37436 | 0 | N/A | 0 | 0
2021-02-10 13:00 | 0.39693 | 0 | N/A | 0 | 0
2021-02-10 13:30 | 0.44378 | 0 | N/A | 0 | 0
2021-02-10 14:00 | 0.49284 | 0 | N/A | 0 | 0
2021-02-10 14:30 | 0.59399 | 0 | N/A | 0 | 0
2021-02-10 15:00 | 0.87367 | 0 | N/A | 0 | 0
2021-02-10 15:30 | 1.1132 | 0 | N/A | 0 | 0
2021-02-10 16:00 | 1.5149 | 0 | N/A | 0 | 0
2021-02-10 16:30 | 2.3792 | 0 | N/A | 0 | 0
2021-02-10 17:00 | 3.348 | 0 | N/A | 0 | 0
2021-02-10 17:30 | 4.5253 | 0 | N/A | 0 | 0
2021-02-10 18:00 | 5.4074 | 0 | N/A | 0 | 0
2021-02-10 18:30 | 5.4681 | 0 | N/A | 0 | 0
2021-02-10 19:00 | 5.6775 | 0 | N/A | 0 | 0
2021-02-10 19:30 | 5.8339 | 0 | N/A | 0 | 0
2021-02-10 20:00 | 5.7133 | 0 | N/A | 0 | 0
2021-02-10 20:30 | 5.5001 | 0 | N/A | 0 | 0
2021-02-10 21:00 | 5.1901 | 0 | N/A | 0 | 0
2021-02-10 21:30 | 4.8407 | 0 | N/A | 0 | 0
2021-02-10 22:00 | 4.3573 | 0 | N/A | 0 | 0
2021-02-10 22:30 | 4.5112 | 0 | N/A | 0 | 0
2021-02-10 23:00 | 4.3969 | 0 | N/A | 0 | 0
2021-02-10 23:30 | 3.8725 | 0 | N/A | 0 | 0
2021-02-11 | 3.8455 | 0 | N/A | 0 | 0
2021-02-11 00:30 | 4.3234 | 0 | N/A | 0 | 0
2021-02-11 01:00 | 4.433 | 0 | N/A | 0 | 0
2021-02-11 01:30 | 3.4502 | 0 | N/A | 0 | 0
2021-02-11 02:00 | 2.7619 | 0 | N/A | 0 | 0
2021-02-11 02:30 | 2.7677 | 0 | N/A | 0 | 0
2021-02-11 03:00 | 2.4483 | 0 | N/A | 0 | 0
2021-02-11 03:30 | 2.2371 | 0 | N/A | 0 | 0
2021-02-11 04:00 | 2.066 | 0 | N/A | 0 | 0
2021-02-11 04:30 | 2.0108 | 0 | N/A | 0 | 0
2021-02-11 05:00 | 2.0275 | 0 | N/A | 0 | 0
2021-02-11 05:30 | 2.1966 | 0 | N/A | 0 | 0
2021-02-11 06:00 | 2.4438 | 0 | N/A | 0 | 0
2021-02-11 06:30 | 3.0354 | 0 | N/A | 0 | 0
2021-02-11 07:00 | 3.4801 | 0 | N/A | 0 | 0
2021-02-11 07:30 | 4.0634 | 0 | N/A | 0 | 0
2021-02-11 08:00 | 4.0486 | 0 | N/A | 0 | 0
2021-02-11 08:30 | 3.258 | 0 | N/A | 0 | 0
2021-02-11 09:00 | 3.18 | 0 | N/A | 0 | 0
2021-02-11 09:30 | 2.8467 | 0 | N/A | 0 | 0
2021-02-11 10:00 | 1.3233 | 0 | N/A | 0 | 0
2021-02-11 10:30 | 2.1334 | 0 | N/A | 0 | 0
2021-02-11 11:00 | 2.5367 | 0 | N/A | 0 | 0
2021-02-11 11:30 | 1.7954 | 0 | N/A | 0 | 0
2021-02-11 12:00 | 1.3528 | 0 | N/A | 0 | 0
2021-02-11 12:30 | 1.0212 | 0 | N/A | 0 | 0
2021-02-11 13:00 | 1.1333 | 0 | N/A | 0 | 0
2021-02-11 13:30 | 1.8984 | 0 | N/A | 0 | 0
2021-02-11 14:00 | 2.0201 | 0 | N/A | 0 | 0
2021-02-11 14:30 | 2.4586 | 0 | N/A | 0 | 0
2021-02-11 15:00 | 3.3788 | 0 | N/A | 0 | 0
2021-02-11 15:30 | 3.463 | 0 | N/A | 0 | 0
2021-02-11 16:00 | 3.1674 | 0 | N/A | 0 | 0
2021-02-11 16:30 | 4.9671 | 0 | N/A | 0 | 0
2021-02-11 17:00 | 6.0614 | 0 | N/A | 0 | 0
2021-02-11 17:30 | 6.1359 | 0 | N/A | 0 | 0
2021-02-11 18:00 | 6.9403 | 0 | N/A | 0 | 0
2021-02-11 18:30 | 6.4998 | 0 | N/A | 0 | 0
2021-02-11 19:00 | 6.2378 | 0 | N/A | 0 | 0
2021-02-11 19:30 | 5.65 | 0 | N/A | 0 | 0
2021-02-11 20:00 | 5.26 | 0 | N/A | 0 | 0
2021-02-11 20:30 | 4.977 | 0 | N/A | 0 | 0
2021-02-11 21:00 | 4.7838 | 0 | N/A | 0 | 0
2021-02-11 21:30 | 4.4202 | 0 | N/A | 0 | 0
2021-02-11 22:00 | 4.0211 | 0 | N/A | 0 | 0
2021-02-11 22:30 | 4.2411 | 0 | N/A | 0 | 0
2021-02-11 23:00 | 4.2597 | 0 | N/A | 0 | 0
2021-02-11 23:30 | 3.8777 | 0 | N/A | 0 | 0
2021-02-12 | 3.7809 | 0 | N/A | 0 | 0
2021-02-12 00:30 | 4.2944 | 0 | N/A | 0 | 0
2021-02-12 01:00 | 4.4308 | 0 | N/A | 0 | 0
2021-02-12 01:30 | 3.354 | 0 | N/A | 0 | 0
2021-02-12 02:00 | 2.6935 | 0 | N/A | 0 | 0
2021-02-12 02:30 | 2.59 | 0 | N/A | 0 | 0
2021-02-12 03:00 | 2.3505 | 0 | N/A | 0 | 0
2021-02-12 03:30 | 2.1173 | 0 | N/A | 0 | 0
2021-02-12 04:00 | 1.9968 | 0 | N/A | 0 | 0
2021-02-12 04:30 | 2.0047 | 0 | N/A | 0 | 0
2021-02-12 05:00 | 2.0495 | 0 | N/A | 0 | 0
2021-02-12 05:30 | 2.1689 | 0 | N/A | 0 | 0
2021-02-12 06:00 | 2.4327 | 0 | N/A | 0 | 0
2021-02-12 06:30 | 2.8957 | 0 | N/A | 0 | 0
2021-02-12 07:00 | 3.5149 | 0 | N/A | 0 | 0
2021-02-12 07:30 | 4.3169 | 0 | N/A | 0 | 0
2021-02-12 08:00 | 4.4067 | 0 | N/A | 0 | 0
2021-02-12 08:30 | 3.9651 | 0 | N/A | 0 | 0
2021-02-12 09:00 | 3.1012 | 0 | N/A | 0 | 0
2021-02-12 09:30 | 2.5689 | 0 | N/A | 0 | 0
2021-02-12 10:00 | 2.0634 | 0 | N/A | 0 | 0
2021-02-12 10:30 | 1.827 | 0 | N/A | 0 | 0
2021-02-12 11:00 | 1.5045 | 0 | N/A | 0 | 0
2021-02-12 11:30 | 1.2839 | 0 | N/A | 0 | 0
2021-02-12 12:00 | 0.77492 | 0 | N/A | 0 | 0
2021-02-12 12:30 | 0.6116 | 0 | N/A | 0 | 0
2021-02-12 13:00 | 0.55658 | 0 | N/A | 0 | 0
2021-02-12 13:30 | 0.36795 | 0 | N/A | 0 | 0
2021-02-12 14:00 | -0.37371 | 0 | N/A | 0 | 0
2021-02-12 14:30 | 0.35668 | 0 | N/A | 0 | 0
2021-02-12 15:00 | 0.24515 | 0 | N/A | 0 | 0
2021-02-12 15:30 | 0.13573 | 0 | N/A | 0 | 0
2021-02-12 16:00 | 0.20333 | 0 | N/A | 0 | 0
2021-02-12 16:30 | 0.65341 | 0 | N/A | 0 | 0
2021-02-12 17:00 | 0.9808 | 0 | N/A | 0 | 0
2021-02-12 17:30 | 1.6352 | 0 | N/A | 0 | 0
2021-02-12 18:00 | 1.9916 | 0 | N/A | 0 | 0
2021-02-12 18:30 | 2.7994 | 0 | N/A | 0 | 0
2021-02-12 19:00 | 3.0019 | 0 | N/A | 0 | 0
2021-02-12 19:30 | 3.4506 | 0 | N/A | 0 | 0
2021-02-12 20:00 | 3.6012 | 0 | N/A | 0 | 0
2021-02-12 20:30 | 3.7579 | 0 | N/A | 0 | 0
2021-02-12 21:00 | 3.7699 | 0 | N/A | 0 | 0
2021-02-12 21:30 | 3.6516 | 0 | N/A | 0 | 0
2021-02-12 22:00 | 3.4529 | 0 | N/A | 0 | 0
2021-02-12 22:30 | 3.8264 | 0 | N/A | 0 | 0
2021-02-12 23:00 | 4.0202 | 0 | N/A | 0 | 0
2021-02-12 23:30 | 3.7028 | 0 | N/A | 0 | 0
2021-02-13 | 3.5977 | 0 | N/A | 0 | 0
2021-02-13 00:30 | 4.171 | 0 | N/A | 0 | 0
2021-02-13 01:00 | 4.4103 | 0 | N/A | 0 | 0
2021-02-13 01:30 | 3.4827 | 0 | N/A | 0 | 0
2021-02-13 02:00 | 2.7359 | 0 | N/A | 0 | 0
2021-02-13 02:30 | 2.7046 | 0 | N/A | 0 | 0
2021-02-13 03:00 | 2.3417 | 0 | N/A | 0 | 0
2021-02-13 03:30 | 2.0678 | 0 | N/A | 0 | 0
2021-02-13 04:00 | 1.9381 | 0 | N/A | 0 | 0
2021-02-13 04:30 | 1.8694 | 0 | N/A | 0 | 0
2021-02-13 05:00 | 1.8359 | 0 | N/A | 0 | 0
2021-02-13 05:30 | 1.8919 | 0 | N/A | 0 | 0
2021-02-13 06:00 | 2.008 | 0 | N/A | 0 | 0
2021-02-13 06:30 | 2.2284 | 0 | N/A | 0 | 0
2021-02-13 07:00 | 2.2895 | 0 | N/A | 0 | 0
2021-02-13 07:30 | 2.5737 | 0 | N/A | 0 | 0
2021-02-13 08:00 | 2.7776 | 0 | N/A | 0 | 0
2021-02-13 08:30 | 2.9405 | 0 | N/A | 0 | 0
2021-02-13 09:00 | 2.9066 | 0 | N/A | 0 | 0
2021-02-13 09:30 | 2.0192 | 0 | N/A | 0 | 0
2021-02-13 10:00 | 1.7111 | 0 | N/A | 0 | 0
2021-02-13 10:30 | 1.1526 | 0 | N/A | 0 | 0
2021-02-13 11:00 | 1.2987 | 0 | N/A | 0 | 0
2021-02-13 11:30 | 2.4947 | 0 | N/A | 0 | 0
2021-02-13 12:00 | 1.6509 | 0 | N/A | 0 | 0
2021-02-13 12:30 | 0.8798 | 0 | N/A | 0 | 0
2021-02-13 13:00 | 1.4297 | 0 | N/A | 0 | 0
2021-02-13 13:30 | 1.3592 | 0 | N/A | 0 | 0
2021-02-13 14:00 | 0.99341 | 0 | N/A | 0 | 0
2021-02-13 14:30 | 0.61378 | 0 | N/A | 0 | 0
2021-02-13 15:00 | 0.57701 | 0 | N/A | 0 | 0
2021-02-13 15:30 | 0.418 | 0 | N/A | 0 | 0
2021-02-13 16:00 | 0.39962 | 0 | N/A | 0 | 0
2021-02-13 16:30 | 0.34231 | 0 | N/A | 0 | 0
2021-02-13 17:00 | 0.72076 | 0 | N/A | 0 | 0
2021-02-13 17:30 | 1.4451 | 0 | N/A | 0 | 0
2021-02-13 18:00 | 2.458 | 0 | N/A | 0 | 0
2021-02-13 18:30 | 2.9724 | 0 | N/A | 0 | 0
2021-02-13 19:00 | 3.2322 | 0 | N/A | 0 | 0
2021-02-13 19:30 | 3.5851 | 0 | N/A | 0 | 0
2021-02-13 20:00 | 3.6859 | 0 | N/A | 0 | 0
2021-02-13 20:30 | 3.8185 | 0 | N/A | 0 | 0
2021-02-13 21:00 | 3.8045 | 0 | N/A | 0 | 0
2021-02-13 21:30 | 3.7622 | 0 | N/A | 0 | 0
2021-02-13 22:00 | 3.5335 | 0 | N/A | 0 | 0
2021-02-13 22:30 | 3.9383 | 0 | N/A | 0 | 0
2021-02-13 23:00 | 4.1942 | 0 | N/A | 0 | 0
2021-02-13 23:30 | 3.9213 | 0 | N/A | 0 | 0
2021-02-14 | 4.0447 | 0 | N/A | 0 | 0
2021-02-14 00:30 | 4.4053 | 0 | N/A | 0 | 0
2021-02-14 01:00 | 4.6832 | 0 | N/A | 0 | 0
2021-02-14 01:30 | 3.8613 | 0 | N/A | 0 | 0
2021-02-14 02:00 | 3.2156 | 0 | N/A | 0 | 0
2021-02-14 02:30 | 3.1188 | 0 | N/A | 0 | 0
2021-02-14 03:00 | 2.7658 | 0 | N/A | 0 | 0
2021-02-14 03:30 | 2.3064 | 0 | N/A | 0 | 0
2021-02-14 04:00 | 2.0619 | 0 | N/A | 0 | 0
2021-02-14 04:30 | 1.9302 | 0 | N/A | 0 | 0
2021-02-14 05:00 | 1.9613 | 0 | N/A | 0 | 0
2021-02-14 05:30 | 2.0483 | 0 | N/A | 0 | 0
2021-02-14 06:00 | 2.059 | 0 | N/A | 0 | 0
2021-02-14 06:30 | 2.2013 | 0 | N/A | 0 | 0
2021-02-14 07:00 | 2.3079 | 0 | N/A | 0 | 0
2021-02-14 07:30 | 2.4603 | 0 | N/A | 0 | 0
2021-02-14 08:00 | 2.5709 | 0 | N/A | 0 | 0
2021-02-14 08:30 | 2.5029 | 0 | N/A | 0 | 0
2021-02-14 09:00 | 2.567 | 0 | N/A | 0 | 0
2021-02-14 09:30 | 2.2706 | 0 | N/A | 0 | 0
2021-02-14 10:00 | 1.7908 | 0 | N/A | 0 | 0
2021-02-14 10:30 | 1.1613 | 0 | N/A | 0 | 0
2021-02-14 11:00 | 0.56806 | 0 | N/A | 0 | 0
2021-02-14 11:30 | -0.36545 | 0 | N/A | 0 | 0
2021-02-14 12:00 | -0.46606 | 0 | N/A | 0 | 0
2021-02-14 12:30 | -0.52355 | 0 | N/A | 0 | 0
2021-02-14 13:00 | -0.65192 | 0 | N/A | 0 | 0
2021-02-14 13:30 | -0.7835 | 0 | N/A | 0 | 0
2021-02-14 14:00 | -0.90873 | 0 | N/A | 0 | 0
2021-02-14 14:30 | -1.0496 | 0 | N/A | 0 | 0
2021-02-14 15:00 | -1.0211 | 0 | N/A | 0 | 0
2021-02-14 15:30 | -0.88328 | 0 | N/A | 0 | 0
2021-02-14 16:00 | -0.73595 | 0 | N/A | 0 | 0
2021-02-14 16:30 | -0.41881 | 0 | N/A | 0 | 0
2021-02-14 17:00 | 0.35509 | 0 | N/A | 0 | 0
2021-02-14 17:30 | 1.0339 | 0 | N/A | 0 | 0
2021-02-14 18:00 | 2.0632 | 0 | N/A | 0 | 0
2021-02-14 18:30 | 2.8912 | 0 | N/A | 0 | 0
2021-02-14 19:00 | 3.479 | 0 | N/A | 0 | 0
2021-02-14 19:30 | 3.7162 | 0 | N/A | 0 | 0
2021-02-14 20:00 | 3.8118 | 0 | N/A | 0 | 0
2021-02-14 20:30 | 3.8541 | 0 | N/A | 0 | 0
2021-02-14 21:00 | 3.853 | 0 | N/A | 0 | 0
2021-02-14 21:30 | 3.7291 | 0 | N/A | 0 | 0
2021-02-14 22:00 | 3.4966 | 0 | N/A | 0 | 0
2021-02-14 22:30 | 3.8935 | 0 | N/A | 0 | 0
2021-02-14 23:00 | 4.1155 | 0 | N/A | 0 | 0
2021-02-14 23:30 | 3.8882 | 0 | N/A | 0 | 0
2021-02-15 | 3.9863 | 0 | N/A | 0 | 0
2021-02-15 00:30 | 4.2741 | 0 | N/A | 0 | 0
2021-02-15 01:00 | 4.6621 | 0 | N/A | 0 | 0
2021-02-15 01:30 | 3.8959 | 0 | N/A | 0 | 0
2021-02-15 02:00 | 3.2214 | 0 | N/A | 0 | 0
2021-02-15 02:30 | 3.1846 | 0 | N/A | 0 | 0
2021-02-15 03:00 | 2.8083 | 0 | N/A | 0 | 0
2021-02-15 03:30 | 2.3454 | 0 | N/A | 0 | 0
2021-02-15 04:00 | 2.1266 | 0 | N/A | 0 | 0
2021-02-15 04:30 | 2.026 | 0 | N/A | 0 | 0
2021-02-15 05:00 | 1.9741 | 0 | N/A | 0 | 0
2021-02-15 05:30 | 2.1269 | 0 | N/A | 0 | 0
2021-02-15 06:00 | 2.3634 | 0 | N/A | 0 | 0
2021-02-15 06:30 | 2.6117 | 0 | N/A | 0 | 0
2021-02-15 07:00 | 2.9362 | 0 | N/A | 0 | 0
2021-02-15 07:30 | 3.4409 | 0 | N/A | 0 | 0
2021-02-15 08:00 | 3.9284 | 0 | N/A | 0 | 0
2021-02-15 08:30 | 3.5546 | 0 | N/A | 0 | 0
2021-02-15 09:00 | 3.1335 | 0 | N/A | 0 | 0
2021-02-15 09:30 | 2.3634 | 0 | N/A | 0 | 0
2021-02-15 10:00 | 1.4979 | 0 | N/A | 0 | 0
2021-02-15 10:30 | 1.2485 | 0 | N/A | 0 | 0
2021-02-15 11:00 | 0.98888 | 0 | N/A | 0 | 0
2021-02-15 11:30 | 0.89115 | 0 | N/A | 0 | 0
2021-02-15 12:00 | 0.73947 | 0 | N/A | 0 | 0
2021-02-15 12:30 | 0.6281 | 0 | N/A | 0 | 0
2021-02-15 13:00 | 0.7394 | 0 | N/A | 0 | 0
2021-02-15 13:30 | 0.88955 | 0 | N/A | 0 | 0
2021-02-15 14:00 | 0.53459 | 0 | N/A | 0 | 0
2021-02-15 14:30 | 0.48828 | 0 | N/A | 0 | 0
2021-02-15 15:00 | 0.80483 | 0 | N/A | 0 | 0
2021-02-15 15:30 | 0.83693 | 0 | N/A | 0 | 0
2021-02-15 16:00 | 0.66321 | 0 | N/A | 0 | 0
2021-02-15 16:30 | 0.90092 | 0 | N/A | 0 | 0
2021-02-15 17:00 | 1.7601 | 0 | N/A | 0 | 0
2021-02-15 17:30 | 2.5933 | 0 | N/A | 0 | 0
2021-02-15 18:00 | 4.0637 | 0 | N/A | 0 | 0
2021-02-15 18:30 | 4.4778 | 0 | N/A | 0 | 0
2021-02-15 19:00 | 4.3926 | 0 | N/A | 0 | 0
2021-02-15 19:30 | 4.7103 | 0 | N/A | 0 | 0
2021-02-15 20:00 | 4.3601 | 0 | N/A | 0 | 0
2021-02-15 20:30 | 4.3328 | 0 | N/A | 0 | 0
2021-02-15 21:00 | 4.3482 | 0 | N/A | 0 | 0
2021-02-15 21:30 | 4.1565 | 0 | N/A | 0 | 0
2021-02-15 22:00 | 3.8324 | 0 | N/A | 0 | 0
2021-02-15 22:30 | 4.0605 | 0 | N/A | 0 | 0
2021-02-15 23:00 | 4.0866 | 0 | N/A | 0 | 0
2021-02-15 23:30 | 3.7095 | 0 | N/A | 0 | 0
2021-02-16 | 3.8387 | 0 | N/A | 0 | 0
2021-02-16 00:30 | 4.3541 | 0 | N/A | 0 | 0
2021-02-16 01:00 | 4.559 | 0 | N/A | 0 | 0
2021-02-16 01:30 | 3.6508 | 0 | N/A | 0 | 0
2021-02-16 02:00 | 2.9094 | 0 | N/A | 0 | 0
2021-02-16 02:30 | 2.9399 | 0 | N/A | 0 | 0
2021-02-16 03:00 | 2.5788 | 0 | N/A | 0 | 0
2021-02-16 03:30 | 2.2339 | 0 | N/A | 0 | 0
2021-02-16 04:00 | 2.1032 | 0 | N/A | 0 | 0
2021-02-16 04:30 | 2.0104 | 0 | N/A | 0 | 0
2021-02-16 05:00 | 1.9988 | 0 | N/A | 0 | 0
2021-02-16 05:30 | 2.1894 | 0 | N/A | 0 | 0
2021-02-16 06:00 | 2.4533 | 0 | N/A | 0 | 0
2021-02-16 06:30 | 2.9388 | 0 | N/A | 0 | 0
2021-02-16 07:00 | 3.218 | 0 | N/A | 0 | 0
2021-02-16 07:30 | 3.7995 | 0 | N/A | 0 | 0
2021-02-16 08:00 | 4.0253 | 0 | N/A | 0 | 0
2021-02-16 08:30 | 3.8333 | 0 | N/A | 0 | 0
2021-02-16 09:00 | 3.4034 | 0 | N/A | 0 | 0
2021-02-16 09:30 | 3.0499 | 0 | N/A | 0 | 0
2021-02-16 10:00 | 2.5941 | 0 | N/A | 0 | 0
2021-02-16 10:30 | 2.1492 | 0 | N/A | 0 | 0
2021-02-16 11:00 | 2.0449 | 0 | N/A | 0 | 0
2021-02-16 11:30 | 1.4955 | 0 | N/A | 0 | 0
2021-02-16 12:00 | 0.72438 | 0 | N/A | 0 | 0
2021-02-16 12:30 | 0.60681 | 0 | N/A | 0 | 0
2021-02-16 13:00 | 0.60386 | 0 | N/A | 0 | 0
2021-02-16 13:30 | 0.4863 | 0 | N/A | 0 | 0
2021-02-16 14:00 | 0.65163 | 0 | N/A | 0 | 0
2021-02-16 14:30 | 0.98543 | 0 | N/A | 0 | 0
2021-02-16 15:00 | 2.3056 | 0 | N/A | 0 | 0
2021-02-16 15:30 | 2.7481 | 0 | N/A | 0 | 0
2021-02-16 16:00 | 2.4214 | 0 | N/A | 0 | 0
2021-02-16 16:30 | 1.6348 | 0 | N/A | 0 | 0
2021-02-16 17:00 | 2.9822 | 0 | N/A | 0 | 0
2021-02-16 17:30 | 4.8506 | 0 | N/A | 0 | 0
2021-02-16 18:00 | 5.625 | 0 | N/A | 0 | 0
2021-02-16 18:30 | 5.2283 | 0 | N/A | 0 | 0
2021-02-16 19:00 | 5.3605 | 0 | N/A | 0 | 0
2021-02-16 19:30 | 5.4201 | 0 | N/A | 0 | 0
2021-02-16 20:00 | 5.6233 | 0 | N/A | 0 | 0
2021-02-16 20:30 | 5.5133 | 0 | N/A | 0 | 0
2021-02-16 21:00 | 5.4167 | 0 | N/A | 0 | 0
2021-02-16 21:30 | 5.0411 | 0 | N/A | 0 | 0
2021-02-16 22:00 | 4.5258 | 0 | N/A | 0 | 0
2021-02-16 22:30 | 4.5888 | 0 | N/A | 0 | 0
2021-02-16 23:00 | 4.4993 | 0 | N/A | 0 | 0
2021-02-16 23:30 | 4.0561 | 0 | N/A | 0 | 0
2021-02-17 | 4.0775 | 0 | N/A | 0 | 0
2021-02-17 00:30 | 4.5969 | 0 | N/A | 0 | 0
2021-02-17 01:00 | 4.7768 | 0 | N/A | 0 | 0
2021-02-17 01:30 | 3.7963 | 0 | N/A | 0 | 0
2021-02-17 02:00 | 3.0332 | 0 | N/A | 0 | 0
2021-02-17 02:30 | 2.9182 | 0 | N/A | 0 | 0
2021-02-17 03:00 | 2.622 | 0 | N/A | 0 | 0
2021-02-17 03:30 | 2.3042 | 0 | N/A | 0 | 0
2021-02-17 04:00 | 2.1758 | 0 | N/A | 0 | 0
2021-02-17 04:30 | 2.1165 | 0 | N/A | 0 | 0
2021-02-17 05:00 | 2.0949 | 0 | N/A | 0 | 0
2021-02-17 05:30 | 2.3109 | 0 | N/A | 0 | 0
2021-02-17 06:00 | 2.5127 | 0 | N/A | 0 | 0
2021-02-17 06:30 | 2.9818 | 0 | N/A | 0 | 0
2021-02-17 07:00 | 3.3553 | 0 | N/A | 0 | 0
2021-02-17 07:30 | 3.8021 | 0 | N/A | 0 | 0
2021-02-17 08:00 | 3.9591 | 0 | N/A | 0 | 0
2021-02-17 08:30 | 4.0565 | 0 | N/A | 0 | 0
2021-02-17 09:00 | 3.6306 | 0 | N/A | 0 | 0
2021-02-17 09:30 | 3.1264 | 0 | N/A | 0 | 0
2021-02-17 10:00 | 2.5717 | 0 | N/A | 0 | 0
2021-02-17 10:30 | 1.9964 | 0 | N/A | 0 | 0
2021-02-17 11:00 | 1.8692 | 0 | N/A | 0 | 0
2021-02-17 11:30 | 1.8313 | 0 | N/A | 0 | 0
2021-02-17 12:00 | 1.9176 | 0 | N/A | 0 | 0
2021-02-17 12:30 | 2.0704 | 0 | N/A | 0 | 0
2021-02-17 13:00 | 2.155 | 0 | N/A | 0 | 0
2021-02-17 13:30 | 2.118 | 0 | N/A | 0 | 0
2021-02-17 14:00 | 2.2894 | 0 | N/A | 0 | 0
2021-02-17 14:30 | 2.5201 | 0 | N/A | 0 | 0
2021-02-17 15:00 | 3.1466 | 0 | N/A | 0 | 0
2021-02-17 15:30 | 4.0558 | 0 | N/A | 0 | 0
2021-02-17 16:00 | 4.3726 | 0 | N/A | 0 | 0
2021-02-17 16:30 | 4.168 | 0 | N/A | 0 | 0
2021-02-17 17:00 | 5.0718 | 0 | N/A | 0 | 0
2021-02-17 17:30 | 6.1624 | 0 | N/A | 0 | 0
2021-02-17 18:00 | 6.7803 | 0 | N/A | 0 | 0
2021-02-17 18:30 | 6.8407 | 0 | N/A | 0 | 0
2021-02-17 19:00 | 7.1602 | 0 | N/A | 0 | 0
2021-02-17 19:30 | 6.9872 | 0 | N/A | 0 | 0
2021-02-17 20:00 | 6.6881 | 0 | N/A | 0 | 0
2021-02-17 20:30 | 6.2501 | 0 | N/A | 0 | 0
2021-02-17 21:00 | 5.7067 | 0 | N/A | 0 | 0
2021-02-17 21:30 | 5.2267 | 0 | N/A | 0 | 0
2021-02-17 22:00 | 4.6339 | 0 | N/A | 0 | 0
2021-02-17 22:30 | 4.6202 | 0 | N/A | 0 | 0
2021-02-17 23:00 | 4.5608 | 0 | N/A | 0 | 0
2021-02-17 23:30 | 4.1133 | 0 | N/A | 0 | 0
2021-02-18 | 4.1239 | 0 | N/A | 0 | 0
2021-02-18 00:30 | 4.6223 | 0 | N/A | 0 | 0
2021-02-18 01:00 | 4.7204 | 0 | N/A | 0 | 0
2021-02-18 01:30 | 3.7558 | 0 | N/A | 0 | 0
2021-02-18 02:00 | 3.0293 | 0 | N/A | 0 | 0
2021-02-18 02:30 | 3.0032 | 0 | N/A | 0 | 0
2021-02-18 03:00 | 2.6451 | 0 | N/A | 0 | 0
2021-02-18 03:30 | 2.3558 | 0 | N/A | 0 | 0
2021-02-18 04:00 | 2.2106 | 0 | N/A | 0 | 0
2021-02-18 04:30 | 2.1934 | 0 | N/A | 0 | 0
2021-02-18 05:00 | 2.2564 | 0 | N/A | 0 | 0
2021-02-18 05:30 | 2.4152 | 0 | N/A | 0 | 0
2021-02-18 06:00 | 2.832 | 0 | N/A | 0 | 0
2021-02-18 06:30 | 3.2857 | 0 | N/A | 0 | 0
2021-02-18 07:00 | 4.0107 | 0 | N/A | 0 | 0
2021-02-18 07:30 | 4.9133 | 0 | N/A | 0 | 0
2021-02-18 08:00 | 4.7967 | 0 | N/A | 0 | 0
2021-02-18 08:30 | 4.1013 | 0 | N/A | 0 | 0
2021-02-18 09:00 | 3.5093 | 0 | N/A | 0 | 0
2021-02-18 09:30 | 3.033 | 0 | N/A | 0 | 0
2021-02-18 10:00 | 2.2466 | 0 | N/A | 0 | 0
2021-02-18 10:30 | 1.6303 | 0 | N/A | 0 | 0
2021-02-18 11:00 | 1.1571 | 0 | N/A | 0 | 0
2021-02-18 11:30 | 0.92333 | 0 | N/A | 0 | 0
2021-02-18 12:00 | 0.75808 | 0 | N/A | 0 | 0
2021-02-18 12:30 | 0.7189 | 0 | N/A | 0 | 0
2021-02-18 13:00 | 0.43417 | 0 | N/A | 0 | 0
2021-02-18 13:30 | 0.36462 | 0 | N/A | 0 | 0
2021-02-18 14:00 | 0.47051 | 0 | N/A | 0 | 0
2021-02-18 14:30 | 0.58214 | 0 | N/A | 0 | 0
2021-02-18 15:00 | 0.92329 | 0 | N/A | 0 | 0
2021-02-18 15:30 | 1.2309 | 0 | N/A | 0 | 0
2021-02-18 16:00 | 1.696 | 0 | N/A | 0 | 0
2021-02-18 16:30 | 2.5214 | 0 | N/A | 0 | 0
2021-02-18 17:00 | 3.1534 | 0 | N/A | 0 | 0
2021-02-18 17:30 | 4.0734 | 0 | N/A | 0 | 0
2021-02-18 18:00 | 5.1578 | 0 | N/A | 0 | 0
2021-02-18 18:30 | 6.0573 | 0 | N/A | 0 | 0
2021-02-18 19:00 | 6.5683 | 0 | N/A | 0 | 0
2021-02-18 19:30 | 6.7894 | 0 | N/A | 0 | 0
2021-02-18 20:00 | 6.6096 | 0 | N/A | 0 | 0
2021-02-18 20:30 | 6.1107 | 0 | N/A | 0 | 0
2021-02-18 21:00 | 5.7905 | 0 | N/A | 0 | 0
2021-02-18 21:30 | 5.3033 | 0 | N/A | 0 | 0
2021-02-18 22:00 | 4.7077 | 0 | N/A | 0 | 0
2021-02-18 22:30 | 4.7091 | 0 | N/A | 0 | 0
2021-02-18 23:00 | 4.5324 | 0 | N/A | 0 | 0
2021-02-18 23:30 | 4.0289 | 0 | N/A | 0 | 0
2021-02-19 | 4.0926 | 0 | N/A | 0 | 0
2021-02-19 00:30 | 4.5592 | 0 | N/A | 0 | 0
2021-02-19 01:00 | 4.5504 | 0 | N/A | 0 | 0
2021-02-19 01:30 | 3.5008 | 0 | N/A | 0 | 0
2021-02-19 02:00 | 2.8121 | 0 | N/A | 0 | 0
2021-02-19 02:30 | 2.8016 | 0 | N/A | 0 | 0
2021-02-19 03:00 | 2.5568 | 0 | N/A | 0 | 0
2021-02-19 03:30 | 2.2996 | 0 | N/A | 0 | 0
2021-02-19 04:00 | 2.1942 | 0 | N/A | 0 | 0
2021-02-19 04:30 | 2.1602 | 0 | N/A | 0 | 0
2021-02-19 05:00 | 2.1968 | 0 | N/A | 0 | 0
2021-02-19 05:30 | 2.3536 | 0 | N/A | 0 | 0
2021-02-19 06:00 | 2.6816 | 0 | N/A | 0 | 0
2021-02-19 06:30 | 3.1874 | 0 | N/A | 0 | 0
2021-02-19 07:00 | 3.5407 | 0 | N/A | 0 | 0
2021-02-19 07:30 | 4.1912 | 0 | N/A | 0 | 0
2021-02-19 08:00 | 4.1461 | 0 | N/A | 0 | 0
2021-02-19 08:30 | 3.5212 | 0 | N/A | 0 | 0
2021-02-19 09:00 | 2.8776 | 0 | N/A | 0 | 0
2021-02-19 09:30 | 2.5761 | 0 | N/A | 0 | 0
2021-02-19 10:00 | 1.5768 | 0 | N/A | 0 | 0
2021-02-19 10:30 | 1.0267 | 0 | N/A | 0 | 0
2021-02-19 11:00 | 1.0251 | 0 | N/A | 0 | 0
2021-02-19 11:30 | 1.0842 | 0 | N/A | 0 | 0
2021-02-19 12:00 | 0.96439 | 0 | N/A | 0 | 0
2021-02-19 12:30 | 0.97165 | 0 | N/A | 0 | 0
2021-02-19 13:00 | 0.97867 | 0 | N/A | 0 | 0
2021-02-19 13:30 | 0.99896 | 0 | N/A | 0 | 0
2021-02-19 14:00 | 1.1484 | 0 | N/A | 0 | 0
2021-02-19 14:30 | 1.47 | 0 | N/A | 0 | 0
2021-02-19 15:00 | 1.1346 | 0 | N/A | 0 | 0
2021-02-19 15:30 | 1.3446 | 0 | N/A | 0 | 0
2021-02-19 16:00 | 1.9314 | 0 | N/A | 0 | 0
2021-02-19 16:30 | 2.6897 | 0 | N/A | 0 | 0
2021-02-19 17:00 | 3.4552 | 0 | N/A | 0 | 0
2021-02-19 17:30 | 4.4789 | 0 | N/A | 0 | 0
2021-02-19 18:00 | 5.3877 | 0 | N/A | 0 | 0
2021-02-19 18:30 | 6.2269 | 0 | N/A | 0 | 0
2021-02-19 19:00 | 6.804 | 0 | N/A | 0 | 0
2021-02-19 19:30 | 7.0246 | 0 | N/A | 0 | 0
2021-02-19 20:00 | 6.5799 | 0 | N/A | 0 | 0
2021-02-19 20:30 | 6.3026 | 0 | N/A | 0 | 0
2021-02-19 21:00 | 5.9458 | 0 | N/A | 0 | 0
2021-02-19 21:30 | 5.4734 | 0 | N/A | 0 | 0
2021-02-19 22:00 | 4.9033 | 0 | N/A | 0 | 0
2021-02-19 22:30 | 4.928 | 0 | N/A | 0 | 0
2021-02-19 23:00 | 4.7512 | 0 | N/A | 0 | 0
2021-02-19 23:30 | 4.2781 | 0 | N/A | 0 | 0
2021-02-20 | 4.2495 | 0 | N/A | 0 | 0
2021-02-20 00:30 | 4.673 | 0 | N/A | 0 | 0
2021-02-20 01:00 | 4.7052 | 0 | N/A | 0 | 0
2021-02-20 01:30 | 3.6757 | 0 | N/A | 0 | 0
2021-02-20 02:00 | 2.9686 | 0 | N/A | 0 | 0
2021-02-20 02:30 | 2.944 | 0 | N/A | 0 | 0
2021-02-20 03:00 | 2.6908 | 0 | N/A | 0 | 0
2021-02-20 03:30 | 2.4101 | 0 | N/A | 0 | 0
2021-02-20 04:00 | 2.3044 | 0 | N/A | 0 | 0
2021-02-20 04:30 | 2.2139 | 0 | N/A | 0 | 0
2021-02-20 05:00 | 2.2192 | 0 | N/A | 0 | 0
2021-02-20 05:30 | 2.2872 | 0 | N/A | 0 | 0
2021-02-20 06:00 | 2.3602 | 0 | N/A | 0 | 0
2021-02-20 06:30 | 2.5789 | 0 | N/A | 0 | 0
2021-02-20 07:00 | 2.8195 | 0 | N/A | 0 | 0
2021-02-20 07:30 | 3.0174 | 0 | N/A | 0 | 0
2021-02-20 08:00 | 3.2075 | 0 | N/A | 0 | 0
2021-02-20 08:30 | 3.1674 | 0 | N/A | 0 | 0
2021-02-20 09:00 | 3.1815 | 0 | N/A | 0 | 0
2021-02-20 09:30 | 2.3781 | 0 | N/A | 0 | 0
2021-02-20 10:00 | 2.0137 | 0 | N/A | 0 | 0
2021-02-20 10:30 | 2.25 | 0 | N/A | 0 | 0
2021-02-20 11:00 | 1.9667 | 0 | N/A | 0 | 0
2021-02-20 11:30 | 2.1867 | 0 | N/A | 0 | 0
2021-02-20 12:00 | 2.1906 | 0 | N/A | 0 | 0
2021-02-20 12:30 | 1.8086 | 0 | N/A | 0 | 0
2021-02-20 13:00 | 1.0749 | 0 | N/A | 0 | 0
2021-02-20 13:30 | 1.2701 | 0 | N/A | 0 | 0
2021-02-20 14:00 | 1.4124 | 0 | N/A | 0 | 0
2021-02-20 14:30 | 1.8968 | 0 | N/A | 0 | 0
2021-02-20 15:00 | 2.791 | 0 | N/A | 0 | 0
2021-02-20 15:30 | 3.4525 | 0 | N/A | 0 | 0
2021-02-20 16:00 | 4.2638 | 0 | N/A | 0 | 0
2021-02-20 16:30 | 4.7035 | 0 | N/A | 0 | 0
2021-02-20 17:00 | 4.975 | 0 | N/A | 0 | 0
2021-02-20 17:30 | 5.1484 | 0 | N/A | 0 | 0
2021-02-20 18:00 | 6.2025 | 0 | N/A | 0 | 0
2021-02-20 18:30 | 6.4882 | 0 | N/A | 0 | 0
2021-02-20 19:00 | 6.2474 | 0 | N/A | 0 | 0
2021-02-20 19:30 | 6.0276 | 0 | N/A | 0 | 0
2021-02-20 20:00 | 5.7834 | 0 | N/A | 0 | 0
2021-02-20 20:30 | 5.1333 | 0 | N/A | 0 | 0
2021-02-20 21:00 | 4.7234 | 0 | N/A | 0 | 0
2021-02-20 21:30 | 4.3194 | 0 | N/A | 0 | 0
2021-02-20 22:00 | 3.879 | 0 | N/A | 0 | 0
2021-02-20 22:30 | 4.1861 | 0 | N/A | 0 | 0
2021-02-20 23:00 | 4.2353 | 0 | N/A | 0 | 0
2021-02-20 23:30 | 3.8784 | 0 | N/A | 0 | 0
2021-02-21 | 3.9369 | 0 | N/A | 0 | 0
2021-02-21 00:30 | 4.3284 | 0 | N/A | 0 | 0
2021-02-21 01:00 | 4.503 | 0 | N/A | 0 | 0
2021-02-21 01:30 | 3.5054 | 0 | N/A | 0 | 0
2021-02-21 02:00 | 2.7907 | 0 | N/A | 0 | 0
2021-02-21 02:30 | 2.8169 | 0 | N/A | 0 | 0
2021-02-21 03:00 | 2.4861 | 0 | N/A | 0 | 0
2021-02-21 03:30 | 2.1644 | 0 | N/A | 0 | 0
2021-02-21 04:00 | 2.0035 | 0 | N/A | 0 | 0
2021-02-21 04:30 | 1.9798 | 0 | N/A | 0 | 0
2021-02-21 05:00 | 1.9744 | 0 | N/A | 0 | 0
2021-02-21 05:30 | 2.0113 | 0 | N/A | 0 | 0
2021-02-21 06:00 | 2.121 | 0 | N/A | 0 | 0
2021-02-21 06:30 | 2.3381 | 0 | N/A | 0 | 0
2021-02-21 07:00 | 2.4747 | 0 | N/A | 0 | 0
2021-02-21 07:30 | 2.6481 | 0 | N/A | 0 | 0
2021-02-21 08:00 | 2.7893 | 0 | N/A | 0 | 0
2021-02-21 08:30 | 2.6674 | 0 | N/A | 0 | 0
2021-02-21 09:00 | 2.5718 | 0 | N/A | 0 | 0
2021-02-21 09:30 | 2.4055 | 0 | N/A | 0 | 0
2021-02-21 10:00 | 2.3715 | 0 | N/A | 0 | 0
2021-02-21 10:30 | 2.0937 | 0 | N/A | 0 | 0
2021-02-21 11:00 | 1.8781 | 0 | N/A | 0 | 0
2021-02-21 11:30 | 1.9625 | 0 | N/A | 0 | 0
2021-02-21 12:00 | 2.0893 | 0 | N/A | 0 | 0
2021-02-21 12:30 | 2.1259 | 0 | N/A | 0 | 0
2021-02-21 13:00 | 2.1685 | 0 | N/A | 0 | 0
2021-02-21 13:30 | 2.001 | 0 | N/A | 0 | 0
2021-02-21 14:00 | 1.7713 | 0 | N/A | 0 | 0
2021-02-21 14:30 | 1.7277 | 0 | N/A | 0 | 0
2021-02-21 15:00 | 1.227 | 0 | N/A | 0 | 0
2021-02-21 15:30 | 0.84816 | 0 | N/A | 0 | 0
2021-02-21 16:00 | 0.45668 | 0 | N/A | 0 | 0
2021-02-21 16:30 | 0.66727 | 0 | N/A | 0 | 0
2021-02-21 17:00 | 0.82325 | 0 | N/A | 0 | 0
2021-02-21 17:30 | 1.3252 | 0 | N/A | 0 | 0
2021-02-21 18:00 | 2.2486 | 0 | N/A | 0 | 0
2021-02-21 18:30 | 3.0062 | 0 | N/A | 0 | 0
2021-02-21 19:00 | 3.7534 | 0 | N/A | 0 | 0
2021-02-21 19:30 | 3.9613 | 0 | N/A | 0 | 0
2021-02-21 20:00 | 4.0684 | 0 | N/A | 0 | 0
2021-02-21 20:30 | 3.9151 | 0 | N/A | 0 | 0
2021-02-21 21:00 | 3.8583 | 0 | N/A | 0 | 0
2021-02-21 21:30 | 3.7751 | 0 | N/A | 0 | 0
2021-02-21 22:00 | 3.4458 | 0 | N/A | 0 | 0
2021-02-21 22:30 | 3.8045 | 0 | N/A | 0 | 0
2021-02-21 23:00 | 3.9933 | 0 | N/A | 0 | 0
2021-02-21 23:30 | 3.7741 | 0 | N/A | 0 | 0
2021-02-22 | 3.7615 | 0 | N/A | 0 | 0
2021-02-22 00:30 | 4.2078 | 0 | N/A | 0 | 0
2021-02-22 01:00 | 4.5909 | 0 | N/A | 0 | 0
2021-02-22 01:30 | 3.7265 | 0 | N/A | 0 | 0
2021-02-22 02:00 | 3.0047 | 0 | N/A | 0 | 0
2021-02-22 02:30 | 2.8757 | 0 | N/A | 0 | 0
2021-02-22 03:00 | 2.4995 | 0 | N/A | 0 | 0
2021-02-22 03:30 | 2.1978 | 0 | N/A | 0 | 0
2021-02-22 04:00 | 2.0528 | 0 | N/A | 0 | 0
2021-02-22 04:30 | 1.9936 | 0 | N/A | 0 | 0
2021-02-22 05:00 | 2.0151 | 0 | N/A | 0 | 0
2021-02-22 05:30 | 2.2105 | 0 | N/A | 0 | 0
2021-02-22 06:00 | 2.437 | 0 | N/A | 0 | 0
2021-02-22 06:30 | 2.9257 | 0 | N/A | 0 | 0
2021-02-22 07:00 | 3.419 | 0 | N/A | 0 | 0
2021-02-22 07:30 | 4.2262 | 0 | N/A | 0 | 0
2021-02-22 08:00 | 4.8334 | 0 | N/A | 0 | 0
2021-02-22 08:30 | 4.3 | 0 | N/A | 0 | 0
2021-02-22 09:00 | 3.7 | 0 | N/A | 0 | 0
2021-02-22 09:30 | 2.8867 | 0 | N/A | 0 | 0
2021-02-22 10:00 | 1.9 | 0 | N/A | 0 | 0
2021-02-22 10:30 | 1.4714 | 0 | N/A | 0 | 0
2021-02-22 11:00 | 1.196 | 0 | N/A | 0 | 0
2021-02-22 11:30 | 1.2224 | 0 | N/A | 0 | 0
2021-02-22 12:00 | 1.5108 | 0 | N/A | 0 | 0
2021-02-22 12:30 | 1.4215 | 0 | N/A | 0 | 0
2021-02-22 13:00 | 1.4264 | 0 | N/A | 0 | 0
2021-02-22 13:30 | 1.0895 | 0 | N/A | 0 | 0
2021-02-22 14:00 | 1.2594 | 0 | N/A | 0 | 0
2021-02-22 14:30 | 1.2903 | 0 | N/A | 0 | 0
2021-02-22 15:00 | 0.95087 | 0 | N/A | 0 | 0
2021-02-22 15:30 | 1.2245 | 0 | N/A | 0 | 0
2021-02-22 16:00 | 0.94405 | 0 | N/A | 0 | 0
2021-02-22 16:30 | 0.96294 | 0 | N/A | 0 | 0
2021-02-22 17:00 | 1.6203 | 0 | N/A | 0 | 0
2021-02-22 17:30 | 2.3626 | 0 | N/A | 0 | 0
2021-02-22 18:00 | 2.9436 | 0 | N/A | 0 | 0
2021-02-22 18:30 | 3.7053 | 0 | N/A | 0 | 0
2021-02-22 19:00 | 4.0283 | 0 | N/A | 0 | 0
2021-02-22 19:30 | 4.1304 | 0 | N/A | 0 | 0
2021-02-22 20:00 | 4.3293 | 0 | N/A | 0 | 0
2021-02-22 20:30 | 4.3338 | 0 | N/A | 0 | 0
2021-02-22 21:00 | 4.1999 | 0 | N/A | 0 | 0
2021-02-22 21:30 | 4.0927 | 0 | N/A | 0 | 0
2021-02-22 22:00 | 3.8274 | 0 | N/A | 0 | 0
2021-02-22 22:30 | 4.0748 | 0 | N/A | 0 | 0
2021-02-22 23:00 | 4.1083 | 0 | N/A | 0 | 0
2021-02-22 23:30 | 3.6891 | 0 | N/A | 0 | 0
2021-02-23 | 3.8201 | 0 | N/A | 0 | 0
2021-02-23 00:30 | 4.4049 | 0 | N/A | 0 | 0
2021-02-23 01:00 | 4.6802 | 0 | N/A | 0 | 0
2021-02-23 01:30 | 3.8772 | 0 | N/A | 0 | 0
2021-02-23 02:00 | 3.0894 | 0 | N/A | 0 | 0
2021-02-23 02:30 | 2.9314 | 0 | N/A | 0 | 0
2021-02-23 03:00 | 2.5559 | 0 | N/A | 0 | 0
2021-02-23 03:30 | 2.3465 | 0 | N/A | 0 | 0
2021-02-23 04:00 | 2.1903 | 0 | N/A | 0 | 0
2021-02-23 04:30 | 2.1504 | 0 | N/A | 0 | 0
2021-02-23 05:00 | 2.2519 | 0 | N/A | 0 | 0
2021-02-23 05:30 | 2.452 | 0 | N/A | 0 | 0
2021-02-23 06:00 | 2.7193 | 0 | N/A | 0 | 0
2021-02-23 06:30 | 3.4111 | 0 | N/A | 0 | 0
2021-02-23 07:00 | 4.0518 | 0 | N/A | 0 | 0
2021-02-23 07:30 | 4.8174 | 0 | N/A | 0 | 0
2021-02-23 08:00 | 4.8713 | 0 | N/A | 0 | 0
2021-02-23 08:30 | 3.8151 | 0 | N/A | 0 | 0
2021-02-23 09:00 | 3.0377 | 0 | N/A | 0 | 0
2021-02-23 09:30 | 2.3952 | 0 | N/A | 0 | 0
2021-02-23 10:00 | 2.3976 | 0 | N/A | 0 | 0
2021-02-23 10:30 | 1.9591 | 0 | N/A | 0 | 0
2021-02-23 11:00 | 1.4966 | 0 | N/A | 0 | 0
2021-02-23 11:30 | 1.964 | 0 | N/A | 0 | 0
2021-02-23 12:00 | 1.5796 | 0 | N/A | 0 | 0
2021-02-23 12:30 | 0.90151 | 0 | N/A | 0 | 0
2021-02-23 13:00 | 0.97942 | 0 | N/A | 0 | 0
2021-02-23 13:30 | 0.92906 | 0 | N/A | 0 | 0
2021-02-23 14:00 | 0.24042 | 0 | N/A | 0 | 0
2021-02-23 14:30 | 0.75726 | 0 | N/A | 0 | 0
2021-02-23 15:00 | 0.92909 | 0 | N/A | 0 | 0
2021-02-23 15:30 | 0.90898 | 0 | N/A | 0 | 0
2021-02-23 16:00 | 1.4181 | 0 | N/A | 0 | 0
2021-02-23 16:30 | 1.9167 | 0 | N/A | 0 | 0
2021-02-23 17:00 | 1.9045 | 0 | N/A | 0 | 0
2021-02-23 17:30 | 2.3026 | 0 | N/A | 0 | 0
2021-02-23 18:00 | 3.3456 | 0 | N/A | 0 | 0
2021-02-23 18:30 | 3.7025 | 0 | N/A | 0 | 0
2021-02-23 19:00 | 4.1677 | 0 | N/A | 0 | 0
2021-02-23 19:30 | 4.3528 | 0 | N/A | 0 | 0
2021-02-23 20:00 | 4.4883 | 0 | N/A | 0 | 0
2021-02-23 20:30 | 4.6777 | 0 | N/A | 0 | 0
2021-02-23 21:00 | 4.644 | 0 | N/A | 0 | 0
2021-02-23 21:30 | 4.4821 | 0 | N/A | 0 | 0
2021-02-23 22:00 | 4.0348 | 0 | N/A | 0 | 0
2021-02-23 22:30 | 4.0645 | 0 | N/A | 0 | 0
2021-02-23 23:00 | 4.239 | 0 | N/A | 0 | 0
2021-02-23 23:30 | 3.7752 | 0 | N/A | 0 | 0
2021-02-24 | 3.8656 | 0 | N/A | 0 | 0
2021-02-24 00:30 | 4.2748 | 0 | N/A | 0 | 0
2021-02-24 01:00 | 4.6637 | 0 | N/A | 0 | 0
2021-02-24 01:30 | 3.8058 | 0 | N/A | 0 | 0
2021-02-24 02:00 | 3.0099 | 0 | N/A | 0 | 0
2021-02-24 02:30 | 3.0018 | 0 | N/A | 0 | 0
2021-02-24 03:00 | 2.7394 | 0 | N/A | 0 | 0
2021-02-24 03:30 | 2.3369 | 0 | N/A | 0 | 0
2021-02-24 04:00 | 2.1821 | 0 | N/A | 0 | 0
2021-02-24 04:30 | 2.1268 | 0 | N/A | 0 | 0
2021-02-24 05:00 | 2.2733 | 0 | N/A | 0 | 0
2021-02-24 05:30 | 2.4967 | 0 | N/A | 0 | 0
2021-02-24 06:00 | 2.8603 | 0 | N/A | 0 | 0
2021-02-24 06:30 | 3.5369 | 0 | N/A | 0 | 0
2021-02-24 07:00 | 4.5022 | 0 | N/A | 0 | 0
2021-02-24 07:30 | 5.4636 | 0 | N/A | 0 | 0
2021-02-24 08:00 | 6.0033 | 0 | N/A | 0 | 0
2021-02-24 08:30 | 5.527 | 0 | N/A | 0 | 0
2021-02-24 09:00 | 4.6601 | 0 | N/A | 0 | 0
2021-02-24 09:30 | 4.3934 | 0 | N/A | 0 | 0
2021-02-24 10:00 | 3.3135 | 0 | N/A | 0 | 0
2021-02-24 10:30 | 3.1702 | 0 | N/A | 0 | 0
2021-02-24 11:00 | 3.3334 | 0 | N/A | 0 | 0
2021-02-24 11:30 | 2.3704 | 0 | N/A | 0 | 0
2021-02-24 12:00 | 1.9741 | 0 | N/A | 0 | 0
2021-02-24 12:30 | 1.1541 | 0 | N/A | 0 | 0
2021-02-24 13:00 | 0.90471 | 0 | N/A | 0 | 0
2021-02-24 13:30 | 0.59067 | 0 | N/A | 0 | 0
2021-02-24 14:00 | 0.5559 | 0 | N/A | 0 | 0
2021-02-24 14:30 | 0.40783 | 0 | N/A | 0 | 0
2021-02-24 15:00 | 0.34184 | 0 | N/A | 0 | 0
2021-02-24 15:30 | 0.46861 | 0 | N/A | 0 | 0
2021-02-24 16:00 | 0.87321 | 0 | N/A | 0 | 0
2021-02-24 16:30 | 0.54452 | 0 | N/A | 0 | 0
2021-02-24 17:00 | 0.77369 | 0 | N/A | 0 | 0
2021-02-24 17:30 | 0.8855 | 0 | N/A | 0 | 0
2021-02-24 18:00 | 1.8612 | 0 | N/A | 0 | 0
2021-02-24 18:30 | 2.663 | 0 | N/A | 0 | 0
2021-02-24 19:00 | 3.3886 | 0 | N/A | 0 | 0
2021-02-24 19:30 | 3.769 | 0 | N/A | 0 | 0
2021-02-24 20:00 | 4.0098 | 0 | N/A | 0 | 0
2021-02-24 20:30 | 4.2375 | 0 | N/A | 0 | 0
2021-02-24 21:00 | 4.2365 | 0 | N/A | 0 | 0
2021-02-24 21:30 | 4.0663 | 0 | N/A | 0 | 0
2021-02-24 22:00 | 3.7644 | 0 | N/A | 0 | 0
2021-02-24 22:30 | 3.9211 | 0 | N/A | 0 | 0
2021-02-24 23:00 | 4.008 | 0 | N/A | 0 | 0
2021-02-24 23:30 | 3.691 | 0 | N/A | 0 | 0
2021-02-25 | 3.6919 | 0 | N/A | 0 | 0
2021-02-25 00:30 | 4.2791 | 0 | N/A | 0 | 0
2021-02-25 01:00 | 4.6112 | 0 | N/A | 0 | 0
2021-02-25 01:30 | 3.7372 | 0 | N/A | 0 | 0
2021-02-25 02:00 | 3.0352 | 0 | N/A | 0 | 0
2021-02-25 02:30 | 2.9873 | 0 | N/A | 0 | 0
2021-02-25 03:00 | 2.6452 | 0 | N/A | 0 | 0
2021-02-25 03:30 | 2.3549 | 0 | N/A | 0 | 0
2021-02-25 04:00 | 2.1606 | 0 | N/A | 0 | 0
2021-02-25 04:30 | 2.086 | 0 | N/A | 0 | 0
2021-02-25 05:00 | 2.1869 | 0 | N/A | 0 | 0
2021-02-25 05:30 | 2.4131 | 0 | N/A | 0 | 0
2021-02-25 06:00 | 2.7378 | 0 | N/A | 0 | 0
2021-02-25 06:30 | 3.4784 | 0 | N/A | 0 | 0
2021-02-25 07:00 | 4.2567 | 0 | N/A | 0 | 0
2021-02-25 07:30 | 5.4447 | 0 | N/A | 0 | 0
2021-02-25 08:00 | 6.1812 | 0 | N/A | 0 | 0
2021-02-25 08:30 | 5.6068 | 0 | N/A | 0 | 0
2021-02-25 09:00 | 4.9571 | 0 | N/A | 0 | 0
2021-02-25 09:30 | 3.7973 | 0 | N/A | 0 | 0
2021-02-25 10:00 | 2.5792 | 0 | N/A | 0 | 0
2021-02-25 10:30 | 2.1012 | 0 | N/A | 0 | 0
2021-02-25 11:00 | 1.6858 | 0 | N/A | 0 | 0
2021-02-25 11:30 | 1.1738 | 0 | N/A | 0 | 0
2021-02-25 12:00 | 0.71378 | 0 | N/A | 0 | 0
2021-02-25 12:30 | 0.43211 | 0 | N/A | 0 | 0
2021-02-25 13:00 | 0.43046 | 0 | N/A | 0 | 0
2021-02-25 13:30 | 0.21 | 0 | N/A | 0 | 0
2021-02-25 14:00 | 0.073333 | 0 | N/A | 0 | 0
2021-02-25 14:30 | 0.20069 | 0 | N/A | 0 | 0
2021-02-25 15:00 | 0.39667 | 0 | N/A | 0 | 0
2021-02-25 15:30 | 0.61667 | 0 | N/A | 0 | 0
2021-02-25 16:00 | 1.0273 | 0 | N/A | 0 | 0
2021-02-25 16:30 | 1.7468 | 0 | N/A | 0 | 0
2021-02-25 17:00 | 2.6708 | 0 | N/A | 0 | 0
2021-02-25 17:30 | 3.475 | 0 | N/A | 0 | 0
2021-02-25 18:00 | 3.6897 | 0 | N/A | 0 | 0
2021-02-25 18:30 | 3.8051 | 0 | N/A | 0 | 0
2021-02-25 19:00 | 4.1637 | 0 | N/A | 0 | 0
2021-02-25 19:30 | 4.4854 | 0 | N/A | 0 | 0
2021-02-25 20:00 | 4.6661 | 0 | N/A | 0 | 0
2021-02-25 20:30 | 4.6303 | 0 | N/A | 0 | 0
2021-02-25 21:00 | 4.6252 | 0 | N/A | 0 | 0
2021-02-25 21:30 | 4.3261 | 0 | N/A | 0 | 0
2021-02-25 22:00 | 3.9141 | 0 | N/A | 0 | 0
2021-02-25 22:30 | 4.089 | 0 | N/A | 0 | 0
2021-02-25 23:00 | 4.098 | 0 | N/A | 0 | 0
2021-02-25 23:30 | 3.7719 | 0 | N/A | 0 | 0
2021-02-26 | 3.836 | 0 | N/A | 0 | 0
2021-02-26 00:30 | 4.2318 | 0 | N/A | 0 | 0
2021-02-26 01:00 | 4.5711 | 0 | N/A | 0 | 0
2021-02-26 01:30 | 3.7182 | 0 | N/A | 0 | 0
2021-02-26 02:00 | 3.0224 | 0 | N/A | 0 | 0
2021-02-26 02:30 | 2.9437 | 0 | N/A | 0 | 0
2021-02-26 03:00 | 2.6634 | 0 | N/A | 0 | 0
2021-02-26 03:30 | 2.2347 | 0 | N/A | 0 | 0
2021-02-26 04:00 | 2.0955 | 0 | N/A | 0 | 0
2021-02-26 04:30 | 2.0669 | 0 | N/A | 0 | 0
2021-02-26 05:00 | 2.1647 | 0 | N/A | 0 | 0
2021-02-26 05:30 | 2.3246 | 0 | N/A | 0 | 0
2021-02-26 06:00 | 2.6527 | 0 | N/A | 0 | 0
2021-02-26 06:30 | 3.1982 | 0 | N/A | 0 | 0
2021-02-26 07:00 | 3.8066 | 0 | N/A | 0 | 0
2021-02-26 07:30 | 4.6871 | 0 | N/A | 0 | 0
2021-02-26 08:00 | 4.9137 | 0 | N/A | 0 | 0
2021-02-26 08:30 | 4.3209 | 0 | N/A | 0 | 0
2021-02-26 09:00 | 3.8435 | 0 | N/A | 0 | 0
2021-02-26 09:30 | 3.4013 | 0 | N/A | 0 | 0
2021-02-26 10:00 | 2.9058 | 0 | N/A | 0 | 0
2021-02-26 10:30 | 2.6062 | 0 | N/A | 0 | 0
2021-02-26 11:00 | 2.5039 | 0 | N/A | 0 | 0
2021-02-26 11:30 | 2.2976 | 0 | N/A | 0 | 0
2021-02-26 12:00 | 2.2369 | 0 | N/A | 0 | 0
2021-02-26 12:30 | 1.2974 | 0 | N/A | 0 | 0
2021-02-26 13:00 | 0.52385 | 0 | N/A | 0 | 0
2021-02-26 13:30 | -0.29533 | 0 | N/A | 0 | 0
2021-02-26 14:00 | -0.59586 | 0 | N/A | 0 | 0
2021-02-26 14:30 | -0.75473 | 0 | N/A | 0 | 0
2021-02-26 15:00 | -0.72446 | 0 | N/A | 0 | 0
2021-02-26 15:30 | -0.56349 | 0 | N/A | 0 | 0
2021-02-26 16:00 | -0.49875 | 0 | N/A | 0 | 0
2021-02-26 16:30 | -0.37106 | 0 | N/A | 0 | 0
2021-02-26 17:00 | 0.20616 | 0 | N/A | 0 | 0
2021-02-26 17:30 | 0.72921 | 0 | N/A | 0 | 0
2021-02-26 18:00 | 1.5474 | 0 | N/A | 0 | 0
2021-02-26 18:30 | 2.2803 | 0 | N/A | 0 | 0
2021-02-26 19:00 | 2.9625 | 0 | N/A | 0 | 0
2021-02-26 19:30 | 3.4126 | 0 | N/A | 0 | 0
2021-02-26 20:00 | 3.7174 | 0 | N/A | 0 | 0
2021-02-26 20:30 | 4.1191 | 0 | N/A | 0 | 0
2021-02-26 21:00 | 4.2836 | 0 | N/A | 0 | 0
2021-02-26 21:30 | 4.0856 | 0 | N/A | 0 | 0
2021-02-26 22:00 | 3.8326 | 0 | N/A | 0 | 0
2021-02-26 22:30 | 4.1979 | 0 | N/A | 0 | 0
2021-02-26 23:00 | 4.3088 | 0 | N/A | 0 | 0
2021-02-26 23:30 | 3.9882 | 0 | N/A | 0 | 0
2021-02-27 | 4.0179 | 0 | N/A | 0 | 0
2021-02-27 00:30 | 4.411 | 0 | N/A | 0 | 0
2021-02-27 01:00 | 4.7386 | 0 | N/A | 0 | 0
2021-02-27 01:30 | 3.9736 | 0 | N/A | 0 | 0
2021-02-27 02:00 | 3.1286 | 0 | N/A | 0 | 0
2021-02-27 02:30 | 2.9913 | 0 | N/A | 0 | 0
2021-02-27 03:00 | 2.7011 | 0 | N/A | 0 | 0
2021-02-27 03:30 | 2.388 | 0 | N/A | 0 | 0
2021-02-27 04:00 | 2.2376 | 0 | N/A | 0 | 0
2021-02-27 04:30 | 2.1392 | 0 | N/A | 0 | 0
2021-02-27 05:00 | 2.1429 | 0 | N/A | 0 | 0
2021-02-27 05:30 | 2.2125 | 0 | N/A | 0 | 0
2021-02-27 06:00 | 2.3636 | 0 | N/A | 0 | 0
2021-02-27 06:30 | 2.6487 | 0 | N/A | 0 | 0
2021-02-27 07:00 | 2.9364 | 0 | N/A | 0 | 0
2021-02-27 07:30 | 3.3158 | 0 | N/A | 0 | 0
2021-02-27 08:00 | 3.4931 | 0 | N/A | 0 | 0
2021-02-27 08:30 | 3.2398 | 0 | N/A | 0 | 0
2021-02-27 09:00 | 3.2438 | 0 | N/A | 0 | 0
2021-02-27 09:30 | 3.1726 | 0 | N/A | 0 | 0
2021-02-27 10:00 | 3.2425 | 0 | N/A | 0 | 0
2021-02-27 10:30 | 3.0973 | 0 | N/A | 0 | 0
2021-02-27 11:00 | 2.674 | 0 | N/A | 0 | 0
2021-02-27 11:30 | 2.0115 | 0 | N/A | 0 | 0
2021-02-27 12:00 | 1.5142 | 0 | N/A | 0 | 0
2021-02-27 12:30 | 1.0518 | 0 | N/A | 0 | 0
2021-02-27 13:00 | 0.69401 | 0 | N/A | 0 | 0
2021-02-27 13:30 | 0.94385 | 0 | N/A | 0 | 0
2021-02-27 14:00 | 0.71868 | 0 | N/A | 0 | 0
2021-02-27 14:30 | 0.62968 | 0 | N/A | 0 | 0
2021-02-27 15:00 | 0.82624 | 0 | N/A | 0 | 0
2021-02-27 15:30 | 1.2565 | 0 | N/A | 0 | 0
2021-02-27 16:00 | 1.301 | 0 | N/A | 0 | 0
2021-02-27 16:30 | 1.1428 | 0 | N/A | 0 | 0
2021-02-27 17:00 | 1.1563 | 0 | N/A | 0 | 0
2021-02-27 17:30 | 1.5241 | 0 | N/A | 0 | 0
2021-02-27 18:00 | 2.1456 | 0 | N/A | 0 | 0
2021-02-27 18:30 | 2.6743 | 0 | N/A | 0 | 0
2021-02-27 19:00 | 3.2782 | 0 | N/A | 0 | 0
2021-02-27 19:30 | 3.4677 | 0 | N/A | 0 | 0
2021-02-27 20:00 | 3.791 | 0 | N/A | 0 | 0
2021-02-27 20:30 | 3.8765 | 0 | N/A | 0 | 0
2021-02-27 21:00 | 4.027 | 0 | N/A | 0 | 0
2021-02-27 21:30 | 3.8161 | 0 | N/A | 0 | 0
2021-02-27 22:00 | 3.6606 | 0 | N/A | 0 | 0
2021-02-27 22:30 | 4.0759 | 0 | N/A | 0 | 0
2021-02-27 23:00 | 4.2872 | 0 | N/A | 0 | 0
2021-02-27 23:30 | 3.9851 | 0 | N/A | 0 | 0
2021-02-28 | 4.0404 | 0 | N/A | 0 | 0
2021-02-28 00:30 | 4.5708 | 0 | N/A | 0 | 0
2021-02-28 01:00 | 4.8465 | 0 | N/A | 0 | 0
2021-02-28 01:30 | 4.0963 | 0 | N/A | 0 | 0
2021-02-28 02:00 | 3.4028 | 0 | N/A | 0 | 0
2021-02-28 02:30 | 3.256 | 0 | N/A | 0 | 0
2021-02-28 03:00 | 2.9404 | 0 | N/A | 0 | 0
2021-02-28 03:30 | 2.4795 | 0 | N/A | 0 | 0
2021-02-28 04:00 | 2.2336 | 0 | N/A | 0 | 0
2021-02-28 04:30 | 2.1275 | 0 | N/A | 0 | 0
2021-02-28 05:00 | 2.078 | 0 | N/A | 0 | 0
2021-02-28 05:30 | 2.1164 | 0 | N/A | 0 | 0
2021-02-28 06:00 | 2.1541 | 0 | N/A | 0 | 0
2021-02-28 06:30 | 2.3763 | 0 | N/A | 0 | 0
2021-02-28 07:00 | 2.567 | 0 | N/A | 0 | 0
2021-02-28 07:30 | 2.9539 | 0 | N/A | 0 | 0
2021-02-28 08:00 | 3.0694 | 0 | N/A | 0 | 0
2021-02-28 08:30 | 2.7768 | 0 | N/A | 0 | 0
2021-02-28 09:00 | 2.4757 | 0 | N/A | 0 | 0
2021-02-28 09:30 | 1.9231 | 0 | N/A | 0 | 0
2021-02-28 10:00 | 1.2405 | 0 | N/A | 0 | 0
2021-02-28 10:30 | 0.80502 | 0 | N/A | 0 | 0
2021-02-28 11:00 | 0.39205 | 0 | N/A | 0 | 0
2021-02-28 11:30 | 0.31514 | 0 | N/A | 0 | 0
2021-02-28 12:00 | -0.24606 | 0 | N/A | 0 | 0
2021-02-28 12:30 | -0.20667 | 0 | N/A | 0 | 0
2021-02-28 13:00 | 0.33713 | 0 | N/A | 0 | 0
2021-02-28 13:30 | -0.67358 | 0 | N/A | 0 | 0
2021-02-28 14:00 | -0.40401 | 0 | N/A | 0 | 0
2021-02-28 14:30 | -0.56945 | 0 | N/A | 0 | 0
2021-02-28 15:00 | -0.35171 | 0 | N/A | 0 | 0
2021-02-28 15:30 | -0.090554 | 0 | N/A | 0 | 0
2021-02-28 16:00 | 0.45686 | 0 | N/A | 0 | 0
2021-02-28 16:30 | 1.6366 | 0 | N/A | 0 | 0
2021-02-28 17:00 | 2.1644 | 0 | N/A | 0 | 0
2021-02-28 17:30 | 2.482 | 0 | N/A | 0 | 0
2021-02-28 18:00 | 3.0829 | 0 | N/A | 0 | 0
2021-02-28 18:30 | 3.782 | 0 | N/A | 0 | 0
2021-02-28 19:00 | 4.1597 | 0 | N/A | 0 | 0
2021-02-28 19:30 | 4.1794 | 0 | N/A | 0 | 0
2021-02-28 20:00 | 4.2063 | 0 | N/A | 0 | 0
2021-02-28 20:30 | 4.0492 | 0 | N/A | 0 | 0
2021-02-28 21:00 | 4.0428 | 0 | N/A | 0 | 0
2021-02-28 21:30 | 3.8501 | 0 | N/A | 0 | 0
2021-02-28 22:00 | 3.4366 | 0 | N/A | 0 | 0
2021-02-28 22:30 | 3.8449 | 0 | N/A | 0 | 0
2021-02-28 23:00 | 3.9557 | 0 | N/A | 0 | 0
2021-02-28 23:30 | 3.6953 | 0 | N/A | 0 | 0
2021-03-01 | 3.8478 | 0 | N/A | 0 | 0
2021-03-01 00:30 | 4.1267 | 0 | N/A | 0 | 0
2021-03-01 01:00 | 4.488 | 0 | N/A | 0 | 0
2021-03-01 01:30 | 3.7028 | 0 | N/A | 0 | 0
2021-03-01 02:00 | 3.0706 | 0 | N/A | 0 | 0
2021-03-01 02:30 | 3.0421 | 0 | N/A | 0 | 0
2021-03-01 03:00 | 2.7083 | 0 | N/A | 0 | 0
2021-03-01 03:30 | 2.2558 | 0 | N/A | 0 | 0
2021-03-01 04:00 | 2.079 | 0 | N/A | 0 | 0
2021-03-01 04:30 | 1.9644 | 0 | N/A | 0 | 0
2021-03-01 05:00 | 2.0323 | 0 | N/A | 0 | 0
2021-03-01 05:30 | 2.1754 | 0 | N/A | 0 | 0
2021-03-01 06:00 | 2.3846 | 0 | N/A | 0 | 0
2021-03-01 06:30 | 2.8946 | 0 | N/A | 0 | 0
2021-03-01 07:00 | 3.7912 | 0 | N/A | 0 | 0
2021-03-01 07:30 | 4.5577 | 0 | N/A | 0 | 0
2021-03-01 08:00 | 4.8605 | 0 | N/A | 0 | 0
2021-03-01 08:30 | 4.2 | 0 | N/A | 0 | 0
2021-03-01 09:00 | 3.7434 | 0 | N/A | 0 | 0
2021-03-01 09:30 | 3.437 | 0 | N/A | 0 | 0
2021-03-01 10:00 | 3.3867 | 0 | N/A | 0 | 0
2021-03-01 10:30 | 3.3767 | 0 | N/A | 0 | 0
2021-03-01 11:00 | 2.7526 | 0 | N/A | 0 | 0
2021-03-01 11:30 | 2.2242 | 0 | N/A | 0 | 0
2021-03-01 12:00 | 2.6051 | 0 | N/A | 0 | 0
2021-03-01 12:30 | 2.2814 | 0 | N/A | 0 | 0
2021-03-01 13:00 | 1.5471 | 0 | N/A | 0 | 0
2021-03-01 13:30 | 1.2179 | 0 | N/A | 0 | 0
2021-03-01 14:00 | 1.0395 | 0 | N/A | 0 | 0
2021-03-01 14:30 | 0.53671 | 0 | N/A | 0 | 0
2021-03-01 15:00 | 0.41526 | 0 | N/A | 0 | 0
2021-03-01 15:30 | 0.53233 | 0 | N/A | 0 | 0
2021-03-01 16:00 | 0.87425 | 0 | N/A | 0 | 0
2021-03-01 16:30 | 1.4929 | 0 | N/A | 0 | 0
2021-03-01 17:00 | 2.036 | 0 | N/A | 0 | 0
2021-03-01 17:30 | 3.1834 | 0 | N/A | 0 | 0
2021-03-01 18:00 | 4.257 | 0 | N/A | 0 | 0
2021-03-01 18:30 | 4.4449 | 0 | N/A | 0 | 0
2021-03-01 19:00 | 4.5811 | 0 | N/A | 0 | 0
2021-03-01 19:30 | 4.7462 | 0 | N/A | 0 | 0
2021-03-01 20:00 | 4.7759 | 0 | N/A | 0 | 0
2021-03-01 20:30 | 4.8105 | 0 | N/A | 0 | 0
2021-03-01 21:00 | 4.7288 | 0 | N/A | 0 | 0
2021-03-01 21:30 | 4.5292 | 0 | N/A | 0 | 0
2021-03-01 22:00 | 4.2045 | 0 | N/A | 0 | 0
2021-03-01 22:30 | 4.2687 | 0 | N/A | 0 | 0
2021-03-01 23:00 | 4.3268 | 0 | N/A | 0 | 0
2021-03-01 23:30 | 3.9036 | 0 | N/A | 0 | 0
2021-03-02 | 3.9654 | 0 | N/A | 0 | 0
2021-03-02 00:30 | 4.4369 | 0 | N/A | 0 | 0
2021-03-02 01:00 | 4.7964 | 0 | N/A | 0 | 0
2021-03-02 01:30 | 3.8519 | 0 | N/A | 0 | 0
2021-03-02 02:00 | 3.1568 | 0 | N/A | 0 | 0
2021-03-02 02:30 | 3.1104 | 0 | N/A | 0 | 0
2021-03-02 03:00 | 2.7662 | 0 | N/A | 0 | 0
2021-03-02 03:30 | 2.4487 | 0 | N/A | 0 | 0
2021-03-02 04:00 | 2.2403 | 0 | N/A | 0 | 0
2021-03-02 04:30 | 2.2273 | 0 | N/A | 0 | 0
2021-03-02 05:00 | 2.3732 | 0 | N/A | 0 | 0
2021-03-02 05:30 | 2.5572 | 0 | N/A | 0 | 0
2021-03-02 06:00 | 2.8754 | 0 | N/A | 0 | 0
2021-03-02 06:30 | 3.5375 | 0 | N/A | 0 | 0
2021-03-02 07:00 | 4.4776 | 0 | N/A | 0 | 0
2021-03-02 07:30 | 5.63 | 0 | N/A | 0 | 0
2021-03-02 08:00 | 5.8267 | 0 | N/A | 0 | 0
2021-03-02 08:30 | 4.9101 | 0 | N/A | 0 | 0
2021-03-02 09:00 | 4.112 | 0 | N/A | 0 | 0
2021-03-02 09:30 | 3.2901 | 0 | N/A | 0 | 0
2021-03-02 10:00 | 3.1134 | 0 | N/A | 0 | 0
2021-03-02 10:30 | 2.8233 | 0 | N/A | 0 | 0
2021-03-02 11:00 | 2.67 | 0 | N/A | 0 | 0
2021-03-02 11:30 | 2.065 | 0 | N/A | 0 | 0
2021-03-02 12:00 | 2.0396 | 0 | N/A | 0 | 0
2021-03-02 12:30 | 1.8256 | 0 | N/A | 0 | 0
2021-03-02 13:00 | 1.5466 | 0 | N/A | 0 | 0
2021-03-02 13:30 | 1.3291 | 0 | N/A | 0 | 0
2021-03-02 14:00 | 1.2356 | 0 | N/A | 0 | 0
2021-03-02 14:30 | 0.9794 | 0 | N/A | 0 | 0
2021-03-02 15:00 | 1.1035 | 0 | N/A | 0 | 0
2021-03-02 15:30 | 0.85776 | 0 | N/A | 0 | 0
2021-03-02 16:00 | 0.84095 | 0 | N/A | 0 | 0
2021-03-02 16:30 | 0.79203 | 0 | N/A | 0 | 0
2021-03-02 17:00 | 1.1022 | 0 | N/A | 0 | 0
2021-03-02 17:30 | 1.8134 | 0 | N/A | 0 | 0
2021-03-02 18:00 | 2.6367 | 0 | N/A | 0 | 0
2021-03-02 18:30 | 3.5697 | 0 | N/A | 0 | 0
2021-03-02 19:00 | 4.0422 | 0 | N/A | 0 | 0
2021-03-02 19:30 | 4.5643 | 0 | N/A | 0 | 0
2021-03-02 20:00 | 4.831 | 0 | N/A | 0 | 0
2021-03-02 20:30 | 5.0561 | 0 | N/A | 0 | 0
2021-03-02 21:00 | 4.9985 | 0 | N/A | 0 | 0
2021-03-02 21:30 | 4.7019 | 0 | N/A | 0 | 0
2021-03-02 22:00 | 4.3492 | 0 | N/A | 0 | 0
2021-03-02 22:30 | 4.4473 | 0 | N/A | 0 | 0
2021-03-02 23:00 | 4.6112 | 0 | N/A | 0 | 0
2021-03-02 23:30 | 4.2695 | 0 | N/A | 0 | 0
2021-03-03 | 4.2937 | 0 | N/A | 0 | 0
2021-03-03 00:30 | 4.6436 | 0 | N/A | 0 | 0
2021-03-03 01:00 | 4.9161 | 0 | N/A | 0 | 0
2021-03-03 01:30 | 4.0109 | 0 | N/A | 0 | 0
2021-03-03 02:00 | 3.3281 | 0 | N/A | 0 | 0
2021-03-03 02:30 | 3.2453 | 0 | N/A | 0 | 0
2021-03-03 03:00 | 2.8692 | 0 | N/A | 0 | 0
2021-03-03 03:30 | 2.5668 | 0 | N/A | 0 | 0
2021-03-03 04:00 | 2.3307 | 0 | N/A | 0 | 0
2021-03-03 04:30 | 2.3854 | 0 | N/A | 0 | 0
2021-03-03 05:00 | 2.3833 | 0 | N/A | 0 | 0
2021-03-03 05:30 | 2.5821 | 0 | N/A | 0 | 0
2021-03-03 06:00 | 2.9315 | 0 | N/A | 0 | 0
2021-03-03 06:30 | 3.5506 | 0 | N/A | 0 | 0
2021-03-03 07:00 | 4.2454 | 0 | N/A | 0 | 0
2021-03-03 07:30 | 5.6167 | 0 | N/A | 0 | 0
2021-03-03 08:00 | 5.7533 | 0 | N/A | 0 | 0
2021-03-03 08:30 | 4.7834 | 0 | N/A | 0 | 0
2021-03-03 09:00 | 3.97 | 0 | N/A | 0 | 0
2021-03-03 09:30 | 3.63 | 0 | N/A | 0 | 0
2021-03-03 10:00 | 3.6167 | 0 | N/A | 0 | 0
2021-03-03 10:30 | 2.8835 | 0 | N/A | 0 | 0
2021-03-03 11:00 | 2.347 | 0 | N/A | 0 | 0
2021-03-03 11:30 | 2.2006 | 0 | N/A | 0 | 0
2021-03-03 12:00 | 1.65 | 0 | N/A | 0 | 0
2021-03-03 12:30 | 2.0011 | 0 | N/A | 0 | 0
2021-03-03 13:00 | 0.99435 | 0 | N/A | 0 | 0
2021-03-03 13:30 | 0.16997 | 0 | N/A | 0 | 0
2021-03-03 14:00 | 0.04714 | 0 | N/A | 0 | 0
2021-03-03 14:30 | -0.32173 | 0 | N/A | 0 | 0
2021-03-03 15:00 | -0.49333 | 0 | N/A | 0 | 0
2021-03-03 15:30 | -0.53105 | 0 | N/A | 0 | 0
2021-03-03 16:00 | -0.6392 | 0 | N/A | 0 | 0
2021-03-03 16:30 | -0.26183 | 0 | N/A | 0 | 0
2021-03-03 17:00 | 0.5717 | 0 | N/A | 0 | 0
2021-03-03 17:30 | 1.5954 | 0 | N/A | 0 | 0
2021-03-03 18:00 | 2.4211 | 0 | N/A | 0 | 0
2021-03-03 18:30 | 3.1203 | 0 | N/A | 0 | 0
2021-03-03 19:00 | 3.9323 | 0 | N/A | 0 | 0
2021-03-03 19:30 | 4.4316 | 0 | N/A | 0 | 0
2021-03-03 20:00 | 4.5708 | 0 | N/A | 0 | 0
2021-03-03 20:30 | 4.7988 | 0 | N/A | 0 | 0
2021-03-03 21:00 | 4.8473 | 0 | N/A | 0 | 0
2021-03-03 21:30 | 4.6286 | 0 | N/A | 0 | 0
2021-03-03 22:00 | 4.2652 | 0 | N/A | 0 | 0
2021-03-03 22:30 | 4.3799 | 0 | N/A | 0 | 0
2021-03-03 23:00 | 4.411 | 0 | N/A | 0 | 0
2021-03-03 23:30 | 3.9834 | 0 | N/A | 0 | 0
2021-03-04 | 4.0247 | 0 | N/A | 0 | 0
2021-03-04 00:30 | 4.5194 | 0 | N/A | 0 | 0
2021-03-04 01:00 | 4.7231 | 0 | N/A | 0 | 0
2021-03-04 01:30 | 3.9009 | 0 | N/A | 0 | 0
2021-03-04 02:00 | 3.1745 | 0 | N/A | 0 | 0
2021-03-04 02:30 | 3.0616 | 0 | N/A | 0 | 0
2021-03-04 03:00 | 2.7885 | 0 | N/A | 0 | 0
2021-03-04 03:30 | 2.4624 | 0 | N/A | 0 | 0
2021-03-04 04:00 | 2.2898 | 0 | N/A | 0 | 0
2021-03-04 04:30 | 2.2094 | 0 | N/A | 0 | 0
2021-03-04 05:00 | 2.2575 | 0 | N/A | 0 | 0
2021-03-04 05:30 | 2.4026 | 0 | N/A | 0 | 0
2021-03-04 06:00 | 2.7551 | 0 | N/A | 0 | 0
2021-03-04 06:30 | 3.4059 | 0 | N/A | 0 | 0
2021-03-04 07:00 | 4.1432 | 0 | N/A | 0 | 0
2021-03-04 07:30 | 5.6534 | 0 | N/A | 0 | 0
2021-03-04 08:00 | 6.0573 | 0 | N/A | 0 | 0
2021-03-04 08:30 | 5.1883 | 0 | N/A | 0 | 0
2021-03-04 09:00 | 4.7009 | 0 | N/A | 0 | 0
2021-03-04 09:30 | 4.3935 | 0 | N/A | 0 | 0
2021-03-04 10:00 | 4.0035 | 0 | N/A | 0 | 0
2021-03-04 10:30 | 3.4133 | 0 | N/A | 0 | 0
2021-03-04 11:00 | 3.2067 | 0 | N/A | 0 | 0
2021-03-04 11:30 | 3.4564 | 0 | N/A | 0 | 0
2021-03-04 12:00 | 3.3746 | 0 | N/A | 0 | 0
2021-03-04 12:30 | 3.0149 | 0 | N/A | 0 | 0
2021-03-04 13:00 | 3.0123 | 0 | N/A | 0 | 0
2021-03-04 13:30 | 2.8306 | 0 | N/A | 0 | 0
2021-03-04 14:00 | 3.0619 | 0 | N/A | 0 | 0
2021-03-04 14:30 | 2.731 | 0 | N/A | 0 | 0
2021-03-04 15:00 | 3.2003 | 0 | N/A | 0 | 0
2021-03-04 15:30 | 3.0567 | 0 | N/A | 0 | 0
2021-03-04 16:00 | 2.6804 | 0 | N/A | 0 | 0
2021-03-04 16:30 | 2.3909 | 0 | N/A | 0 | 0
2021-03-04 17:00 | 2.7922 | 0 | N/A | 0 | 0
2021-03-04 17:30 | 3.12 | 0 | N/A | 0 | 0
2021-03-04 18:00 | 3.8199 | 0 | N/A | 0 | 0
2021-03-04 18:30 | 4.4624 | 0 | N/A | 0 | 0
2021-03-04 19:00 | 4.9079 | 0 | N/A | 0 | 0
2021-03-04 19:30 | 4.9679 | 0 | N/A | 0 | 0
2021-03-04 20:00 | 4.9487 | 0 | N/A | 0 | 0
2021-03-04 20:30 | 4.9587 | 0 | N/A | 0 | 0
2021-03-04 21:00 | 4.8637 | 0 | N/A | 0 | 0
2021-03-04 21:30 | 4.5763 | 0 | N/A | 0 | 0
2021-03-04 22:00 | 4.1928 | 0 | N/A | 0 | 0
2021-03-04 22:30 | 4.4912 | 0 | N/A | 0 | 0
2021-03-04 23:00 | 4.4469 | 0 | N/A | 0 | 0
2021-03-04 23:30 | 4.0199 | 0 | N/A | 0 | 0
2021-03-05 | 4.1327 | 0 | N/A | 0 | 0
2021-03-05 00:30 | 4.6577 | 0 | N/A | 0 | 0
2021-03-05 01:00 | 4.956 | 0 | N/A | 0 | 0
2021-03-05 01:30 | 4.0656 | 0 | N/A | 0 | 0
2021-03-05 02:00 | 3.2485 | 0 | N/A | 0 | 0
2021-03-05 02:30 | 3.1409 | 0 | N/A | 0 | 0
2021-03-05 03:00 | 2.7532 | 0 | N/A | 0 | 0
2021-03-05 03:30 | 2.4223 | 0 | N/A | 0 | 0
2021-03-05 04:00 | 2.2815 | 0 | N/A | 0 | 0
2021-03-05 04:30 | 2.2262 | 0 | N/A | 0 | 0
2021-03-05 05:00 | 2.2624 | 0 | N/A | 0 | 0
2021-03-05 05:30 | 2.4593 | 0 | N/A | 0 | 0
2021-03-05 06:00 | 2.697 | 0 | N/A | 0 | 0
2021-03-05 06:30 | 3.409 | 0 | N/A | 0 | 0
2021-03-05 07:00 | 4.2561 | 0 | N/A | 0 | 0
2021-03-05 07:30 | 5.3934 | 0 | N/A | 0 | 0
2021-03-05 08:00 | 5.6301 | 0 | N/A | 0 | 0
2021-03-05 08:30 | 4.8267 | 0 | N/A | 0 | 0
2021-03-05 09:00 | 4.4533 | 0 | N/A | 0 | 0
2021-03-05 09:30 | 3.9769 | 0 | N/A | 0 | 0
2021-03-05 10:00 | 3.94 | 0 | N/A | 0 | 0
2021-03-05 10:30 | 3.3833 | 0 | N/A | 0 | 0
2021-03-05 11:00 | 2.92 | 0 | N/A | 0 | 0
2021-03-05 11:30 | 3.4467 | 0 | N/A | 0 | 0
2021-03-05 12:00 | 3.1635 | 0 | N/A | 0 | 0
2021-03-05 12:30 | 2.5985 | 0 | N/A | 0 | 0
2021-03-05 13:00 | 2.5101 | 0 | N/A | 0 | 0
2021-03-05 13:30 | 1.77 | 0 | N/A | 0 | 0
2021-03-05 14:00 | 1.6114 | 0 | N/A | 0 | 0
2021-03-05 14:30 | 1.2933 | 0 | N/A | 0 | 0
2021-03-05 15:00 | 0.32718 | 0 | N/A | 0 | 0
2021-03-05 15:30 | -0.53009 | 0 | N/A | 0 | 0
2021-03-05 16:00 | -0.45198 | 0 | N/A | 0 | 0
2021-03-05 16:30 | -0.66242 | 0 | N/A | 0 | 0
2021-03-05 17:00 | -0.38037 | 0 | N/A | 0 | 0
2021-03-05 17:30 | 0.774 | 0 | N/A | 0 | 0
2021-03-05 18:00 | 1.6602 | 0 | N/A | 0 | 0
2021-03-05 18:30 | 2.36 | 0 | N/A | 0 | 0
2021-03-05 19:00 | 3.1039 | 0 | N/A | 0 | 0
2021-03-05 19:30 | 3.6984 | 0 | N/A | 0 | 0
2021-03-05 20:00 | 4.1438 | 0 | N/A | 0 | 0
2021-03-05 20:30 | 4.3699 | 0 | N/A | 0 | 0
2021-03-05 21:00 | 4.3987 | 0 | N/A | 0 | 0
2021-03-05 21:30 | 4.1828 | 0 | N/A | 0 | 0
2021-03-05 22:00 | 4.009 | 0 | N/A | 0 | 0
2021-03-05 22:30 | 4.3053 | 0 | N/A | 0 | 0
2021-03-05 23:00 | 4.4053 | 0 | N/A | 0 | 0
2021-03-05 23:30 | 4.0465 | 0 | N/A | 0 | 0
2021-03-06 | 4.11 | 0 | N/A | 0 | 0
2021-03-06 00:30 | 4.5513 | 0 | N/A | 0 | 0
2021-03-06 01:00 | 4.8376 | 0 | N/A | 0 | 0
2021-03-06 01:30 | 4.0357 | 0 | N/A | 0 | 0
2021-03-06 02:00 | 3.2532 | 0 | N/A | 0 | 0
2021-03-06 02:30 | 3.2016 | 0 | N/A | 0 | 0
2021-03-06 03:00 | 2.8237 | 0 | N/A | 0 | 0
2021-03-06 03:30 | 2.435 | 0 | N/A | 0 | 0
2021-03-06 04:00 | 2.264 | 0 | N/A | 0 | 0
2021-03-06 04:30 | 2.1246 | 0 | N/A | 0 | 0
2021-03-06 05:00 | 2.1728 | 0 | N/A | 0 | 0
2021-03-06 05:30 | 2.1616 | 0 | N/A | 0 | 0
2021-03-06 06:00 | 2.2643 | 0 | N/A | 0 | 0
2021-03-06 06:30 | 2.6312 | 0 | N/A | 0 | 0
2021-03-06 07:00 | 2.7848 | 0 | N/A | 0 | 0
2021-03-06 07:30 | 3.3539 | 0 | N/A | 0 | 0
2021-03-06 08:00 | 3.6582 | 0 | N/A | 0 | 0
2021-03-06 08:30 | 3.5074 | 0 | N/A | 0 | 0
2021-03-06 09:00 | 3.2269 | 0 | N/A | 0 | 0
2021-03-06 09:30 | 2.7532 | 0 | N/A | 0 | 0
2021-03-06 10:00 | 1.9667 | 0 | N/A | 0 | 0
2021-03-06 10:30 | 1.1678 | 0 | N/A | 0 | 0
2021-03-06 11:00 | 0.56694 | 0 | N/A | 0 | 0
2021-03-06 11:30 | -0.32804 | 0 | N/A | 0 | 0
2021-03-06 12:00 | -0.44548 | 0 | N/A | 0 | 0
2021-03-06 12:30 | -0.56399 | 0 | N/A | 0 | 0
2021-03-06 13:00 | -0.8359 | 0 | N/A | 0 | 0
2021-03-06 13:30 | -1.0227 | 0 | N/A | 0 | 0
2021-03-06 14:00 | -1.1205 | 0 | N/A | 0 | 0
2021-03-06 14:30 | -1.1029 | 0 | N/A | 0 | 0
2021-03-06 15:00 | -1.0152 | 0 | N/A | 0 | 0
2021-03-06 15:30 | -0.99716 | 0 | N/A | 0 | 0
2021-03-06 16:00 | -0.81274 | 0 | N/A | 0 | 0
2021-03-06 16:30 | -0.50413 | 0 | N/A | 0 | 0
2021-03-06 17:00 | 0.34796 | 0 | N/A | 0 | 0
2021-03-06 17:30 | 0.91547 | 0 | N/A | 0 | 0
2021-03-06 18:00 | 2.2227 | 0 | N/A | 0 | 0
2021-03-06 18:30 | 2.3292 | 0 | N/A | 0 | 0
2021-03-06 19:00 | 2.9658 | 0 | N/A | 0 | 0
2021-03-06 19:30 | 3.5889 | 0 | N/A | 0 | 0
2021-03-06 20:00 | 3.75 | 0 | N/A | 0 | 0
2021-03-06 20:30 | 3.7551 | 0 | N/A | 0 | 0
2021-03-06 21:00 | 3.7282 | 0 | N/A | 0 | 0
2021-03-06 21:30 | 3.5155 | 0 | N/A | 0 | 0
2021-03-06 22:00 | 3.385 | 0 | N/A | 0 | 0
2021-03-06 22:30 | 3.8329 | 0 | N/A | 0 | 0
2021-03-06 23:00 | 4.0937 | 0 | N/A | 0 | 0
2021-03-06 23:30 | 3.8705 | 0 | N/A | 0 | 0
2021-03-07 | 4.0295 | 0 | N/A | 0 | 0
2021-03-07 00:30 | 4.3975 | 0 | N/A | 0 | 0
2021-03-07 01:00 | 4.6481 | 0 | N/A | 0 | 0
2021-03-07 01:30 | 3.8485 | 0 | N/A | 0 | 0
2021-03-07 02:00 | 3.1896 | 0 | N/A | 0 | 0
2021-03-07 02:30 | 3.0926 | 0 | N/A | 0 | 0
2021-03-07 03:00 | 2.7729 | 0 | N/A | 0 | 0
2021-03-07 03:30 | 2.4424 | 0 | N/A | 0 | 0
2021-03-07 04:00 | 2.1819 | 0 | N/A | 0 | 0
2021-03-07 04:30 | 2.1046 | 0 | N/A | 0 | 0
2021-03-07 05:00 | 2.0493 | 0 | N/A | 0 | 0
2021-03-07 05:30 | 2.073 | 0 | N/A | 0 | 0
2021-03-07 06:00 | 2.104 | 0 | N/A | 0 | 0
2021-03-07 06:30 | 2.382 | 0 | N/A | 0 | 0
2021-03-07 07:00 | 2.5456 | 0 | N/A | 0 | 0
2021-03-07 07:30 | 2.8928 | 0 | N/A | 0 | 0
2021-03-07 08:00 | 3.0563 | 0 | N/A | 0 | 0
2021-03-07 08:30 | 2.8311 | 0 | N/A | 0 | 0
2021-03-07 09:00 | 2.5799 | 0 | N/A | 0 | 0
2021-03-07 09:30 | 2.4419 | 0 | N/A | 0 | 0
2021-03-07 10:00 | 1.6824 | 0 | N/A | 0 | 0
2021-03-07 10:30 | 1.3893 | 0 | N/A | 0 | 0
2021-03-07 11:00 | 0.88383 | 0 | N/A | 0 | 0
2021-03-07 11:30 | 0.53505 | 0 | N/A | 0 | 0
2021-03-07 12:00 | -0.48555 | 0 | N/A | 0 | 0
2021-03-07 12:30 | 0.34913 | 0 | N/A | 0 | 0
2021-03-07 13:00 | -0.6716 | 0 | N/A | 0 | 0
2021-03-07 13:30 | -1.033 | 0 | N/A | 0 | 0
2021-03-07 14:00 | -0.9208 | 0 | N/A | 0 | 0
2021-03-07 14:30 | -0.38326 | 0 | N/A | 0 | 0
2021-03-07 15:00 | -0.32484 | 0 | N/A | 0 | 0
2021-03-07 15:30 | 0.61602 | 0 | N/A | 0 | 0
2021-03-07 16:00 | 0.65327 | 0 | N/A | 0 | 0
2021-03-07 16:30 | 0.39229 | 0 | N/A | 0 | 0
2021-03-07 17:00 | 1.2612 | 0 | N/A | 0 | 0
2021-03-07 17:30 | 2.6179 | 0 | N/A | 0 | 0
2021-03-07 18:00 | 3.1174 | 0 | N/A | 0 | 0
2021-03-07 18:30 | 3.4314 | 0 | N/A | 0 | 0
2021-03-07 19:00 | 3.6678 | 0 | N/A | 0 | 0
2021-03-07 19:30 | 3.7549 | 0 | N/A | 0 | 0
2021-03-07 20:00 | 3.8592 | 0 | N/A | 0 | 0
2021-03-07 20:30 | 3.772 | 0 | N/A | 0 | 0
2021-03-07 21:00 | 3.5596 | 0 | N/A | 0 | 0
2021-03-07 21:30 | 3.43 | 0 | N/A | 0 | 0
2021-03-07 22:00 | 3.2239 | 0 | N/A | 0 | 0
2021-03-07 22:30 | 3.6816 | 0 | N/A | 0 | 0
2021-03-07 23:00 | 3.8401 | 0 | N/A | 0 | 0
2021-03-07 23:30 | 3.5866 | 0 | N/A | 0 | 0
2021-03-08 | 3.7023 | 0 | N/A | 0 | 0
2021-03-08 00:30 | 4.1771 | 0 | N/A | 0 | 0
2021-03-08 01:00 | 4.4852 | 0 | N/A | 0 | 0
2021-03-08 01:30 | 3.585 | 0 | N/A | 0 | 0
2021-03-08 02:00 | 2.9413 | 0 | N/A | 0 | 0
2021-03-08 02:30 | 2.828 | 0 | N/A | 0 | 0
2021-03-08 03:00 | 2.5134 | 0 | N/A | 0 | 0
2021-03-08 03:30 | 2.1789 | 0 | N/A | 0 | 0
2021-03-08 04:00 | 2.0235 | 0 | N/A | 0 | 0
2021-03-08 04:30 | 1.9082 | 0 | N/A | 0 | 0
2021-03-08 05:00 | 1.826 | 0 | N/A | 0 | 0
2021-03-08 05:30 | 1.8639 | 0 | N/A | 0 | 0
2021-03-08 06:00 | 1.9898 | 0 | N/A | 0 | 0
2021-03-08 06:30 | 2.2554 | 0 | N/A | 0 | 0
2021-03-08 07:00 | 2.416 | 0 | N/A | 0 | 0
2021-03-08 07:30 | 2.6832 | 0 | N/A | 0 | 0
2021-03-08 08:00 | 2.8687 | 0 | N/A | 0 | 0
2021-03-08 08:30 | 2.755 | 0 | N/A | 0 | 0
2021-03-08 09:00 | 2.7464 | 0 | N/A | 0 | 0
2021-03-08 09:30 | 3.1495 | 0 | N/A | 0 | 0
2021-03-08 10:00 | 3.4922 | 0 | N/A | 0 | 0
2021-03-08 10:30 | 3.3347 | 0 | N/A | 0 | 0
2021-03-08 11:00 | 3.2859 | 0 | N/A | 0 | 0
2021-03-08 11:30 | 3.1196 | 0 | N/A | 0 | 0
2021-03-08 12:00 | 3.2382 | 0 | N/A | 0 | 0
2021-03-08 12:30 | 2.946 | 0 | N/A | 0 | 0
2021-03-08 13:00 | 2.8106 | 0 | N/A | 0 | 0
2021-03-08 13:30 | 2.4913 | 0 | N/A | 0 | 0
2021-03-08 14:00 | 2.5521 | 0 | N/A | 0 | 0
2021-03-08 14:30 | 2.5404 | 0 | N/A | 0 | 0
2021-03-08 15:00 | 2.1007 | 0 | N/A | 0 | 0
2021-03-08 15:30 | 1.5221 | 0 | N/A | 0 | 0
2021-03-08 16:00 | 2.6398 | 0 | N/A | 0 | 0
2021-03-08 16:30 | 3.3181 | 0 | N/A | 0 | 0
2021-03-08 17:00 | 3.965 | 0 | N/A | 0 | 0
2021-03-08 17:30 | 4.5397 | 0 | N/A | 0 | 0
2021-03-08 18:00 | 5.1914 | 0 | N/A | 0 | 0
2021-03-08 18:30 | 5.3238 | 0 | N/A | 0 | 0
2021-03-08 19:00 | 5.4943 | 0 | N/A | 0 | 0
2021-03-08 19:30 | 5.1852 | 0 | N/A | 0 | 0
2021-03-08 20:00 | 5.0134 | 0 | N/A | 0 | 0
2021-03-08 20:30 | 4.8631 | 0 | N/A | 0 | 0
2021-03-08 21:00 | 4.7031 | 0 | N/A | 0 | 0
2021-03-08 21:30 | 4.3186 | 0 | N/A | 0 | 0
2021-03-08 22:00 | 3.9859 | 0 | N/A | 0 | 0
2021-03-08 22:30 | 4.1874 | 0 | N/A | 0 | 0
2021-03-08 23:00 | 4.2936 | 0 | N/A | 0 | 0
2021-03-08 23:30 | 3.9703 | 0 | N/A | 0 | 0
2021-03-09 | 4.0585 | 0 | N/A | 0 | 0
2021-03-09 00:30 | 4.5595 | 0 | N/A | 0 | 0
2021-03-09 01:00 | 4.8678 | 0 | N/A | 0 | 0
2021-03-09 01:30 | 4.2404 | 0 | N/A | 0 | 0
2021-03-09 02:00 | 3.5432 | 0 | N/A | 0 | 0
2021-03-09 02:30 | 3.4095 | 0 | N/A | 0 | 0
2021-03-09 03:00 | 2.9728 | 0 | N/A | 0 | 0
2021-03-09 03:30 | 2.5636 | 0 | N/A | 0 | 0
2021-03-09 04:00 | 2.3658 | 0 | N/A | 0 | 0
2021-03-09 04:30 | 2.2753 | 0 | N/A | 0 | 0
2021-03-09 05:00 | 2.3159 | 0 | N/A | 0 | 0
2021-03-09 05:30 | 2.4751 | 0 | N/A | 0 | 0
2021-03-09 06:00 | 2.6376 | 0 | N/A | 0 | 0
2021-03-09 06:30 | 3.2667 | 0 | N/A | 0 | 0
2021-03-09 07:00 | 3.9819 | 0 | N/A | 0 | 0
2021-03-09 07:30 | 5.1597 | 0 | N/A | 0 | 0
2021-03-09 08:00 | 5.7169 | 0 | N/A | 0 | 0
2021-03-09 08:30 | 4.97 | 0 | N/A | 0 | 0
2021-03-09 09:00 | 4.7533 | 0 | N/A | 0 | 0
2021-03-09 09:30 | 4.2667 | 0 | N/A | 0 | 0
2021-03-09 10:00 | 3.2333 | 0 | N/A | 0 | 0
2021-03-09 10:30 | 2.8184 | 0 | N/A | 0 | 0
2021-03-09 11:00 | 2.8985 | 0 | N/A | 0 | 0
2021-03-09 11:30 | 2.9473 | 0 | N/A | 0 | 0
2021-03-09 12:00 | 2.6734 | 0 | N/A | 0 | 0
2021-03-09 12:30 | 2.674 | 0 | N/A | 0 | 0
2021-03-09 13:00 | 1.9113 | 0 | N/A | 0 | 0
2021-03-09 13:30 | 1.6816 | 0 | N/A | 0 | 0
2021-03-09 14:00 | 1.7332 | 0 | N/A | 0 | 0
2021-03-09 14:30 | 1.365 | 0 | N/A | 0 | 0
2021-03-09 15:00 | 1.3311 | 0 | N/A | 0 | 0
2021-03-09 15:30 | 0.94611 | 0 | N/A | 0 | 0
2021-03-09 16:00 | 0.72396 | 0 | N/A | 0 | 0
2021-03-09 16:30 | 1.5663 | 0 | N/A | 0 | 0
2021-03-09 17:00 | 1.5554 | 0 | N/A | 0 | 0
2021-03-09 17:30 | 1.8233 | 0 | N/A | 0 | 0
2021-03-09 18:00 | 2.8812 | 0 | N/A | 0 | 0
2021-03-09 18:30 | 3.6756 | 0 | N/A | 0 | 0
2021-03-09 19:00 | 3.9667 | 0 | N/A | 0 | 0
2021-03-09 19:30 | 4.4475 | 0 | N/A | 0 | 0
2021-03-09 20:00 | 4.5761 | 0 | N/A | 0 | 0
2021-03-09 20:30 | 4.7269 | 0 | N/A | 0 | 0
2021-03-09 21:00 | 4.6322 | 0 | N/A | 0 | 0
2021-03-09 21:30 | 4.3493 | 0 | N/A | 0 | 0
2021-03-09 22:00 | 4.1804 | 0 | N/A | 0 | 0
2021-03-09 22:30 | 4.3403 | 0 | N/A | 0 | 0
2021-03-09 23:00 | 4.4629 | 0 | N/A | 0 | 0
2021-03-09 23:30 | 3.9987 | 0 | N/A | 0 | 0
2021-03-10 | 4.0475 | 0 | N/A | 0 | 0
2021-03-10 00:30 | 4.567 | 0 | N/A | 0 | 0
2021-03-10 01:00 | 4.7716 | 0 | N/A | 0 | 0
2021-03-10 01:30 | 3.9492 | 0 | N/A | 0 | 0
2021-03-10 02:00 | 3.1101 | 0 | N/A | 0 | 0
2021-03-10 02:30 | 3.0617 | 0 | N/A | 0 | 0
2021-03-10 03:00 | 2.7634 | 0 | N/A | 0 | 0
2021-03-10 03:30 | 2.4226 | 0 | N/A | 0 | 0
2021-03-10 04:00 | 2.3347 | 0 | N/A | 0 | 0
2021-03-10 04:30 | 2.2317 | 0 | N/A | 0 | 0
2021-03-10 05:00 | 2.2285 | 0 | N/A | 0 | 0
2021-03-10 05:30 | 2.4404 | 0 | N/A | 0 | 0
2021-03-10 06:00 | 2.8127 | 0 | N/A | 0 | 0
2021-03-10 06:30 | 3.6321 | 0 | N/A | 0 | 0
2021-03-10 07:00 | 4.6352 | 0 | N/A | 0 | 0
2021-03-10 07:30 | 5.7302 | 0 | N/A | 0 | 0
2021-03-10 08:00 | 6.0402 | 0 | N/A | 0 | 0
2021-03-10 08:30 | 5.0605 | 0 | N/A | 0 | 0
2021-03-10 09:00 | 4.51 | 0 | N/A | 0 | 0
2021-03-10 09:30 | 4.1806 | 0 | N/A | 0 | 0
2021-03-10 10:00 | 3.5104 | 0 | N/A | 0 | 0
2021-03-10 10:30 | 2.5807 | 0 | N/A | 0 | 0
2021-03-10 11:00 | 1.6302 | 0 | N/A | 0 | 0
2021-03-10 11:30 | 1.08 | 0 | N/A | 0 | 0
2021-03-10 12:00 | 0.45564 | 0 | N/A | 0 | 0
2021-03-10 12:30 | 0.14181 | 0 | N/A | 0 | 0
2021-03-10 13:00 | -0.24141 | 0 | N/A | 0 | 0
2021-03-10 13:30 | -0.30971 | 0 | N/A | 0 | 0
2021-03-10 14:00 | -0.36545 | 0 | N/A | 0 | 0
2021-03-10 14:30 | -0.34158 | 0 | N/A | 0 | 0
2021-03-10 15:00 | -0.31447 | 0 | N/A | 0 | 0
2021-03-10 15:30 | -0.31213 | 0 | N/A | 0 | 0
2021-03-10 16:00 | 0.2523 | 0 | N/A | 0 | 0
2021-03-10 16:30 | 0.22423 | 0 | N/A | 0 | 0
2021-03-10 17:00 | 0.91741 | 0 | N/A | 0 | 0
2021-03-10 17:30 | 1.882 | 0 | N/A | 0 | 0
2021-03-10 18:00 | 2.7891 | 0 | N/A | 0 | 0
2021-03-10 18:30 | 3.331 | 0 | N/A | 0 | 0
2021-03-10 19:00 | 3.9705 | 0 | N/A | 0 | 0
2021-03-10 19:30 | 4.1144 | 0 | N/A | 0 | 0
2021-03-10 20:00 | 4.2833 | 0 | N/A | 0 | 0
2021-03-10 20:30 | 4.4092 | 0 | N/A | 0 | 0
2021-03-10 21:00 | 4.4369 | 0 | N/A | 0 | 0
2021-03-10 21:30 | 4.0469 | 0 | N/A | 0 | 0
2021-03-10 22:00 | 3.7117 | 0 | N/A | 0 | 0
2021-03-10 22:30 | 3.9801 | 0 | N/A | 0 | 0
2021-03-10 23:00 | 4.0717 | 0 | N/A | 0 | 0
2021-03-10 23:30 | 3.7192 | 0 | N/A | 0 | 0
2021-03-11 | 3.7948 | 0 | N/A | 0 | 0
2021-03-11 00:30 | 4.2454 | 0 | N/A | 0 | 0
2021-03-11 01:00 | 4.5038 | 0 | N/A | 0 | 0
2021-03-11 01:30 | 3.6981 | 0 | N/A | 0 | 0
2021-03-11 02:00 | 2.9721 | 0 | N/A | 0 | 0
2021-03-11 02:30 | 2.9015 | 0 | N/A | 0 | 0
2021-03-11 03:00 | 2.6672 | 0 | N/A | 0 | 0
2021-03-11 03:30 | 2.3479 | 0 | N/A | 0 | 0
2021-03-11 04:00 | 2.2259 | 0 | N/A | 0 | 0
2021-03-11 04:30 | 2.1343 | 0 | N/A | 0 | 0
2021-03-11 05:00 | 2.1735 | 0 | N/A | 0 | 0
2021-03-11 05:30 | 2.3627 | 0 | N/A | 0 | 0
2021-03-11 06:00 | 2.672 | 0 | N/A | 0 | 0
2021-03-11 06:30 | 3.2935 | 0 | N/A | 0 | 0
2021-03-11 07:00 | 4.0868 | 0 | N/A | 0 | 0
2021-03-11 07:30 | 5.2572 | 0 | N/A | 0 | 0
2021-03-11 08:00 | 5.6933 | 0 | N/A | 0 | 0
2021-03-11 08:30 | 5.02 | 0 | N/A | 0 | 0
2021-03-11 09:00 | 4.1133 | 0 | N/A | 0 | 0
2021-03-11 09:30 | 3.8701 | 0 | N/A | 0 | 0
2021-03-11 10:00 | 2.9509 | 0 | N/A | 0 | 0
2021-03-11 10:30 | 2.6747 | 0 | N/A | 0 | 0
2021-03-11 11:00 | 2.4311 | 0 | N/A | 0 | 0
2021-03-11 11:30 | 1.8758 | 0 | N/A | 0 | 0
2021-03-11 12:00 | 1.4562 | 0 | N/A | 0 | 0
2021-03-11 12:30 | 0.62681 | 0 | N/A | 0 | 0
2021-03-11 13:00 | 0.36448 | 0 | N/A | 0 | 0
2021-03-11 13:30 | -0.31693 | 0 | N/A | 0 | 0
2021-03-11 14:00 | -0.39532 | 0 | N/A | 0 | 0
2021-03-11 14:30 | -0.37696 | 0 | N/A | 0 | 0
2021-03-11 15:00 | 0.92339 | 0 | N/A | 0 | 0
2021-03-11 15:30 | 1.8403 | 0 | N/A | 0 | 0
2021-03-11 16:00 | 3.0733 | 0 | N/A | 0 | 0
2021-03-11 16:30 | 3.6967 | 0 | N/A | 0 | 0
2021-03-11 17:00 | 3.9331 | 0 | N/A | 0 | 0
2021-03-11 17:30 | 4.1815 | 0 | N/A | 0 | 0
2021-03-11 18:00 | 4.4634 | 0 | N/A | 0 | 0
2021-03-11 18:30 | 4.4655 | 0 | N/A | 0 | 0
2021-03-11 19:00 | 4.4873 | 0 | N/A | 0 | 0
2021-03-11 19:30 | 4.4001 | 0 | N/A | 0 | 0
2021-03-11 20:00 | 4.3938 | 0 | N/A | 0 | 0
2021-03-11 20:30 | 4.4227 | 0 | N/A | 0 | 0
2021-03-11 21:00 | 4.2851 | 0 | N/A | 0 | 0
2021-03-11 21:30 | 4.0034 | 0 | N/A | 0 | 0
2021-03-11 22:00 | 3.6461 | 0 | N/A | 0 | 0
2021-03-11 22:30 | 3.9071 | 0 | N/A | 0 | 0
2021-03-11 23:00 | 4.0344 | 0 | N/A | 0 | 0
2021-03-11 23:30 | 3.5769 | 0 | N/A | 0 | 0
2021-03-12 | 3.7127 | 0 | N/A | 0 | 0
2021-03-12 00:30 | 4.1628 | 0 | N/A | 0 | 0
2021-03-12 01:00 | 4.4502 | 0 | N/A | 0 | 0
2021-03-12 01:30 | 3.6108 | 0 | N/A | 0 | 0
2021-03-12 02:00 | 2.9023 | 0 | N/A | 0 | 0
2021-03-12 02:30 | 2.7999 | 0 | N/A | 0 | 0
2021-03-12 03:00 | 2.4634 | 0 | N/A | 0 | 0
2021-03-12 03:30 | 2.1609 | 0 | N/A | 0 | 0
2021-03-12 04:00 | 1.982 | 0 | N/A | 0 | 0
2021-03-12 04:30 | 1.9312 | 0 | N/A | 0 | 0
2021-03-12 05:00 | 1.9942 | 0 | N/A | 0 | 0
2021-03-12 05:30 | 2.1931 | 0 | N/A | 0 | 0
2021-03-12 06:00 | 2.4297 | 0 | N/A | 0 | 0
2021-03-12 06:30 | 2.9495 | 0 | N/A | 0 | 0
2021-03-12 07:00 | 3.6242 | 0 | N/A | 0 | 0
2021-03-12 07:30 | 4.4745 | 0 | N/A | 0 | 0
2021-03-12 08:00 | 4.7736 | 0 | N/A | 0 | 0
2021-03-12 08:30 | 3.8037 | 0 | N/A | 0 | 0
2021-03-12 09:00 | 3.2711 | 0 | N/A | 0 | 0
2021-03-12 09:30 | 2.9034 | 0 | N/A | 0 | 0
2021-03-12 10:00 | 2.527 | 0 | N/A | 0 | 0
2021-03-12 10:30 | 1.871 | 0 | N/A | 0 | 0
2021-03-12 11:00 | 1.2742 | 0 | N/A | 0 | 0
2021-03-12 11:30 | 0.9794 | 0 | N/A | 0 | 0
2021-03-12 12:00 | 0.73361 | 0 | N/A | 0 | 0
2021-03-12 12:30 | 0.63795 | 0 | N/A | 0 | 0
2021-03-12 13:00 | 0.59034 | 0 | N/A | 0 | 0
2021-03-12 13:30 | 0.39148 | 0 | N/A | 0 | 0
2021-03-12 14:00 | 0.56117 | 0 | N/A | 0 | 0
2021-03-12 14:30 | 0.82529 | 0 | N/A | 0 | 0
2021-03-12 15:00 | 0.85593 | 0 | N/A | 0 | 0
2021-03-12 15:30 | 0.89846 | 0 | N/A | 0 | 0
2021-03-12 16:00 | 1.2034 | 0 | N/A | 0 | 0
2021-03-12 16:30 | 1.6033 | 0 | N/A | 0 | 0
2021-03-12 17:00 | 2.0533 | 0 | N/A | 0 | 0
2021-03-12 17:30 | 2.4536 | 0 | N/A | 0 | 0
2021-03-12 18:00 | 3.4204 | 0 | N/A | 0 | 0
2021-03-12 18:30 | 3.8968 | 0 | N/A | 0 | 0
2021-03-12 19:00 | 4.3806 | 0 | N/A | 0 | 0
2021-03-12 19:30 | 4.5327 | 0 | N/A | 0 | 0
2021-03-12 20:00 | 4.5394 | 0 | N/A | 0 | 0
2021-03-12 20:30 | 4.557 | 0 | N/A | 0 | 0
2021-03-12 21:00 | 4.3982 | 0 | N/A | 0 | 0
2021-03-12 21:30 | 4.1025 | 0 | N/A | 0 | 0
2021-03-12 22:00 | 3.7306 | 0 | N/A | 0 | 0
2021-03-12 22:30 | 4.022 | 0 | N/A | 0 | 0
2021-03-12 23:00 | 4.1407 | 0 | N/A | 0 | 0
2021-03-12 23:30 | 3.7071 | 0 | N/A | 0 | 0
2021-03-13 | 3.7415 | 0 | N/A | 0 | 0
2021-03-13 00:30 | 4.2447 | 0 | N/A | 0 | 0
2021-03-13 01:00 | 4.3553 | 0 | N/A | 0 | 0
2021-03-13 01:30 | 3.3795 | 0 | N/A | 0 | 0
2021-03-13 02:00 | 2.7164 | 0 | N/A | 0 | 0
2021-03-13 02:30 | 2.6754 | 0 | N/A | 0 | 0
2021-03-13 03:00 | 2.4032 | 0 | N/A | 0 | 0
2021-03-13 03:30 | 2.1546 | 0 | N/A | 0 | 0
2021-03-13 04:00 | 1.9987 | 0 | N/A | 0 | 0
2021-03-13 04:30 | 1.9519 | 0 | N/A | 0 | 0
2021-03-13 05:00 | 1.9275 | 0 | N/A | 0 | 0
2021-03-13 05:30 | 1.9251 | 0 | N/A | 0 | 0
2021-03-13 06:00 | 2.042 | 0 | N/A | 0 | 0
2021-03-13 06:30 | 2.3627 | 0 | N/A | 0 | 0
2021-03-13 07:00 | 2.4466 | 0 | N/A | 0 | 0
2021-03-13 07:30 | 2.832 | 0 | N/A | 0 | 0
2021-03-13 08:00 | 2.9646 | 0 | N/A | 0 | 0
2021-03-13 08:30 | 2.7666 | 0 | N/A | 0 | 0
2021-03-13 09:00 | 2.1117 | 0 | N/A | 0 | 0
2021-03-13 09:30 | 2.6507 | 0 | N/A | 0 | 0
2021-03-13 10:00 | 2.8737 | 0 | N/A | 0 | 0
2021-03-13 10:30 | 2.4956 | 0 | N/A | 0 | 0
2021-03-13 11:00 | 2.5701 | 0 | N/A | 0 | 0
2021-03-13 11:30 | 2.8619 | 0 | N/A | 0 | 0
2021-03-13 12:00 | 3.4711 | 0 | N/A | 0 | 0
2021-03-13 12:30 | 3.8154 | 0 | N/A | 0 | 0
2021-03-13 13:00 | 3.9575 | 0 | N/A | 0 | 0
2021-03-13 13:30 | 3.8013 | 0 | N/A | 0 | 0
2021-03-13 14:00 | 3.6793 | 0 | N/A | 0 | 0
2021-03-13 14:30 | 3.9052 | 0 | N/A | 0 | 0
2021-03-13 15:00 | 3.863 | 0 | N/A | 0 | 0
2021-03-13 15:30 | 3.9485 | 0 | N/A | 0 | 0
2021-03-13 16:00 | 3.876 | 0 | N/A | 0 | 0
2021-03-13 16:30 | 3.9099 | 0 | N/A | 0 | 0
2021-03-13 17:00 | 4.1894 | 0 | N/A | 0 | 0
2021-03-13 17:30 | 4.7097 | 0 | N/A | 0 | 0
2021-03-13 18:00 | 4.9514 | 0 | N/A | 0 | 0
2021-03-13 18:30 | 5.0585 | 0 | N/A | 0 | 0
2021-03-13 19:00 | 4.8824 | 0 | N/A | 0 | 0
2021-03-13 19:30 | 4.7142 | 0 | N/A | 0 | 0
2021-03-13 20:00 | 4.8824 | 0 | N/A | 0 | 0
2021-03-13 20:30 | 4.7762 | 0 | N/A | 0 | 0
2021-03-13 21:00 | 4.5389 | 0 | N/A | 0 | 0
2021-03-13 21:30 | 4.3223 | 0 | N/A | 0 | 0
2021-03-13 22:00 | 4.0459 | 0 | N/A | 0 | 0
2021-03-13 22:30 | 4.5279 | 0 | N/A | 0 | 0
2021-03-13 23:00 | 4.7023 | 0 | N/A | 0 | 0
2021-03-13 23:30 | 4.3001 | 0 | N/A | 0 | 0
2021-03-14 | 4.3719 | 0 | N/A | 0 | 0
2021-03-14 00:30 | 4.7891 | 0 | N/A | 0 | 0
2021-03-14 01:00 | 5.2711 | 0 | N/A | 0 | 0
2021-03-14 01:30 | 4.4218 | 0 | N/A | 0 | 0
2021-03-14 02:00 | 3.5643 | 0 | N/A | 0 | 0
2021-03-14 02:30 | 3.5473 | 0 | N/A | 0 | 0
2021-03-14 03:00 | 3.1323 | 0 | N/A | 0 | 0
2021-03-14 03:30 | 2.7684 | 0 | N/A | 0 | 0
2021-03-14 04:00 | 2.5723 | 0 | N/A | 0 | 0
2021-03-14 04:30 | 2.4719 | 0 | N/A | 0 | 0
2021-03-14 05:00 | 2.3875 | 0 | N/A | 0 | 0
2021-03-14 05:30 | 2.4692 | 0 | N/A | 0 | 0
2021-03-14 06:00 | 2.4505 | 0 | N/A | 0 | 0
2021-03-14 06:30 | 2.8 | 0 | N/A | 0 | 0
2021-03-14 07:00 | 3.044 | 0 | N/A | 0 | 0
2021-03-14 07:30 | 3.4952 | 0 | N/A | 0 | 0
2021-03-14 08:00 | 3.8415 | 0 | N/A | 0 | 0
2021-03-14 08:30 | 3.7101 | 0 | N/A | 0 | 0
2021-03-14 09:00 | 3.3802 | 0 | N/A | 0 | 0
2021-03-14 09:30 | 2.8595 | 0 | N/A | 0 | 0
2021-03-14 10:00 | 2.1373 | 0 | N/A | 0 | 0
2021-03-14 10:30 | 1.4141 | 0 | N/A | 0 | 0
2021-03-14 11:00 | 0.98741 | 0 | N/A | 0 | 0
2021-03-14 11:30 | 1.1346 | 0 | N/A | 0 | 0
2021-03-14 12:00 | 1.2059 | 0 | N/A | 0 | 0
2021-03-14 12:30 | 1.3647 | 0 | N/A | 0 | 0
2021-03-14 13:00 | 1.3703 | 0 | N/A | 0 | 0
2021-03-14 13:30 | 1.2012 | 0 | N/A | 0 | 0
2021-03-14 14:00 | 1.0559 | 0 | N/A | 0 | 0
2021-03-14 14:30 | 0.55214 | 0 | N/A | 0 | 0
2021-03-14 15:00 | 0.80904 | 0 | N/A | 0 | 0
2021-03-14 15:30 | 0.77092 | 0 | N/A | 0 | 0
2021-03-14 16:00 | 1.2122 | 0 | N/A | 0 | 0
2021-03-14 16:30 | 1.2779 | 0 | N/A | 0 | 0
2021-03-14 17:00 | 1.9249 | 0 | N/A | 0 | 0
2021-03-14 17:30 | 2.0466 | 0 | N/A | 0 | 0
2021-03-14 18:00 | 3.4334 | 0 | N/A | 0 | 0
2021-03-14 18:30 | 4.0113 | 0 | N/A | 0 | 0
2021-03-14 19:00 | 4.4354 | 0 | N/A | 0 | 0
2021-03-14 19:30 | 4.8405 | 0 | N/A | 0 | 0
2021-03-14 20:00 | 5.1185 | 0 | N/A | 0 | 0
2021-03-14 20:30 | 5.0581 | 0 | N/A | 0 | 0
2021-03-14 21:00 | 4.9329 | 0 | N/A | 0 | 0
2021-03-14 21:30 | 4.7509 | 0 | N/A | 0 | 0
2021-03-14 22:00 | 4.3155 | 0 | N/A | 0 | 0
2021-03-14 22:30 | 4.53 | 0 | N/A | 0 | 0
2021-03-14 23:00 | 4.524 | 0 | N/A | 0 | 0
2021-03-14 23:30 | 4.3145 | 0 | N/A | 0 | 0
2021-03-15 | 4.386 | 0 | N/A | 0 | 0
2021-03-15 00:30 | 4.787 | 0 | N/A | 0 | 0
2021-03-15 01:00 | 5.1265 | 0 | N/A | 0 | 0
2021-03-15 01:30 | 4.3684 | 0 | N/A | 0 | 0
2021-03-15 02:00 | 3.7641 | 0 | N/A | 0 | 0
2021-03-15 02:30 | 3.729 | 0 | N/A | 0 | 0
2021-03-15 03:00 | 3.4004 | 0 | N/A | 0 | 0
2021-03-15 03:30 | 2.9181 | 0 | N/A | 0 | 0
2021-03-15 04:00 | 2.6169 | 0 | N/A | 0 | 0
2021-03-15 04:30 | 2.4614 | 0 | N/A | 0 | 0
2021-03-15 05:00 | 2.5059 | 0 | N/A | 0 | 0
2021-03-15 05:30 | 2.7522 | 0 | N/A | 0 | 0
2021-03-15 06:00 | 3.0792 | 0 | N/A | 0 | 0
2021-03-15 06:30 | 3.7054 | 0 | N/A | 0 | 0
2021-03-15 07:00 | 4.4815 | 0 | N/A | 0 | 0
2021-03-15 07:30 | 5.7322 | 0 | N/A | 0 | 0
2021-03-15 08:00 | 6.174 | 0 | N/A | 0 | 0
2021-03-15 08:30 | 5.4833 | 0 | N/A | 0 | 0
2021-03-15 09:00 | 5.1258 | 0 | N/A | 0 | 0
2021-03-15 09:30 | 4.6558 | 0 | N/A | 0 | 0
2021-03-15 10:00 | 3.7763 | 0 | N/A | 0 | 0
2021-03-15 10:30 | 3.3406 | 0 | N/A | 0 | 0
2021-03-15 11:00 | 2.7441 | 0 | N/A | 0 | 0
2021-03-15 11:30 | 2.6145 | 0 | N/A | 0 | 0
2021-03-15 12:00 | 2.9305 | 0 | N/A | 0 | 0
2021-03-15 12:30 | 3.1309 | 0 | N/A | 0 | 0
2021-03-15 13:00 | 3.2549 | 0 | N/A | 0 | 0
2021-03-15 13:30 | 2.8972 | 0 | N/A | 0 | 0
2021-03-15 14:00 | 3.0433 | 0 | N/A | 0 | 0
2021-03-15 14:30 | 3.5379 | 0 | N/A | 0 | 0
2021-03-15 15:00 | 3.7816 | 0 | N/A | 0 | 0
2021-03-15 15:30 | 3.71 | 0 | N/A | 0 | 0
2021-03-15 16:00 | 3.5334 | 0 | N/A | 0 | 0
2021-03-15 16:30 | 3.2826 | 0 | N/A | 0 | 0
2021-03-15 17:00 | 3.5059 | 0 | N/A | 0 | 0
2021-03-15 17:30 | 4.1966 | 0 | N/A | 0 | 0
2021-03-15 18:00 | 4.538 | 0 | N/A | 0 | 0
2021-03-15 18:30 | 4.9788 | 0 | N/A | 0 | 0
2021-03-15 19:00 | 5.2927 | 0 | N/A | 0 | 0
2021-03-15 19:30 | 5.0637 | 0 | N/A | 0 | 0
2021-03-15 20:00 | 5.1364 | 0 | N/A | 0 | 0
2021-03-15 20:30 | 5.233 | 0 | N/A | 0 | 0
2021-03-15 21:00 | 4.9653 | 0 | N/A | 0 | 0
2021-03-15 21:30 | 4.6257 | 0 | N/A | 0 | 0
2021-03-15 22:00 | 4.2248 | 0 | N/A | 0 | 0
2021-03-15 22:30 | 4.3557 | 0 | N/A | 0 | 0
2021-03-15 23:00 | 4.4967 | 0 | N/A | 0 | 0
2021-03-15 23:30 | 4.0459 | 0 | N/A | 0 | 0
2021-03-16 | 4.0085 | 0 | N/A | 0 | 0
2021-03-16 00:30 | 4.5688 | 0 | N/A | 0 | 0
2021-03-16 01:00 | 4.9309 | 0 | N/A | 0 | 0
2021-03-16 01:30 | 4.1796 | 0 | N/A | 0 | 0
2021-03-16 02:00 | 3.4493 | 0 | N/A | 0 | 0
2021-03-16 02:30 | 3.4377 | 0 | N/A | 0 | 0
2021-03-16 03:00 | 3.0679 | 0 | N/A | 0 | 0
2021-03-16 03:30 | 2.5425 | 0 | N/A | 0 | 0
2021-03-16 04:00 | 2.4436 | 0 | N/A | 0 | 0
2021-03-16 04:30 | 2.3732 | 0 | N/A | 0 | 0
2021-03-16 05:00 | 2.4104 | 0 | N/A | 0 | 0
2021-03-16 05:30 | 2.5425 | 0 | N/A | 0 | 0
2021-03-16 06:00 | 2.8984 | 0 | N/A | 0 | 0
2021-03-16 06:30 | 3.5628 | 0 | N/A | 0 | 0
2021-03-16 07:00 | 4.2248 | 0 | N/A | 0 | 0
2021-03-16 07:30 | 5.5868 | 0 | N/A | 0 | 0
2021-03-16 08:00 | 5.8733 | 0 | N/A | 0 | 0
2021-03-16 08:30 | 5.51 | 0 | N/A | 0 | 0
2021-03-16 09:00 | 5.34 | 0 | N/A | 0 | 0
2021-03-16 09:30 | 4.76 | 0 | N/A | 0 | 0
2021-03-16 10:00 | 3.8233 | 0 | N/A | 0 | 0
2021-03-16 10:30 | 2.8435 | 0 | N/A | 0 | 0
2021-03-16 11:00 | 1.9867 | 0 | N/A | 0 | 0
2021-03-16 11:30 | 1.5307 | 0 | N/A | 0 | 0
2021-03-16 12:00 | 1.1262 | 0 | N/A | 0 | 0
2021-03-16 12:30 | 0.88494 | 0 | N/A | 0 | 0
2021-03-16 13:00 | 0.65906 | 0 | N/A | 0 | 0
2021-03-16 13:30 | 0.59203 | 0 | N/A | 0 | 0
2021-03-16 14:00 | 0.6568 | 0 | N/A | 0 | 0
2021-03-16 14:30 | 0.69507 | 0 | N/A | 0 | 0
2021-03-16 15:00 | 0.69851 | 0 | N/A | 0 | 0
2021-03-16 15:30 | 0.75664 | 0 | N/A | 0 | 0
2021-03-16 16:00 | 1.0212 | 0 | N/A | 0 | 0
2021-03-16 16:30 | 0.74964 | 0 | N/A | 0 | 0
2021-03-16 17:00 | 0.97443 | 0 | N/A | 0 | 0
2021-03-16 17:30 | 1.8014 | 0 | N/A | 0 | 0
2021-03-16 18:00 | 2.8123 | 0 | N/A | 0 | 0
2021-03-16 18:30 | 3.613 | 0 | N/A | 0 | 0
2021-03-16 19:00 | 4.0885 | 0 | N/A | 0 | 0
2021-03-16 19:30 | 4.3149 | 0 | N/A | 0 | 0
2021-03-16 20:00 | 4.3706 | 0 | N/A | 0 | 0
2021-03-16 20:30 | 4.4751 | 0 | N/A | 0 | 0
2021-03-16 21:00 | 4.3592 | 0 | N/A | 0 | 0
2021-03-16 21:30 | 4.0621 | 0 | N/A | 0 | 0
2021-03-16 22:00 | 3.6936 | 0 | N/A | 0 | 0
2021-03-16 22:30 | 3.9379 | 0 | N/A | 0 | 0
2021-03-16 23:00 | 4.1743 | 0 | N/A | 0 | 0
2021-03-16 23:30 | 3.8136 | 0 | N/A | 0 | 0
2021-03-17 | 3.8499 | 0 | N/A | 0 | 0
2021-03-17 00:30 | 4.1916 | 0 | N/A | 0 | 0
2021-03-17 01:00 | 4.3929 | 0 | N/A | 0 | 0
2021-03-17 01:30 | 3.6393 | 0 | N/A | 0 | 0
2021-03-17 02:00 | 2.9833 | 0 | N/A | 0 | 0
2021-03-17 02:30 | 2.9842 | 0 | N/A | 0 | 0
2021-03-17 03:00 | 2.6772 | 0 | N/A | 0 | 0
2021-03-17 03:30 | 2.3019 | 0 | N/A | 0 | 0
2021-03-17 04:00 | 2.1697 | 0 | N/A | 0 | 0
2021-03-17 04:30 | 2.1324 | 0 | N/A | 0 | 0
2021-03-17 05:00 | 2.2216 | 0 | N/A | 0 | 0
2021-03-17 05:30 | 2.3994 | 0 | N/A | 0 | 0
2021-03-17 06:00 | 2.7088 | 0 | N/A | 0 | 0
2021-03-17 06:30 | 3.2695 | 0 | N/A | 0 | 0
2021-03-17 07:00 | 3.8826 | 0 | N/A | 0 | 0
2021-03-17 07:30 | 5.0213 | 0 | N/A | 0 | 0
2021-03-17 08:00 | 5.4275 | 0 | N/A | 0 | 0
2021-03-17 08:30 | 4.4835 | 0 | N/A | 0 | 0
2021-03-17 09:00 | 4.1968 | 0 | N/A | 0 | 0
2021-03-17 09:30 | 3.03 | 0 | N/A | 0 | 0
2021-03-17 10:00 | 2.4033 | 0 | N/A | 0 | 0
2021-03-17 10:30 | 1.6092 | 0 | N/A | 0 | 0
2021-03-17 11:00 | 1.0911 | 0 | N/A | 0 | 0
2021-03-17 11:30 | 0.67036 | 0 | N/A | 0 | 0
2021-03-17 12:00 | 0.55202 | 0 | N/A | 0 | 0
2021-03-17 12:30 | 0.55563 | 0 | N/A | 0 | 0
2021-03-17 13:00 | 0.3899 | 0 | N/A | 0 | 0
2021-03-17 13:30 | 1.1776 | 0 | N/A | 0 | 0
2021-03-17 14:00 | 1.5553 | 0 | N/A | 0 | 0
2021-03-17 14:30 | 2.042 | 0 | N/A | 0 | 0
2021-03-17 15:00 | 1.3171 | 0 | N/A | 0 | 0
2021-03-17 15:30 | 1.7539 | 0 | N/A | 0 | 0
2021-03-17 16:00 | 1.6318 | 0 | N/A | 0 | 0
2021-03-17 16:30 | 1.8787 | 0 | N/A | 0 | 0
2021-03-17 17:00 | 3.1336 | 0 | N/A | 0 | 0
2021-03-17 17:30 | 2.7907 | 0 | N/A | 0 | 0
2021-03-17 18:00 | 3.6314 | 0 | N/A | 0 | 0
2021-03-17 18:30 | 4.3112 | 0 | N/A | 0 | 0
2021-03-17 19:00 | 4.455 | 0 | N/A | 0 | 0
2021-03-17 19:30 | 4.5395 | 0 | N/A | 0 | 0
2021-03-17 20:00 | 4.5368 | 0 | N/A | 0 | 0
2021-03-17 20:30 | 4.5235 | 0 | N/A | 0 | 0
2021-03-17 21:00 | 4.3899 | 0 | N/A | 0 | 0
2021-03-17 21:30 | 4.0161 | 0 | N/A | 0 | 0
2021-03-17 22:00 | 3.7011 | 0 | N/A | 0 | 0
2021-03-17 22:30 | 4.0767 | 0 | N/A | 0 | 0
2021-03-17 23:00 | 4.0013 | 0 | N/A | 0 | 0
2021-03-17 23:30 | 3.6058 | 0 | N/A | 0 | 0
2021-03-18 | 3.6312 | 0 | N/A | 0 | 0
2021-03-18 00:30 | 4.1542 | 0 | N/A | 0 | 0
2021-03-18 01:00 | 4.4128 | 0 | N/A | 0 | 0
2021-03-18 01:30 | 3.5 | 0 | N/A | 0 | 0
2021-03-18 02:00 | 2.8369 | 0 | N/A | 0 | 0
2021-03-18 02:30 | 2.7935 | 0 | N/A | 0 | 0
2021-03-18 03:00 | 2.5399 | 0 | N/A | 0 | 0
2021-03-18 03:30 | 2.1997 | 0 | N/A | 0 | 0
2021-03-18 04:00 | 2.0533 | 0 | N/A | 0 | 0
2021-03-18 04:30 | 2.016 | 0 | N/A | 0 | 0
2021-03-18 05:00 | 2.0854 | 0 | N/A | 0 | 0
2021-03-18 05:30 | 2.2417 | 0 | N/A | 0 | 0
2021-03-18 06:00 | 2.5861 | 0 | N/A | 0 | 0
2021-03-18 06:30 | 3.0606 | 0 | N/A | 0 | 0
2021-03-18 07:00 | 3.6349 | 0 | N/A | 0 | 0
2021-03-18 07:30 | 4.8778 | 0 | N/A | 0 | 0
2021-03-18 08:00 | 5.0938 | 0 | N/A | 0 | 0
2021-03-18 08:30 | 4.37 | 0 | N/A | 0 | 0
2021-03-18 09:00 | 3.7267 | 0 | N/A | 0 | 0
2021-03-18 09:30 | 3.17 | 0 | N/A | 0 | 0
2021-03-18 10:00 | 2.6509 | 0 | N/A | 0 | 0
2021-03-18 10:30 | 1.8277 | 0 | N/A | 0 | 0
2021-03-18 11:00 | 1.4182 | 0 | N/A | 0 | 0
2021-03-18 11:30 | 1.0575 | 0 | N/A | 0 | 0
2021-03-18 12:00 | 0.92947 | 0 | N/A | 0 | 0
2021-03-18 12:30 | 1.2927 | 0 | N/A | 0 | 0
2021-03-18 13:00 | 0.70715 | 0 | N/A | 0 | 0
2021-03-18 13:30 | 0.62241 | 0 | N/A | 0 | 0
2021-03-18 14:00 | 0.54203 | 0 | N/A | 0 | 0
2021-03-18 14:30 | 1.0208 | 0 | N/A | 0 | 0
2021-03-18 15:00 | 1.3802 | 0 | N/A | 0 | 0
2021-03-18 15:30 | 1.2266 | 0 | N/A | 0 | 0
2021-03-18 16:00 | 0.65809 | 0 | N/A | 0 | 0
2021-03-18 16:30 | 1.3125 | 0 | N/A | 0 | 0
2021-03-18 17:00 | 1.9757 | 0 | N/A | 0 | 0
2021-03-18 17:30 | 2.4878 | 0 | N/A | 0 | 0
2021-03-18 18:00 | 3.2237 | 0 | N/A | 0 | 0
2021-03-18 18:30 | 3.7022 | 0 | N/A | 0 | 0
2021-03-18 19:00 | 4.2022 | 0 | N/A | 0 | 0
2021-03-18 19:30 | 4.5192 | 0 | N/A | 0 | 0
2021-03-18 20:00 | 4.5706 | 0 | N/A | 0 | 0
2021-03-18 20:30 | 4.549 | 0 | N/A | 0 | 0
2021-03-18 21:00 | 4.3355 | 0 | N/A | 0 | 0
2021-03-18 21:30 | 4.0127 | 0 | N/A | 0 | 0
2021-03-18 22:00 | 3.6479 | 0 | N/A | 0 | 0
2021-03-18 22:30 | 3.9847 | 0 | N/A | 0 | 0
2021-03-18 23:00 | 4.0452 | 0 | N/A | 0 | 0
2021-03-18 23:30 | 3.6034 | 0 | N/A | 0 | 0
2021-03-19 | 3.6735 | 0 | N/A | 0 | 0
2021-03-19 00:30 | 4.2143 | 0 | N/A | 0 | 0
2021-03-19 01:00 | 4.5326 | 0 | N/A | 0 | 0
2021-03-19 01:30 | 3.6551 | 0 | N/A | 0 | 0
2021-03-19 02:00 | 2.9395 | 0 | N/A | 0 | 0
2021-03-19 02:30 | 2.9064 | 0 | N/A | 0 | 0
2021-03-19 03:00 | 2.5817 | 0 | N/A | 0 | 0
2021-03-19 03:30 | 2.2425 | 0 | N/A | 0 | 0
2021-03-19 04:00 | 2.1312 | 0 | N/A | 0 | 0
2021-03-19 04:30 | 2.039 | 0 | N/A | 0 | 0
2021-03-19 05:00 | 2.0978 | 0 | N/A | 0 | 0
2021-03-19 05:30 | 2.3507 | 0 | N/A | 0 | 0
2021-03-19 06:00 | 2.6319 | 0 | N/A | 0 | 0
2021-03-19 06:30 | 3.1851 | 0 | N/A | 0 | 0
2021-03-19 07:00 | 3.6656 | 0 | N/A | 0 | 0
2021-03-19 07:30 | 4.4339 | 0 | N/A | 0 | 0
2021-03-19 08:00 | 4.6998 | 0 | N/A | 0 | 0
2021-03-19 08:30 | 4.1359 | 0 | N/A | 0 | 0
2021-03-19 09:00 | 3.5721 | 0 | N/A | 0 | 0
2021-03-19 09:30 | 2.8493 | 0 | N/A | 0 | 0
2021-03-19 10:00 | 2.0621 | 0 | N/A | 0 | 0
2021-03-19 10:30 | 1.5169 | 0 | N/A | 0 | 0
2021-03-19 11:00 | 1.1149 | 0 | N/A | 0 | 0
2021-03-19 11:30 | 0.84387 | 0 | N/A | 0 | 0
2021-03-19 12:00 | 0.39319 | 0 | N/A | 0 | 0
2021-03-19 12:30 | 0.19624 | 0 | N/A | 0 | 0
2021-03-19 13:00 | 0.24166 | 0 | N/A | 0 | 0
2021-03-19 13:30 | 0.18406 | 0 | N/A | 0 | 0
2021-03-19 14:00 | 0.13812 | 0 | N/A | 0 | 0
2021-03-19 14:30 | 0.17337 | 0 | N/A | 0 | 0
2021-03-19 15:00 | 0.46491 | 0 | N/A | 0 | 0
2021-03-19 15:30 | 1.149 | 0 | N/A | 0 | 0
2021-03-19 16:00 | 1.0289 | 0 | N/A | 0 | 0
2021-03-19 16:30 | 1.1223 | 0 | N/A | 0 | 0
2021-03-19 17:00 | 1.3765 | 0 | N/A | 0 | 0
2021-03-19 17:30 | 2.1579 | 0 | N/A | 0 | 0
2021-03-19 18:00 | 2.9503 | 0 | N/A | 0 | 0
2021-03-19 18:30 | 3.5119 | 0 | N/A | 0 | 0
2021-03-19 19:00 | 4.0386 | 0 | N/A | 0 | 0
2021-03-19 19:30 | 4.2031 | 0 | N/A | 0 | 0
2021-03-19 20:00 | 4.2428 | 0 | N/A | 0 | 0
2021-03-19 20:30 | 4.226 | 0 | N/A | 0 | 0
2021-03-19 21:00 | 4.1155 | 0 | N/A | 0 | 0
2021-03-19 21:30 | 3.9198 | 0 | N/A | 0 | 0
2021-03-19 22:00 | 3.5829 | 0 | N/A | 0 | 0
2021-03-19 22:30 | 3.8484 | 0 | N/A | 0 | 0
2021-03-19 23:00 | 4.0431 | 0 | N/A | 0 | 0
2021-03-19 23:30 | 3.746 | 0 | N/A | 0 | 0
2021-03-20 | 3.7329 | 0 | N/A | 0 | 0
2021-03-20 00:30 | 4.1791 | 0 | N/A | 0 | 0
2021-03-20 01:00 | 4.4081 | 0 | N/A | 0 | 0
2021-03-20 01:30 | 3.5177 | 0 | N/A | 0 | 0
2021-03-20 02:00 | 2.868 | 0 | N/A | 0 | 0
2021-03-20 02:30 | 2.8379 | 0 | N/A | 0 | 0
2021-03-20 03:00 | 2.433 | 0 | N/A | 0 | 0
2021-03-20 03:30 | 2.2516 | 0 | N/A | 0 | 0
2021-03-20 04:00 | 2.1049 | 0 | N/A | 0 | 0
2021-03-20 04:30 | 1.9742 | 0 | N/A | 0 | 0
2021-03-20 05:00 | 1.9805 | 0 | N/A | 0 | 0
2021-03-20 05:30 | 1.9898 | 0 | N/A | 0 | 0
2021-03-20 06:00 | 2.1889 | 0 | N/A | 0 | 0
2021-03-20 06:30 | 2.429 | 0 | N/A | 0 | 0
2021-03-20 07:00 | 2.6142 | 0 | N/A | 0 | 0
2021-03-20 07:30 | 2.9648 | 0 | N/A | 0 | 0
2021-03-20 08:00 | 3.154 | 0 | N/A | 0 | 0
2021-03-20 08:30 | 2.9987 | 0 | N/A | 0 | 0
2021-03-20 09:00 | 2.9865 | 0 | N/A | 0 | 0
2021-03-20 09:30 | 2.5243 | 0 | N/A | 0 | 0
2021-03-20 10:00 | 1.9682 | 0 | N/A | 0 | 0
2021-03-20 10:30 | 1.3871 | 0 | N/A | 0 | 0
2021-03-20 11:00 | 0.97755 | 0 | N/A | 0 | 0
2021-03-20 11:30 | 0.46021 | 0 | N/A | 0 | 0
2021-03-20 12:00 | 0.3334 | 0 | N/A | 0 | 0
2021-03-20 12:30 | -0.38211 | 0 | N/A | 0 | 0
2021-03-20 13:00 | -0.61724 | 0 | N/A | 0 | 0
2021-03-20 13:30 | -0.62774 | 0 | N/A | 0 | 0
2021-03-20 14:00 | -0.74967 | 0 | N/A | 0 | 0
2021-03-20 14:30 | -0.71568 | 0 | N/A | 0 | 0
2021-03-20 15:00 | -0.47347 | 0 | N/A | 0 | 0
2021-03-20 15:30 | 0.47876 | 0 | N/A | 0 | 0
2021-03-20 16:00 | 1.3842 | 0 | N/A | 0 | 0
2021-03-20 16:30 | 2.251 | 0 | N/A | 0 | 0
2021-03-20 17:00 | 2.4658 | 0 | N/A | 0 | 0
2021-03-20 17:30 | 2.9114 | 0 | N/A | 0 | 0
2021-03-20 18:00 | 3.5346 | 0 | N/A | 0 | 0
2021-03-20 18:30 | 3.868 | 0 | N/A | 0 | 0
2021-03-20 19:00 | 4.0944 | 0 | N/A | 0 | 0
2021-03-20 19:30 | 4.0621 | 0 | N/A | 0 | 0
2021-03-20 20:00 | 4.0324 | 0 | N/A | 0 | 0
2021-03-20 20:30 | 4.0192 | 0 | N/A | 0 | 0
2021-03-20 21:00 | 3.7637 | 0 | N/A | 0 | 0
2021-03-20 21:30 | 3.5543 | 0 | N/A | 0 | 0
2021-03-20 22:00 | 3.3952 | 0 | N/A | 0 | 0
2021-03-20 22:30 | 3.7889 | 0 | N/A | 0 | 0
2021-03-20 23:00 | 3.9407 | 0 | N/A | 0 | 0
2021-03-20 23:30 | 3.7002 | 0 | N/A | 0 | 0
2021-03-21 | 3.9256 | 0 | N/A | 0 | 0
2021-03-21 00:30 | 4.2865 | 0 | N/A | 0 | 0
2021-03-21 01:00 | 4.591 | 0 | N/A | 0 | 0
2021-03-21 01:30 | 3.6827 | 0 | N/A | 0 | 0
2021-03-21 02:00 | 3.0375 | 0 | N/A | 0 | 0
2021-03-21 02:30 | 2.9323 | 0 | N/A | 0 | 0
2021-03-21 03:00 | 2.5915 | 0 | N/A | 0 | 0
2021-03-21 03:30 | 2.2747 | 0 | N/A | 0 | 0
2021-03-21 04:00 | 2.1513 | 0 | N/A | 0 | 0
2021-03-21 04:30 | 2.0396 | 0 | N/A | 0 | 0
2021-03-21 05:00 | 1.9872 | 0 | N/A | 0 | 0
2021-03-21 05:30 | 2.0064 | 0 | N/A | 0 | 0
2021-03-21 06:00 | 2.1417 | 0 | N/A | 0 | 0
2021-03-21 06:30 | 2.314 | 0 | N/A | 0 | 0
2021-03-21 07:00 | 2.4012 | 0 | N/A | 0 | 0
2021-03-21 07:30 | 2.7075 | 0 | N/A | 0 | 0
2021-03-21 08:00 | 2.9808 | 0 | N/A | 0 | 0
2021-03-21 08:30 | 3.1258 | 0 | N/A | 0 | 0
2021-03-21 09:00 | 3.2876 | 0 | N/A | 0 | 0
2021-03-21 09:30 | 3.5105 | 0 | N/A | 0 | 0
2021-03-21 10:00 | 3.6211 | 0 | N/A | 0 | 0
2021-03-21 10:30 | 3.6371 | 0 | N/A | 0 | 0
2021-03-21 11:00 | 3.7369 | 0 | N/A | 0 | 0
2021-03-21 11:30 | 3.6064 | 0 | N/A | 0 | 0
2021-03-21 12:00 | 3.5908 | 0 | N/A | 0 | 0
2021-03-21 12:30 | 3.5742 | 0 | N/A | 0 | 0
2021-03-21 13:00 | 3.2376 | 0 | N/A | 0 | 0
2021-03-21 13:30 | 3.2666 | 0 | N/A | 0 | 0
2021-03-21 14:00 | 3.5374 | 0 | N/A | 0 | 0
2021-03-21 14:30 | 3.3511 | 0 | N/A | 0 | 0
2021-03-21 15:00 | 3.4132 | 0 | N/A | 0 | 0
2021-03-21 15:30 | 3.3115 | 0 | N/A | 0 | 0
2021-03-21 16:00 | 3.6783 | 0 | N/A | 0 | 0
2021-03-21 16:30 | 3.9462 | 0 | N/A | 0 | 0
2021-03-21 17:00 | 4.5799 | 0 | N/A | 0 | 0
2021-03-21 17:30 | 4.9987 | 0 | N/A | 0 | 0
2021-03-21 18:00 | 5.3988 | 0 | N/A | 0 | 0
2021-03-21 18:30 | 5.5389 | 0 | N/A | 0 | 0
2021-03-21 19:00 | 5.38 | 0 | N/A | 0 | 0
2021-03-21 19:30 | 5.2795 | 0 | N/A | 0 | 0
2021-03-21 20:00 | 5.0227 | 0 | N/A | 0 | 0
2021-03-21 20:30 | 4.6536 | 0 | N/A | 0 | 0
2021-03-21 21:00 | 4.3938 | 0 | N/A | 0 | 0
2021-03-21 21:30 | 4.0476 | 0 | N/A | 0 | 0
2021-03-21 22:00 | 3.7264 | 0 | N/A | 0 | 0
2021-03-21 22:30 | 4.0174 | 0 | N/A | 0 | 0
2021-03-21 23:00 | 4.2414 | 0 | N/A | 0 | 0
2021-03-21 23:30 | 3.9232 | 0 | N/A | 0 | 0
2021-03-22 | 3.9185 | 0 | N/A | 0 | 0
2021-03-22 00:30 | 4.3889 | 0 | N/A | 0 | 0
2021-03-22 01:00 | 4.7778 | 0 | N/A | 0 | 0
2021-03-22 01:30 | 4.0569 | 0 | N/A | 0 | 0
2021-03-22 02:00 | 3.3152 | 0 | N/A | 0 | 0
2021-03-22 02:30 | 3.1998 | 0 | N/A | 0 | 0
2021-03-22 03:00 | 2.9638 | 0 | N/A | 0 | 0
2021-03-22 03:30 | 2.4747 | 0 | N/A | 0 | 0
2021-03-22 04:00 | 2.2853 | 0 | N/A | 0 | 0
2021-03-22 04:30 | 2.1598 | 0 | N/A | 0 | 0
2021-03-22 05:00 | 2.1783 | 0 | N/A | 0 | 0
2021-03-22 05:30 | 2.3317 | 0 | N/A | 0 | 0
2021-03-22 06:00 | 2.636 | 0 | N/A | 0 | 0
2021-03-22 06:30 | 3.1022 | 0 | N/A | 0 | 0
2021-03-22 07:00 | 3.75 | 0 | N/A | 0 | 0
2021-03-22 07:30 | 4.8942 | 0 | N/A | 0 | 0
2021-03-22 08:00 | 4.9275 | 0 | N/A | 0 | 0
2021-03-22 08:30 | 3.9733 | 0 | N/A | 0 | 0
2021-03-22 09:00 | 3.6367 | 0 | N/A | 0 | 0
2021-03-22 09:30 | 3.0467 | 0 | N/A | 0 | 0
2021-03-22 10:00 | 3.33 | 0 | N/A | 0 | 0
2021-03-22 10:30 | 3.27 | 0 | N/A | 0 | 0
2021-03-22 11:00 | 2.8335 | 0 | N/A | 0 | 0
2021-03-22 11:30 | 2.1182 | 0 | N/A | 0 | 0
2021-03-22 12:00 | 2.2701 | 0 | N/A | 0 | 0
2021-03-22 12:30 | 2.6604 | 0 | N/A | 0 | 0
2021-03-22 13:00 | 2.27 | 0 | N/A | 0 | 0
2021-03-22 13:30 | 2.2478 | 0 | N/A | 0 | 0
2021-03-22 14:00 | 2.4202 | 0 | N/A | 0 | 0
2021-03-22 14:30 | 1.9543 | 0 | N/A | 0 | 0
2021-03-22 15:00 | 1.5603 | 0 | N/A | 0 | 0
2021-03-22 15:30 | 1.9275 | 0 | N/A | 0 | 0
2021-03-22 16:00 | 2.4069 | 0 | N/A | 0 | 0
2021-03-22 16:30 | 2.9306 | 0 | N/A | 0 | 0
2021-03-22 17:00 | 3.6337 | 0 | N/A | 0 | 0
2021-03-22 17:30 | 4.0628 | 0 | N/A | 0 | 0
2021-03-22 18:00 | 4.5547 | 0 | N/A | 0 | 0
2021-03-22 18:30 | 4.8409 | 0 | N/A | 0 | 0
2021-03-22 19:00 | 4.7716 | 0 | N/A | 0 | 0
2021-03-22 19:30 | 4.7218 | 0 | N/A | 0 | 0
2021-03-22 20:00 | 4.7424 | 0 | N/A | 0 | 0
2021-03-22 20:30 | 4.637 | 0 | N/A | 0 | 0
2021-03-22 21:00 | 4.3805 | 0 | N/A | 0 | 0
2021-03-22 21:30 | 4.0758 | 0 | N/A | 0 | 0
2021-03-22 22:00 | 3.7814 | 0 | N/A | 0 | 0
2021-03-22 22:30 | 3.9632 | 0 | N/A | 0 | 0
2021-03-22 23:00 | 4.0863 | 0 | N/A | 0 | 0
2021-03-22 23:30 | 3.71 | 0 | N/A | 0 | 0
2021-03-23 | 3.7686 | 0 | N/A | 0 | 0
2021-03-23 00:30 | 4.2338 | 0 | N/A | 0 | 0
2021-03-23 01:00 | 4.5601 | 0 | N/A | 0 | 0
2021-03-23 01:30 | 3.6675 | 0 | N/A | 0 | 0
2021-03-23 02:00 | 3.0166 | 0 | N/A | 0 | 0
2021-03-23 02:30 | 2.9048 | 0 | N/A | 0 | 0
2021-03-23 03:00 | 2.5467 | 0 | N/A | 0 | 0
2021-03-23 03:30 | 2.1978 | 0 | N/A | 0 | 0
2021-03-23 04:00 | 2.1253 | 0 | N/A | 0 | 0
2021-03-23 04:30 | 2.0244 | 0 | N/A | 0 | 0
2021-03-23 05:00 | 2.136 | 0 | N/A | 0 | 0
2021-03-23 05:30 | 2.2348 | 0 | N/A | 0 | 0
2021-03-23 06:00 | 2.5389 | 0 | N/A | 0 | 0
2021-03-23 06:30 | 3.0411 | 0 | N/A | 0 | 0
2021-03-23 07:00 | 3.7729 | 0 | N/A | 0 | 0
2021-03-23 07:30 | 4.8868 | 0 | N/A | 0 | 0
2021-03-23 08:00 | 5.2134 | 0 | N/A | 0 | 0
2021-03-23 08:30 | 4.608 | 0 | N/A | 0 | 0
2021-03-23 09:00 | 4.3393 | 0 | N/A | 0 | 0
2021-03-23 09:30 | 4.1741 | 0 | N/A | 0 | 0
2021-03-23 10:00 | 4.0373 | 0 | N/A | 0 | 0
2021-03-23 10:30 | 3.4876 | 0 | N/A | 0 | 0
2021-03-23 11:00 | 3.2535 | 0 | N/A | 0 | 0
2021-03-23 11:30 | 3.2271 | 0 | N/A | 0 | 0
2021-03-23 12:00 | 2.5333 | 0 | N/A | 0 | 0
2021-03-23 12:30 | 1.9267 | 0 | N/A | 0 | 0
2021-03-23 13:00 | 1.8467 | 0 | N/A | 0 | 0
2021-03-23 13:30 | 2.362 | 0 | N/A | 0 | 0
2021-03-23 14:00 | 2.917 | 0 | N/A | 0 | 0
2021-03-23 14:30 | 2.8267 | 0 | N/A | 0 | 0
2021-03-23 15:00 | 3.1967 | 0 | N/A | 0 | 0
2021-03-23 15:30 | 3.2371 | 0 | N/A | 0 | 0
2021-03-23 16:00 | 2.8614 | 0 | N/A | 0 | 0
2021-03-23 16:30 | 2.877 | 0 | N/A | 0 | 0
2021-03-23 17:00 | 2.7879 | 0 | N/A | 0 | 0
2021-03-23 17:30 | 3.2975 | 0 | N/A | 0 | 0
2021-03-23 18:00 | 3.6446 | 0 | N/A | 0 | 0
2021-03-23 18:30 | 4.4681 | 0 | N/A | 0 | 0
2021-03-23 19:00 | 4.9229 | 0 | N/A | 0 | 0
2021-03-23 19:30 | 5.0102 | 0 | N/A | 0 | 0
2021-03-23 20:00 | 4.9346 | 0 | N/A | 0 | 0
2021-03-23 20:30 | 4.7399 | 0 | N/A | 0 | 0
2021-03-23 21:00 | 4.423 | 0 | N/A | 0 | 0
2021-03-23 21:30 | 4.0581 | 0 | N/A | 0 | 0
2021-03-23 22:00 | 3.7454 | 0 | N/A | 0 | 0
2021-03-23 22:30 | 4.0602 | 0 | N/A | 0 | 0
2021-03-23 23:00 | 4.1338 | 0 | N/A | 0 | 0
2021-03-23 23:30 | 3.6973 | 0 | N/A | 0 | 0
2021-03-24 | 3.733 | 0 | N/A | 0 | 0
2021-03-24 00:30 | 4.2589 | 0 | N/A | 0 | 0
2021-03-24 01:00 | 4.5039 | 0 | N/A | 0 | 0
2021-03-24 01:30 | 3.6027 | 0 | N/A | 0 | 0
2021-03-24 02:00 | 2.9355 | 0 | N/A | 0 | 0
2021-03-24 02:30 | 2.8468 | 0 | N/A | 0 | 0
2021-03-24 03:00 | 2.5495 | 0 | N/A | 0 | 0
2021-03-24 03:30 | 2.2512 | 0 | N/A | 0 | 0
2021-03-24 04:00 | 2.0544 | 0 | N/A | 0 | 0
2021-03-24 04:30 | 2.0328 | 0 | N/A | 0 | 0
2021-03-24 05:00 | 2.034 | 0 | N/A | 0 | 0
2021-03-24 05:30 | 2.2121 | 0 | N/A | 0 | 0
2021-03-24 06:00 | 2.4898 | 0 | N/A | 0 | 0
2021-03-24 06:30 | 3.057 | 0 | N/A | 0 | 0
2021-03-24 07:00 | 3.7163 | 0 | N/A | 0 | 0
2021-03-24 07:30 | 4.9137 | 0 | N/A | 0 | 0
2021-03-24 08:00 | 5.2933 | 0 | N/A | 0 | 0
2021-03-24 08:30 | 4.8637 | 0 | N/A | 0 | 0
2021-03-24 09:00 | 4.4833 | 0 | N/A | 0 | 0
2021-03-24 09:30 | 4.0967 | 0 | N/A | 0 | 0
2021-03-24 10:00 | 3.8367 | 0 | N/A | 0 | 0
2021-03-24 10:30 | 4.14 | 0 | N/A | 0 | 0
2021-03-24 11:00 | 3.9333 | 0 | N/A | 0 | 0
2021-03-24 11:30 | 3.39 | 0 | N/A | 0 | 0
2021-03-24 12:00 | 2.9936 | 0 | N/A | 0 | 0
2021-03-24 12:30 | 3.86 | 0 | N/A | 0 | 0
2021-03-24 13:00 | 3.8367 | 0 | N/A | 0 | 0
2021-03-24 13:30 | 4.0733 | 0 | N/A | 0 | 0
2021-03-24 14:00 | 3.3979 | 0 | N/A | 0 | 0
2021-03-24 14:30 | 3.1941 | 0 | N/A | 0 | 0
2021-03-24 15:00 | 3.6135 | 0 | N/A | 0 | 0
2021-03-24 15:30 | 4.03 | 0 | N/A | 0 | 0
2021-03-24 16:00 | 3.73 | 0 | N/A | 0 | 0
2021-03-24 16:30 | 3.4651 | 0 | N/A | 0 | 0
2021-03-24 17:00 | 3.561 | 0 | N/A | 0 | 0
2021-03-24 17:30 | 3.8489 | 0 | N/A | 0 | 0
2021-03-24 18:00 | 4.5939 | 0 | N/A | 0 | 0
2021-03-24 18:30 | 5.0423 | 0 | N/A | 0 | 0
2021-03-24 19:00 | 5.1461 | 0 | N/A | 0 | 0
2021-03-24 19:30 | 5.0769 | 0 | N/A | 0 | 0
2021-03-24 20:00 | 5.0691 | 0 | N/A | 0 | 0
2021-03-24 20:30 | 4.8756 | 0 | N/A | 0 | 0
2021-03-24 21:00 | 4.6505 | 0 | N/A | 0 | 0
2021-03-24 21:30 | 4.3363 | 0 | N/A | 0 | 0
2021-03-24 22:00 | 3.9548 | 0 | N/A | 0 | 0
2021-03-24 22:30 | 4.1729 | 0 | N/A | 0 | 0
2021-03-24 23:00 | 4.2474 | 0 | N/A | 0 | 0
2021-03-24 23:30 | 3.8995 | 0 | N/A | 0 | 0
2021-03-25 | 3.9379 | 0 | N/A | 0 | 0
2021-03-25 00:30 | 4.4412 | 0 | N/A | 0 | 0
2021-03-25 01:00 | 4.7284 | 0 | N/A | 0 | 0
2021-03-25 01:30 | 3.8997 | 0 | N/A | 0 | 0
2021-03-25 02:00 | 3.1528 | 0 | N/A | 0 | 0
2021-03-25 02:30 | 3.0188 | 0 | N/A | 0 | 0
2021-03-25 03:00 | 2.7604 | 0 | N/A | 0 | 0
2021-03-25 03:30 | 2.3733 | 0 | N/A | 0 | 0
2021-03-25 04:00 | 2.2539 | 0 | N/A | 0 | 0
2021-03-25 04:30 | 2.1559 | 0 | N/A | 0 | 0
2021-03-25 05:00 | 2.1965 | 0 | N/A | 0 | 0
2021-03-25 05:30 | 2.3714 | 0 | N/A | 0 | 0
2021-03-25 06:00 | 2.6893 | 0 | N/A | 0 | 0
2021-03-25 06:30 | 3.3282 | 0 | N/A | 0 | 0
2021-03-25 07:00 | 4.09 | 0 | N/A | 0 | 0
2021-03-25 07:30 | 5.4703 | 0 | N/A | 0 | 0
2021-03-25 08:00 | 5.8133 | 0 | N/A | 0 | 0
2021-03-25 08:30 | 5.2567 | 0 | N/A | 0 | 0
2021-03-25 09:00 | 4.9468 | 0 | N/A | 0 | 0
2021-03-25 09:30 | 4.3567 | 0 | N/A | 0 | 0
2021-03-25 10:00 | 3.8238 | 0 | N/A | 0 | 0
2021-03-25 10:30 | 3.4502 | 0 | N/A | 0 | 0
2021-03-25 11:00 | 2.3916 | 0 | N/A | 0 | 0
2021-03-25 11:30 | 2.4577 | 0 | N/A | 0 | 0
2021-03-25 12:00 | 2.4838 | 0 | N/A | 0 | 0
2021-03-25 12:30 | 2.3393 | 0 | N/A | 0 | 0
2021-03-25 13:00 | 2.6194 | 0 | N/A | 0 | 0
2021-03-25 13:30 | 2.2336 | 0 | N/A | 0 | 0
2021-03-25 14:00 | 2.0051 | 0 | N/A | 0 | 0
2021-03-25 14:30 | 2.5818 | 0 | N/A | 0 | 0
2021-03-25 15:00 | 2.8038 | 0 | N/A | 0 | 0
2021-03-25 15:30 | 2.5377 | 0 | N/A | 0 | 0
2021-03-25 16:00 | 1.7055 | 0 | N/A | 0 | 0
2021-03-25 16:30 | 3.1316 | 0 | N/A | 0 | 0
2021-03-25 17:00 | 2.7733 | 0 | N/A | 0 | 0
2021-03-25 17:30 | 2.5427 | 0 | N/A | 0 | 0
2021-03-25 18:00 | 3.6211 | 0 | N/A | 0 | 0
2021-03-25 18:30 | 4.0759 | 0 | N/A | 0 | 0
2021-03-25 19:00 | 4.6894 | 0 | N/A | 0 | 0
2021-03-25 19:30 | 5.0077 | 0 | N/A | 0 | 0
2021-03-25 20:00 | 5.2635 | 0 | N/A | 0 | 0
2021-03-25 20:30 | 5.2723 | 0 | N/A | 0 | 0
2021-03-25 21:00 | 4.9905 | 0 | N/A | 0 | 0
2021-03-25 21:30 | 4.6922 | 0 | N/A | 0 | 0
2021-03-25 22:00 | 4.386 | 0 | N/A | 0 | 0
2021-03-25 22:30 | 4.5726 | 0 | N/A | 0 | 0
2021-03-25 23:00 | 4.644 | 0 | N/A | 0 | 0
2021-03-25 23:30 | 4.2575 | 0 | N/A | 0 | 0
2021-03-26 | 4.1566 | 0 | N/A | 0 | 0
2021-03-26 00:30 | 4.5511 | 0 | N/A | 0 | 0
2021-03-26 01:00 | 5.0392 | 0 | N/A | 0 | 0
2021-03-26 01:30 | 4.2246 | 0 | N/A | 0 | 0
2021-03-26 02:00 | 3.4364 | 0 | N/A | 0 | 0
2021-03-26 02:30 | 3.2904 | 0 | N/A | 0 | 0
2021-03-26 03:00 | 3.0212 | 0 | N/A | 0 | 0
2021-03-26 03:30 | 2.5773 | 0 | N/A | 0 | 0
2021-03-26 04:00 | 2.3956 | 0 | N/A | 0 | 0
2021-03-26 04:30 | 2.4295 | 0 | N/A | 0 | 0
2021-03-26 05:00 | 2.4544 | 0 | N/A | 0 | 0
2021-03-26 05:30 | 2.6985 | 0 | N/A | 0 | 0
2021-03-26 06:00 | 3.0306 | 0 | N/A | 0 | 0
2021-03-26 06:30 | 3.9185 | 0 | N/A | 0 | 0
2021-03-26 07:00 | 4.8363 | 0 | N/A | 0 | 0
2021-03-26 07:30 | 6.0967 | 0 | N/A | 0 | 0
2021-03-26 08:00 | 6.54 | 0 | N/A | 0 | 0
2021-03-26 08:30 | 5.5567 | 0 | N/A | 0 | 0
2021-03-26 09:00 | 4.8534 | 0 | N/A | 0 | 0
2021-03-26 09:30 | 3.9201 | 0 | N/A | 0 | 0
2021-03-26 10:00 | 3.0334 | 0 | N/A | 0 | 0
2021-03-26 10:30 | 2.3634 | 0 | N/A | 0 | 0
2021-03-26 11:00 | 2.1567 | 0 | N/A | 0 | 0
2021-03-26 11:30 | 2.02 | 0 | N/A | 0 | 0
2021-03-26 12:00 | 2.3225 | 0 | N/A | 0 | 0
2021-03-26 12:30 | 2.3184 | 0 | N/A | 0 | 0
2021-03-26 13:00 | 1.8368 | 0 | N/A | 0 | 0
2021-03-26 13:30 | 2.5309 | 0 | N/A | 0 | 0
2021-03-26 14:00 | 2.2628 | 0 | N/A | 0 | 0
2021-03-26 14:30 | 2.1054 | 0 | N/A | 0 | 0
2021-03-26 15:00 | 1.5692 | 0 | N/A | 0 | 0
2021-03-26 15:30 | 0.7436 | 0 | N/A | 0 | 0
2021-03-26 16:00 | 0.91829 | 0 | N/A | 0 | 0
2021-03-26 16:30 | 1.1595 | 0 | N/A | 0 | 0
2021-03-26 17:00 | 1.7749 | 0 | N/A | 0 | 0
2021-03-26 17:30 | 2.5848 | 0 | N/A | 0 | 0
2021-03-26 18:00 | 3.1148 | 0 | N/A | 0 | 0
2021-03-26 18:30 | 3.5667 | 0 | N/A | 0 | 0
2021-03-26 19:00 | 4.1782 | 0 | N/A | 0 | 0
2021-03-26 19:30 | 4.5707 | 0 | N/A | 0 | 0
2021-03-26 20:00 | 4.8434 | 0 | N/A | 0 | 0
2021-03-26 20:30 | 4.8541 | 0 | N/A | 0 | 0
2021-03-26 21:00 | 4.6764 | 0 | N/A | 0 | 0
2021-03-26 21:30 | 4.4309 | 0 | N/A | 0 | 0
2021-03-26 22:00 | 4.1512 | 0 | N/A | 0 | 0
2021-03-26 22:30 | 4.4363 | 0 | N/A | 0 | 0
2021-03-26 23:00 | 4.5623 | 0 | N/A | 0 | 0
2021-03-26 23:30 | 4.2218 | 0 | N/A | 0 | 0
2021-03-27 | 4.2086 | 0 | N/A | 0 | 0
2021-03-27 00:30 | 4.5719 | 0 | N/A | 0 | 0
2021-03-27 01:00 | 4.837 | 0 | N/A | 0 | 0
2021-03-27 01:30 | 3.8818 | 0 | N/A | 0 | 0
2021-03-27 02:00 | 3.18 | 0 | N/A | 0 | 0
2021-03-27 02:30 | 3.1653 | 0 | N/A | 0 | 0
2021-03-27 03:00 | 2.8104 | 0 | N/A | 0 | 0
2021-03-27 03:30 | 2.4792 | 0 | N/A | 0 | 0
2021-03-27 04:00 | 2.2752 | 0 | N/A | 0 | 0
2021-03-27 04:30 | 2.2164 | 0 | N/A | 0 | 0
2021-03-27 05:00 | 2.1585 | 0 | N/A | 0 | 0
2021-03-27 05:30 | 2.1764 | 0 | N/A | 0 | 0
2021-03-27 06:00 | 2.3985 | 0 | N/A | 0 | 0
2021-03-27 06:30 | 2.6471 | 0 | N/A | 0 | 0
2021-03-27 07:00 | 2.9025 | 0 | N/A | 0 | 0
2021-03-27 07:30 | 3.3425 | 0 | N/A | 0 | 0
2021-03-27 08:00 | 3.6733 | 0 | N/A | 0 | 0
2021-03-27 08:30 | 3.7393 | 0 | N/A | 0 | 0
2021-03-27 09:00 | 3.8946 | 0 | N/A | 0 | 0
2021-03-27 09:30 | 3.4841 | 0 | N/A | 0 | 0
2021-03-27 10:00 | 3.3807 | 0 | N/A | 0 | 0
2021-03-27 10:30 | 2.5796 | 0 | N/A | 0 | 0
2021-03-27 11:00 | 1.5781 | 0 | N/A | 0 | 0
2021-03-27 11:30 | 1.1958 | 0 | N/A | 0 | 0
2021-03-27 12:00 | 1.1785 | 0 | N/A | 0 | 0
2021-03-27 12:30 | 1.4249 | 0 | N/A | 0 | 0
2021-03-27 13:00 | 1.3869 | 0 | N/A | 0 | 0
2021-03-27 13:30 | 0.84308 | 0 | N/A | 0 | 0
2021-03-27 14:00 | 1.3187 | 0 | N/A | 0 | 0
2021-03-27 14:30 | 0.53759 | 0 | N/A | 0 | 0
2021-03-27 15:00 | 0.67617 | 0 | N/A | 0 | 0
2021-03-27 15:30 | 0.94549 | 0 | N/A | 0 | 0
2021-03-27 16:00 | 1.4012 | 0 | N/A | 0 | 0
2021-03-27 16:30 | 1.8135 | 0 | N/A | 0 | 0
2021-03-27 17:00 | 1.3544 | 0 | N/A | 0 | 0
2021-03-27 17:30 | 2.3931 | 0 | N/A | 0 | 0
2021-03-27 18:00 | 3.4299 | 0 | N/A | 0 | 0
2021-03-27 18:30 | 4.1993 | 0 | N/A | 0 | 0
2021-03-27 19:00 | 4.4502 | 0 | N/A | 0 | 0
2021-03-27 19:30 | 4.7531 | 0 | N/A | 0 | 0
2021-03-27 20:00 | 4.7262 | 0 | N/A | 0 | 0
2021-03-27 20:30 | 4.6157 | 0 | N/A | 0 | 0
2021-03-27 21:00 | 4.3768 | 0 | N/A | 0 | 0
2021-03-27 21:30 | 4.1994 | 0 | N/A | 0 | 0
2021-03-27 22:00 | 3.9561 | 0 | N/A | 0 | 0
2021-03-27 22:30 | 4.3391 | 0 | N/A | 0 | 0
2021-03-27 23:00 | 4.5996 | 0 | N/A | 0 | 0
2021-03-27 23:30 | 4.344 | 0 | N/A | 0 | 0
2021-03-28 | 4.3741 | 0 | N/A | 0 | 0
2021-03-28 00:30 | 4.8758 | 0 | N/A | 0 | 0
2021-03-28 01:00 | 5.2289 | 0 | N/A | 0 | 0
2021-03-28 01:30 | 4.3911 | 0 | N/A | 0 | 0
2021-03-28 02:00 | 3.6538 | 0 | N/A | 0 | 0
2021-03-28 02:30 | 3.5026 | 0 | N/A | 0 | 0
2021-03-28 03:00 | 3.2209 | 0 | N/A | 0 | 0
2021-03-28 03:30 | 2.8262 | 0 | N/A | 0 | 0
2021-03-28 04:00 | 2.5478 | 0 | N/A | 0 | 0
2021-03-28 04:30 | 2.4193 | 0 | N/A | 0 | 0
2021-03-28 05:00 | 2.3633 | 0 | N/A | 0 | 0
2021-03-28 05:30 | 2.4009 | 0 | N/A | 0 | 0
2021-03-28 06:00 | 2.5013 | 0 | N/A | 0 | 0
2021-03-28 06:30 | 2.726 | 0 | N/A | 0 | 0
2021-03-28 07:00 | 2.9075 | 0 | N/A | 0 | 0
2021-03-28 07:30 | 3.3577 | 0 | N/A | 0 | 0
2021-03-28 08:00 | 3.7936 | 0 | N/A | 0 | 0
2021-03-28 08:30 | 3.9262 | 0 | N/A | 0 | 0
2021-03-28 09:00 | 3.8533 | 0 | N/A | 0 | 0
2021-03-28 09:30 | 3.3893 | 0 | N/A | 0 | 0
2021-03-28 10:00 | 2.9832 | 0 | N/A | 0 | 0
2021-03-28 10:30 | 2.8936 | 0 | N/A | 0 | 0
2021-03-28 11:00 | 2.678 | 0 | N/A | 0 | 0
2021-03-28 11:30 | 2.3527 | 0 | N/A | 0 | 0
2021-03-28 12:00 | 3.1045 | 0 | N/A | 0 | 0
2021-03-28 12:30 | 3.1511 | 0 | N/A | 0 | 0
2021-03-28 13:00 | 2.8666 | 0 | N/A | 0 | 0
2021-03-28 13:30 | 2.1035 | 0 | N/A | 0 | 0
2021-03-28 14:00 | 1.7267 | 0 | N/A | 0 | 0
2021-03-28 14:30 | 2.1529 | 0 | N/A | 0 | 0
2021-03-28 15:00 | 2.2885 | 0 | N/A | 0 | 0
2021-03-28 15:30 | 2.2944 | 0 | N/A | 0 | 0
2021-03-28 16:00 | 2.3728 | 0 | N/A | 0 | 0
2021-03-28 16:30 | 2.4377 | 0 | N/A | 0 | 0
2021-03-28 17:00 | 2.9814 | 0 | N/A | 0 | 0
2021-03-28 17:30 | 3.8455 | 0 | N/A | 0 | 0
2021-03-28 18:00 | 4.5857 | 0 | N/A | 0 | 0
2021-03-28 18:30 | 5.1579 | 0 | N/A | 0 | 0
2021-03-28 19:00 | 5.4397 | 0 | N/A | 0 | 0
2021-03-28 19:30 | 5.318 | 0 | N/A | 0 | 0
2021-03-28 20:00 | 5.2147 | 0 | N/A | 0 | 0
2021-03-28 20:30 | 5.0008 | 0 | N/A | 0 | 0
2021-03-28 21:00 | 4.7303 | 0 | N/A | 0 | 0
2021-03-28 21:30 | 4.4322 | 0 | N/A | 0 | 0
2021-03-28 22:00 | 4.0404 | 0 | N/A | 0 | 0
2021-03-28 22:30 | 4.3013 | 0 | N/A | 0 | 0
2021-03-28 23:00 | 4.3899 | 0 | N/A | 0 | 0
2021-03-28 23:30 | 4.1436 | 0 | N/A | 0 | 0
2021-03-29 | 4.2053 | 0 | N/A | 0 | 0
2021-03-29 00:30 | 4.577 | 0 | N/A | 0 | 0
2021-03-29 01:00 | 5.0144 | 0 | N/A | 0 | 0
2021-03-29 01:30 | 4.2997 | 0 | N/A | 0 | 0
2021-03-29 02:00 | 3.6163 | 0 | N/A | 0 | 0
2021-03-29 02:30 | 3.6253 | 0 | N/A | 0 | 0
2021-03-29 03:00 | 3.2581 | 0 | N/A | 0 | 0
2021-03-29 03:30 | 2.7723 | 0 | N/A | 0 | 0
2021-03-29 04:00 | 2.5598 | 0 | N/A | 0 | 0
2021-03-29 04:30 | 2.4045 | 0 | N/A | 0 | 0
2021-03-29 05:00 | 2.3891 | 0 | N/A | 0 | 0
2021-03-29 05:30 | 2.6078 | 0 | N/A | 0 | 0
2021-03-29 06:00 | 2.907 | 0 | N/A | 0 | 0
2021-03-29 06:30 | 3.4948 | 0 | N/A | 0 | 0
2021-03-29 07:00 | 4.2217 | 0 | N/A | 0 | 0
2021-03-29 07:30 | 5.6503 | 0 | N/A | 0 | 0
2021-03-29 08:00 | 6.2234 | 0 | N/A | 0 | 0
2021-03-29 08:30 | 5.4337 | 0 | N/A | 0 | 0
2021-03-29 09:00 | 4.8067 | 0 | N/A | 0 | 0
2021-03-29 09:30 | 4.0101 | 0 | N/A | 0 | 0
2021-03-29 10:00 | 3.1605 | 0 | N/A | 0 | 0
2021-03-29 10:30 | 3.2481 | 0 | N/A | 0 | 0
2021-03-29 11:00 | 3.4303 | 0 | N/A | 0 | 0
2021-03-29 11:30 | 2.5285 | 0 | N/A | 0 | 0
2021-03-29 12:00 | 1.8833 | 0 | N/A | 0 | 0
2021-03-29 12:30 | 1.3567 | 0 | N/A | 0 | 0
2021-03-29 13:00 | 0.87 | 0 | N/A | 0 | 0
2021-03-29 13:30 | 0.78102 | 0 | N/A | 0 | 0
2021-03-29 14:00 | 1.0667 | 0 | N/A | 0 | 0
2021-03-29 14:30 | 0.53943 | 0 | N/A | 0 | 0
2021-03-29 15:00 | 0.20243 | 0 | N/A | 0 | 0
2021-03-29 15:30 | -0.12333 | 0 | N/A | 0 | 0
2021-03-29 16:00 | 0.11705 | 0 | N/A | 0 | 0
2021-03-29 16:30 | 0.64502 | 0 | N/A | 0 | 0
2021-03-29 17:00 | 1.3194 | 0 | N/A | 0 | 0
2021-03-29 17:30 | 2.0818 | 0 | N/A | 0 | 0
2021-03-29 18:00 | 3.0745 | 0 | N/A | 0 | 0
2021-03-29 18:30 | 4.0867 | 0 | N/A | 0 | 0
2021-03-29 19:00 | 4.6032 | 0 | N/A | 0 | 0
2021-03-29 19:30 | 4.9021 | 0 | N/A | 0 | 0
2021-03-29 20:00 | 5.1213 | 0 | N/A | 0 | 0
2021-03-29 20:30 | 5.0257 | 0 | N/A | 0 | 0
2021-03-29 21:00 | 4.9719 | 0 | N/A | 0 | 0
2021-03-29 21:30 | 4.6382 | 0 | N/A | 0 | 0
2021-03-29 22:00 | 4.344 | 0 | N/A | 0 | 0
2021-03-29 22:30 | 4.5191 | 0 | N/A | 0 | 0
2021-03-29 23:00 | 4.6339 | 0 | N/A | 0 | 0
2021-03-29 23:30 | 4.2568 | 0 | N/A | 0 | 0
2021-03-30 | 4.3303 | 0 | N/A | 0 | 0
2021-03-30 00:30 | 4.6418 | 0 | N/A | 0 | 0
2021-03-30 01:00 | 4.9139 | 0 | N/A | 0 | 0
2021-03-30 01:30 | 4.0655 | 0 | N/A | 0 | 0
2021-03-30 02:00 | 3.3859 | 0 | N/A | 0 | 0
2021-03-30 02:30 | 3.3607 | 0 | N/A | 0 | 0
2021-03-30 03:00 | 3.0829 | 0 | N/A | 0 | 0
2021-03-30 03:30 | 2.7059 | 0 | N/A | 0 | 0
2021-03-30 04:00 | 2.4569 | 0 | N/A | 0 | 0
2021-03-30 04:30 | 2.4622 | 0 | N/A | 0 | 0
2021-03-30 05:00 | 2.5273 | 0 | N/A | 0 | 0
2021-03-30 05:30 | 2.7765 | 0 | N/A | 0 | 0
2021-03-30 06:00 | 3.1235 | 0 | N/A | 0 | 0
2021-03-30 06:30 | 3.9543 | 0 | N/A | 0 | 0
2021-03-30 07:00 | 4.8963 | 0 | N/A | 0 | 0
2021-03-30 07:30 | 6.4033 | 0 | N/A | 0 | 0
2021-03-30 08:00 | 6.76 | 0 | N/A | 0 | 0
2021-03-30 08:30 | 5.85 | 0 | N/A | 0 | 0
2021-03-30 09:00 | 5.1567 | 0 | N/A | 0 | 0
2021-03-30 09:30 | 4.1868 | 0 | N/A | 0 | 0
2021-03-30 10:00 | 3.3813 | 0 | N/A | 0 | 0
2021-03-30 10:30 | 2.6136 | 0 | N/A | 0 | 0
2021-03-30 11:00 | 1.6851 | 0 | N/A | 0 | 0
2021-03-30 11:30 | 1.1091 | 0 | N/A | 0 | 0
2021-03-30 12:00 | 0.6414 | 0 | N/A | 0 | 0
2021-03-30 12:30 | 0.21851 | 0 | N/A | 0 | 0
2021-03-30 13:00 | -0.056765 | 0 | N/A | 0 | 0
2021-03-30 13:30 | -0.11837 | 0 | N/A | 0 | 0
2021-03-30 14:00 | -0.15206 | 0 | N/A | 0 | 0
2021-03-30 14:30 | -0.13275 | 0 | N/A | 0 | 0
2021-03-30 15:00 | -0.11 | 0 | N/A | 0 | 0
2021-03-30 15:30 | 0.21045 | 0 | N/A | 0 | 0
2021-03-30 16:00 | 0.3 | 0 | N/A | 0 | 0
2021-03-30 16:30 | 0.82001 | 0 | N/A | 0 | 0
2021-03-30 17:00 | 1.3445 | 0 | N/A | 0 | 0
2021-03-30 17:30 | 2.1838 | 0 | N/A | 0 | 0
2021-03-30 18:00 | 3.1895 | 0 | N/A | 0 | 0
2021-03-30 18:30 | 4.0151 | 0 | N/A | 0 | 0
2021-03-30 19:00 | 4.4751 | 0 | N/A | 0 | 0
2021-03-30 19:30 | 4.7958 | 0 | N/A | 0 | 0
2021-03-30 20:00 | 4.9497 | 0 | N/A | 0 | 0
2021-03-30 20:30 | 4.8888 | 0 | N/A | 0 | 0
2021-03-30 21:00 | 4.7357 | 0 | N/A | 0 | 0
2021-03-30 21:30 | 4.3698 | 0 | N/A | 0 | 0
2021-03-30 22:00 | 4.0315 | 0 | N/A | 0 | 0
2021-03-30 22:30 | 4.1917 | 0 | N/A | 0 | 0
2021-03-30 23:00 | 4.3561 | 0 | N/A | 0 | 0
2021-03-30 23:30 | 4.0261 | 0 | N/A | 0 | 0
2021-03-31 | 4.1769 | 0 | N/A | 0 | 0
2021-03-31 00:30 | 4.4689 | 0 | N/A | 0 | 0
2021-03-31 01:00 | 4.7471 | 0 | N/A | 0 | 0
2021-03-31 01:30 | 3.9958 | 0 | N/A | 0 | 0
2021-03-31 02:00 | 3.3001 | 0 | N/A | 0 | 0
2021-03-31 02:30 | 3.246 | 0 | N/A | 0 | 0
2021-03-31 03:00 | 3.0197 | 0 | N/A | 0 | 0
2021-03-31 03:30 | 2.5712 | 0 | N/A | 0 | 0
2021-03-31 04:00 | 2.3849 | 0 | N/A | 0 | 0
2021-03-31 04:30 | 2.2712 | 0 | N/A | 0 | 0
2021-03-31 05:00 | 2.3592 | 0 | N/A | 0 | 0
2021-03-31 05:30 | 2.6555 | 0 | N/A | 0 | 0
2021-03-31 06:00 | 3.0683 | 0 | N/A | 0 | 0
2021-03-31 06:30 | 3.6645 | 0 | N/A | 0 | 0
2021-03-31 07:00 | 4.5181 | 0 | N/A | 0 | 0
2021-03-31 07:30 | 5.7907 | 0 | N/A | 0 | 0
2021-03-31 08:00 | 6.3167 | 0 | N/A | 0 | 0
2021-03-31 08:30 | 5.5733 | 0 | N/A | 0 | 0
2021-03-31 09:00 | 4.8269 | 0 | N/A | 0 | 0
2021-03-31 09:30 | 3.9734 | 0 | N/A | 0 | 0
2021-03-31 10:00 | 3.0005 | 0 | N/A | 0 | 0
2021-03-31 10:30 | 2.2301 | 0 | N/A | 0 | 0
2021-03-31 11:00 | 1.6999 | 0 | N/A | 0 | 0
2021-03-31 11:30 | 1.28 | 0 | N/A | 0 | 0
2021-03-31 12:00 | 0.82641 | 0 | N/A | 0 | 0
2021-03-31 12:30 | 0.51382 | 0 | N/A | 0 | 0
2021-03-31 13:00 | 0.20423 | 0 | N/A | 0 | 0
2021-03-31 13:30 | 0.23345 | 0 | N/A | 0 | 0
2021-03-31 14:00 | 0.31328 | 0 | N/A | 0 | 0
2021-03-31 14:30 | 0.30516 | 0 | N/A | 0 | 0
2021-03-31 15:00 | 0.27115 | 0 | N/A | 0 | 0
2021-03-31 15:30 | 0.37566 | 0 | N/A | 0 | 0
2021-03-31 16:00 | 0.491 | 0 | N/A | 0 | 0
2021-03-31 16:30 | 0.90339 | 0 | N/A | 0 | 0
2021-03-31 17:00 | 1.5568 | 0 | N/A | 0 | 0
2021-03-31 17:30 | 2.1087 | 0 | N/A | 0 | 0
2021-03-31 18:00 | 3.0587 | 0 | N/A | 0 | 0
2021-03-31 18:30 | 3.8764 | 0 | N/A | 0 | 0
2021-03-31 19:00 | 4.3145 | 0 | N/A | 0 | 0
2021-03-31 19:30 | 4.5115 | 0 | N/A | 0 | 0
2021-03-31 20:00 | 4.5971 | 0 | N/A | 0 | 0
2021-03-31 20:30 | 4.5284 | 0 | N/A | 0 | 0
2021-03-31 21:00 | 4.3333 | 0 | N/A | 0 | 0
2021-03-31 21:30 | 4.1407 | 0 | N/A | 0 | 0
2021-03-31 22:00 | 3.8433 | 0 | N/A | 0 | 0
2021-03-31 22:30 | 4.1906 | 0 | N/A | 0 | 0
2021-03-31 23:00 | 4.2584 | 0 | N/A | 0 | 0
2021-03-31 23:30 | 3.9364 | 0 | N/A | 0 | 0
2021-04-01 | 3.9895 | 0 | N/A | 0 | 0
2021-04-01 00:30 | 4.3599 | 0 | N/A | 0 | 0
2021-04-01 01:00 | 4.5737 | 0 | N/A | 0 | 0
2021-04-01 01:30 | 3.6445 | 0 | N/A | 0 | 0
2021-04-01 02:00 | 2.9657 | 0 | N/A | 0 | 0
2021-04-01 02:30 | 2.9987 | 0 | N/A | 0 | 0
2021-04-01 03:00 | 2.6588 | 0 | N/A | 0 | 0
2021-04-01 03:30 | 2.3429 | 0 | N/A | 0 | 0
2021-04-01 04:00 | 2.1783 | 0 | N/A | 0 | 0
2021-04-01 04:30 | 2.0965 | 0 | N/A | 0 | 0
2021-04-01 05:00 | 2.1937 | 0 | N/A | 0 | 0
2021-04-01 05:30 | 2.4295 | 0 | N/A | 0 | 0
2021-04-01 06:00 | 2.7931 | 0 | N/A | 0 | 0
2021-04-01 06:30 | 3.4886 | 0 | N/A | 0 | 0
2021-04-01 07:00 | 4.2278 | 0 | N/A | 0 | 0
2021-04-01 07:30 | 5.4835 | 0 | N/A | 0 | 0
2021-04-01 08:00 | 6.0234 | 0 | N/A | 0 | 0
2021-04-01 08:30 | 4.98 | 0 | N/A | 0 | 0
2021-04-01 09:00 | 4.3367 | 0 | N/A | 0 | 0
2021-04-01 09:30 | 3.4 | 0 | N/A | 0 | 0
2021-04-01 10:00 | 2.8218 | 0 | N/A | 0 | 0
2021-04-01 10:30 | 1.9868 | 0 | N/A | 0 | 0
2021-04-01 11:00 | 1.1467 | 0 | N/A | 0 | 0
2021-04-01 11:30 | 0.90814 | 0 | N/A | 0 | 0
2021-04-01 12:00 | 0.57975 | 0 | N/A | 0 | 0
2021-04-01 12:30 | 0.4875 | 0 | N/A | 0 | 0
2021-04-01 13:00 | 0.34442 | 0 | N/A | 0 | 0
2021-04-01 13:30 | 0.31418 | 0 | N/A | 0 | 0
2021-04-01 14:00 | -0.095975 | 0 | N/A | 0 | 0
2021-04-01 14:30 | -0.13812 | 0 | N/A | 0 | 0
2021-04-01 15:00 | -0.054263 | 0 | N/A | 0 | 0
2021-04-01 15:30 | 0.090062 | 0 | N/A | 0 | 0
2021-04-01 16:00 | 0.3772 | 0 | N/A | 0 | 0
2021-04-01 16:30 | 0.82593 | 0 | N/A | 0 | 0
2021-04-01 17:00 | 1.6035 | 0 | N/A | 0 | 0
2021-04-01 17:30 | 2.5094 | 0 | N/A | 0 | 0
2021-04-01 18:00 | 3.163 | 0 | N/A | 0 | 0
2021-04-01 18:30 | 3.8865 | 0 | N/A | 0 | 0
2021-04-01 19:00 | 4.2083 | 0 | N/A | 0 | 0
2021-04-01 19:30 | 4.3148 | 0 | N/A | 0 | 0
2021-04-01 20:00 | 4.3464 | 0 | N/A | 0 | 0
2021-04-01 20:30 | 4.1443 | 0 | N/A | 0 | 0
2021-04-01 21:00 | 3.9365 | 0 | N/A | 0 | 0
2021-04-01 21:30 | 3.7712 | 0 | N/A | 0 | 0
2021-04-01 22:00 | 3.5275 | 0 | N/A | 0 | 0
2021-04-01 22:30 | 3.8261 | 0 | N/A | 0 | 0
2021-04-01 23:00 | 4.0174 | 0 | N/A | 0 | 0
2021-04-01 23:30 | 3.6556 | 0 | N/A | 0 | 0
2021-04-02 | 3.7231 | 0 | N/A | 0 | 0
2021-04-02 00:30 | 4.2949 | 0 | N/A | 0 | 0
2021-04-02 01:00 | 4.4758 | 0 | N/A | 0 | 0
2021-04-02 01:30 | 3.5197 | 0 | N/A | 0 | 0
2021-04-02 02:00 | 2.8215 | 0 | N/A | 0 | 0
2021-04-02 02:30 | 2.8516 | 0 | N/A | 0 | 0
2021-04-02 03:00 | 2.5563 | 0 | N/A | 0 | 0
2021-04-02 03:30 | 2.2542 | 0 | N/A | 0 | 0
2021-04-02 04:00 | 2.08 | 0 | N/A | 0 | 0
2021-04-02 04:30 | 1.9816 | 0 | N/A | 0 | 0
2021-04-02 05:00 | 1.9945 | 0 | N/A | 0 | 0
2021-04-02 05:30 | 1.9868 | 0 | N/A | 0 | 0
2021-04-02 06:00 | 2.0677 | 0 | N/A | 0 | 0
2021-04-02 06:30 | 2.2575 | 0 | N/A | 0 | 0
2021-04-02 07:00 | 2.4541 | 0 | N/A | 0 | 0
2021-04-02 07:30 | 2.7889 | 0 | N/A | 0 | 0
2021-04-02 08:00 | 2.9666 | 0 | N/A | 0 | 0
2021-04-02 08:30 | 2.6644 | 0 | N/A | 0 | 0
2021-04-02 09:00 | 2.4522 | 0 | N/A | 0 | 0
2021-04-02 09:30 | 2.0165 | 0 | N/A | 0 | 0
2021-04-02 10:00 | 1.4633 | 0 | N/A | 0 | 0
2021-04-02 10:30 | 0.96169 | 0 | N/A | 0 | 0
2021-04-02 11:00 | 0.50423 | 0 | N/A | 0 | 0
2021-04-02 11:30 | -0.37133 | 0 | N/A | 0 | 0
2021-04-02 12:00 | -0.5863 | 0 | N/A | 0 | 0
2021-04-02 12:30 | -0.72087 | 0 | N/A | 0 | 0
2021-04-02 13:00 | -0.97552 | 0 | N/A | 0 | 0
2021-04-02 13:30 | -1.0786 | 0 | N/A | 0 | 0
2021-04-02 14:00 | -1.1081 | 0 | N/A | 0 | 0
2021-04-02 14:30 | -1.082 | 0 | N/A | 0 | 0
2021-04-02 15:00 | -0.98354 | 0 | N/A | 0 | 0
2021-04-02 15:30 | -0.73714 | 0 | N/A | 0 | 0
2021-04-02 16:00 | -0.42017 | 0 | N/A | 0 | 0
2021-04-02 16:30 | 0.47527 | 0 | N/A | 0 | 0
2021-04-02 17:00 | 1.1247 | 0 | N/A | 0 | 0
2021-04-02 17:30 | 2.0246 | 0 | N/A | 0 | 0
2021-04-02 18:00 | 2.8756 | 0 | N/A | 0 | 0
2021-04-02 18:30 | 3.5839 | 0 | N/A | 0 | 0
2021-04-02 19:00 | 3.8637 | 0 | N/A | 0 | 0
2021-04-02 19:30 | 3.9111 | 0 | N/A | 0 | 0
2021-04-02 20:00 | 3.9126 | 0 | N/A | 0 | 0
2021-04-02 20:30 | 3.7711 | 0 | N/A | 0 | 0
2021-04-02 21:00 | 3.5252 | 0 | N/A | 0 | 0
2021-04-02 21:30 | 3.248 | 0 | N/A | 0 | 0
2021-04-02 22:00 | 3.0588 | 0 | N/A | 0 | 0
2021-04-02 22:30 | 3.5327 | 0 | N/A | 0 | 0
2021-04-02 23:00 | 3.7587 | 0 | N/A | 0 | 0
2021-04-02 23:30 | 3.5366 | 0 | N/A | 0 | 0
2021-04-03 | 3.674 | 0 | N/A | 0 | 0
2021-04-03 00:30 | 4.2125 | 0 | N/A | 0 | 0
2021-04-03 01:00 | 4.4614 | 0 | N/A | 0 | 0
2021-04-03 01:30 | 3.6635 | 0 | N/A | 0 | 0
2021-04-03 02:00 | 2.9646 | 0 | N/A | 0 | 0
2021-04-03 02:30 | 2.8944 | 0 | N/A | 0 | 0
2021-04-03 03:00 | 2.5088 | 0 | N/A | 0 | 0
2021-04-03 03:30 | 2.2558 | 0 | N/A | 0 | 0
2021-04-03 04:00 | 1.9841 | 0 | N/A | 0 | 0
2021-04-03 04:30 | 1.9181 | 0 | N/A | 0 | 0
2021-04-03 05:00 | 1.9104 | 0 | N/A | 0 | 0
2021-04-03 05:30 | 2.0064 | 0 | N/A | 0 | 0
2021-04-03 06:00 | 2.1041 | 0 | N/A | 0 | 0
2021-04-03 06:30 | 2.1863 | 0 | N/A | 0 | 0
2021-04-03 07:00 | 2.3766 | 0 | N/A | 0 | 0
2021-04-03 07:30 | 2.6647 | 0 | N/A | 0 | 0
2021-04-03 08:00 | 2.7889 | 0 | N/A | 0 | 0
2021-04-03 08:30 | 2.6996 | 0 | N/A | 0 | 0
2021-04-03 09:00 | 2.4995 | 0 | N/A | 0 | 0
2021-04-03 09:30 | 2.1355 | 0 | N/A | 0 | 0
2021-04-03 10:00 | 1.5981 | 0 | N/A | 0 | 0
2021-04-03 10:30 | 1.029 | 0 | N/A | 0 | 0
2021-04-03 11:00 | 0.50677 | 0 | N/A | 0 | 0
2021-04-03 11:30 | 0.31216 | 0 | N/A | 0 | 0
2021-04-03 12:00 | -0.28363 | 0 | N/A | 0 | 0
2021-04-03 12:30 | -0.418 | 0 | N/A | 0 | 0
2021-04-03 13:00 | -0.4924 | 0 | N/A | 0 | 0
2021-04-03 13:30 | -0.38281 | 0 | N/A | 0 | 0
2021-04-03 14:00 | -0.41979 | 0 | N/A | 0 | 0
2021-04-03 14:30 | -0.29159 | 0 | N/A | 0 | 0
2021-04-03 15:00 | -0.14851 | 0 | N/A | 0 | 0
2021-04-03 15:30 | 0.070317 | 0 | N/A | 0 | 0
2021-04-03 16:00 | 0.43134 | 0 | N/A | 0 | 0
2021-04-03 16:30 | 1.0252 | 0 | N/A | 0 | 0
2021-04-03 17:00 | 1.7066 | 0 | N/A | 0 | 0
2021-04-03 17:30 | 2.538 | 0 | N/A | 0 | 0
2021-04-03 18:00 | 3.3354 | 0 | N/A | 0 | 0
2021-04-03 18:30 | 3.959 | 0 | N/A | 0 | 0
2021-04-03 19:00 | 4.3131 | 0 | N/A | 0 | 0
2021-04-03 19:30 | 4.2849 | 0 | N/A | 0 | 0
2021-04-03 20:00 | 4.1775 | 0 | N/A | 0 | 0
2021-04-03 20:30 | 3.8611 | 0 | N/A | 0 | 0
2021-04-03 21:00 | 3.6147 | 0 | N/A | 0 | 0
2021-04-03 21:30 | 3.4028 | 0 | N/A | 0 | 0
2021-04-03 22:00 | 3.1594 | 0 | N/A | 0 | 0
2021-04-03 22:30 | 3.6383 | 0 | N/A | 0 | 0
2021-04-03 23:00 | 3.8088 | 0 | N/A | 0 | 0
2021-04-03 23:30 | 3.6229 | 0 | N/A | 0 | 0
2021-04-04 | 3.7083 | 0 | N/A | 0 | 0
2021-04-04 00:30 | 4.0459 | 0 | N/A | 0 | 0
2021-04-04 01:00 | 4.2615 | 0 | N/A | 0 | 0
2021-04-04 01:30 | 3.4621 | 0 | N/A | 0 | 0
2021-04-04 02:00 | 2.883 | 0 | N/A | 0 | 0
2021-04-04 02:30 | 2.1915 | 0 | N/A | 0 | 0
2021-04-04 03:00 | 2.0234 | 0 | N/A | 0 | 0
2021-04-04 03:30 | 1.9018 | 0 | N/A | 0 | 0
2021-04-04 04:00 | 1.8853 | 0 | N/A | 0 | 0
2021-04-04 04:30 | 1.8535 | 0 | N/A | 0 | 0
2021-04-04 05:00 | 1.8547 | 0 | N/A | 0 | 0
2021-04-04 05:30 | 1.8851 | 0 | N/A | 0 | 0
2021-04-04 06:00 | 1.985 | 0 | N/A | 0 | 0
2021-04-04 06:30 | 2.2804 | 0 | N/A | 0 | 0
2021-04-04 07:00 | 2.4194 | 0 | N/A | 0 | 0
2021-04-04 07:30 | 2.3726 | 0 | N/A | 0 | 0
2021-04-04 08:00 | 2.2273 | 0 | N/A | 0 | 0
2021-04-04 08:30 | 1.8824 | 0 | N/A | 0 | 0
2021-04-04 09:00 | 1.4997 | 0 | N/A | 0 | 0
2021-04-04 09:30 | 1.0009 | 0 | N/A | 0 | 0
2021-04-04 10:00 | 0.56303 | 0 | N/A | 0 | 0
2021-04-04 10:30 | 0.38326 | 0 | N/A | 0 | 0
2021-04-04 11:00 | -0.35103 | 0 | N/A | 0 | 0
2021-04-04 11:30 | -0.51614 | 0 | N/A | 0 | 0
2021-04-04 12:00 | -0.56891 | 0 | N/A | 0 | 0
2021-04-04 12:30 | -0.61103 | 0 | N/A | 0 | 0
2021-04-04 13:00 | -0.67889 | 0 | N/A | 0 | 0
2021-04-04 13:30 | -0.68308 | 0 | N/A | 0 | 0
2021-04-04 14:00 | -0.52223 | 0 | N/A | 0 | 0
2021-04-04 14:30 | -0.27578 | 0 | N/A | 0 | 0
2021-04-04 15:00 | 0.2848 | 0 | N/A | 0 | 0
2021-04-04 15:30 | 0.60668 | 0 | N/A | 0 | 0
2021-04-04 16:00 | 1.2112 | 0 | N/A | 0 | 0
2021-04-04 16:30 | 2.1013 | 0 | N/A | 0 | 0
2021-04-04 17:00 | 2.8145 | 0 | N/A | 0 | 0
2021-04-04 17:30 | 3.4747 | 0 | N/A | 0 | 0
2021-04-04 18:00 | 4.0816 | 0 | N/A | 0 | 0
2021-04-04 18:30 | 4.2102 | 0 | N/A | 0 | 0
2021-04-04 19:00 | 4.2255 | 0 | N/A | 0 | 0
2021-04-04 19:30 | 4.0566 | 0 | N/A | 0 | 0
2021-04-04 20:00 | 3.8152 | 0 | N/A | 0 | 0
2021-04-04 20:30 | 3.4981 | 0 | N/A | 0 | 0
2021-04-04 21:00 | 3.2761 | 0 | N/A | 0 | 0
2021-04-04 21:30 | 3.8541 | 0 | N/A | 0 | 0
2021-04-04 22:00 | 4.0508 | 0 | N/A | 0 | 0
2021-04-04 22:30 | 3.7656 | 0 | N/A | 0 | 0
2021-04-04 23:00 | 3.9844 | 0 | N/A | 0 | 0
2021-04-04 23:30 | 4.4037 | 0 | N/A | 0 | 0
2021-04-05 | 4.5992 | 0 | N/A | 0 | 0
2021-04-05 00:30 | 3.8275 | 0 | N/A | 0 | 0
2021-04-05 01:00 | 3.1104 | 0 | N/A | 0 | 0
2021-04-05 01:30 | 3.0299 | 0 | N/A | 0 | 0
2021-04-05 02:00 | 2.7225 | 0 | N/A | 0 | 0
2021-04-05 02:30 | 2.3014 | 0 | N/A | 0 | 0
2021-04-05 03:00 | 2.0923 | 0 | N/A | 0 | 0
2021-04-05 03:30 | 2.0751 | 0 | N/A | 0 | 0
2021-04-05 04:00 | 1.9614 | 0 | N/A | 0 | 0
2021-04-05 04:30 | 1.8741 | 0 | N/A | 0 | 0
2021-04-05 05:00 | 1.9429 | 0 | N/A | 0 | 0
2021-04-05 05:30 | 2.0084 | 0 | N/A | 0 | 0
2021-04-05 06:00 | 2.1372 | 0 | N/A | 0 | 0
2021-04-05 06:30 | 2.4119 | 0 | N/A | 0 | 0
2021-04-05 07:00 | 2.4942 | 0 | N/A | 0 | 0
2021-04-05 07:30 | 2.4494 | 0 | N/A | 0 | 0
2021-04-05 08:00 | 2.4631 | 0 | N/A | 0 | 0
2021-04-05 08:30 | 2.2154 | 0 | N/A | 0 | 0
2021-04-05 09:00 | 2.0622 | 0 | N/A | 0 | 0
2021-04-05 09:30 | 2.1198 | 0 | N/A | 0 | 0
2021-04-05 10:00 | 1.6813 | 0 | N/A | 0 | 0
2021-04-05 10:30 | 1.3615 | 0 | N/A | 0 | 0
2021-04-05 11:00 | 0.60411 | 0 | N/A | 0 | 0
2021-04-05 11:30 | -0.57529 | 0 | N/A | 0 | 0
2021-04-05 12:00 | -0.70291 | 0 | N/A | 0 | 0
2021-04-05 12:30 | -0.6675 | 0 | N/A | 0 | 0
2021-04-05 13:00 | -0.7731 | 0 | N/A | 0 | 0
2021-04-05 13:30 | -0.80053 | 0 | N/A | 0 | 0
2021-04-05 14:00 | -0.7314 | 0 | N/A | 0 | 0
2021-04-05 14:30 | -0.6284 | 0 | N/A | 0 | 0
2021-04-05 15:00 | -0.44728 | 0 | N/A | 0 | 0
2021-04-05 15:30 | 0.48005 | 0 | N/A | 0 | 0
2021-04-05 16:00 | 0.89162 | 0 | N/A | 0 | 0
2021-04-05 16:30 | 1.6014 | 0 | N/A | 0 | 0
2021-04-05 17:00 | 2.5814 | 0 | N/A | 0 | 0
2021-04-05 17:30 | 3.6603 | 0 | N/A | 0 | 0
2021-04-05 18:00 | 4.5826 | 0 | N/A | 0 | 0
2021-04-05 18:30 | 5.1502 | 0 | N/A | 0 | 0
2021-04-05 19:00 | 5.3993 | 0 | N/A | 0 | 0
2021-04-05 19:30 | 5.2326 | 0 | N/A | 0 | 0
2021-04-05 20:00 | 4.8487 | 0 | N/A | 0 | 0
2021-04-05 20:30 | 4.4888 | 0 | N/A | 0 | 0
2021-04-05 21:00 | 4.1897 | 0 | N/A | 0 | 0
2021-04-05 21:30 | 4.5448 | 0 | N/A | 0 | 0
2021-04-05 22:00 | 4.837 | 0 | N/A | 0 | 0
2021-04-05 22:30 | 4.4664 | 0 | N/A | 0 | 0
2021-04-05 23:00 | 4.4559 | 0 | N/A | 0 | 0
2021-04-05 23:30 | 4.6411 | 0 | N/A | 0 | 0
2021-04-06 | 5.0672 | 0 | N/A | 0 | 0
2021-04-06 00:30 | 4.2958 | 0 | N/A | 0 | 0
2021-04-06 01:00 | 3.6094 | 0 | N/A | 0 | 0
2021-04-06 01:30 | 3.531 | 0 | N/A | 0 | 0
2021-04-06 02:00 | 3.1203 | 0 | N/A | 0 | 0
2021-04-06 02:30 | 2.592 | 0 | N/A | 0 | 0
2021-04-06 03:00 | 2.3537 | 0 | N/A | 0 | 0
2021-04-06 03:30 | 2.2021 | 0 | N/A | 0 | 0
2021-04-06 04:00 | 2.1299 | 0 | N/A | 0 | 0
2021-04-06 04:30 | 2.1137 | 0 | N/A | 0 | 0
2021-04-06 05:00 | 2.1753 | 0 | N/A | 0 | 0
2021-04-06 05:30 | 2.375 | 0 | N/A | 0 | 0
2021-04-06 06:00 | 2.5477 | 0 | N/A | 0 | 0
2021-04-06 06:30 | 3.1982 | 0 | N/A | 0 | 0
2021-04-06 07:00 | 3.479 | 0 | N/A | 0 | 0
2021-04-06 07:30 | 3.8348 | 0 | N/A | 0 | 0
2021-04-06 08:00 | 3.9353 | 0 | N/A | 0 | 0
2021-04-06 08:30 | 3.4543 | 0 | N/A | 0 | 0
2021-04-06 09:00 | 2.7867 | 0 | N/A | 0 | 0
2021-04-06 09:30 | 2.0601 | 0 | N/A | 0 | 0
2021-04-06 10:00 | 1.49 | 0 | N/A | 0 | 0
2021-04-06 10:30 | 0.98347 | 0 | N/A | 0 | 0
2021-04-06 11:00 | 0.59707 | 0 | N/A | 0 | 0
2021-04-06 11:30 | 0.39872 | 0 | N/A | 0 | 0
2021-04-06 12:00 | 0.21812 | 0 | N/A | 0 | 0
2021-04-06 12:30 | -0.11823 | 0 | N/A | 0 | 0
2021-04-06 13:00 | -0.15902 | 0 | N/A | 0 | 0
2021-04-06 13:30 | -0.19232 | 0 | N/A | 0 | 0
2021-04-06 14:00 | -0.19827 | 0 | N/A | 0 | 0
2021-04-06 14:30 | 0.14866 | 0 | N/A | 0 | 0
2021-04-06 15:00 | 0.44922 | 0 | N/A | 0 | 0
2021-04-06 15:30 | 0.81044 | 0 | N/A | 0 | 0
2021-04-06 16:00 | 1.2841 | 0 | N/A | 0 | 0
2021-04-06 16:30 | 1.965 | 0 | N/A | 0 | 0
2021-04-06 17:00 | 2.5769 | 0 | N/A | 0 | 0
2021-04-06 17:30 | 3.5974 | 0 | N/A | 0 | 0
2021-04-06 18:00 | 4.4484 | 0 | N/A | 0 | 0
2021-04-06 18:30 | 5.0165 | 0 | N/A | 0 | 0
2021-04-06 19:00 | 5.4392 | 0 | N/A | 0 | 0
2021-04-06 19:30 | 5.2543 | 0 | N/A | 0 | 0
2021-04-06 20:00 | 5.0073 | 0 | N/A | 0 | 0
2021-04-06 20:30 | 4.7265 | 0 | N/A | 0 | 0
2021-04-06 21:00 | 4.4322 | 0 | N/A | 0 | 0
2021-04-06 21:30 | 4.794 | 0 | N/A | 0 | 0
2021-04-06 22:00 | 4.9499 | 0 | N/A | 0 | 0
2021-04-06 22:30 | 4.3824 | 0 | N/A | 0 | 0
2021-04-06 23:00 | 4.3993 | 0 | N/A | 0 | 0
2021-04-06 23:30 | 4.7786 | 0 | N/A | 0 | 0
2021-04-07 | 4.9264 | 0 | N/A | 0 | 0
2021-04-07 00:30 | 4.1489 | 0 | N/A | 0 | 0
2021-04-07 01:00 | 3.3747 | 0 | N/A | 0 | 0
2021-04-07 01:30 | 3.2346 | 0 | N/A | 0 | 0
2021-04-07 02:00 | 2.9139 | 0 | N/A | 0 | 0
2021-04-07 02:30 | 2.4342 | 0 | N/A | 0 | 0
2021-04-07 03:00 | 2.213 | 0 | N/A | 0 | 0
2021-04-07 03:30 | 2.1176 | 0 | N/A | 0 | 0
2021-04-07 04:00 | 2.0462 | 0 | N/A | 0 | 0
2021-04-07 04:30 | 2.0265 | 0 | N/A | 0 | 0
2021-04-07 05:00 | 2.0274 | 0 | N/A | 0 | 0
2021-04-07 05:30 | 2.2913 | 0 | N/A | 0 | 0
2021-04-07 06:00 | 2.591 | 0 | N/A | 0 | 0
2021-04-07 06:30 | 3.2164 | 0 | N/A | 0 | 0
2021-04-07 07:00 | 3.6293 | 0 | N/A | 0 | 0
2021-04-07 07:30 | 3.7849 | 0 | N/A | 0 | 0
2021-04-07 08:00 | 3.6606 | 0 | N/A | 0 | 0
2021-04-07 08:30 | 3.257 | 0 | N/A | 0 | 0
2021-04-07 09:00 | 2.6873 | 0 | N/A | 0 | 0
2021-04-07 09:30 | 2.1138 | 0 | N/A | 0 | 0
2021-04-07 10:00 | 1.3665 | 0 | N/A | 0 | 0
2021-04-07 10:30 | 1.0462 | 0 | N/A | 0 | 0
2021-04-07 11:00 | 0.66483 | 0 | N/A | 0 | 0
2021-04-07 11:30 | 0.38246 | 0 | N/A | 0 | 0
2021-04-07 12:00 | 0.33302 | 0 | N/A | 0 | 0
2021-04-07 12:30 | 0.429 | 0 | N/A | 0 | 0
2021-04-07 13:00 | 0.42381 | 0 | N/A | 0 | 0
2021-04-07 13:30 | 0.54923 | 0 | N/A | 0 | 0
2021-04-07 14:00 | 0.67775 | 0 | N/A | 0 | 0
2021-04-07 14:30 | 0.89825 | 0 | N/A | 0 | 0
2021-04-07 15:00 | 1.1321 | 0 | N/A | 0 | 0
2021-04-07 15:30 | 1.5011 | 0 | N/A | 0 | 0
2021-04-07 16:00 | 2.1346 | 0 | N/A | 0 | 0
2021-04-07 16:30 | 2.7774 | 0 | N/A | 0 | 0
2021-04-07 17:00 | 3.1739 | 0 | N/A | 0 | 0
2021-04-07 17:30 | 3.8814 | 0 | N/A | 0 | 0
2021-04-07 18:00 | 4.5706 | 0 | N/A | 0 | 0
2021-04-07 18:30 | 4.8789 | 0 | N/A | 0 | 0
2021-04-07 19:00 | 5.0057 | 0 | N/A | 0 | 0
2021-04-07 19:30 | 4.7353 | 0 | N/A | 0 | 0
2021-04-07 20:00 | 4.3749 | 0 | N/A | 0 | 0
2021-04-07 20:30 | 4.1238 | 0 | N/A | 0 | 0
2021-04-07 21:00 | 3.917 | 0 | N/A | 0 | 0
2021-04-07 21:30 | 4.3318 | 0 | N/A | 0 | 0
2021-04-07 22:00 | 4.6608 | 0 | N/A | 0 | 0
2021-04-07 22:30 | 4.2399 | 0 | N/A | 0 | 0
2021-04-07 23:00 | 4.3666 | 0 | N/A | 0 | 0
2021-04-07 23:30 | 4.6622 | 0 | N/A | 0 | 0
2021-04-08 | 4.9213 | 0 | N/A | 0 | 0
2021-04-08 00:30 | 4.0508 | 0 | N/A | 0 | 0
2021-04-08 01:00 | 3.2028 | 0 | N/A | 0 | 0
2021-04-08 01:30 | 3.1249 | 0 | N/A | 0 | 0
2021-04-08 02:00 | 2.6695 | 0 | N/A | 0 | 0
2021-04-08 02:30 | 2.2999 | 0 | N/A | 0 | 0
2021-04-08 03:00 | 2.1059 | 0 | N/A | 0 | 0
2021-04-08 03:30 | 2.0769 | 0 | N/A | 0 | 0
2021-04-08 04:00 | 1.9959 | 0 | N/A | 0 | 0
2021-04-08 04:30 | 1.9388 | 0 | N/A | 0 | 0
2021-04-08 05:00 | 2.0279 | 0 | N/A | 0 | 0
2021-04-08 05:30 | 2.1973 | 0 | N/A | 0 | 0
2021-04-08 06:00 | 2.5335 | 0 | N/A | 0 | 0
2021-04-08 06:30 | 3.236 | 0 | N/A | 0 | 0
2021-04-08 07:00 | 3.5832 | 0 | N/A | 0 | 0
2021-04-08 07:30 | 3.6956 | 0 | N/A | 0 | 0
2021-04-08 08:00 | 3.5494 | 0 | N/A | 0 | 0
2021-04-08 08:30 | 3.1451 | 0 | N/A | 0 | 0
2021-04-08 09:00 | 2.5474 | 0 | N/A | 0 | 0
2021-04-08 09:30 | 1.8672 | 0 | N/A | 0 | 0
2021-04-08 10:00 | 1.2702 | 0 | N/A | 0 | 0
2021-04-08 10:30 | 0.80003 | 0 | N/A | 0 | 0
2021-04-08 11:00 | 0.51676 | 0 | N/A | 0 | 0
2021-04-08 11:30 | 0.36271 | 0 | N/A | 0 | 0
2021-04-08 12:00 | 0.24597 | 0 | N/A | 0 | 0
2021-04-08 12:30 | 0.29069 | 0 | N/A | 0 | 0
2021-04-08 13:00 | 0.2182 | 0 | N/A | 0 | 0
2021-04-08 13:30 | 0.61364 | 0 | N/A | 0 | 0
2021-04-08 14:00 | 0.99471 | 0 | N/A | 0 | 0
2021-04-08 14:30 | 1.3868 | 0 | N/A | 0 | 0
2021-04-08 15:00 | 1.6149 | 0 | N/A | 0 | 0
2021-04-08 15:30 | 1.698 | 0 | N/A | 0 | 0
2021-04-08 16:00 | 2.6 | 0 | N/A | 0 | 0
2021-04-08 16:30 | 3.0333 | 0 | N/A | 0 | 0
2021-04-08 17:00 | 3.685 | 0 | N/A | 0 | 0
2021-04-08 17:30 | 4.3019 | 0 | N/A | 0 | 0
2021-04-08 18:00 | 4.8457 | 0 | N/A | 0 | 0
2021-04-08 18:30 | 5.1612 | 0 | N/A | 0 | 0
2021-04-08 19:00 | 5.0189 | 0 | N/A | 0 | 0
2021-04-08 19:30 | 4.8332 | 0 | N/A | 0 | 0
2021-04-08 20:00 | 4.5935 | 0 | N/A | 0 | 0
2021-04-08 20:30 | 4.276 | 0 | N/A | 0 | 0
2021-04-08 21:00 | 4.0485 | 0 | N/A | 0 | 0
2021-04-08 21:30 | 4.4431 | 0 | N/A | 0 | 0
2021-04-08 22:00 | 4.519 | 0 | N/A | 0 | 0
2021-04-08 22:30 | 4.1036 | 0 | N/A | 0 | 0
2021-04-08 23:00 | 4.138 | 0 | N/A | 0 | 0
2021-04-08 23:30 | 4.5883 | 0 | N/A | 0 | 0
2021-04-09 | 4.846 | 0 | N/A | 0 | 0
2021-04-09 00:30 | 3.9549 | 0 | N/A | 0 | 0
2021-04-09 01:00 | 3.0863 | 0 | N/A | 0 | 0
2021-04-09 01:30 | 3.0588 | 0 | N/A | 0 | 0
2021-04-09 02:00 | 2.768 | 0 | N/A | 0 | 0
2021-04-09 02:30 | 2.3454 | 0 | N/A | 0 | 0
2021-04-09 03:00 | 2.1021 | 0 | N/A | 0 | 0
2021-04-09 03:30 | 2.0838 | 0 | N/A | 0 | 0
2021-04-09 04:00 | 1.957 | 0 | N/A | 0 | 0
2021-04-09 04:30 | 1.96 | 0 | N/A | 0 | 0
2021-04-09 05:00 | 2.0847 | 0 | N/A | 0 | 0
2021-04-09 05:30 | 2.3354 | 0 | N/A | 0 | 0
2021-04-09 06:00 | 2.5489 | 0 | N/A | 0 | 0
2021-04-09 06:30 | 3.0733 | 0 | N/A | 0 | 0
2021-04-09 07:00 | 3.5125 | 0 | N/A | 0 | 0
2021-04-09 07:30 | 3.7535 | 0 | N/A | 0 | 0
2021-04-09 08:00 | 3.8122 | 0 | N/A | 0 | 0
2021-04-09 08:30 | 3.4863 | 0 | N/A | 0 | 0
2021-04-09 09:00 | 3.7118 | 0 | N/A | 0 | 0
2021-04-09 09:30 | 3.2779 | 0 | N/A | 0 | 0
2021-04-09 10:00 | 2.7034 | 0 | N/A | 0 | 0
2021-04-09 10:30 | 3.1202 | 0 | N/A | 0 | 0
2021-04-09 11:00 | 2.1267 | 0 | N/A | 0 | 0
2021-04-09 11:30 | 2.3533 | 0 | N/A | 0 | 0
2021-04-09 12:00 | 2.17 | 0 | N/A | 0 | 0
2021-04-09 12:30 | 2.65 | 0 | N/A | 0 | 0
2021-04-09 13:00 | 2.81 | 0 | N/A | 0 | 0
2021-04-09 13:30 | 1.0967 | 0 | N/A | 0 | 0
2021-04-09 14:00 | 1.591 | 0 | N/A | 0 | 0
2021-04-09 14:30 | 2.4101 | 0 | N/A | 0 | 0
2021-04-09 15:00 | 2.3569 | 0 | N/A | 0 | 0
2021-04-09 15:30 | 2.4897 | 0 | N/A | 0 | 0
2021-04-09 16:00 | 3.0954 | 0 | N/A | 0 | 0
2021-04-09 16:30 | 3.1203 | 0 | N/A | 0 | 0
2021-04-09 17:00 | 3.4588 | 0 | N/A | 0 | 0
2021-04-09 17:30 | 4.0854 | 0 | N/A | 0 | 0
2021-04-09 18:00 | 4.9762 | 0 | N/A | 0 | 0
2021-04-09 18:30 | 5.4688 | 0 | N/A | 0 | 0
2021-04-09 19:00 | 5.7761 | 0 | N/A | 0 | 0
2021-04-09 19:30 | 5.5409 | 0 | N/A | 0 | 0
2021-04-09 20:00 | 5.4093 | 0 | N/A | 0 | 0
2021-04-09 20:30 | 5.2773 | 0 | N/A | 0 | 0
2021-04-09 21:00 | 5.0806 | 0 | N/A | 0 | 0
2021-04-09 21:30 | 5.4822 | 0 | N/A | 0 | 0
2021-04-09 22:00 | 5.574 | 0 | N/A | 0 | 0
2021-04-09 22:30 | 5.0992 | 0 | N/A | 0 | 0
2021-04-09 23:00 | 5.0586 | 0 | N/A | 0 | 0
2021-04-09 23:30 | 5.3353 | 0 | N/A | 0 | 0
2021-04-10 | 5.5415 | 0 | N/A | 0 | 0
2021-04-10 00:30 | 4.5354 | 0 | N/A | 0 | 0
2021-04-10 01:00 | 3.6131 | 0 | N/A | 0 | 0
2021-04-10 01:30 | 3.4129 | 0 | N/A | 0 | 0
2021-04-10 02:00 | 3.1652 | 0 | N/A | 0 | 0
2021-04-10 02:30 | 2.7083 | 0 | N/A | 0 | 0
2021-04-10 03:00 | 2.493 | 0 | N/A | 0 | 0
2021-04-10 03:30 | 2.3386 | 0 | N/A | 0 | 0
2021-04-10 04:00 | 2.3072 | 0 | N/A | 0 | 0
2021-04-10 04:30 | 2.241 | 0 | N/A | 0 | 0
2021-04-10 05:00 | 2.2114 | 0 | N/A | 0 | 0
2021-04-10 05:30 | 2.2718 | 0 | N/A | 0 | 0
2021-04-10 06:00 | 2.5004 | 0 | N/A | 0 | 0
2021-04-10 06:30 | 2.7956 | 0 | N/A | 0 | 0
2021-04-10 07:00 | 2.9601 | 0 | N/A | 0 | 0
2021-04-10 07:30 | 3.0638 | 0 | N/A | 0 | 0
2021-04-10 08:00 | 3.5574 | 0 | N/A | 0 | 0
2021-04-10 08:30 | 3.8674 | 0 | N/A | 0 | 0
2021-04-10 09:00 | 3.5834 | 0 | N/A | 0 | 0
2021-04-10 09:30 | 3.6097 | 0 | N/A | 0 | 0
2021-04-10 10:00 | 4.0386 | 0 | N/A | 0 | 0
2021-04-10 10:30 | 3.8019 | 0 | N/A | 0 | 0
2021-04-10 11:00 | 3.9035 | 0 | N/A | 0 | 0
2021-04-10 11:30 | 2.2653 | 0 | N/A | 0 | 0
2021-04-10 12:00 | 1.4019 | 0 | N/A | 0 | 0
2021-04-10 12:30 | 1.5696 | 0 | N/A | 0 | 0
2021-04-10 13:00 | 1.4694 | 0 | N/A | 0 | 0
2021-04-10 13:30 | 2.7215 | 0 | N/A | 0 | 0
2021-04-10 14:00 | 1.3777 | 0 | N/A | 0 | 0
2021-04-10 14:30 | 2.0288 | 0 | N/A | 0 | 0
2021-04-10 15:00 | 2.9732 | 0 | N/A | 0 | 0
2021-04-10 15:30 | 2.5632 | 0 | N/A | 0 | 0
2021-04-10 16:00 | 3.5404 | 0 | N/A | 0 | 0
2021-04-10 16:30 | 4.0544 | 0 | N/A | 0 | 0
2021-04-10 17:00 | 4.41 | 0 | N/A | 0 | 0
2021-04-10 17:30 | 5.4547 | 0 | N/A | 0 | 0
2021-04-10 18:00 | 6.3584 | 0 | N/A | 0 | 0
2021-04-10 18:30 | 6.5996 | 0 | N/A | 0 | 0
2021-04-10 19:00 | 6.62 | 0 | N/A | 0 | 0
2021-04-10 19:30 | 6.4953 | 0 | N/A | 0 | 0
2021-04-10 20:00 | 6.1172 | 0 | N/A | 0 | 0
2021-04-10 20:30 | 5.8517 | 0 | N/A | 0 | 0
2021-04-10 21:00 | 5.3845 | 0 | N/A | 0 | 0
2021-04-10 21:30 | 5.855 | 0 | N/A | 0 | 0
2021-04-10 22:00 | 6.2173 | 0 | N/A | 0 | 0
2021-04-10 22:30 | 5.7753 | 0 | N/A | 0 | 0
2021-04-10 23:00 | 5.6081 | 0 | N/A | 0 | 0
2021-04-10 23:30 | 5.7826 | 0 | N/A | 0 | 0
2021-04-11 | 6.2105 | 0 | N/A | 0 | 0
2021-04-11 00:30 | 5.4365 | 0 | N/A | 0 | 0
2021-04-11 01:00 | 4.6426 | 0 | N/A | 0 | 0
2021-04-11 01:30 | 4.5725 | 0 | N/A | 0 | 0
2021-04-11 02:00 | 4.1113 | 0 | N/A | 0 | 0
2021-04-11 02:30 | 3.5763 | 0 | N/A | 0 | 0
2021-04-11 03:00 | 3.223 | 0 | N/A | 0 | 0
2021-04-11 03:30 | 2.9581 | 0 | N/A | 0 | 0
2021-04-11 04:00 | 2.8218 | 0 | N/A | 0 | 0
2021-04-11 04:30 | 2.74 | 0 | N/A | 0 | 0
2021-04-11 05:00 | 2.7882 | 0 | N/A | 0 | 0
2021-04-11 05:30 | 2.9009 | 0 | N/A | 0 | 0
2021-04-11 06:00 | 3.0267 | 0 | N/A | 0 | 0
2021-04-11 06:30 | 3.2767 | 0 | N/A | 0 | 0
2021-04-11 07:00 | 3.5678 | 0 | N/A | 0 | 0
2021-04-11 07:30 | 3.6206 | 0 | N/A | 0 | 0
2021-04-11 08:00 | 3.7904 | 0 | N/A | 0 | 0
2021-04-11 08:30 | 3.9226 | 0 | N/A | 0 | 0
2021-04-11 09:00 | 4.065 | 0 | N/A | 0 | 0
2021-04-11 09:30 | 3.8253 | 0 | N/A | 0 | 0
2021-04-11 10:00 | 3.727 | 0 | N/A | 0 | 0
2021-04-11 10:30 | 3.7161 | 0 | N/A | 0 | 0
2021-04-11 11:00 | 2.9123 | 0 | N/A | 0 | 0
2021-04-11 11:30 | 4.2303 | 0 | N/A | 0 | 0
2021-04-11 12:00 | 2.6428 | 0 | N/A | 0 | 0
2021-04-11 12:30 | 3.3159 | 0 | N/A | 0 | 0
2021-04-11 13:00 | 3.0761 | 0 | N/A | 0 | 0
2021-04-11 13:30 | 2.8688 | 0 | N/A | 0 | 0
2021-04-11 14:00 | 2.8764 | 0 | N/A | 0 | 0
2021-04-11 14:30 | 2.8267 | 0 | N/A | 0 | 0
2021-04-11 15:00 | 3.3489 | 0 | N/A | 0 | 0
2021-04-11 15:30 | 3.6281 | 0 | N/A | 0 | 0
2021-04-11 16:00 | 3.5836 | 0 | N/A | 0 | 0
2021-04-11 16:30 | 4.7302 | 0 | N/A | 0 | 0
2021-04-11 17:00 | 5.4251 | 0 | N/A | 0 | 0
2021-04-11 17:30 | 6.4791 | 0 | N/A | 0 | 0
2021-04-11 18:00 | 7.1169 | 0 | N/A | 0 | 0
2021-04-11 18:30 | 7.397 | 0 | N/A | 0 | 0
2021-04-11 19:00 | 7.3627 | 0 | N/A | 0 | 0
2021-04-11 19:30 | 7.0209 | 0 | N/A | 0 | 0
2021-04-11 20:00 | 6.459 | 0 | N/A | 0 | 0
2021-04-11 20:30 | 6.1404 | 0 | N/A | 0 | 0
2021-04-11 21:00 | 5.7812 | 0 | N/A | 0 | 0
2021-04-11 21:30 | 6.1797 | 0 | N/A | 0 | 0
2021-04-11 22:00 | 6.2145 | 0 | N/A | 0 | 0
2021-04-11 22:30 | 5.7756 | 0 | N/A | 0 | 0
2021-04-11 23:00 | 5.6505 | 0 | N/A | 0 | 0
2021-04-11 23:30 | 5.8065 | 0 | N/A | 0 | 0
2021-04-12 | 6.1132 | 0 | N/A | 0 | 0
2021-04-12 00:30 | 5.3158 | 0 | N/A | 0 | 0
2021-04-12 01:00 | 4.6268 | 0 | N/A | 0 | 0
2021-04-12 01:30 | 4.4213 | 0 | N/A | 0 | 0
2021-04-12 02:00 | 4.0276 | 0 | N/A | 0 | 0
2021-04-12 02:30 | 3.419 | 0 | N/A | 0 | 0
2021-04-12 03:00 | 3.0746 | 0 | N/A | 0 | 0
2021-04-12 03:30 | 2.9179 | 0 | N/A | 0 | 0
2021-04-12 04:00 | 2.7638 | 0 | N/A | 0 | 0
2021-04-12 04:30 | 2.764 | 0 | N/A | 0 | 0
2021-04-12 05:00 | 2.8134 | 0 | N/A | 0 | 0
2021-04-12 05:30 | 3.1543 | 0 | N/A | 0 | 0
2021-04-12 06:00 | 3.531 | 0 | N/A | 0 | 0
2021-04-12 06:30 | 4.1675 | 0 | N/A | 0 | 0
2021-04-12 07:00 | 4.7182 | 0 | N/A | 0 | 0
2021-04-12 07:30 | 4.9979 | 0 | N/A | 0 | 0
2021-04-12 08:00 | 5.46 | 0 | N/A | 0 | 0
2021-04-12 08:30 | 5.1934 | 0 | N/A | 0 | 0
2021-04-12 09:00 | 4.8036 | 0 | N/A | 0 | 0
2021-04-12 09:30 | 4.6509 | 0 | N/A | 0 | 0
2021-04-12 10:00 | 2.9701 | 0 | N/A | 0 | 0
2021-04-12 10:30 | 3.1344 | 0 | N/A | 0 | 0
2021-04-12 11:00 | 3.6402 | 0 | N/A | 0 | 0
2021-04-12 11:30 | 4.0003 | 0 | N/A | 0 | 0
2021-04-12 12:00 | 3.8528 | 0 | N/A | 0 | 0
2021-04-12 12:30 | 3.2145 | 0 | N/A | 0 | 0
2021-04-12 13:00 | 2.7922 | 0 | N/A | 0 | 0
2021-04-12 13:30 | 4.2753 | 0 | N/A | 0 | 0
2021-04-12 14:00 | 3.7786 | 0 | N/A | 0 | 0
2021-04-12 14:30 | 3.2727 | 0 | N/A | 0 | 0
2021-04-12 15:00 | 3.514 | 0 | N/A | 0 | 0
2021-04-12 15:30 | 3.82 | 0 | N/A | 0 | 0
2021-04-12 16:00 | 4.1968 | 0 | N/A | 0 | 0
2021-04-12 16:30 | 4.6343 | 0 | N/A | 0 | 0
2021-04-12 17:00 | 4.8305 | 0 | N/A | 0 | 0
2021-04-12 17:30 | 5.548 | 0 | N/A | 0 | 0
2021-04-12 18:00 | 6.2097 | 0 | N/A | 0 | 0
2021-04-12 18:30 | 6.6979 | 0 | N/A | 0 | 0
2021-04-12 19:00 | 6.7675 | 0 | N/A | 0 | 0
2021-04-12 19:30 | 6.4296 | 0 | N/A | 0 | 0
2021-04-12 20:00 | 6.0348 | 0 | N/A | 0 | 0
2021-04-12 20:30 | 5.6058 | 0 | N/A | 0 | 0
2021-04-12 21:00 | 5.2357 | 0 | N/A | 0 | 0
2021-04-12 21:30 | 5.6872 | 0 | N/A | 0 | 0
2021-04-12 22:00 | 5.8223 | 0 | N/A | 0 | 0
2021-04-12 22:30 | 5.3988 | 0 | N/A | 0 | 0
2021-04-12 23:00 | 5.2805 | 0 | N/A | 0 | 0
2021-04-12 23:30 | 5.4797 | 0 | N/A | 0 | 0
2021-04-13 | 5.7188 | 0 | N/A | 0 | 0
2021-04-13 00:30 | 4.8652 | 0 | N/A | 0 | 0
2021-04-13 01:00 | 3.9626 | 0 | N/A | 0 | 0
2021-04-13 01:30 | 3.8556 | 0 | N/A | 0 | 0
2021-04-13 02:00 | 3.4681 | 0 | N/A | 0 | 0
2021-04-13 02:30 | 3.0501 | 0 | N/A | 0 | 0
2021-04-13 03:00 | 2.8159 | 0 | N/A | 0 | 0
2021-04-13 03:30 | 2.6378 | 0 | N/A | 0 | 0
2021-04-13 04:00 | 2.5582 | 0 | N/A | 0 | 0
2021-04-13 04:30 | 2.5208 | 0 | N/A | 0 | 0
2021-04-13 05:00 | 2.6383 | 0 | N/A | 0 | 0
2021-04-13 05:30 | 2.8872 | 0 | N/A | 0 | 0
2021-04-13 06:00 | 3.3059 | 0 | N/A | 0 | 0
2021-04-13 06:30 | 4.0334 | 0 | N/A | 0 | 0
2021-04-13 07:00 | 4.6849 | 0 | N/A | 0 | 0
2021-04-13 07:30 | 4.6825 | 0 | N/A | 0 | 0
2021-04-13 08:00 | 4.9816 | 0 | N/A | 0 | 0
2021-04-13 08:30 | 5.1733 | 0 | N/A | 0 | 0
2021-04-13 09:00 | 5.1867 | 0 | N/A | 0 | 0
2021-04-13 09:30 | 5.1734 | 0 | N/A | 0 | 0
2021-04-13 10:00 | 4.6546 | 0 | N/A | 0 | 0
2021-04-13 10:30 | 3.4677 | 0 | N/A | 0 | 0
2021-04-13 11:00 | 4.1873 | 0 | N/A | 0 | 0
2021-04-13 11:30 | 4.1567 | 0 | N/A | 0 | 0
2021-04-13 12:00 | 3.4061 | 0 | N/A | 0 | 0
2021-04-13 12:30 | 3.3501 | 0 | N/A | 0 | 0
2021-04-13 13:00 | 3.1467 | 0 | N/A | 0 | 0
2021-04-13 13:30 | 3.2461 | 0 | N/A | 0 | 0
2021-04-13 14:00 | 4.1818 | 0 | N/A | 0 | 0
2021-04-13 14:30 | 3.2668 | 0 | N/A | 0 | 0
2021-04-13 15:00 | 3.8478 | 0 | N/A | 0 | 0
2021-04-13 15:30 | 4.24 | 0 | N/A | 0 | 0
2021-04-13 16:00 | 4.6167 | 0 | N/A | 0 | 0
2021-04-13 16:30 | 4.647 | 0 | N/A | 0 | 0
2021-04-13 17:00 | 5.3298 | 0 | N/A | 0 | 0
2021-04-13 17:30 | 6.1243 | 0 | N/A | 0 | 0
2021-04-13 18:00 | 6.5807 | 0 | N/A | 0 | 0
2021-04-13 18:30 | 6.9061 | 0 | N/A | 0 | 0
2021-04-13 19:00 | 6.763 | 0 | N/A | 0 | 0
2021-04-13 19:30 | 6.3279 | 0 | N/A | 0 | 0
2021-04-13 20:00 | 5.9544 | 0 | N/A | 0 | 0
2021-04-13 20:30 | 5.6315 | 0 | N/A | 0 | 0
2021-04-13 21:00 | 5.2801 | 0 | N/A | 0 | 0
2021-04-13 21:30 | 5.6518 | 0 | N/A | 0 | 0
2021-04-13 22:00 | 5.8244 | 0 | N/A | 0 | 0
2021-04-13 22:30 | 5.2304 | 0 | N/A | 0 | 0
2021-04-13 23:00 | 5.039 | 0 | N/A | 0 | 0
2021-04-13 23:30 | 5.2444 | 0 | N/A | 0 | 0
2021-04-14 | 5.5769 | 0 | N/A | 0 | 0
2021-04-14 00:30 | 4.7828 | 0 | N/A | 0 | 0
2021-04-14 01:00 | 3.9656 | 0 | N/A | 0 | 0
2021-04-14 01:30 | 3.7014 | 0 | N/A | 0 | 0
2021-04-14 02:00 | 3.331 | 0 | N/A | 0 | 0
2021-04-14 02:30 | 2.8499 | 0 | N/A | 0 | 0
2021-04-14 03:00 | 2.5766 | 0 | N/A | 0 | 0
2021-04-14 03:30 | 2.2925 | 0 | N/A | 0 | 0
2021-04-14 04:00 | 2.2851 | 0 | N/A | 0 | 0
2021-04-14 04:30 | 2.3521 | 0 | N/A | 0 | 0
2021-04-14 05:00 | 2.4743 | 0 | N/A | 0 | 0
2021-04-14 05:30 | 2.6861 | 0 | N/A | 0 | 0
2021-04-14 06:00 | 3.0364 | 0 | N/A | 0 | 0
2021-04-14 06:30 | 3.6514 | 0 | N/A | 0 | 0
2021-04-14 07:00 | 4.1522 | 0 | N/A | 0 | 0
2021-04-14 07:30 | 4.1374 | 0 | N/A | 0 | 0
2021-04-14 08:00 | 4.2585 | 0 | N/A | 0 | 0
2021-04-14 08:30 | 4.7155 | 0 | N/A | 0 | 0
2021-04-14 09:00 | 4.7133 | 0 | N/A | 0 | 0
2021-04-14 09:30 | 4.7167 | 0 | N/A | 0 | 0
2021-04-14 10:00 | 4.36 | 0 | N/A | 0 | 0
2021-04-14 10:30 | 4.4367 | 0 | N/A | 0 | 0
2021-04-14 11:00 | 4.3768 | 0 | N/A | 0 | 0
2021-04-14 11:30 | 4.6901 | 0 | N/A | 0 | 0
2021-04-14 12:00 | 4.52 | 0 | N/A | 0 | 0
2021-04-14 12:30 | 2.9034 | 0 | N/A | 0 | 0
2021-04-14 13:00 | 2.0167 | 0 | N/A | 0 | 0
2021-04-14 13:30 | 3.2772 | 0 | N/A | 0 | 0
2021-04-14 14:00 | 3.4509 | 0 | N/A | 0 | 0
2021-04-14 14:30 | 3.2138 | 0 | N/A | 0 | 0
2021-04-14 15:00 | 2.8834 | 0 | N/A | 0 | 0
2021-04-14 15:30 | 3.8138 | 0 | N/A | 0 | 0
2021-04-14 16:00 | 3.1153 | 0 | N/A | 0 | 0
2021-04-14 16:30 | 3.0773 | 0 | N/A | 0 | 0
2021-04-14 17:00 | 4.068 | 0 | N/A | 0 | 0
2021-04-14 17:30 | 4.7795 | 0 | N/A | 0 | 0
2021-04-14 18:00 | 5.5473 | 0 | N/A | 0 | 0
2021-04-14 18:30 | 6.0413 | 0 | N/A | 0 | 0
2021-04-14 19:00 | 6.0026 | 0 | N/A | 0 | 0
2021-04-14 19:30 | 5.856 | 0 | N/A | 0 | 0
2021-04-14 20:00 | 5.7027 | 0 | N/A | 0 | 0
2021-04-14 20:30 | 5.3419 | 0 | N/A | 0 | 0
2021-04-14 21:00 | 5.1159 | 0 | N/A | 0 | 0
2021-04-14 21:30 | 5.5436 | 0 | N/A | 0 | 0
2021-04-14 22:00 | 5.7682 | 0 | N/A | 0 | 0
2021-04-14 22:30 | 5.1719 | 0 | N/A | 0 | 0
2021-04-14 23:00 | 5.1001 | 0 | N/A | 0 | 0
2021-04-14 23:30 | 5.1833 | 0 | N/A | 0 | 0
2021-04-15 | 5.5328 | 0 | N/A | 0 | 0
2021-04-15 00:30 | 4.6843 | 0 | N/A | 0 | 0
2021-04-15 01:00 | 3.8604 | 0 | N/A | 0 | 0
2021-04-15 01:30 | 3.7532 | 0 | N/A | 0 | 0
2021-04-15 02:00 | 3.2608 | 0 | N/A | 0 | 0
2021-04-15 02:30 | 2.8987 | 0 | N/A | 0 | 0
2021-04-15 03:00 | 2.6249 | 0 | N/A | 0 | 0
2021-04-15 03:30 | 2.4284 | 0 | N/A | 0 | 0
2021-04-15 04:00 | 2.3584 | 0 | N/A | 0 | 0
2021-04-15 04:30 | 2.3231 | 0 | N/A | 0 | 0
2021-04-15 05:00 | 2.3837 | 0 | N/A | 0 | 0
2021-04-15 05:30 | 2.6163 | 0 | N/A | 0 | 0
2021-04-15 06:00 | 3.1022 | 0 | N/A | 0 | 0
2021-04-15 06:30 | 3.6793 | 0 | N/A | 0 | 0
2021-04-15 07:00 | 4.2349 | 0 | N/A | 0 | 0
2021-04-15 07:30 | 4.5067 | 0 | N/A | 0 | 0
2021-04-15 08:00 | 4.8336 | 0 | N/A | 0 | 0
2021-04-15 08:30 | 4.8333 | 0 | N/A | 0 | 0
2021-04-15 09:00 | 4.3141 | 0 | N/A | 0 | 0
2021-04-15 09:30 | 3.8668 | 0 | N/A | 0 | 0
2021-04-15 10:00 | 2.6723 | 0 | N/A | 0 | 0
2021-04-15 10:30 | 2.5898 | 0 | N/A | 0 | 0
2021-04-15 11:00 | 3.0601 | 0 | N/A | 0 | 0
2021-04-15 11:30 | 2.2975 | 0 | N/A | 0 | 0
2021-04-15 12:00 | 1.5654 | 0 | N/A | 0 | 0
2021-04-15 12:30 | 2.2438 | 0 | N/A | 0 | 0
2021-04-15 13:00 | 2.3168 | 0 | N/A | 0 | 0
2021-04-15 13:30 | 2.34 | 0 | N/A | 0 | 0
2021-04-15 14:00 | 3.3 | 0 | N/A | 0 | 0
2021-04-15 14:30 | 4.5733 | 0 | N/A | 0 | 0
2021-04-15 15:00 | 4.4369 | 0 | N/A | 0 | 0
2021-04-15 15:30 | 4.0681 | 0 | N/A | 0 | 0
2021-04-15 16:00 | 3.7802 | 0 | N/A | 0 | 0
2021-04-15 16:30 | 3.7928 | 0 | N/A | 0 | 0
2021-04-15 17:00 | 4.0548 | 0 | N/A | 0 | 0
2021-04-15 17:30 | 4.6772 | 0 | N/A | 0 | 0
2021-04-15 18:00 | 5.9022 | 0 | N/A | 0 | 0
2021-04-15 18:30 | 6.7636 | 0 | N/A | 0 | 0
2021-04-15 19:00 | 6.7501 | 0 | N/A | 0 | 0
2021-04-15 19:30 | 6.522 | 0 | N/A | 0 | 0
2021-04-15 20:00 | 6.1483 | 0 | N/A | 0 | 0
2021-04-15 20:30 | 5.8333 | 0 | N/A | 0 | 0
2021-04-15 21:00 | 5.6648 | 0 | N/A | 0 | 0
2021-04-15 21:30 | 6.024 | 0 | N/A | 0 | 0
2021-04-15 22:00 | 6.075 | 0 | N/A | 0 | 0
2021-04-15 22:30 | 5.5125 | 0 | N/A | 0 | 0
2021-04-15 23:00 | 5.4731 | 0 | N/A | 0 | 0
2021-04-15 23:30 | 5.5916 | 0 | N/A | 0 | 0
2021-04-16 | 5.7597 | 0 | N/A | 0 | 0
2021-04-16 00:30 | 4.9267 | 0 | N/A | 0 | 0
2021-04-16 01:00 | 4.1853 | 0 | N/A | 0 | 0
2021-04-16 01:30 | 3.9714 | 0 | N/A | 0 | 0
2021-04-16 02:00 | 3.6994 | 0 | N/A | 0 | 0
2021-04-16 02:30 | 3.1791 | 0 | N/A | 0 | 0
2021-04-16 03:00 | 2.8343 | 0 | N/A | 0 | 0
2021-04-16 03:30 | 2.7197 | 0 | N/A | 0 | 0
2021-04-16 04:00 | 2.6243 | 0 | N/A | 0 | 0
2021-04-16 04:30 | 2.6027 | 0 | N/A | 0 | 0
2021-04-16 05:00 | 2.6485 | 0 | N/A | 0 | 0
2021-04-16 05:30 | 2.9551 | 0 | N/A | 0 | 0
2021-04-16 06:00 | 3.3317 | 0 | N/A | 0 | 0
2021-04-16 06:30 | 4.044 | 0 | N/A | 0 | 0
2021-04-16 07:00 | 4.5037 | 0 | N/A | 0 | 0
2021-04-16 07:30 | 4.7366 | 0 | N/A | 0 | 0
2021-04-16 08:00 | 5.3004 | 0 | N/A | 0 | 0
2021-04-16 08:30 | 5.3067 | 0 | N/A | 0 | 0
2021-04-16 09:00 | 4.91 | 0 | N/A | 0 | 0
2021-04-16 09:30 | 4.6834 | 0 | N/A | 0 | 0
2021-04-16 10:00 | 4.0934 | 0 | N/A | 0 | 0
2021-04-16 10:30 | 4.7234 | 0 | N/A | 0 | 0
2021-04-16 11:00 | 5.4167 | 0 | N/A | 0 | 0
2021-04-16 11:30 | 4.6339 | 0 | N/A | 0 | 0
2021-04-16 12:00 | 4.4971 | 0 | N/A | 0 | 0
2021-04-16 12:30 | 4.5067 | 0 | N/A | 0 | 0
2021-04-16 13:00 | 4.0327 | 0 | N/A | 0 | 0
2021-04-16 13:30 | 4.155 | 0 | N/A | 0 | 0
2021-04-16 14:00 | 4.029 | 0 | N/A | 0 | 0
2021-04-16 14:30 | 3.5482 | 0 | N/A | 0 | 0
2021-04-16 15:00 | 3.8084 | 0 | N/A | 0 | 0
2021-04-16 15:30 | 4.1462 | 0 | N/A | 0 | 0
2021-04-16 16:00 | 4.3224 | 0 | N/A | 0 | 0
2021-04-16 16:30 | 4.5527 | 0 | N/A | 0 | 0
2021-04-16 17:00 | 4.8038 | 0 | N/A | 0 | 0
2021-04-16 17:30 | 5.5236 | 0 | N/A | 0 | 0
2021-04-16 18:00 | 6.1435 | 0 | N/A | 0 | 0
2021-04-16 18:30 | 6.4493 | 0 | N/A | 0 | 0
2021-04-16 19:00 | 6.5284 | 0 | N/A | 0 | 0
2021-04-16 19:30 | 6.4121 | 0 | N/A | 0 | 0
2021-04-16 20:00 | 6.17 | 0 | N/A | 0 | 0
2021-04-16 20:30 | 5.8817 | 0 | N/A | 0 | 0
2021-04-16 21:00 | 5.6411 | 0 | N/A | 0 | 0
2021-04-16 21:30 | 6.0145 | 0 | N/A | 0 | 0
2021-04-16 22:00 | 6.3286 | 0 | N/A | 0 | 0
2021-04-16 22:30 | 5.8875 | 0 | N/A | 0 | 0
2021-04-16 23:00 | 5.8315 | 0 | N/A | 0 | 0
2021-04-16 23:30 | 5.7822 | 0 | N/A | 0 | 0
2021-04-17 | 5.9733 | 0 | N/A | 0 | 0
2021-04-17 00:30 | 5.1909 | 0 | N/A | 0 | 0
2021-04-17 01:00 | 4.4098 | 0 | N/A | 0 | 0
2021-04-17 01:30 | 4.2383 | 0 | N/A | 0 | 0
2021-04-17 02:00 | 3.7518 | 0 | N/A | 0 | 0
2021-04-17 02:30 | 3.1557 | 0 | N/A | 0 | 0
2021-04-17 03:00 | 2.8529 | 0 | N/A | 0 | 0
2021-04-17 03:30 | 2.7608 | 0 | N/A | 0 | 0
2021-04-17 04:00 | 2.6101 | 0 | N/A | 0 | 0
2021-04-17 04:30 | 2.5227 | 0 | N/A | 0 | 0
2021-04-17 05:00 | 2.504 | 0 | N/A | 0 | 0
2021-04-17 05:30 | 2.5737 | 0 | N/A | 0 | 0
2021-04-17 06:00 | 2.766 | 0 | N/A | 0 | 0
2021-04-17 06:30 | 3.0976 | 0 | N/A | 0 | 0
2021-04-17 07:00 | 3.3349 | 0 | N/A | 0 | 0
2021-04-17 07:30 | 3.4631 | 0 | N/A | 0 | 0
2021-04-17 08:00 | 3.7537 | 0 | N/A | 0 | 0
2021-04-17 08:30 | 3.9154 | 0 | N/A | 0 | 0
2021-04-17 09:00 | 3.7916 | 0 | N/A | 0 | 0
2021-04-17 09:30 | 3.8154 | 0 | N/A | 0 | 0
2021-04-17 10:00 | 3.2947 | 0 | N/A | 0 | 0
2021-04-17 10:30 | 3.0151 | 0 | N/A | 0 | 0
2021-04-17 11:00 | 3.0487 | 0 | N/A | 0 | 0
2021-04-17 11:30 | 2.9018 | 0 | N/A | 0 | 0
2021-04-17 12:00 | 2.1691 | 0 | N/A | 0 | 0
2021-04-17 12:30 | 2.3276 | 0 | N/A | 0 | 0
2021-04-17 13:00 | 2.3469 | 0 | N/A | 0 | 0
2021-04-17 13:30 | 2.3292 | 0 | N/A | 0 | 0
2021-04-17 14:00 | 2.2189 | 0 | N/A | 0 | 0
2021-04-17 14:30 | 2.0355 | 0 | N/A | 0 | 0
2021-04-17 15:00 | 2.6526 | 0 | N/A | 0 | 0
2021-04-17 15:30 | 2.4718 | 0 | N/A | 0 | 0
2021-04-17 16:00 | 2.8627 | 0 | N/A | 0 | 0
2021-04-17 16:30 | 3.4817 | 0 | N/A | 0 | 0
2021-04-17 17:00 | 4.0871 | 0 | N/A | 0 | 0
2021-04-17 17:30 | 4.9039 | 0 | N/A | 0 | 0
2021-04-17 18:00 | 5.5891 | 0 | N/A | 0 | 0
2021-04-17 18:30 | 5.9791 | 0 | N/A | 0 | 0
2021-04-17 19:00 | 5.9914 | 0 | N/A | 0 | 0
2021-04-17 19:30 | 5.7403 | 0 | N/A | 0 | 0
2021-04-17 20:00 | 5.373 | 0 | N/A | 0 | 0
2021-04-17 20:30 | 5.07 | 0 | N/A | 0 | 0
2021-04-17 21:00 | 4.8909 | 0 | N/A | 0 | 0
2021-04-17 21:30 | 5.3983 | 0 | N/A | 0 | 0
2021-04-17 22:00 | 5.6186 | 0 | N/A | 0 | 0
2021-04-17 22:30 | 5.2974 | 0 | N/A | 0 | 0
2021-04-17 23:00 | 5.3099 | 0 | N/A | 0 | 0
2021-04-17 23:30 | 5.5646 | 0 | N/A | 0 | 0
2021-04-18 | 5.9404 | 0 | N/A | 0 | 0
2021-04-18 00:30 | 5.1463 | 0 | N/A | 0 | 0
2021-04-18 01:00 | 4.3094 | 0 | N/A | 0 | 0
2021-04-18 01:30 | 4.1203 | 0 | N/A | 0 | 0
2021-04-18 02:00 | 3.6191 | 0 | N/A | 0 | 0
2021-04-18 02:30 | 3.0779 | 0 | N/A | 0 | 0
2021-04-18 03:00 | 2.7586 | 0 | N/A | 0 | 0
2021-04-18 03:30 | 2.5627 | 0 | N/A | 0 | 0
2021-04-18 04:00 | 2.421 | 0 | N/A | 0 | 0
2021-04-18 04:30 | 2.3413 | 0 | N/A | 0 | 0
2021-04-18 05:00 | 2.3603 | 0 | N/A | 0 | 0
2021-04-18 05:30 | 2.4079 | 0 | N/A | 0 | 0
2021-04-18 06:00 | 2.5273 | 0 | N/A | 0 | 0
2021-04-18 06:30 | 2.7734 | 0 | N/A | 0 | 0
2021-04-18 07:00 | 2.947 | 0 | N/A | 0 | 0
2021-04-18 07:30 | 2.8894 | 0 | N/A | 0 | 0
2021-04-18 08:00 | 3.0906 | 0 | N/A | 0 | 0
2021-04-18 08:30 | 3.3195 | 0 | N/A | 0 | 0
2021-04-18 09:00 | 3.3747 | 0 | N/A | 0 | 0
2021-04-18 09:30 | 3.092 | 0 | N/A | 0 | 0
2021-04-18 10:00 | 2.853 | 0 | N/A | 0 | 0
2021-04-18 10:30 | 2.746 | 0 | N/A | 0 | 0
2021-04-18 11:00 | 2.8489 | 0 | N/A | 0 | 0
2021-04-18 11:30 | 2.622 | 0 | N/A | 0 | 0
2021-04-18 12:00 | 2.9705 | 0 | N/A | 0 | 0
2021-04-18 12:30 | 3.3872 | 0 | N/A | 0 | 0
2021-04-18 13:00 | 3.3921 | 0 | N/A | 0 | 0
2021-04-18 13:30 | 3.5401 | 0 | N/A | 0 | 0
2021-04-18 14:00 | 3.5456 | 0 | N/A | 0 | 0
2021-04-18 14:30 | 3.5395 | 0 | N/A | 0 | 0
2021-04-18 15:00 | 3.8462 | 0 | N/A | 0 | 0
2021-04-18 15:30 | 4.3082 | 0 | N/A | 0 | 0
2021-04-18 16:00 | 4.615 | 0 | N/A | 0 | 0
2021-04-18 16:30 | 4.7758 | 0 | N/A | 0 | 0
2021-04-18 17:00 | 5.2568 | 0 | N/A | 0 | 0
2021-04-18 17:30 | 5.7758 | 0 | N/A | 0 | 0
2021-04-18 18:00 | 6.5317 | 0 | N/A | 0 | 0
2021-04-18 18:30 | 6.6843 | 0 | N/A | 0 | 0
2021-04-18 19:00 | 6.5685 | 0 | N/A | 0 | 0
2021-04-18 19:30 | 6.169 | 0 | N/A | 0 | 0
2021-04-18 20:00 | 5.773 | 0 | N/A | 0 | 0
2021-04-18 20:30 | 5.386 | 0 | N/A | 0 | 0
2021-04-18 21:00 | 5.0203 | 0 | N/A | 0 | 0
2021-04-18 21:30 | 5.4074 | 0 | N/A | 0 | 0
2021-04-18 22:00 | 5.6473 | 0 | N/A | 0 | 0
2021-04-18 22:30 | 5.1632 | 0 | N/A | 0 | 0
2021-04-18 23:00 | 5.0751 | 0 | N/A | 0 | 0
2021-04-18 23:30 | 5.3237 | 0 | N/A | 0 | 0
2021-04-19 | 5.6148 | 0 | N/A | 0 | 0
2021-04-19 00:30 | 4.8338 | 0 | N/A | 0 | 0
2021-04-19 01:00 | 4.1275 | 0 | N/A | 0 | 0
2021-04-19 01:30 | 4.0622 | 0 | N/A | 0 | 0
2021-04-19 02:00 | 3.6423 | 0 | N/A | 0 | 0
2021-04-19 02:30 | 3.0952 | 0 | N/A | 0 | 0
2021-04-19 03:00 | 2.7111 | 0 | N/A | 0 | 0
2021-04-19 03:30 | 2.5168 | 0 | N/A | 0 | 0
2021-04-19 04:00 | 2.493 | 0 | N/A | 0 | 0
2021-04-19 04:30 | 2.4407 | 0 | N/A | 0 | 0
2021-04-19 05:00 | 2.5367 | 0 | N/A | 0 | 0
2021-04-19 05:30 | 2.8102 | 0 | N/A | 0 | 0
2021-04-19 06:00 | 3.279 | 0 | N/A | 0 | 0
2021-04-19 06:30 | 3.9569 | 0 | N/A | 0 | 0
2021-04-19 07:00 | 4.7072 | 0 | N/A | 0 | 0
2021-04-19 07:30 | 4.8074 | 0 | N/A | 0 | 0
2021-04-19 08:00 | 5.0136 | 0 | N/A | 0 | 0
2021-04-19 08:30 | 4.7899 | 0 | N/A | 0 | 0
2021-04-19 09:00 | 4.3422 | 0 | N/A | 0 | 0
2021-04-19 09:30 | 4.0031 | 0 | N/A | 0 | 0
2021-04-19 10:00 | 3.8172 | 0 | N/A | 0 | 0
2021-04-19 10:30 | 3.3113 | 0 | N/A | 0 | 0
2021-04-19 11:00 | 2.5909 | 0 | N/A | 0 | 0
2021-04-19 11:30 | 1.4935 | 0 | N/A | 0 | 0
2021-04-19 12:00 | 1.4204 | 0 | N/A | 0 | 0
2021-04-19 12:30 | 2.4034 | 0 | N/A | 0 | 0
2021-04-19 13:00 | 2.8576 | 0 | N/A | 0 | 0
2021-04-19 13:30 | 2.8501 | 0 | N/A | 0 | 0
2021-04-19 14:00 | 2.9133 | 0 | N/A | 0 | 0
2021-04-19 14:30 | 3.62 | 0 | N/A | 0 | 0
2021-04-19 15:00 | 3.5867 | 0 | N/A | 0 | 0
2021-04-19 15:30 | 3.3467 | 0 | N/A | 0 | 0
2021-04-19 16:00 | 3.6723 | 0 | N/A | 0 | 0
2021-04-19 16:30 | 4.2692 | 0 | N/A | 0 | 0
2021-04-19 17:00 | 4.8555 | 0 | N/A | 0 | 0
2021-04-19 17:30 | 5.7388 | 0 | N/A | 0 | 0
2021-04-19 18:00 | 6.4965 | 0 | N/A | 0 | 0
2021-04-19 18:30 | 6.8242 | 0 | N/A | 0 | 0
2021-04-19 19:00 | 6.7623 | 0 | N/A | 0 | 0
2021-04-19 19:30 | 6.3292 | 0 | N/A | 0 | 0
2021-04-19 20:00 | 6.0026 | 0 | N/A | 0 | 0
2021-04-19 20:30 | 5.6464 | 0 | N/A | 0 | 0
2021-04-19 21:00 | 5.2881 | 0 | N/A | 0 | 0
2021-04-19 21:30 | 5.5516 | 0 | N/A | 0 | 0
2021-04-19 22:00 | 5.607 | 0 | N/A | 0 | 0
2021-04-19 22:30 | 5.0781 | 0 | N/A | 0 | 0
2021-04-19 23:00 | 5.0094 | 0 | N/A | 0 | 0
2021-04-19 23:30 | 5.2518 | 0 | N/A | 0 | 0
2021-04-20 | 5.5577 | 0 | N/A | 0 | 0
2021-04-20 00:30 | 4.6905 | 0 | N/A | 0 | 0
2021-04-20 01:00 | 3.8742 | 0 | N/A | 0 | 0
2021-04-20 01:30 | 3.6805 | 0 | N/A | 0 | 0
2021-04-20 02:00 | 3.2992 | 0 | N/A | 0 | 0
2021-04-20 02:30 | 2.8333 | 0 | N/A | 0 | 0
2021-04-20 03:00 | 2.624 | 0 | N/A | 0 | 0
2021-04-20 03:30 | 2.4308 | 0 | N/A | 0 | 0
2021-04-20 04:00 | 2.3219 | 0 | N/A | 0 | 0
2021-04-20 04:30 | 2.2884 | 0 | N/A | 0 | 0
2021-04-20 05:00 | 2.388 | 0 | N/A | 0 | 0
2021-04-20 05:30 | 2.7634 | 0 | N/A | 0 | 0
2021-04-20 06:00 | 3.1473 | 0 | N/A | 0 | 0
2021-04-20 06:30 | 3.7647 | 0 | N/A | 0 | 0
2021-04-20 07:00 | 4.6003 | 0 | N/A | 0 | 0
2021-04-20 07:30 | 5.1334 | 0 | N/A | 0 | 0
2021-04-20 08:00 | 5.2404 | 0 | N/A | 0 | 0
2021-04-20 08:30 | 4.812 | 0 | N/A | 0 | 0
2021-04-20 09:00 | 4.2105 | 0 | N/A | 0 | 0
2021-04-20 09:30 | 4.3435 | 0 | N/A | 0 | 0
2021-04-20 10:00 | 5.2067 | 0 | N/A | 0 | 0
2021-04-20 10:30 | 5.4811 | 0 | N/A | 0 | 0
2021-04-20 11:00 | 6.3672 | 0 | N/A | 0 | 0
2021-04-20 11:30 | 6.3706 | 0 | N/A | 0 | 0
2021-04-20 12:00 | 6.514 | 0 | N/A | 0 | 0
2021-04-20 12:30 | 6.6242 | 0 | N/A | 0 | 0
2021-04-20 13:00 | 6.0989 | 0 | N/A | 0 | 0
2021-04-20 13:30 | 5.8476 | 0 | N/A | 0 | 0
2021-04-20 14:00 | 5.5446 | 0 | N/A | 0 | 0
2021-04-20 14:30 | 5.5804 | 0 | N/A | 0 | 0
2021-04-20 15:00 | 5.2723 | 0 | N/A | 0 | 0
2021-04-20 15:30 | 3.9475 | 0 | N/A | 0 | 0
2021-04-20 16:00 | 4.9048 | 0 | N/A | 0 | 0
2021-04-20 16:30 | 5.5331 | 0 | N/A | 0 | 0
2021-04-20 17:00 | 5.7666 | 0 | N/A | 0 | 0
2021-04-20 17:30 | 6.5374 | 0 | N/A | 0 | 0
2021-04-20 18:00 | 7.4985 | 0 | N/A | 0 | 0
2021-04-20 18:30 | 8.0067 | 0 | N/A | 0 | 0
2021-04-20 19:00 | 8.06 | 0 | N/A | 0 | 0
2021-04-20 19:30 | 7.7203 | 0 | N/A | 0 | 0
2021-04-20 20:00 | 7.4969 | 0 | N/A | 0 | 0
2021-04-20 20:30 | 7.1282 | 0 | N/A | 0 | 0
2021-04-20 21:00 | 6.6023 | 0 | N/A | 0 | 0
2021-04-20 21:30 | 6.9106 | 0 | N/A | 0 | 0
2021-04-20 22:00 | 7.0474 | 0 | N/A | 0 | 0
2021-04-20 22:30 | 6.4702 | 0 | N/A | 0 | 0
2021-04-20 23:00 | 6.3157 | 0 | N/A | 0 | 0
2021-04-20 23:30 | 6.4277 | 0 | N/A | 0 | 0
2021-04-21 | 6.7077 | 0 | N/A | 0 | 0
2021-04-21 00:30 | 5.8821 | 0 | N/A | 0 | 0
2021-04-21 01:00 | 5.0638 | 0 | N/A | 0 | 0
2021-04-21 01:30 | 4.9328 | 0 | N/A | 0 | 0
2021-04-21 02:00 | 4.5287 | 0 | N/A | 0 | 0
2021-04-21 02:30 | 3.9838 | 0 | N/A | 0 | 0
2021-04-21 03:00 | 3.7131 | 0 | N/A | 0 | 0
2021-04-21 03:30 | 3.5181 | 0 | N/A | 0 | 0
2021-04-21 04:00 | 3.3308 | 0 | N/A | 0 | 0
2021-04-21 04:30 | 3.3656 | 0 | N/A | 0 | 0
2021-04-21 05:00 | 3.5367 | 0 | N/A | 0 | 0
2021-04-21 05:30 | 3.8983 | 0 | N/A | 0 | 0
2021-04-21 06:00 | 4.4292 | 0 | N/A | 0 | 0
2021-04-21 06:30 | 5.5087 | 0 | N/A | 0 | 0
2021-04-21 07:00 | 6.3344 | 0 | N/A | 0 | 0
2021-04-21 07:30 | 6.7635 | 0 | N/A | 0 | 0
2021-04-21 08:00 | 7.3238 | 0 | N/A | 0 | 0
2021-04-21 08:30 | 6.9619 | 0 | N/A | 0 | 0
2021-04-21 09:00 | 5.8989 | 0 | N/A | 0 | 0
2021-04-21 09:30 | 4.659 | 0 | N/A | 0 | 0
2021-04-21 10:00 | 3.878 | 0 | N/A | 0 | 0
2021-04-21 10:30 | 2.9837 | 0 | N/A | 0 | 0
2021-04-21 11:00 | 3.385 | 0 | N/A | 0 | 0
2021-04-21 11:30 | 3.2529 | 0 | N/A | 0 | 0
2021-04-21 12:00 | 2.7567 | 0 | N/A | 0 | 0
2021-04-21 12:30 | 3.6267 | 0 | N/A | 0 | 0
2021-04-21 13:00 | 3.647 | 0 | N/A | 0 | 0
2021-04-21 13:30 | 4.2119 | 0 | N/A | 0 | 0
2021-04-21 14:00 | 4.3834 | 0 | N/A | 0 | 0
2021-04-21 14:30 | 4.3717 | 0 | N/A | 0 | 0
2021-04-21 15:00 | 4.7772 | 0 | N/A | 0 | 0
2021-04-21 15:30 | 4.766 | 0 | N/A | 0 | 0
2021-04-21 16:00 | 5.0434 | 0 | N/A | 0 | 0
2021-04-21 16:30 | 5.2714 | 0 | N/A | 0 | 0
2021-04-21 17:00 | 5.6842 | 0 | N/A | 0 | 0
2021-04-21 17:30 | 6.5896 | 0 | N/A | 0 | 0
2021-04-21 18:00 | 7.1965 | 0 | N/A | 0 | 0
2021-04-21 18:30 | 7.8072 | 0 | N/A | 0 | 0
2021-04-21 19:00 | 7.8633 | 0 | N/A | 0 | 0
2021-04-21 19:30 | 7.6237 | 0 | N/A | 0 | 0
2021-04-21 20:00 | 7.3074 | 0 | N/A | 0 | 0
2021-04-21 20:30 | 6.8796 | 0 | N/A | 0 | 0
2021-04-21 21:00 | 6.4365 | 0 | N/A | 0 | 0
2021-04-21 21:30 | 6.677 | 0 | N/A | 0 | 0
2021-04-21 22:00 | 6.6682 | 0 | N/A | 0 | 0
2021-04-21 22:30 | 6.2201 | 0 | N/A | 0 | 0
2021-04-21 23:00 | 5.9232 | 0 | N/A | 0 | 0
2021-04-21 23:30 | 6.0553 | 0 | N/A | 0 | 0
2021-04-22 | 6.3397 | 0 | N/A | 0 | 0
2021-04-22 00:30 | 5.4439 | 0 | N/A | 0 | 0
2021-04-22 01:00 | 4.6396 | 0 | N/A | 0 | 0
2021-04-22 01:30 | 4.4592 | 0 | N/A | 0 | 0
2021-04-22 02:00 | 4.0539 | 0 | N/A | 0 | 0
2021-04-22 02:30 | 3.4998 | 0 | N/A | 0 | 0
2021-04-22 03:00 | 3.1215 | 0 | N/A | 0 | 0
2021-04-22 03:30 | 2.9084 | 0 | N/A | 0 | 0
2021-04-22 04:00 | 2.775 | 0 | N/A | 0 | 0
2021-04-22 04:30 | 2.7857 | 0 | N/A | 0 | 0
2021-04-22 05:00 | 2.9487 | 0 | N/A | 0 | 0
2021-04-22 05:30 | 3.2751 | 0 | N/A | 0 | 0
2021-04-22 06:00 | 3.7996 | 0 | N/A | 0 | 0
2021-04-22 06:30 | 4.45 | 0 | N/A | 0 | 0
2021-04-22 07:00 | 5.3893 | 0 | N/A | 0 | 0
2021-04-22 07:30 | 6.2278 | 0 | N/A | 0 | 0
2021-04-22 08:00 | 6.3709 | 0 | N/A | 0 | 0
2021-04-22 08:30 | 6.2095 | 0 | N/A | 0 | 0
2021-04-22 09:00 | 5.8274 | 0 | N/A | 0 | 0
2021-04-22 09:30 | 5.9575 | 0 | N/A | 0 | 0
2021-04-22 10:00 | 5.3418 | 0 | N/A | 0 | 0
2021-04-22 10:30 | 4.7943 | 0 | N/A | 0 | 0
2021-04-22 11:00 | 4.5974 | 0 | N/A | 0 | 0
2021-04-22 11:30 | 4.0129 | 0 | N/A | 0 | 0
2021-04-22 12:00 | 3.8801 | 0 | N/A | 0 | 0
2021-04-22 12:30 | 3.8271 | 0 | N/A | 0 | 0
2021-04-22 13:00 | 3.917 | 0 | N/A | 0 | 0
2021-04-22 13:30 | 4.1071 | 0 | N/A | 0 | 0
2021-04-22 14:00 | 3.3657 | 0 | N/A | 0 | 0
2021-04-22 14:30 | 4.4137 | 0 | N/A | 0 | 0
2021-04-22 15:00 | 4.2572 | 0 | N/A | 0 | 0
2021-04-22 15:30 | 4.5919 | 0 | N/A | 0 | 0
2021-04-22 16:00 | 4.6124 | 0 | N/A | 0 | 0
2021-04-22 16:30 | 5.0017 | 0 | N/A | 0 | 0
2021-04-22 17:00 | 5.561 | 0 | N/A | 0 | 0
2021-04-22 17:30 | 6.0763 | 0 | N/A | 0 | 0
2021-04-22 18:00 | 6.7162 | 0 | N/A | 0 | 0
2021-04-22 18:30 | 7.2706 | 0 | N/A | 0 | 0
2021-04-22 19:00 | 7.3601 | 0 | N/A | 0 | 0
2021-04-22 19:30 | 7.0706 | 0 | N/A | 0 | 0
2021-04-22 20:00 | 6.7644 | 0 | N/A | 0 | 0
2021-04-22 20:30 | 6.4608 | 0 | N/A | 0 | 0
2021-04-22 21:00 | 6.056 | 0 | N/A | 0 | 0
2021-04-22 21:30 | 6.1613 | 0 | N/A | 0 | 0
2021-04-22 22:00 | 6.3349 | 0 | N/A | 0 | 0
2021-04-22 22:30 | 5.9112 | 0 | N/A | 0 | 0
2021-04-22 23:00 | 5.8565 | 0 | N/A | 0 | 0
2021-04-22 23:30 | 5.8191 | 0 | N/A | 0 | 0
2021-04-23 | 6.0837 | 0 | N/A | 0 | 0
2021-04-23 00:30 | 5.0689 | 0 | N/A | 0 | 0
2021-04-23 01:00 | 4.367 | 0 | N/A | 0 | 0
2021-04-23 01:30 | 4.2323 | 0 | N/A | 0 | 0
2021-04-23 02:00 | 3.7525 | 0 | N/A | 0 | 0
2021-04-23 02:30 | 3.2072 | 0 | N/A | 0 | 0
2021-04-23 03:00 | 2.9812 | 0 | N/A | 0 | 0
2021-04-23 03:30 | 2.7525 | 0 | N/A | 0 | 0
2021-04-23 04:00 | 2.6871 | 0 | N/A | 0 | 0
2021-04-23 04:30 | 2.5979 | 0 | N/A | 0 | 0
2021-04-23 05:00 | 2.7681 | 0 | N/A | 0 | 0
2021-04-23 05:30 | 3.0115 | 0 | N/A | 0 | 0
2021-04-23 06:00 | 3.4346 | 0 | N/A | 0 | 0
2021-04-23 06:30 | 4.214 | 0 | N/A | 0 | 0
2021-04-23 07:00 | 5.0627 | 0 | N/A | 0 | 0
2021-04-23 07:30 | 5.4543 | 0 | N/A | 0 | 0
2021-04-23 08:00 | 5.6869 | 0 | N/A | 0 | 0
2021-04-23 08:30 | 5.6234 | 0 | N/A | 0 | 0
2021-04-23 09:00 | 5.2567 | 0 | N/A | 0 | 0
2021-04-23 09:30 | 4.8167 | 0 | N/A | 0 | 0
2021-04-23 10:00 | 3.9667 | 0 | N/A | 0 | 0
2021-04-23 10:30 | 3.2501 | 0 | N/A | 0 | 0
2021-04-23 11:00 | 3.6067 | 0 | N/A | 0 | 0
2021-04-23 11:30 | 4.33 | 0 | N/A | 0 | 0
2021-04-23 12:00 | 4.0167 | 0 | N/A | 0 | 0
2021-04-23 12:30 | 3.8333 | 0 | N/A | 0 | 0
2021-04-23 13:00 | 4.3267 | 0 | N/A | 0 | 0
2021-04-23 13:30 | 4.24 | 0 | N/A | 0 | 0
2021-04-23 14:00 | 3.8097 | 0 | N/A | 0 | 0
2021-04-23 14:30 | 3.7823 | 0 | N/A | 0 | 0
2021-04-23 15:00 | 4.1686 | 0 | N/A | 0 | 0
2021-04-23 15:30 | 4.3306 | 0 | N/A | 0 | 0
2021-04-23 16:00 | 4.3946 | 0 | N/A | 0 | 0
2021-04-23 16:30 | 4.6176 | 0 | N/A | 0 | 0
2021-04-23 17:00 | 5.2189 | 0 | N/A | 0 | 0
2021-04-23 17:30 | 5.7829 | 0 | N/A | 0 | 0
2021-04-23 18:00 | 6.4543 | 0 | N/A | 0 | 0
2021-04-23 18:30 | 6.581 | 0 | N/A | 0 | 0
2021-04-23 19:00 | 6.6266 | 0 | N/A | 0 | 0
2021-04-23 19:30 | 6.3415 | 0 | N/A | 0 | 0
2021-04-23 20:00 | 6.0017 | 0 | N/A | 0 | 0
2021-04-23 20:30 | 5.9037 | 0 | N/A | 0 | 0
2021-04-23 21:00 | 5.739 | 0 | N/A | 0 | 0
2021-04-23 21:30 | 6.1324 | 0 | N/A | 0 | 0
2021-04-23 22:00 | 6.3007 | 0 | N/A | 0 | 0
2021-04-23 22:30 | 5.852 | 0 | N/A | 0 | 0
2021-04-23 23:00 | 5.8534 | 0 | N/A | 0 | 0
2021-04-23 23:30 | 5.9555 | 0 | N/A | 0 | 0
2021-04-24 | 6.2171 | 0 | N/A | 0 | 0
2021-04-24 00:30 | 5.3007 | 0 | N/A | 0 | 0
2021-04-24 01:00 | 4.4176 | 0 | N/A | 0 | 0
2021-04-24 01:30 | 4.2492 | 0 | N/A | 0 | 0
2021-04-24 02:00 | 3.8491 | 0 | N/A | 0 | 0
2021-04-24 02:30 | 3.1675 | 0 | N/A | 0 | 0
2021-04-24 03:00 | 2.8336 | 0 | N/A | 0 | 0
2021-04-24 03:30 | 2.7473 | 0 | N/A | 0 | 0
2021-04-24 04:00 | 2.6342 | 0 | N/A | 0 | 0
2021-04-24 04:30 | 2.5406 | 0 | N/A | 0 | 0
2021-04-24 05:00 | 2.5785 | 0 | N/A | 0 | 0
2021-04-24 05:30 | 2.6904 | 0 | N/A | 0 | 0
2021-04-24 06:00 | 2.9175 | 0 | N/A | 0 | 0
2021-04-24 06:30 | 3.2047 | 0 | N/A | 0 | 0
2021-04-24 07:00 | 3.5061 | 0 | N/A | 0 | 0
2021-04-24 07:30 | 3.572 | 0 | N/A | 0 | 0
2021-04-24 08:00 | 3.736 | 0 | N/A | 0 | 0
2021-04-24 08:30 | 4.0807 | 0 | N/A | 0 | 0
2021-04-24 09:00 | 3.825 | 0 | N/A | 0 | 0
2021-04-24 09:30 | 3.4771 | 0 | N/A | 0 | 0
2021-04-24 10:00 | 3.6529 | 0 | N/A | 0 | 0
2021-04-24 10:30 | 2.1456 | 0 | N/A | 0 | 0
2021-04-24 11:00 | 2.4823 | 0 | N/A | 0 | 0
2021-04-24 11:30 | 1.8205 | 0 | N/A | 0 | 0
2021-04-24 12:00 | 2.4647 | 0 | N/A | 0 | 0
2021-04-24 12:30 | 3.2978 | 0 | N/A | 0 | 0
2021-04-24 13:00 | 2.594 | 0 | N/A | 0 | 0
2021-04-24 13:30 | 2.5931 | 0 | N/A | 0 | 0
2021-04-24 14:00 | 2.1837 | 0 | N/A | 0 | 0
2021-04-24 14:30 | 2.951 | 0 | N/A | 0 | 0
2021-04-24 15:00 | 3.6151 | 0 | N/A | 0 | 0
2021-04-24 15:30 | 2.9594 | 0 | N/A | 0 | 0
2021-04-24 16:00 | 3.6084 | 0 | N/A | 0 | 0
2021-04-24 16:30 | 3.7656 | 0 | N/A | 0 | 0
2021-04-24 17:00 | 4.4496 | 0 | N/A | 0 | 0
2021-04-24 17:30 | 5.2104 | 0 | N/A | 0 | 0
2021-04-24 18:00 | 5.9612 | 0 | N/A | 0 | 0
2021-04-24 18:30 | 6.3336 | 0 | N/A | 0 | 0
2021-04-24 19:00 | 6.2369 | 0 | N/A | 0 | 0
2021-04-24 19:30 | 5.9649 | 0 | N/A | 0 | 0
2021-04-24 20:00 | 5.653 | 0 | N/A | 0 | 0
2021-04-24 20:30 | 5.342 | 0 | N/A | 0 | 0
2021-04-24 21:00 | 5.1138 | 0 | N/A | 0 | 0
2021-04-24 21:30 | 5.5527 | 0 | N/A | 0 | 0
2021-04-24 22:00 | 5.8177 | 0 | N/A | 0 | 0
2021-04-24 22:30 | 5.4874 | 0 | N/A | 0 | 0
2021-04-24 23:00 | 5.5991 | 0 | N/A | 0 | 0
2021-04-24 23:30 | 5.8475 | 0 | N/A | 0 | 0
2021-04-25 | 6.0751 | 0 | N/A | 0 | 0
2021-04-25 00:30 | 5.2012 | 0 | N/A | 0 | 0
2021-04-25 01:00 | 4.4158 | 0 | N/A | 0 | 0
2021-04-25 01:30 | 4.3298 | 0 | N/A | 0 | 0
2021-04-25 02:00 | 3.8106 | 0 | N/A | 0 | 0
2021-04-25 02:30 | 3.2694 | 0 | N/A | 0 | 0
2021-04-25 03:00 | 2.971 | 0 | N/A | 0 | 0
2021-04-25 03:30 | 2.8137 | 0 | N/A | 0 | 0
2021-04-25 04:00 | 2.629 | 0 | N/A | 0 | 0
2021-04-25 04:30 | 2.6181 | 0 | N/A | 0 | 0
2021-04-25 05:00 | 2.5902 | 0 | N/A | 0 | 0
2021-04-25 05:30 | 2.7554 | 0 | N/A | 0 | 0
2021-04-25 06:00 | 2.7988 | 0 | N/A | 0 | 0
2021-04-25 06:30 | 2.9217 | 0 | N/A | 0 | 0
2021-04-25 07:00 | 3.0935 | 0 | N/A | 0 | 0
2021-04-25 07:30 | 3.1191 | 0 | N/A | 0 | 0
2021-04-25 08:00 | 3.4215 | 0 | N/A | 0 | 0
2021-04-25 08:30 | 3.7382 | 0 | N/A | 0 | 0
2021-04-25 09:00 | 3.6373 | 0 | N/A | 0 | 0
2021-04-25 09:30 | 3.5197 | 0 | N/A | 0 | 0
2021-04-25 10:00 | 3.4752 | 0 | N/A | 0 | 0
2021-04-25 10:30 | 3.2379 | 0 | N/A | 0 | 0
2021-04-25 11:00 | 2.7779 | 0 | N/A | 0 | 0
2021-04-25 11:30 | 2.5927 | 0 | N/A | 0 | 0
2021-04-25 12:00 | 2.9004 | 0 | N/A | 0 | 0
2021-04-25 12:30 | 2.4019 | 0 | N/A | 0 | 0
2021-04-25 13:00 | 2.5597 | 0 | N/A | 0 | 0
2021-04-25 13:30 | 2.5402 | 0 | N/A | 0 | 0
2021-04-25 14:00 | 3.1739 | 0 | N/A | 0 | 0
2021-04-25 14:30 | 3.5023 | 0 | N/A | 0 | 0
2021-04-25 15:00 | 3.761 | 0 | N/A | 0 | 0
2021-04-25 15:30 | 4.0989 | 0 | N/A | 0 | 0
2021-04-25 16:00 | 3.9345 | 0 | N/A | 0 | 0
2021-04-25 16:30 | 4.6098 | 0 | N/A | 0 | 0
2021-04-25 17:00 | 5.2967 | 0 | N/A | 0 | 0
2021-04-25 17:30 | 5.7592 | 0 | N/A | 0 | 0
2021-04-25 18:00 | 6.4778 | 0 | N/A | 0 | 0
2021-04-25 18:30 | 6.8684 | 0 | N/A | 0 | 0
2021-04-25 19:00 | 6.9048 | 0 | N/A | 0 | 0
2021-04-25 19:30 | 6.5602 | 0 | N/A | 0 | 0
2021-04-25 20:00 | 6.3115 | 0 | N/A | 0 | 0
2021-04-25 20:30 | 5.9131 | 0 | N/A | 0 | 0
2021-04-25 21:00 | 5.5804 | 0 | N/A | 0 | 0
2021-04-25 21:30 | 6.0895 | 0 | N/A | 0 | 0
2021-04-25 22:00 | 6.0713 | 0 | N/A | 0 | 0
2021-04-25 22:30 | 5.7759 | 0 | N/A | 0 | 0
2021-04-25 23:00 | 5.7639 | 0 | N/A | 0 | 0
2021-04-25 23:30 | 5.8661 | 0 | N/A | 0 | 0
2021-04-26 | 6.1495 | 0 | N/A | 0 | 0
2021-04-26 00:30 | 5.4145 | 0 | N/A | 0 | 0
2021-04-26 01:00 | 4.6278 | 0 | N/A | 0 | 0
2021-04-26 01:30 | 4.5002 | 0 | N/A | 0 | 0
2021-04-26 02:00 | 4.1123 | 0 | N/A | 0 | 0
2021-04-26 02:30 | 3.5748 | 0 | N/A | 0 | 0
2021-04-26 03:00 | 3.2363 | 0 | N/A | 0 | 0
2021-04-26 03:30 | 3.0957 | 0 | N/A | 0 | 0
2021-04-26 04:00 | 2.8946 | 0 | N/A | 0 | 0
2021-04-26 04:30 | 2.8197 | 0 | N/A | 0 | 0
2021-04-26 05:00 | 2.9093 | 0 | N/A | 0 | 0
2021-04-26 05:30 | 3.2016 | 0 | N/A | 0 | 0
2021-04-26 06:00 | 3.6837 | 0 | N/A | 0 | 0
2021-04-26 06:30 | 4.4091 | 0 | N/A | 0 | 0
2021-04-26 07:00 | 5.2441 | 0 | N/A | 0 | 0
2021-04-26 07:30 | 5.6933 | 0 | N/A | 0 | 0
2021-04-26 08:00 | 6.1405 | 0 | N/A | 0 | 0
2021-04-26 08:30 | 6.1053 | 0 | N/A | 0 | 0
2021-04-26 09:00 | 5.5734 | 0 | N/A | 0 | 0
2021-04-26 09:30 | 6.2333 | 0 | N/A | 0 | 0
2021-04-26 10:00 | 6.1967 | 0 | N/A | 0 | 0
2021-04-26 10:30 | 5.36 | 0 | N/A | 0 | 0
2021-04-26 11:00 | 5.4174 | 0 | N/A | 0 | 0
2021-04-26 11:30 | 4.5712 | 0 | N/A | 0 | 0
2021-04-26 12:00 | 4.4814 | 0 | N/A | 0 | 0
2021-04-26 12:30 | 4.6234 | 0 | N/A | 0 | 0
2021-04-26 13:00 | 4.7934 | 0 | N/A | 0 | 0
2021-04-26 13:30 | 4.9107 | 0 | N/A | 0 | 0
2021-04-26 14:00 | 4.8317 | 0 | N/A | 0 | 0
2021-04-26 14:30 | 4.6015 | 0 | N/A | 0 | 0
2021-04-26 15:00 | 4.7168 | 0 | N/A | 0 | 0
2021-04-26 15:30 | 4.8133 | 0 | N/A | 0 | 0
2021-04-26 16:00 | 4.96 | 0 | N/A | 0 | 0
2021-04-26 16:30 | 5.241 | 0 | N/A | 0 | 0
2021-04-26 17:00 | 5.6401 | 0 | N/A | 0 | 0
2021-04-26 17:30 | 6.2699 | 0 | N/A | 0 | 0
2021-04-26 18:00 | 7.0187 | 0 | N/A | 0 | 0
2021-04-26 18:30 | 7.3801 | 0 | N/A | 0 | 0
2021-04-26 19:00 | 7.0575 | 0 | N/A | 0 | 0
2021-04-26 19:30 | 6.6805 | 0 | N/A | 0 | 0
2021-04-26 20:00 | 6.3599 | 0 | N/A | 0 | 0
2021-04-26 20:30 | 5.9714 | 0 | N/A | 0 | 0
2021-04-26 21:00 | 5.6357 | 0 | N/A | 0 | 0
2021-04-26 21:30 | 6.0222 | 0 | N/A | 0 | 0
2021-04-26 22:00 | 6.063 | 0 | N/A | 0 | 0
2021-04-26 22:30 | 5.4694 | 0 | N/A | 0 | 0
2021-04-26 23:00 | 5.1881 | 0 | N/A | 0 | 0
2021-04-26 23:30 | 5.3611 | 0 | N/A | 0 | 0
2021-04-27 | 5.6715 | 0 | N/A | 0 | 0
2021-04-27 00:30 | 5.0011 | 0 | N/A | 0 | 0
2021-04-27 01:00 | 4.2442 | 0 | N/A | 0 | 0
2021-04-27 01:30 | 4.0881 | 0 | N/A | 0 | 0
2021-04-27 02:00 | 3.5884 | 0 | N/A | 0 | 0
2021-04-27 02:30 | 3.1119 | 0 | N/A | 0 | 0
2021-04-27 03:00 | 2.8151 | 0 | N/A | 0 | 0
2021-04-27 03:30 | 2.6376 | 0 | N/A | 0 | 0
2021-04-27 04:00 | 2.5204 | 0 | N/A | 0 | 0
2021-04-27 04:30 | 2.5214 | 0 | N/A | 0 | 0
2021-04-27 05:00 | 2.5646 | 0 | N/A | 0 | 0
2021-04-27 05:30 | 2.9189 | 0 | N/A | 0 | 0
2021-04-27 06:00 | 3.3314 | 0 | N/A | 0 | 0
2021-04-27 06:30 | 4.1378 | 0 | N/A | 0 | 0
2021-04-27 07:00 | 5.151 | 0 | N/A | 0 | 0
2021-04-27 07:30 | 5.4633 | 0 | N/A | 0 | 0
2021-04-27 08:00 | 5.6533 | 0 | N/A | 0 | 0
2021-04-27 08:30 | 6.2535 | 0 | N/A | 0 | 0
2021-04-27 09:00 | 5.9268 | 0 | N/A | 0 | 0
2021-04-27 09:30 | 5.6702 | 0 | N/A | 0 | 0
2021-04-27 10:00 | 5.5269 | 0 | N/A | 0 | 0
2021-04-27 10:30 | 5.3034 | 0 | N/A | 0 | 0
2021-04-27 11:00 | 5.1567 | 0 | N/A | 0 | 0
2021-04-27 11:30 | 5.094 | 0 | N/A | 0 | 0
2021-04-27 12:00 | 5.0014 | 0 | N/A | 0 | 0
2021-04-27 12:30 | 4.864 | 0 | N/A | 0 | 0
2021-04-27 13:00 | 4.65 | 0 | N/A | 0 | 0
2021-04-27 13:30 | 4.5367 | 0 | N/A | 0 | 0
2021-04-27 14:00 | 4.7267 | 0 | N/A | 0 | 0
2021-04-27 14:30 | 4.4879 | 0 | N/A | 0 | 0
2021-04-27 15:00 | 3.8934 | 0 | N/A | 0 | 0
2021-04-27 15:30 | 3.9033 | 0 | N/A | 0 | 0
2021-04-27 16:00 | 3.7956 | 0 | N/A | 0 | 0
2021-04-27 16:30 | 4.009 | 0 | N/A | 0 | 0
2021-04-27 17:00 | 4.4198 | 0 | N/A | 0 | 0
2021-04-27 17:30 | 5.3501 | 0 | N/A | 0 | 0
2021-04-27 18:00 | 6.3885 | 0 | N/A | 0 | 0
2021-04-27 18:30 | 7.1407 | 0 | N/A | 0 | 0
2021-04-27 19:00 | 7.1107 | 0 | N/A | 0 | 0
2021-04-27 19:30 | 6.8754 | 0 | N/A | 0 | 0
2021-04-27 20:00 | 6.6563 | 0 | N/A | 0 | 0
2021-04-27 20:30 | 6.4026 | 0 | N/A | 0 | 0
2021-04-27 21:00 | 5.9817 | 0 | N/A | 0 | 0
2021-04-27 21:30 | 6.3249 | 0 | N/A | 0 | 0
2021-04-27 22:00 | 6.361 | 0 | N/A | 0 | 0
2021-04-27 22:30 | 5.7808 | 0 | N/A | 0 | 0
2021-04-27 23:00 | 5.7235 | 0 | N/A | 0 | 0
2021-04-27 23:30 | 5.8475 | 0 | N/A | 0 | 0
2021-04-28 | 6.1852 | 0 | N/A | 0 | 0
2021-04-28 00:30 | 5.3946 | 0 | N/A | 0 | 0
2021-04-28 01:00 | 4.5382 | 0 | N/A | 0 | 0
2021-04-28 01:30 | 4.4487 | 0 | N/A | 0 | 0
2021-04-28 02:00 | 4.0283 | 0 | N/A | 0 | 0
2021-04-28 02:30 | 3.4783 | 0 | N/A | 0 | 0
2021-04-28 03:00 | 3.2253 | 0 | N/A | 0 | 0
2021-04-28 03:30 | 3.0297 | 0 | N/A | 0 | 0
2021-04-28 04:00 | 3.0002 | 0 | N/A | 0 | 0
2021-04-28 04:30 | 2.8505 | 0 | N/A | 0 | 0
2021-04-28 05:00 | 3.0079 | 0 | N/A | 0 | 0
2021-04-28 05:30 | 3.4579 | 0 | N/A | 0 | 0
2021-04-28 06:00 | 4.0674 | 0 | N/A | 0 | 0
2021-04-28 06:30 | 4.8805 | 0 | N/A | 0 | 0
2021-04-28 07:00 | 5.7267 | 0 | N/A | 0 | 0
2021-04-28 07:30 | 6.3167 | 0 | N/A | 0 | 0
2021-04-28 08:00 | 6.5535 | 0 | N/A | 0 | 0
2021-04-28 08:30 | 6.7347 | 0 | N/A | 0 | 0
2021-04-28 09:00 | 6.0637 | 0 | N/A | 0 | 0
2021-04-28 09:30 | 5.2602 | 0 | N/A | 0 | 0
2021-04-28 10:00 | 4.6909 | 0 | N/A | 0 | 0
2021-04-28 10:30 | 4.2453 | 0 | N/A | 0 | 0
2021-04-28 11:00 | 3.6998 | 0 | N/A | 0 | 0
2021-04-28 11:30 | 3.047 | 0 | N/A | 0 | 0
2021-04-28 12:00 | 2.9435 | 0 | N/A | 0 | 0
2021-04-28 12:30 | 3.06 | 0 | N/A | 0 | 0
2021-04-28 13:00 | 3.0353 | 0 | N/A | 0 | 0
2021-04-28 13:30 | 3.1002 | 0 | N/A | 0 | 0
2021-04-28 14:00 | 2.9568 | 0 | N/A | 0 | 0
2021-04-28 14:30 | 2.6 | 0 | N/A | 0 | 0
2021-04-28 15:00 | 2.18 | 0 | N/A | 0 | 0
2021-04-28 15:30 | 3.0067 | 0 | N/A | 0 | 0
2021-04-28 16:00 | 2.8809 | 0 | N/A | 0 | 0
2021-04-28 16:30 | 3.5635 | 0 | N/A | 0 | 0
2021-04-28 17:00 | 4.5899 | 0 | N/A | 0 | 0
2021-04-28 17:30 | 5.6644 | 0 | N/A | 0 | 0
2021-04-28 18:00 | 6.5421 | 0 | N/A | 0 | 0
2021-04-28 18:30 | 7.1053 | 0 | N/A | 0 | 0
2021-04-28 19:00 | 7.0555 | 0 | N/A | 0 | 0
2021-04-28 19:30 | 6.9031 | 0 | N/A | 0 | 0
2021-04-28 20:00 | 6.5925 | 0 | N/A | 0 | 0
2021-04-28 20:30 | 6.2881 | 0 | N/A | 0 | 0
2021-04-28 21:00 | 6.0366 | 0 | N/A | 0 | 0
2021-04-28 21:30 | 6.4308 | 0 | N/A | 0 | 0
2021-04-28 22:00 | 6.5107 | 0 | N/A | 0 | 0
2021-04-28 22:30 | 5.984 | 0 | N/A | 0 | 0
2021-04-28 23:00 | 5.8471 | 0 | N/A | 0 | 0
2021-04-28 23:30 | 5.9487 | 0 | N/A | 0 | 0
2021-04-29 | 6.275 | 0 | N/A | 0 | 0
2021-04-29 00:30 | 5.3927 | 0 | N/A | 0 | 0
2021-04-29 01:00 | 4.6266 | 0 | N/A | 0 | 0
2021-04-29 01:30 | 4.5184 | 0 | N/A | 0 | 0
2021-04-29 02:00 | 4.2321 | 0 | N/A | 0 | 0
2021-04-29 02:30 | 3.6685 | 0 | N/A | 0 | 0
2021-04-29 03:00 | 3.3013 | 0 | N/A | 0 | 0
2021-04-29 03:30 | 3.1094 | 0 | N/A | 0 | 0
2021-04-29 04:00 | 3.0255 | 0 | N/A | 0 | 0
2021-04-29 04:30 | 3.0041 | 0 | N/A | 0 | 0
2021-04-29 05:00 | 3.2592 | 0 | N/A | 0 | 0
2021-04-29 05:30 | 3.6578 | 0 | N/A | 0 | 0
2021-04-29 06:00 | 4.2442 | 0 | N/A | 0 | 0
2021-04-29 06:30 | 5.1251 | 0 | N/A | 0 | 0
2021-04-29 07:00 | 6.2338 | 0 | N/A | 0 | 0
2021-04-29 07:30 | 6.7633 | 0 | N/A | 0 | 0
2021-04-29 08:00 | 7.1842 | 0 | N/A | 0 | 0
2021-04-29 08:30 | 7.2645 | 0 | N/A | 0 | 0
2021-04-29 09:00 | 5.9944 | 0 | N/A | 0 | 0
2021-04-29 09:30 | 5.0605 | 0 | N/A | 0 | 0
2021-04-29 10:00 | 3.9943 | 0 | N/A | 0 | 0
2021-04-29 10:30 | 3.178 | 0 | N/A | 0 | 0
2021-04-29 11:00 | 2.5805 | 0 | N/A | 0 | 0
2021-04-29 11:30 | 2.0824 | 0 | N/A | 0 | 0
2021-04-29 12:00 | 1.739 | 0 | N/A | 0 | 0
2021-04-29 12:30 | 1.4702 | 0 | N/A | 0 | 0
2021-04-29 13:00 | 1.3067 | 0 | N/A | 0 | 0
2021-04-29 13:30 | 1.3967 | 0 | N/A | 0 | 0
2021-04-29 14:00 | 1.61 | 0 | N/A | 0 | 0
2021-04-29 14:30 | 1.1073 | 0 | N/A | 0 | 0
2021-04-29 15:00 | 1.38 | 0 | N/A | 0 | 0
2021-04-29 15:30 | 1.7305 | 0 | N/A | 0 | 0
2021-04-29 16:00 | 2.1935 | 0 | N/A | 0 | 0
2021-04-29 16:30 | 2.7756 | 0 | N/A | 0 | 0
2021-04-29 17:00 | 3.6878 | 0 | N/A | 0 | 0
2021-04-29 17:30 | 4.7287 | 0 | N/A | 0 | 0
2021-04-29 18:00 | 5.653 | 0 | N/A | 0 | 0
2021-04-29 18:30 | 6.2941 | 0 | N/A | 0 | 0
2021-04-29 19:00 | 6.2214 | 0 | N/A | 0 | 0
2021-04-29 19:30 | 6.0615 | 0 | N/A | 0 | 0
2021-04-29 20:00 | 5.9464 | 0 | N/A | 0 | 0
2021-04-29 20:30 | 5.7582 | 0 | N/A | 0 | 0
2021-04-29 21:00 | 5.5728 | 0 | N/A | 0 | 0
2021-04-29 21:30 | 5.8717 | 0 | N/A | 0 | 0
2021-04-29 22:00 | 5.9461 | 0 | N/A | 0 | 0
2021-04-29 22:30 | 5.4637 | 0 | N/A | 0 | 0
2021-04-29 23:00 | 5.4402 | 0 | N/A | 0 | 0
2021-04-29 23:30 | 5.7537 | 0 | N/A | 0 | 0
2021-04-30 | 6.0065 | 0 | N/A | 0 | 0
2021-04-30 00:30 | 5.15 | 0 | N/A | 0 | 0
2021-04-30 01:00 | 4.2777 | 0 | N/A | 0 | 0
2021-04-30 01:30 | 4.1564 | 0 | N/A | 0 | 0
2021-04-30 02:00 | 3.7229 | 0 | N/A | 0 | 0
2021-04-30 02:30 | 3.2314 | 0 | N/A | 0 | 0
2021-04-30 03:00 | 2.9698 | 0 | N/A | 0 | 0
2021-04-30 03:30 | 2.832 | 0 | N/A | 0 | 0
2021-04-30 04:00 | 2.7806 | 0 | N/A | 0 | 0
2021-04-30 04:30 | 2.7105 | 0 | N/A | 0 | 0
2021-04-30 05:00 | 2.9172 | 0 | N/A | 0 | 0
2021-04-30 05:30 | 3.2116 | 0 | N/A | 0 | 0
2021-04-30 06:00 | 3.6491 | 0 | N/A | 0 | 0
2021-04-30 06:30 | 4.4471 | 0 | N/A | 0 | 0
2021-04-30 07:00 | 5.4657 | 0 | N/A | 0 | 0
2021-04-30 07:30 | 5.7202 | 0 | N/A | 0 | 0
2021-04-30 08:00 | 5.8067 | 0 | N/A | 0 | 0
2021-04-30 08:30 | 5.3935 | 0 | N/A | 0 | 0
2021-04-30 09:00 | 4.5067 | 0 | N/A | 0 | 0
2021-04-30 09:30 | 3.2 | 0 | N/A | 0 | 0
2021-04-30 10:00 | 2.3632 | 0 | N/A | 0 | 0
2021-04-30 10:30 | 1.9467 | 0 | N/A | 0 | 0
2021-04-30 11:00 | 1.5576 | 0 | N/A | 0 | 0
2021-04-30 11:30 | 1.0539 | 0 | N/A | 0 | 0
2021-04-30 12:00 | 0.81159 | 0 | N/A | 0 | 0
2021-04-30 12:30 | 0.68394 | 0 | N/A | 0 | 0
2021-04-30 13:00 | 0.67133 | 0 | N/A | 0 | 0
2021-04-30 13:30 | 0.77735 | 0 | N/A | 0 | 0
2021-04-30 14:00 | 0.78638 | 0 | N/A | 0 | 0
2021-04-30 14:30 | 0.95343 | 0 | N/A | 0 | 0
2021-04-30 15:00 | 1.3933 | 0 | N/A | 0 | 0
2021-04-30 15:30 | 1.5887 | 0 | N/A | 0 | 0
2021-04-30 16:00 | 1.7737 | 0 | N/A | 0 | 0
2021-04-30 16:30 | 2.4993 | 0 | N/A | 0 | 0
2021-04-30 17:00 | 3.2918 | 0 | N/A | 0 | 0
2021-04-30 17:30 | 4.056 | 0 | N/A | 0 | 0
2021-04-30 18:00 | 4.7983 | 0 | N/A | 0 | 0
2021-04-30 18:30 | 5.4357 | 0 | N/A | 0 | 0
2021-04-30 19:00 | 5.5419 | 0 | N/A | 0 | 0
2021-04-30 19:30 | 5.5155 | 0 | N/A | 0 | 0
2021-04-30 20:00 | 5.3946 | 0 | N/A | 0 | 0
2021-04-30 20:30 | 5.3097 | 0 | N/A | 0 | 0
2021-04-30 21:00 | 5.0924 | 0 | N/A | 0 | 0
2021-04-30 21:30 | 5.5963 | 0 | N/A | 0 | 0
2021-04-30 22:00 | 5.7055 | 0 | N/A | 0 | 0
2021-04-30 22:30 | 5.3383 | 0 | N/A | 0 | 0
2021-04-30 23:00 | 5.3096 | 0 | N/A | 0 | 0
2021-04-30 23:30 | 5.5596 | 0 | N/A | 0 | 0
2021-05-01 | 5.8432 | 0 | N/A | 0 | 0
2021-05-01 00:30 | 4.8536 | 0 | N/A | 0 | 0
2021-05-01 01:00 | 3.9315 | 0 | N/A | 0 | 0
2021-05-01 01:30 | 3.9028 | 0 | N/A | 0 | 0
2021-05-01 02:00 | 3.578 | 0 | N/A | 0 | 0
2021-05-01 02:30 | 3.072 | 0 | N/A | 0 | 0
2021-05-01 03:00 | 2.7769 | 0 | N/A | 0 | 0
2021-05-01 03:30 | 2.589 | 0 | N/A | 0 | 0
2021-05-01 04:00 | 2.4657 | 0 | N/A | 0 | 0
2021-05-01 04:30 | 2.4248 | 0 | N/A | 0 | 0
2021-05-01 05:00 | 2.4419 | 0 | N/A | 0 | 0
2021-05-01 05:30 | 2.5678 | 0 | N/A | 0 | 0
2021-05-01 06:00 | 2.6996 | 0 | N/A | 0 | 0
2021-05-01 06:30 | 3.1922 | 0 | N/A | 0 | 0
2021-05-01 07:00 | 3.3608 | 0 | N/A | 0 | 0
2021-05-01 07:30 | 3.3567 | 0 | N/A | 0 | 0
2021-05-01 08:00 | 3.5295 | 0 | N/A | 0 | 0
2021-05-01 08:30 | 3.3275 | 0 | N/A | 0 | 0
2021-05-01 09:00 | 3.1209 | 0 | N/A | 0 | 0
2021-05-01 09:30 | 3.2283 | 0 | N/A | 0 | 0
2021-05-01 10:00 | 2.4659 | 0 | N/A | 0 | 0
2021-05-01 10:30 | 1.6261 | 0 | N/A | 0 | 0
2021-05-01 11:00 | 1.5232 | 0 | N/A | 0 | 0
2021-05-01 11:30 | 1.8061 | 0 | N/A | 0 | 0
2021-05-01 12:00 | 1.3968 | 0 | N/A | 0 | 0
2021-05-01 12:30 | 1.2095 | 0 | N/A | 0 | 0
2021-05-01 13:00 | 1.4378 | 0 | N/A | 0 | 0
2021-05-01 13:30 | 1.347 | 0 | N/A | 0 | 0
2021-05-01 14:00 | 1.4401 | 0 | N/A | 0 | 0
2021-05-01 14:30 | 2.0735 | 0 | N/A | 0 | 0
2021-05-01 15:00 | 2.4028 | 0 | N/A | 0 | 0
2021-05-01 15:30 | 2.685 | 0 | N/A | 0 | 0
2021-05-01 16:00 | 2.8811 | 0 | N/A | 0 | 0
2021-05-01 16:30 | 3.3283 | 0 | N/A | 0 | 0
2021-05-01 17:00 | 3.902 | 0 | N/A | 0 | 0
2021-05-01 17:30 | 4.5932 | 0 | N/A | 0 | 0
2021-05-01 18:00 | 5.3619 | 0 | N/A | 0 | 0
2021-05-01 18:30 | 5.7197 | 0 | N/A | 0 | 0
2021-05-01 19:00 | 5.4445 | 0 | N/A | 0 | 0
2021-05-01 19:30 | 5.1563 | 0 | N/A | 0 | 0
2021-05-01 20:00 | 4.8402 | 0 | N/A | 0 | 0
2021-05-01 20:30 | 4.6864 | 0 | N/A | 0 | 0
2021-05-01 21:00 | 4.4537 | 0 | N/A | 0 | 0
2021-05-01 21:30 | 4.9085 | 0 | N/A | 0 | 0
2021-05-01 22:00 | 5.214 | 0 | N/A | 0 | 0
2021-05-01 22:30 | 5.0107 | 0 | N/A | 0 | 0
2021-05-01 23:00 | 5.0657 | 0 | N/A | 0 | 0
2021-05-01 23:30 | 5.2282 | 0 | N/A | 0 | 0
2021-05-02 | 5.5324 | 0 | N/A | 0 | 0
2021-05-02 00:30 | 4.785 | 0 | N/A | 0 | 0
2021-05-02 01:00 | 3.9716 | 0 | N/A | 0 | 0
2021-05-02 01:30 | 3.7288 | 0 | N/A | 0 | 0
2021-05-02 02:00 | 3.3442 | 0 | N/A | 0 | 0
2021-05-02 02:30 | 2.9066 | 0 | N/A | 0 | 0
2021-05-02 03:00 | 2.5826 | 0 | N/A | 0 | 0
2021-05-02 03:30 | 2.4039 | 0 | N/A | 0 | 0
2021-05-02 04:00 | 2.2707 | 0 | N/A | 0 | 0
2021-05-02 04:30 | 2.2458 | 0 | N/A | 0 | 0
2021-05-02 05:00 | 2.1833 | 0 | N/A | 0 | 0
2021-05-02 05:30 | 2.2632 | 0 | N/A | 0 | 0
2021-05-02 06:00 | 2.3709 | 0 | N/A | 0 | 0
2021-05-02 06:30 | 2.6674 | 0 | N/A | 0 | 0
2021-05-02 07:00 | 2.7912 | 0 | N/A | 0 | 0
2021-05-02 07:30 | 2.6784 | 0 | N/A | 0 | 0
2021-05-02 08:00 | 2.8176 | 0 | N/A | 0 | 0
2021-05-02 08:30 | 2.7582 | 0 | N/A | 0 | 0
2021-05-02 09:00 | 2.5609 | 0 | N/A | 0 | 0
2021-05-02 09:30 | 1.9522 | 0 | N/A | 0 | 0
2021-05-02 10:00 | 1.4051 | 0 | N/A | 0 | 0
2021-05-02 10:30 | 0.92856 | 0 | N/A | 0 | 0
2021-05-02 11:00 | 0.61029 | 0 | N/A | 0 | 0
2021-05-02 11:30 | 0.49334 | 0 | N/A | 0 | 0
2021-05-02 12:00 | -0.49191 | 0 | N/A | 0 | 0
2021-05-02 12:30 | -0.44783 | 0 | N/A | 0 | 0
2021-05-02 13:00 | 0.5226 | 0 | N/A | 0 | 0
2021-05-02 13:30 | 0.94953 | 0 | N/A | 0 | 0
2021-05-02 14:00 | 2.2166 | 0 | N/A | 0 | 0
2021-05-02 14:30 | 2.2462 | 0 | N/A | 0 | 0
2021-05-02 15:00 | 2.6522 | 0 | N/A | 0 | 0
2021-05-02 15:30 | 3.0196 | 0 | N/A | 0 | 0
2021-05-02 16:00 | 3.45 | 0 | N/A | 0 | 0
2021-05-02 16:30 | 3.7271 | 0 | N/A | 0 | 0
2021-05-02 17:00 | 4.1173 | 0 | N/A | 0 | 0
2021-05-02 17:30 | 4.928 | 0 | N/A | 0 | 0
2021-05-02 18:00 | 5.7639 | 0 | N/A | 0 | 0
2021-05-02 18:30 | 6.1613 | 0 | N/A | 0 | 0
2021-05-02 19:00 | 5.9071 | 0 | N/A | 0 | 0
2021-05-02 19:30 | 5.6687 | 0 | N/A | 0 | 0
2021-05-02 20:00 | 5.2466 | 0 | N/A | 0 | 0
2021-05-02 20:30 | 4.9963 | 0 | N/A | 0 | 0
2021-05-02 21:00 | 4.7216 | 0 | N/A | 0 | 0
2021-05-02 21:30 | 5.1019 | 0 | N/A | 0 | 0
2021-05-02 22:00 | 5.3033 | 0 | N/A | 0 | 0
2021-05-02 22:30 | 4.9042 | 0 | N/A | 0 | 0
2021-05-02 23:00 | 4.9192 | 0 | N/A | 0 | 0
2021-05-02 23:30 | 5.1276 | 0 | N/A | 0 | 0
2021-05-03 | 5.477 | 0 | N/A | 0 | 0
2021-05-03 00:30 | 4.7518 | 0 | N/A | 0 | 0
2021-05-03 01:00 | 4.1332 | 0 | N/A | 0 | 0
2021-05-03 01:30 | 4.0027 | 0 | N/A | 0 | 0
2021-05-03 02:00 | 3.6032 | 0 | N/A | 0 | 0
2021-05-03 02:30 | 3.0023 | 0 | N/A | 0 | 0
2021-05-03 03:00 | 2.6883 | 0 | N/A | 0 | 0
2021-05-03 03:30 | 2.6195 | 0 | N/A | 0 | 0
2021-05-03 04:00 | 2.46 | 0 | N/A | 0 | 0
2021-05-03 04:30 | 2.4841 | 0 | N/A | 0 | 0
2021-05-03 05:00 | 2.5644 | 0 | N/A | 0 | 0
2021-05-03 05:30 | 2.8792 | 0 | N/A | 0 | 0
2021-05-03 06:00 | 3.2969 | 0 | N/A | 0 | 0
2021-05-03 06:30 | 4.12 | 0 | N/A | 0 | 0
2021-05-03 07:00 | 5.0056 | 0 | N/A | 0 | 0
2021-05-03 07:30 | 5.4433 | 0 | N/A | 0 | 0
2021-05-03 08:00 | 5.6634 | 0 | N/A | 0 | 0
2021-05-03 08:30 | 5.4739 | 0 | N/A | 0 | 0
2021-05-03 09:00 | 4.3176 | 0 | N/A | 0 | 0
2021-05-03 09:30 | 3.7843 | 0 | N/A | 0 | 0
2021-05-03 10:00 | 3.7617 | 0 | N/A | 0 | 0
2021-05-03 10:30 | 3.494 | 0 | N/A | 0 | 0
2021-05-03 11:00 | 3.4802 | 0 | N/A | 0 | 0
2021-05-03 11:30 | 3.344 | 0 | N/A | 0 | 0
2021-05-03 12:00 | 4.0937 | 0 | N/A | 0 | 0
2021-05-03 12:30 | 4.4267 | 0 | N/A | 0 | 0
2021-05-03 13:00 | 3.94 | 0 | N/A | 0 | 0
2021-05-03 13:30 | 4.0667 | 0 | N/A | 0 | 0
2021-05-03 14:00 | 4.0924 | 0 | N/A | 0 | 0
2021-05-03 14:30 | 4.4636 | 0 | N/A | 0 | 0
2021-05-03 15:00 | 4.5635 | 0 | N/A | 0 | 0
2021-05-03 15:30 | 4.9201 | 0 | N/A | 0 | 0
2021-05-03 16:00 | 4.5602 | 0 | N/A | 0 | 0
2021-05-03 16:30 | 4.951 | 0 | N/A | 0 | 0
2021-05-03 17:00 | 5.6164 | 0 | N/A | 0 | 0
2021-05-03 17:30 | 6.319 | 0 | N/A | 0 | 0
2021-05-03 18:00 | 7.1599 | 0 | N/A | 0 | 0
2021-05-03 18:30 | 7.6252 | 0 | N/A | 0 | 0
2021-05-03 19:00 | 7.3013 | 0 | N/A | 0 | 0
2021-05-03 19:30 | 6.8502 | 0 | N/A | 0 | 0
2021-05-03 20:00 | 6.3559 | 0 | N/A | 0 | 0
2021-05-03 20:30 | 6.1096 | 0 | N/A | 0 | 0
2021-05-03 21:00 | 5.7249 | 0 | N/A | 0 | 0
2021-05-03 21:30 | 6.0387 | 0 | N/A | 0 | 0
2021-05-03 22:00 | 6.3253 | 0 | N/A | 0 | 0
2021-05-03 22:30 | 5.7889 | 0 | N/A | 0 | 0
2021-05-03 23:00 | 5.8163 | 0 | N/A | 0 | 0
2021-05-03 23:30 | 5.9387 | 0 | N/A | 0 | 0
2021-05-04 | 6.0502 | 0 | N/A | 0 | 0
2021-05-04 00:30 | 5.2992 | 0 | N/A | 0 | 0
2021-05-04 01:00 | 4.5813 | 0 | N/A | 0 | 0
2021-05-04 01:30 | 4.3878 | 0 | N/A | 0 | 0
2021-05-04 02:00 | 3.9904 | 0 | N/A | 0 | 0
2021-05-04 02:30 | 3.4157 | 0 | N/A | 0 | 0
2021-05-04 03:00 | 3.2002 | 0 | N/A | 0 | 0
2021-05-04 03:30 | 3.0152 | 0 | N/A | 0 | 0
2021-05-04 04:00 | 2.8921 | 0 | N/A | 0 | 0
2021-05-04 04:30 | 3.0027 | 0 | N/A | 0 | 0
2021-05-04 05:00 | 3.0348 | 0 | N/A | 0 | 0
2021-05-04 05:30 | 3.4677 | 0 | N/A | 0 | 0
2021-05-04 06:00 | 4.0321 | 0 | N/A | 0 | 0
2021-05-04 06:30 | 4.6873 | 0 | N/A | 0 | 0
2021-05-04 07:00 | 5.4663 | 0 | N/A | 0 | 0
2021-05-04 07:30 | 6.19 | 0 | N/A | 0 | 0
2021-05-04 08:00 | 6.8114 | 0 | N/A | 0 | 0
2021-05-04 08:30 | 7.1114 | 0 | N/A | 0 | 0
2021-05-04 09:00 | 6.8069 | 0 | N/A | 0 | 0
2021-05-04 09:30 | 7.426 | 0 | N/A | 0 | 0
2021-05-04 10:00 | 7.3182 | 0 | N/A | 0 | 0
2021-05-04 10:30 | 7.1698 | 0 | N/A | 0 | 0
2021-05-04 11:00 | 6.9699 | 0 | N/A | 0 | 0
2021-05-04 11:30 | 7.0557 | 0 | N/A | 0 | 0
2021-05-04 12:00 | 7.0554 | 0 | N/A | 0 | 0
2021-05-04 12:30 | 6.9892 | 0 | N/A | 0 | 0
2021-05-04 13:00 | 6.3966 | 0 | N/A | 0 | 0
2021-05-04 13:30 | 6.5322 | 0 | N/A | 0 | 0
2021-05-04 14:00 | 6.8007 | 0 | N/A | 0 | 0
2021-05-04 14:30 | 7.0316 | 0 | N/A | 0 | 0
2021-05-04 15:00 | 6.9295 | 0 | N/A | 0 | 0
2021-05-04 15:30 | 6.1537 | 0 | N/A | 0 | 0
2021-05-04 16:00 | 6.3574 | 0 | N/A | 0 | 0
2021-05-04 16:30 | 6.3743 | 0 | N/A | 0 | 0
2021-05-04 17:00 | 6.81 | 0 | N/A | 0 | 0
2021-05-04 17:30 | 7.51 | 0 | N/A | 0 | 0
2021-05-04 18:00 | 8.19 | 0 | N/A | 0 | 0
2021-05-04 18:30 | 8.5034 | 0 | N/A | 0 | 0
2021-05-04 19:00 | 8.2567 | 0 | N/A | 0 | 0
2021-05-04 19:30 | 7.88 | 0 | N/A | 0 | 0
2021-05-04 20:00 | 7.5069 | 0 | N/A | 0 | 0
2021-05-04 20:30 | 7.0713 | 0 | N/A | 0 | 0
2021-05-04 21:00 | 6.6463 | 0 | N/A | 0 | 0
2021-05-04 21:30 | 6.8312 | 0 | N/A | 0 | 0
2021-05-04 22:00 | 6.8844 | 0 | N/A | 0 | 0
2021-05-04 22:30 | 6.2152 | 0 | N/A | 0 | 0
2021-05-04 23:00 | 6.0261 | 0 | N/A | 0 | 0
2021-05-04 23:30 | 6.2859 | 0 | N/A | 0 | 0
2021-05-05 | 6.4203 | 0 | N/A | 0 | 0
2021-05-05 00:30 | 5.5956 | 0 | N/A | 0 | 0
2021-05-05 01:00 | 4.8239 | 0 | N/A | 0 | 0
2021-05-05 01:30 | 4.8216 | 0 | N/A | 0 | 0
2021-05-05 02:00 | 4.4082 | 0 | N/A | 0 | 0
2021-05-05 02:30 | 3.8167 | 0 | N/A | 0 | 0
2021-05-05 03:00 | 3.4969 | 0 | N/A | 0 | 0
2021-05-05 03:30 | 3.2912 | 0 | N/A | 0 | 0
2021-05-05 04:00 | 3.0792 | 0 | N/A | 0 | 0
2021-05-05 04:30 | 3.1332 | 0 | N/A | 0 | 0
2021-05-05 05:00 | 3.2399 | 0 | N/A | 0 | 0
2021-05-05 05:30 | 3.6748 | 0 | N/A | 0 | 0
2021-05-05 06:00 | 4.1917 | 0 | N/A | 0 | 0
2021-05-05 06:30 | 4.9921 | 0 | N/A | 0 | 0
2021-05-05 07:00 | 5.7078 | 0 | N/A | 0 | 0
2021-05-05 07:30 | 5.9392 | 0 | N/A | 0 | 0
2021-05-05 08:00 | 6.3533 | 0 | N/A | 0 | 0
2021-05-05 08:30 | 6.8279 | 0 | N/A | 0 | 0
2021-05-05 09:00 | 6.0276 | 0 | N/A | 0 | 0
2021-05-05 09:30 | 5.0774 | 0 | N/A | 0 | 0
2021-05-05 10:00 | 3.9169 | 0 | N/A | 0 | 0
2021-05-05 10:30 | 3.39 | 0 | N/A | 0 | 0
2021-05-05 11:00 | 3.239 | 0 | N/A | 0 | 0
2021-05-05 11:30 | 2.9776 | 0 | N/A | 0 | 0
2021-05-05 12:00 | 2.643 | 0 | N/A | 0 | 0
2021-05-05 12:30 | 2.7684 | 0 | N/A | 0 | 0
2021-05-05 13:00 | 2.6934 | 0 | N/A | 0 | 0
2021-05-05 13:30 | 2.5452 | 0 | N/A | 0 | 0
2021-05-05 14:00 | 2.3864 | 0 | N/A | 0 | 0
2021-05-05 14:30 | 1.8883 | 0 | N/A | 0 | 0
2021-05-05 15:00 | 2.4967 | 0 | N/A | 0 | 0
2021-05-05 15:30 | 3.4168 | 0 | N/A | 0 | 0
2021-05-05 16:00 | 3.9543 | 0 | N/A | 0 | 0
2021-05-05 16:30 | 4.4814 | 0 | N/A | 0 | 0
2021-05-05 17:00 | 5.3335 | 0 | N/A | 0 | 0
2021-05-05 17:30 | 6.2622 | 0 | N/A | 0 | 0
2021-05-05 18:00 | 7.1452 | 0 | N/A | 0 | 0
2021-05-05 18:30 | 7.4073 | 0 | N/A | 0 | 0
2021-05-05 19:00 | 7.2878 | 0 | N/A | 0 | 0
2021-05-05 19:30 | 7.0052 | 0 | N/A | 0 | 0
2021-05-05 20:00 | 6.6961 | 0 | N/A | 0 | 0
2021-05-05 20:30 | 6.5776 | 0 | N/A | 0 | 0
2021-05-05 21:00 | 6.1517 | 0 | N/A | 0 | 0
2021-05-05 21:30 | 6.4849 | 0 | N/A | 0 | 0
2021-05-05 22:00 | 6.5891 | 0 | N/A | 0 | 0
2021-05-05 22:30 | 5.9422 | 0 | N/A | 0 | 0
2021-05-05 23:00 | 5.6661 | 0 | N/A | 0 | 0
2021-05-05 23:30 | 5.8406 | 0 | N/A | 0 | 0
2021-05-06 | 6.1598 | 0 | N/A | 0 | 0
2021-05-06 00:30 | 5.4634 | 0 | N/A | 0 | 0
2021-05-06 01:00 | 4.5931 | 0 | N/A | 0 | 0
2021-05-06 01:30 | 4.4245 | 0 | N/A | 0 | 0
2021-05-06 02:00 | 4.0179 | 0 | N/A | 0 | 0
2021-05-06 02:30 | 3.5206 | 0 | N/A | 0 | 0
2021-05-06 03:00 | 3.1669 | 0 | N/A | 0 | 0
2021-05-06 03:30 | 2.9473 | 0 | N/A | 0 | 0
2021-05-06 04:00 | 2.8368 | 0 | N/A | 0 | 0
2021-05-06 04:30 | 2.7746 | 0 | N/A | 0 | 0
2021-05-06 05:00 | 2.8738 | 0 | N/A | 0 | 0
2021-05-06 05:30 | 3.1847 | 0 | N/A | 0 | 0
2021-05-06 06:00 | 3.6726 | 0 | N/A | 0 | 0
2021-05-06 06:30 | 4.4739 | 0 | N/A | 0 | 0
2021-05-06 07:00 | 5.1628 | 0 | N/A | 0 | 0
2021-05-06 07:30 | 5.4678 | 0 | N/A | 0 | 0
2021-05-06 08:00 | 6.4133 | 0 | N/A | 0 | 0
2021-05-06 08:30 | 6.4013 | 0 | N/A | 0 | 0
2021-05-06 09:00 | 5.498 | 0 | N/A | 0 | 0
2021-05-06 09:30 | 4.5908 | 0 | N/A | 0 | 0
2021-05-06 10:00 | 3.7908 | 0 | N/A | 0 | 0
2021-05-06 10:30 | 3.1334 | 0 | N/A | 0 | 0
2021-05-06 11:00 | 2.5981 | 0 | N/A | 0 | 0
2021-05-06 11:30 | 2.2322 | 0 | N/A | 0 | 0
2021-05-06 12:00 | 1.9661 | 0 | N/A | 0 | 0
2021-05-06 12:30 | 1.6753 | 0 | N/A | 0 | 0
2021-05-06 13:00 | 0.57855 | 0 | N/A | 0 | 0
2021-05-06 13:30 | 0.69985 | 0 | N/A | 0 | 0
2021-05-06 14:00 | 1.4146 | 0 | N/A | 0 | 0
2021-05-06 14:30 | 2.2167 | 0 | N/A | 0 | 0
2021-05-06 15:00 | 1.86 | 0 | N/A | 0 | 0
2021-05-06 15:30 | 2.45 | 0 | N/A | 0 | 0
2021-05-06 16:00 | 3.2089 | 0 | N/A | 0 | 0
2021-05-06 16:30 | 3.3022 | 0 | N/A | 0 | 0
2021-05-06 17:00 | 3.7261 | 0 | N/A | 0 | 0
2021-05-06 17:30 | 4.61 | 0 | N/A | 0 | 0
2021-05-06 18:00 | 5.7732 | 0 | N/A | 0 | 0
2021-05-06 18:30 | 6.2422 | 0 | N/A | 0 | 0
2021-05-06 19:00 | 6.2668 | 0 | N/A | 0 | 0
2021-05-06 19:30 | 6.0106 | 0 | N/A | 0 | 0
2021-05-06 20:00 | 5.891 | 0 | N/A | 0 | 0
2021-05-06 20:30 | 5.6715 | 0 | N/A | 0 | 0
2021-05-06 21:00 | 5.4892 | 0 | N/A | 0 | 0
2021-05-06 21:30 | 5.8356 | 0 | N/A | 0 | 0
2021-05-06 22:00 | 6.1056 | 0 | N/A | 0 | 0
2021-05-06 22:30 | 5.5556 | 0 | N/A | 0 | 0
2021-05-06 23:00 | 5.3725 | 0 | N/A | 0 | 0
2021-05-06 23:30 | 5.4659 | 0 | N/A | 0 | 0
2021-05-07 | 5.6659 | 0 | N/A | 0 | 0
2021-05-07 00:30 | 4.8767 | 0 | N/A | 0 | 0
2021-05-07 01:00 | 4.1555 | 0 | N/A | 0 | 0
2021-05-07 01:30 | 3.9877 | 0 | N/A | 0 | 0
2021-05-07 02:00 | 3.6952 | 0 | N/A | 0 | 0
2021-05-07 02:30 | 3.1403 | 0 | N/A | 0 | 0
2021-05-07 03:00 | 2.9076 | 0 | N/A | 0 | 0
2021-05-07 03:30 | 2.7044 | 0 | N/A | 0 | 0
2021-05-07 04:00 | 2.63 | 0 | N/A | 0 | 0
2021-05-07 04:30 | 2.6001 | 0 | N/A | 0 | 0
2021-05-07 05:00 | 2.7502 | 0 | N/A | 0 | 0
2021-05-07 05:30 | 3.0293 | 0 | N/A | 0 | 0
2021-05-07 06:00 | 3.4786 | 0 | N/A | 0 | 0
2021-05-07 06:30 | 4.2417 | 0 | N/A | 0 | 0
2021-05-07 07:00 | 5.1118 | 0 | N/A | 0 | 0
2021-05-07 07:30 | 5.5901 | 0 | N/A | 0 | 0
2021-05-07 08:00 | 5.98 | 0 | N/A | 0 | 0
2021-05-07 08:30 | 6.0434 | 0 | N/A | 0 | 0
2021-05-07 09:00 | 5.6675 | 0 | N/A | 0 | 0
2021-05-07 09:30 | 5.0613 | 0 | N/A | 0 | 0
2021-05-07 10:00 | 4.5576 | 0 | N/A | 0 | 0
2021-05-07 10:30 | 4.6006 | 0 | N/A | 0 | 0
2021-05-07 11:00 | 4.7184 | 0 | N/A | 0 | 0
2021-05-07 11:30 | 4.3841 | 0 | N/A | 0 | 0
2021-05-07 12:00 | 3.5577 | 0 | N/A | 0 | 0
2021-05-07 12:30 | 2.7576 | 0 | N/A | 0 | 0
2021-05-07 13:00 | 1.0802 | 0 | N/A | 0 | 0
2021-05-07 13:30 | 1.2219 | 0 | N/A | 0 | 0
2021-05-07 14:00 | 0.84012 | 0 | N/A | 0 | 0
2021-05-07 14:30 | 1.2331 | 0 | N/A | 0 | 0
2021-05-07 15:00 | 2.4572 | 0 | N/A | 0 | 0
2021-05-07 15:30 | 2.7356 | 0 | N/A | 0 | 0
2021-05-07 16:00 | 3.3782 | 0 | N/A | 0 | 0
2021-05-07 16:30 | 3.651 | 0 | N/A | 0 | 0
2021-05-07 17:00 | 4.0052 | 0 | N/A | 0 | 0
2021-05-07 17:30 | 4.691 | 0 | N/A | 0 | 0
2021-05-07 18:00 | 5.5984 | 0 | N/A | 0 | 0
2021-05-07 18:30 | 5.991 | 0 | N/A | 0 | 0
2021-05-07 19:00 | 5.9112 | 0 | N/A | 0 | 0
2021-05-07 19:30 | 5.8611 | 0 | N/A | 0 | 0
2021-05-07 20:00 | 5.7102 | 0 | N/A | 0 | 0
2021-05-07 20:30 | 5.6209 | 0 | N/A | 0 | 0
2021-05-07 21:00 | 5.4476 | 0 | N/A | 0 | 0
2021-05-07 21:30 | 5.8374 | 0 | N/A | 0 | 0
2021-05-07 22:00 | 6.165 | 0 | N/A | 0 | 0
2021-05-07 22:30 | 5.7633 | 0 | N/A | 0 | 0
2021-05-07 23:00 | 5.7046 | 0 | N/A | 0 | 0
2021-05-07 23:30 | 5.9311 | 0 | N/A | 0 | 0
2021-05-08 | 6.0774 | 0 | N/A | 0 | 0
2021-05-08 00:30 | 5.157 | 0 | N/A | 0 | 0
2021-05-08 01:00 | 4.2819 | 0 | N/A | 0 | 0
2021-05-08 01:30 | 4.2029 | 0 | N/A | 0 | 0
2021-05-08 02:00 | 3.7008 | 0 | N/A | 0 | 0
2021-05-08 02:30 | 3.2107 | 0 | N/A | 0 | 0
2021-05-08 03:00 | 2.9661 | 0 | N/A | 0 | 0
2021-05-08 03:30 | 2.7676 | 0 | N/A | 0 | 0
2021-05-08 04:00 | 2.6173 | 0 | N/A | 0 | 0
2021-05-08 04:30 | 2.5941 | 0 | N/A | 0 | 0
2021-05-08 05:00 | 2.5827 | 0 | N/A | 0 | 0
2021-05-08 05:30 | 2.6246 | 0 | N/A | 0 | 0
2021-05-08 06:00 | 2.8007 | 0 | N/A | 0 | 0
2021-05-08 06:30 | 3.1232 | 0 | N/A | 0 | 0
2021-05-08 07:00 | 3.3366 | 0 | N/A | 0 | 0
2021-05-08 07:30 | 3.4589 | 0 | N/A | 0 | 0
2021-05-08 08:00 | 3.8321 | 0 | N/A | 0 | 0
2021-05-08 08:30 | 3.8504 | 0 | N/A | 0 | 0
2021-05-08 09:00 | 3.3467 | 0 | N/A | 0 | 0
2021-05-08 09:30 | 2.8182 | 0 | N/A | 0 | 0
2021-05-08 10:00 | 2.1402 | 0 | N/A | 0 | 0
2021-05-08 10:30 | 1.6043 | 0 | N/A | 0 | 0
2021-05-08 11:00 | 1.1649 | 0 | N/A | 0 | 0
2021-05-08 11:30 | 1.4206 | 0 | N/A | 0 | 0
2021-05-08 12:00 | 1.5302 | 0 | N/A | 0 | 0
2021-05-08 12:30 | 2.5807 | 0 | N/A | 0 | 0
2021-05-08 13:00 | 3.0725 | 0 | N/A | 0 | 0
2021-05-08 13:30 | 2.3553 | 0 | N/A | 0 | 0
2021-05-08 14:00 | 3.1707 | 0 | N/A | 0 | 0
2021-05-08 14:30 | 3.572 | 0 | N/A | 0 | 0
2021-05-08 15:00 | 3.8499 | 0 | N/A | 0 | 0
2021-05-08 15:30 | 3.7999 | 0 | N/A | 0 | 0
2021-05-08 16:00 | 4.0229 | 0 | N/A | 0 | 0
2021-05-08 16:30 | 4.2315 | 0 | N/A | 0 | 0
2021-05-08 17:00 | 4.7071 | 0 | N/A | 0 | 0
2021-05-08 17:30 | 5.3789 | 0 | N/A | 0 | 0
2021-05-08 18:00 | 6.138 | 0 | N/A | 0 | 0
2021-05-08 18:30 | 6.3068 | 0 | N/A | 0 | 0
2021-05-08 19:00 | 6.1291 | 0 | N/A | 0 | 0
2021-05-08 19:30 | 5.8408 | 0 | N/A | 0 | 0
2021-05-08 20:00 | 5.5183 | 0 | N/A | 0 | 0
2021-05-08 20:30 | 5.2028 | 0 | N/A | 0 | 0
2021-05-08 21:00 | 4.9818 | 0 | N/A | 0 | 0
2021-05-08 21:30 | 5.4373 | 0 | N/A | 0 | 0
2021-05-08 22:00 | 5.657 | 0 | N/A | 0 | 0
2021-05-08 22:30 | 5.3796 | 0 | N/A | 0 | 0
2021-05-08 23:00 | 5.2967 | 0 | N/A | 0 | 0
2021-05-08 23:30 | 5.6096 | 0 | N/A | 0 | 0
2021-05-09 | 5.9676 | 0 | N/A | 0 | 0
2021-05-09 00:30 | 5.1877 | 0 | N/A | 0 | 0
2021-05-09 01:00 | 4.3703 | 0 | N/A | 0 | 0
2021-05-09 01:30 | 4.2983 | 0 | N/A | 0 | 0
2021-05-09 02:00 | 3.9099 | 0 | N/A | 0 | 0
2021-05-09 02:30 | 3.3147 | 0 | N/A | 0 | 0
2021-05-09 03:00 | 3.0181 | 0 | N/A | 0 | 0
2021-05-09 03:30 | 2.8841 | 0 | N/A | 0 | 0
2021-05-09 04:00 | 2.7692 | 0 | N/A | 0 | 0
2021-05-09 04:30 | 2.7103 | 0 | N/A | 0 | 0
2021-05-09 05:00 | 2.7264 | 0 | N/A | 0 | 0
2021-05-09 05:30 | 2.8239 | 0 | N/A | 0 | 0
2021-05-09 06:00 | 2.9846 | 0 | N/A | 0 | 0
2021-05-09 06:30 | 3.2767 | 0 | N/A | 0 | 0
2021-05-09 07:00 | 3.5786 | 0 | N/A | 0 | 0
2021-05-09 07:30 | 3.6637 | 0 | N/A | 0 | 0
2021-05-09 08:00 | 3.9473 | 0 | N/A | 0 | 0
2021-05-09 08:30 | 4.1892 | 0 | N/A | 0 | 0
2021-05-09 09:00 | 3.9256 | 0 | N/A | 0 | 0
2021-05-09 09:30 | 3.42 | 0 | N/A | 0 | 0
2021-05-09 10:00 | 2.6626 | 0 | N/A | 0 | 0
2021-05-09 10:30 | 2.2816 | 0 | N/A | 0 | 0
2021-05-09 11:00 | 2.0891 | 0 | N/A | 0 | 0
2021-05-09 11:30 | 1.6447 | 0 | N/A | 0 | 0
2021-05-09 12:00 | 1.3278 | 0 | N/A | 0 | 0
2021-05-09 12:30 | 1.2987 | 0 | N/A | 0 | 0
2021-05-09 13:00 | 1.1482 | 0 | N/A | 0 | 0
2021-05-09 13:30 | 1.2113 | 0 | N/A | 0 | 0
2021-05-09 14:00 | 1.3119 | 0 | N/A | 0 | 0
2021-05-09 14:30 | 1.5962 | 0 | N/A | 0 | 0
2021-05-09 15:00 | 2.1641 | 0 | N/A | 0 | 0
2021-05-09 15:30 | 2.5316 | 0 | N/A | 0 | 0
2021-05-09 16:00 | 2.7888 | 0 | N/A | 0 | 0
2021-05-09 16:30 | 3.5237 | 0 | N/A | 0 | 0
2021-05-09 17:00 | 4.3775 | 0 | N/A | 0 | 0
2021-05-09 17:30 | 5.1152 | 0 | N/A | 0 | 0
2021-05-09 18:00 | 5.9427 | 0 | N/A | 0 | 0
2021-05-09 18:30 | 6.2587 | 0 | N/A | 0 | 0
2021-05-09 19:00 | 6.2979 | 0 | N/A | 0 | 0
2021-05-09 19:30 | 6.1226 | 0 | N/A | 0 | 0
2021-05-09 20:00 | 5.8541 | 0 | N/A | 0 | 0
2021-05-09 20:30 | 5.6178 | 0 | N/A | 0 | 0
2021-05-09 21:00 | 5.3245 | 0 | N/A | 0 | 0
2021-05-09 21:30 | 5.7189 | 0 | N/A | 0 | 0
2021-05-09 22:00 | 5.8486 | 0 | N/A | 0 | 0
2021-05-09 22:30 | 5.3489 | 0 | N/A | 0 | 0
2021-05-09 23:00 | 5.2301 | 0 | N/A | 0 | 0
2021-05-09 23:30 | 5.4244 | 0 | N/A | 0 | 0
2021-05-10 | 5.8585 | 0 | N/A | 0 | 0
2021-05-10 00:30 | 5.1368 | 0 | N/A | 0 | 0
2021-05-10 01:00 | 4.2143 | 0 | N/A | 0 | 0
2021-05-10 01:30 | 4.1382 | 0 | N/A | 0 | 0
2021-05-10 02:00 | 3.7844 | 0 | N/A | 0 | 0
2021-05-10 02:30 | 3.2993 | 0 | N/A | 0 | 0
2021-05-10 03:00 | 3.0696 | 0 | N/A | 0 | 0
2021-05-10 03:30 | 2.8343 | 0 | N/A | 0 | 0
2021-05-10 04:00 | 2.6524 | 0 | N/A | 0 | 0
2021-05-10 04:30 | 2.5788 | 0 | N/A | 0 | 0
2021-05-10 05:00 | 2.6881 | 0 | N/A | 0 | 0
2021-05-10 05:30 | 3.0178 | 0 | N/A | 0 | 0
2021-05-10 06:00 | 3.4059 | 0 | N/A | 0 | 0
2021-05-10 06:30 | 4.2205 | 0 | N/A | 0 | 0
2021-05-10 07:00 | 4.8435 | 0 | N/A | 0 | 0
2021-05-10 07:30 | 5.3829 | 0 | N/A | 0 | 0
2021-05-10 08:00 | 6.0669 | 0 | N/A | 0 | 0
2021-05-10 08:30 | 6.1109 | 0 | N/A | 0 | 0
2021-05-10 09:00 | 5.53 | 0 | N/A | 0 | 0
2021-05-10 09:30 | 5.1979 | 0 | N/A | 0 | 0
2021-05-10 10:00 | 4.7869 | 0 | N/A | 0 | 0
2021-05-10 10:30 | 4.8918 | 0 | N/A | 0 | 0
2021-05-10 11:00 | 5.2909 | 0 | N/A | 0 | 0
2021-05-10 11:30 | 5.2073 | 0 | N/A | 0 | 0
2021-05-10 12:00 | 5.4706 | 0 | N/A | 0 | 0
2021-05-10 12:30 | 5.2852 | 0 | N/A | 0 | 0
2021-05-10 13:00 | 5.0943 | 0 | N/A | 0 | 0
2021-05-10 13:30 | 4.6242 | 0 | N/A | 0 | 0
2021-05-10 14:00 | 4.8203 | 0 | N/A | 0 | 0
2021-05-10 14:30 | 4.0537 | 0 | N/A | 0 | 0
2021-05-10 15:00 | 3.3773 | 0 | N/A | 0 | 0
2021-05-10 15:30 | 4.3993 | 0 | N/A | 0 | 0
2021-05-10 16:00 | 5.0262 | 0 | N/A | 0 | 0
2021-05-10 16:30 | 5.5148 | 0 | N/A | 0 | 0
2021-05-10 17:00 | 6.2044 | 0 | N/A | 0 | 0
2021-05-10 17:30 | 7.0256 | 0 | N/A | 0 | 0
2021-05-10 18:00 | 7.8567 | 0 | N/A | 0 | 0
2021-05-10 18:30 | 7.9901 | 0 | N/A | 0 | 0
2021-05-10 19:00 | 7.6468 | 0 | N/A | 0 | 0
2021-05-10 19:30 | 7.2072 | 0 | N/A | 0 | 0
2021-05-10 20:00 | 6.8749 | 0 | N/A | 0 | 0
2021-05-10 20:30 | 6.5753 | 0 | N/A | 0 | 0
2021-05-10 21:00 | 6.2077 | 0 | N/A | 0 | 0
2021-05-10 21:30 | 6.4231 | 0 | N/A | 0 | 0
2021-05-10 22:00 | 6.5767 | 0 | N/A | 0 | 0
2021-05-10 22:30 | 6.0084 | 0 | N/A | 0 | 0
2021-05-10 23:00 | 5.8728 | 0 | N/A | 0 | 0
2021-05-10 23:30 | 5.9917 | 0 | N/A | 0 | 0
2021-05-11 | 6.3566 | 0 | N/A | 0 | 0
2021-05-11 00:30 | 5.6714 | 0 | N/A | 0 | 0
2021-05-11 01:00 | 4.823 | 0 | N/A | 0 | 0
2021-05-11 01:30 | 4.746 | 0 | N/A | 0 | 0
2021-05-11 02:00 | 4.2468 | 0 | N/A | 0 | 0
2021-05-11 02:30 | 3.6383 | 0 | N/A | 0 | 0
2021-05-11 03:00 | 3.3205 | 0 | N/A | 0 | 0
2021-05-11 03:30 | 3.0954 | 0 | N/A | 0 | 0
2021-05-11 04:00 | 3.0013 | 0 | N/A | 0 | 0
2021-05-11 04:30 | 2.9954 | 0 | N/A | 0 | 0
2021-05-11 05:00 | 3.2005 | 0 | N/A | 0 | 0
2021-05-11 05:30 | 3.4929 | 0 | N/A | 0 | 0
2021-05-11 06:00 | 4.0382 | 0 | N/A | 0 | 0
2021-05-11 06:30 | 4.905 | 0 | N/A | 0 | 0
2021-05-11 07:00 | 5.6143 | 0 | N/A | 0 | 0
2021-05-11 07:30 | 6.1375 | 0 | N/A | 0 | 0
2021-05-11 08:00 | 6.6334 | 0 | N/A | 0 | 0
2021-05-11 08:30 | 6.8998 | 0 | N/A | 0 | 0
2021-05-11 09:00 | 6.4589 | 0 | N/A | 0 | 0
2021-05-11 09:30 | 6.1715 | 0 | N/A | 0 | 0
2021-05-11 10:00 | 5.8564 | 0 | N/A | 0 | 0
2021-05-11 10:30 | 5.4802 | 0 | N/A | 0 | 0
2021-05-11 11:00 | 5.6833 | 0 | N/A | 0 | 0
2021-05-11 11:30 | 5.6841 | 0 | N/A | 0 | 0
2021-05-11 12:00 | 5.061 | 0 | N/A | 0 | 0
2021-05-11 12:30 | 5.6182 | 0 | N/A | 0 | 0
2021-05-11 13:00 | 5.624 | 0 | N/A | 0 | 0
2021-05-11 13:30 | 5.6679 | 0 | N/A | 0 | 0
2021-05-11 14:00 | 5.8791 | 0 | N/A | 0 | 0
2021-05-11 14:30 | 5.608 | 0 | N/A | 0 | 0
2021-05-11 15:00 | 5.4372 | 0 | N/A | 0 | 0
2021-05-11 15:30 | 5.3776 | 0 | N/A | 0 | 0
2021-05-11 16:00 | 5.6518 | 0 | N/A | 0 | 0
2021-05-11 16:30 | 5.9649 | 0 | N/A | 0 | 0
2021-05-11 17:00 | 6.4634 | 0 | N/A | 0 | 0
2021-05-11 17:30 | 7.2812 | 0 | N/A | 0 | 0
2021-05-11 18:00 | 8.11 | 0 | N/A | 0 | 0
2021-05-11 18:30 | 8.4133 | 0 | N/A | 0 | 0
2021-05-11 19:00 | 8.16 | 0 | N/A | 0 | 0
2021-05-11 19:30 | 7.7901 | 0 | N/A | 0 | 0
2021-05-11 20:00 | 7.457 | 0 | N/A | 0 | 0
2021-05-11 20:30 | 7.0515 | 0 | N/A | 0 | 0
2021-05-11 21:00 | 6.5585 | 0 | N/A | 0 | 0
2021-05-11 21:30 | 6.759 | 0 | N/A | 0 | 0
2021-05-11 22:00 | 6.8178 | 0 | N/A | 0 | 0
2021-05-11 22:30 | 6.1892 | 0 | N/A | 0 | 0
2021-05-11 23:00 | 5.878 | 0 | N/A | 0 | 0
2021-05-11 23:30 | 6.022 | 0 | N/A | 0 | 0
2021-05-12 | 6.3303 | 0 | N/A | 0 | 0
2021-05-12 00:30 | 5.5971 | 0 | N/A | 0 | 0
2021-05-12 01:00 | 4.8141 | 0 | N/A | 0 | 0
2021-05-12 01:30 | 4.6311 | 0 | N/A | 0 | 0
2021-05-12 02:00 | 4.2667 | 0 | N/A | 0 | 0
2021-05-12 02:30 | 3.7041 | 0 | N/A | 0 | 0
2021-05-12 03:00 | 3.4045 | 0 | N/A | 0 | 0
2021-05-12 03:30 | 3.2832 | 0 | N/A | 0 | 0
2021-05-12 04:00 | 3.1209 | 0 | N/A | 0 | 0
2021-05-12 04:30 | 3.1034 | 0 | N/A | 0 | 0
2021-05-12 05:00 | 3.19 | 0 | N/A | 0 | 0
2021-05-12 05:30 | 3.5624 | 0 | N/A | 0 | 0
2021-05-12 06:00 | 4.0975 | 0 | N/A | 0 | 0
2021-05-12 06:30 | 4.8729 | 0 | N/A | 0 | 0
2021-05-12 07:00 | 5.8236 | 0 | N/A | 0 | 0
2021-05-12 07:30 | 6.3036 | 0 | N/A | 0 | 0
2021-05-12 08:00 | 6.7884 | 0 | N/A | 0 | 0
2021-05-12 08:30 | 6.6472 | 0 | N/A | 0 | 0
2021-05-12 09:00 | 5.9889 | 0 | N/A | 0 | 0
2021-05-12 09:30 | 5.7161 | 0 | N/A | 0 | 0
2021-05-12 10:00 | 5.1629 | 0 | N/A | 0 | 0
2021-05-12 10:30 | 4.0334 | 0 | N/A | 0 | 0
2021-05-12 11:00 | 2.9876 | 0 | N/A | 0 | 0
2021-05-12 11:30 | 2.2747 | 0 | N/A | 0 | 0
2021-05-12 12:00 | 2.1432 | 0 | N/A | 0 | 0
2021-05-12 12:30 | 2.3684 | 0 | N/A | 0 | 0
2021-05-12 13:00 | 2.1358 | 0 | N/A | 0 | 0
2021-05-12 13:30 | 2.0402 | 0 | N/A | 0 | 0
2021-05-12 14:00 | 2.0167 | 0 | N/A | 0 | 0
2021-05-12 14:30 | 2.4101 | 0 | N/A | 0 | 0
2021-05-12 15:00 | 2.25 | 0 | N/A | 0 | 0
2021-05-12 15:30 | 2.19 | 0 | N/A | 0 | 0
2021-05-12 16:00 | 2.7085 | 0 | N/A | 0 | 0
2021-05-12 16:30 | 3.3949 | 0 | N/A | 0 | 0
2021-05-12 17:00 | 4.0996 | 0 | N/A | 0 | 0
2021-05-12 17:30 | 5.2642 | 0 | N/A | 0 | 0
2021-05-12 18:00 | 6.3494 | 0 | N/A | 0 | 0
2021-05-12 18:30 | 6.9497 | 0 | N/A | 0 | 0
2021-05-12 19:00 | 6.9587 | 0 | N/A | 0 | 0
2021-05-12 19:30 | 6.8369 | 0 | N/A | 0 | 0
2021-05-12 20:00 | 6.6038 | 0 | N/A | 0 | 0
2021-05-12 20:30 | 6.3102 | 0 | N/A | 0 | 0
2021-05-12 21:00 | 6.052 | 0 | N/A | 0 | 0
2021-05-12 21:30 | 6.3798 | 0 | N/A | 0 | 0
2021-05-12 22:00 | 6.4142 | 0 | N/A | 0 | 0
2021-05-12 22:30 | 5.9072 | 0 | N/A | 0 | 0
2021-05-12 23:00 | 5.7075 | 0 | N/A | 0 | 0
2021-05-12 23:30 | 5.9119 | 0 | N/A | 0 | 0
2021-05-13 | 6.1623 | 0 | N/A | 0 | 0
2021-05-13 00:30 | 5.3928 | 0 | N/A | 0 | 0
2021-05-13 01:00 | 4.5182 | 0 | N/A | 0 | 0
2021-05-13 01:30 | 4.4119 | 0 | N/A | 0 | 0
2021-05-13 02:00 | 3.9616 | 0 | N/A | 0 | 0
2021-05-13 02:30 | 3.4572 | 0 | N/A | 0 | 0
2021-05-13 03:00 | 3.1834 | 0 | N/A | 0 | 0
2021-05-13 03:30 | 3.0459 | 0 | N/A | 0 | 0
2021-05-13 04:00 | 2.93 | 0 | N/A | 0 | 0
2021-05-13 04:30 | 2.8546 | 0 | N/A | 0 | 0
2021-05-13 05:00 | 2.9907 | 0 | N/A | 0 | 0
2021-05-13 05:30 | 3.3899 | 0 | N/A | 0 | 0
2021-05-13 06:00 | 3.8336 | 0 | N/A | 0 | 0
2021-05-13 06:30 | 4.5954 | 0 | N/A | 0 | 0
2021-05-13 07:00 | 5.4456 | 0 | N/A | 0 | 0
2021-05-13 07:30 | 5.8536 | 0 | N/A | 0 | 0
2021-05-13 08:00 | 6.6579 | 0 | N/A | 0 | 0
2021-05-13 08:30 | 7.0371 | 0 | N/A | 0 | 0
2021-05-13 09:00 | 6.7559 | 0 | N/A | 0 | 0
2021-05-13 09:30 | 6.294 | 0 | N/A | 0 | 0
2021-05-13 10:00 | 5.8362 | 0 | N/A | 0 | 0
2021-05-13 10:30 | 5.2123 | 0 | N/A | 0 | 0
2021-05-13 11:00 | 3.3526 | 0 | N/A | 0 | 0
2021-05-13 11:30 | 2.8069 | 0 | N/A | 0 | 0
2021-05-13 12:00 | 4.1881 | 0 | N/A | 0 | 0
2021-05-13 12:30 | 5.6376 | 0 | N/A | 0 | 0
2021-05-13 13:00 | 5.8677 | 0 | N/A | 0 | 0
2021-05-13 13:30 | 6.0671 | 0 | N/A | 0 | 0
2021-05-13 14:00 | 6.1425 | 0 | N/A | 0 | 0
2021-05-13 14:30 | 6.0934 | 0 | N/A | 0 | 0
2021-05-13 15:00 | 6.277 | 0 | N/A | 0 | 0
2021-05-13 15:30 | 6.1783 | 0 | N/A | 0 | 0
2021-05-13 16:00 | 5.9968 | 0 | N/A | 0 | 0
2021-05-13 16:30 | 6.1573 | 0 | N/A | 0 | 0
2021-05-13 17:00 | 6.3847 | 0 | N/A | 0 | 0
2021-05-13 17:30 | 7.4705 | 0 | N/A | 0 | 0
2021-05-13 18:00 | 8.24 | 0 | N/A | 0 | 0
2021-05-13 18:30 | 8.517 | 0 | N/A | 0 | 0
2021-05-13 19:00 | 8.4934 | 0 | N/A | 0 | 0
2021-05-13 19:30 | 8.09 | 0 | N/A | 0 | 0
2021-05-13 20:00 | 7.7833 | 0 | N/A | 0 | 0
2021-05-13 20:30 | 7.407 | 0 | N/A | 0 | 0
2021-05-13 21:00 | 7.0906 | 0 | N/A | 0 | 0
2021-05-13 21:30 | 7.2922 | 0 | N/A | 0 | 0
2021-05-13 22:00 | 7.1226 | 0 | N/A | 0 | 0
2021-05-13 22:30 | 6.4517 | 0 | N/A | 0 | 0
2021-05-13 23:00 | 6.2705 | 0 | N/A | 0 | 0
2021-05-13 23:30 | 6.4078 | 0 | N/A | 0 | 0
2021-05-14 | 6.7657 | 0 | N/A | 0 | 0
2021-05-14 00:30 | 5.9895 | 0 | N/A | 0 | 0
2021-05-14 01:00 | 5.2144 | 0 | N/A | 0 | 0
2021-05-14 01:30 | 4.9691 | 0 | N/A | 0 | 0
2021-05-14 02:00 | 4.6137 | 0 | N/A | 0 | 0
2021-05-14 02:30 | 4.048 | 0 | N/A | 0 | 0
2021-05-14 03:00 | 3.6127 | 0 | N/A | 0 | 0
2021-05-14 03:30 | 3.4529 | 0 | N/A | 0 | 0
2021-05-14 04:00 | 3.2476 | 0 | N/A | 0 | 0
2021-05-14 04:30 | 3.1902 | 0 | N/A | 0 | 0
2021-05-14 05:00 | 3.2954 | 0 | N/A | 0 | 0
2021-05-14 05:30 | 3.7008 | 0 | N/A | 0 | 0
2021-05-14 06:00 | 4.1517 | 0 | N/A | 0 | 0
2021-05-14 06:30 | 4.9305 | 0 | N/A | 0 | 0
2021-05-14 07:00 | 5.7713 | 0 | N/A | 0 | 0
2021-05-14 07:30 | 6.5334 | 0 | N/A | 0 | 0
2021-05-14 08:00 | 7.2253 | 0 | N/A | 0 | 0
2021-05-14 08:30 | 7.4592 | 0 | N/A | 0 | 0
2021-05-14 09:00 | 7.1335 | 0 | N/A | 0 | 0
2021-05-14 09:30 | 6.7504 | 0 | N/A | 0 | 0
2021-05-14 10:00 | 5.9824 | 0 | N/A | 0 | 0
2021-05-14 10:30 | 5.8912 | 0 | N/A | 0 | 0
2021-05-14 11:00 | 5.3663 | 0 | N/A | 0 | 0
2021-05-14 11:30 | 5.2175 | 0 | N/A | 0 | 0
2021-05-14 12:00 | 4.2175 | 0 | N/A | 0 | 0
2021-05-14 12:30 | 3.9421 | 0 | N/A | 0 | 0
2021-05-14 13:00 | 4.1776 | 0 | N/A | 0 | 0
2021-05-14 13:30 | 4.3915 | 0 | N/A | 0 | 0
2021-05-14 14:00 | 3.9507 | 0 | N/A | 0 | 0
2021-05-14 14:30 | 4.6867 | 0 | N/A | 0 | 0
2021-05-14 15:00 | 4.632 | 0 | N/A | 0 | 0
2021-05-14 15:30 | 4.4663 | 0 | N/A | 0 | 0
2021-05-14 16:00 | 5.2991 | 0 | N/A | 0 | 0
2021-05-14 16:30 | 5.0494 | 0 | N/A | 0 | 0
2021-05-14 17:00 | 6.0872 | 0 | N/A | 0 | 0
2021-05-14 17:30 | 7.0641 | 0 | N/A | 0 | 0
2021-05-14 18:00 | 7.7967 | 0 | N/A | 0 | 0
2021-05-14 18:30 | 8.0367 | 0 | N/A | 0 | 0
2021-05-14 19:00 | 7.9033 | 0 | N/A | 0 | 0
2021-05-14 19:30 | 7.5468 | 0 | N/A | 0 | 0
2021-05-14 20:00 | 7.2339 | 0 | N/A | 0 | 0
2021-05-14 20:30 | 7.0217 | 0 | N/A | 0 | 0
2021-05-14 21:00 | 6.6933 | 0 | N/A | 0 | 0
2021-05-14 21:30 | 6.8664 | 0 | N/A | 0 | 0
2021-05-14 22:00 | 7.0735 | 0 | N/A | 0 | 0
2021-05-14 22:30 | 6.5999 | 0 | N/A | 0 | 0
2021-05-14 23:00 | 6.3011 | 0 | N/A | 0 | 0
2021-05-14 23:30 | 6.521 | 0 | N/A | 0 | 0
2021-05-15 | 6.7792 | 0 | N/A | 0 | 0
2021-05-15 00:30 | 5.9564 | 0 | N/A | 0 | 0
2021-05-15 01:00 | 5.1046 | 0 | N/A | 0 | 0
2021-05-15 01:30 | 4.9319 | 0 | N/A | 0 | 0
2021-05-15 02:00 | 4.5529 | 0 | N/A | 0 | 0
2021-05-15 02:30 | 3.9838 | 0 | N/A | 0 | 0
2021-05-15 03:00 | 3.6715 | 0 | N/A | 0 | 0
2021-05-15 03:30 | 3.5076 | 0 | N/A | 0 | 0
2021-05-15 04:00 | 3.3438 | 0 | N/A | 0 | 0
2021-05-15 04:30 | 3.2396 | 0 | N/A | 0 | 0
2021-05-15 05:00 | 3.3123 | 0 | N/A | 0 | 0
2021-05-15 05:30 | 3.5581 | 0 | N/A | 0 | 0
2021-05-15 06:00 | 3.657 | 0 | N/A | 0 | 0
2021-05-15 06:30 | 4.0739 | 0 | N/A | 0 | 0
2021-05-15 07:00 | 4.3605 | 0 | N/A | 0 | 0
2021-05-15 07:30 | 4.4477 | 0 | N/A | 0 | 0
2021-05-15 08:00 | 5.2614 | 0 | N/A | 0 | 0
2021-05-15 08:30 | 5.6034 | 0 | N/A | 0 | 0
2021-05-15 09:00 | 5.6812 | 0 | N/A | 0 | 0
2021-05-15 09:30 | 5.4716 | 0 | N/A | 0 | 0
2021-05-15 10:00 | 5.2731 | 0 | N/A | 0 | 0
2021-05-15 10:30 | 4.0461 | 0 | N/A | 0 | 0
2021-05-15 11:00 | 3.3025 | 0 | N/A | 0 | 0
2021-05-15 11:30 | 3.3408 | 0 | N/A | 0 | 0
2021-05-15 12:00 | 3.8602 | 0 | N/A | 0 | 0
2021-05-15 12:30 | 2.9155 | 0 | N/A | 0 | 0
2021-05-15 13:00 | 2.5059 | 0 | N/A | 0 | 0
2021-05-15 13:30 | 2.7078 | 0 | N/A | 0 | 0
2021-05-15 14:00 | 3.11 | 0 | N/A | 0 | 0
2021-05-15 14:30 | 3.1033 | 0 | N/A | 0 | 0
2021-05-15 15:00 | 3.4655 | 0 | N/A | 0 | 0
2021-05-15 15:30 | 3.4946 | 0 | N/A | 0 | 0
2021-05-15 16:00 | 4.5524 | 0 | N/A | 0 | 0
2021-05-15 16:30 | 5.4424 | 0 | N/A | 0 | 0
2021-05-15 17:00 | 5.89 | 0 | N/A | 0 | 0
2021-05-15 17:30 | 6.7647 | 0 | N/A | 0 | 0
2021-05-15 18:00 | 7.5209 | 0 | N/A | 0 | 0
2021-05-15 18:30 | 7.7669 | 0 | N/A | 0 | 0
2021-05-15 19:00 | 7.5473 | 0 | N/A | 0 | 0
2021-05-15 19:30 | 7.382 | 0 | N/A | 0 | 0
2021-05-15 20:00 | 7.1028 | 0 | N/A | 0 | 0
2021-05-15 20:30 | 6.7951 | 0 | N/A | 0 | 0
2021-05-15 21:00 | 6.5673 | 0 | N/A | 0 | 0
2021-05-15 21:30 | 6.9327 | 0 | N/A | 0 | 0
2021-05-15 22:00 | 7.0091 | 0 | N/A | 0 | 0
2021-05-15 22:30 | 6.7017 | 0 | N/A | 0 | 0
2021-05-15 23:00 | 6.5714 | 0 | N/A | 0 | 0
2021-05-15 23:30 | 6.6491 | 0 | N/A | 0 | 0
2021-05-16 | 7.0662 | 0 | N/A | 0 | 0
2021-05-16 00:30 | 6.3956 | 0 | N/A | 0 | 0
2021-05-16 01:00 | 5.4965 | 0 | N/A | 0 | 0
2021-05-16 01:30 | 5.2927 | 0 | N/A | 0 | 0
2021-05-16 02:00 | 4.8244 | 0 | N/A | 0 | 0
2021-05-16 02:30 | 4.2815 | 0 | N/A | 0 | 0
2021-05-16 03:00 | 3.8916 | 0 | N/A | 0 | 0
2021-05-16 03:30 | 3.7338 | 0 | N/A | 0 | 0
2021-05-16 04:00 | 3.4635 | 0 | N/A | 0 | 0
2021-05-16 04:30 | 3.3454 | 0 | N/A | 0 | 0
2021-05-16 05:00 | 3.3284 | 0 | N/A | 0 | 0
2021-05-16 05:30 | 3.4102 | 0 | N/A | 0 | 0
2021-05-16 06:00 | 3.5101 | 0 | N/A | 0 | 0
2021-05-16 06:30 | 3.9286 | 0 | N/A | 0 | 0
2021-05-16 07:00 | 4.1357 | 0 | N/A | 0 | 0
2021-05-16 07:30 | 4.1319 | 0 | N/A | 0 | 0
2021-05-16 08:00 | 4.4996 | 0 | N/A | 0 | 0
2021-05-16 08:30 | 4.7903 | 0 | N/A | 0 | 0
2021-05-16 09:00 | 4.7986 | 0 | N/A | 0 | 0
2021-05-16 09:30 | 4.5034 | 0 | N/A | 0 | 0
2021-05-16 10:00 | 4.5968 | 0 | N/A | 0 | 0
2021-05-16 10:30 | 4.8784 | 0 | N/A | 0 | 0
2021-05-16 11:00 | 4.6174 | 0 | N/A | 0 | 0
2021-05-16 11:30 | 4.72 | 0 | N/A | 0 | 0
2021-05-16 12:00 | 4.8991 | 0 | N/A | 0 | 0
2021-05-16 12:30 | 5.0553 | 0 | N/A | 0 | 0
2021-05-16 13:00 | 5.108 | 0 | N/A | 0 | 0
2021-05-16 13:30 | 5.0354 | 0 | N/A | 0 | 0
2021-05-16 14:00 | 4.9211 | 0 | N/A | 0 | 0
2021-05-16 14:30 | 5.1558 | 0 | N/A | 0 | 0
2021-05-16 15:00 | 5.2302 | 0 | N/A | 0 | 0
2021-05-16 15:30 | 5.482 | 0 | N/A | 0 | 0
2021-05-16 16:00 | 5.8022 | 0 | N/A | 0 | 0
2021-05-16 16:30 | 6.0669 | 0 | N/A | 0 | 0
2021-05-16 17:00 | 6.6515 | 0 | N/A | 0 | 0
2021-05-16 17:30 | 7.4057 | 0 | N/A | 0 | 0
2021-05-16 18:00 | 8.1334 | 0 | N/A | 0 | 0
2021-05-16 18:30 | 8.3333 | 0 | N/A | 0 | 0
2021-05-16 19:00 | 7.8802 | 0 | N/A | 0 | 0
2021-05-16 19:30 | 7.4615 | 0 | N/A | 0 | 0
2021-05-16 20:00 | 6.9996 | 0 | N/A | 0 | 0
2021-05-16 20:30 | 6.567 | 0 | N/A | 0 | 0
2021-05-16 21:00 | 6.1905 | 0 | N/A | 0 | 0
2021-05-16 21:30 | 6.5277 | 0 | N/A | 0 | 0
2021-05-16 22:00 | 6.4917 | 0 | N/A | 0 | 0
2021-05-16 22:30 | 6.0504 | 0 | N/A | 0 | 0
2021-05-16 23:00 | 6.0406 | 0 | N/A | 0 | 0
2021-05-16 23:30 | 6.0084 | 0 | N/A | 0 | 0
2021-05-17 | 6.5199 | 0 | N/A | 0 | 0
2021-05-17 00:30 | 5.8492 | 0 | N/A | 0 | 0
2021-05-17 01:00 | 5.1463 | 0 | N/A | 0 | 0
2021-05-17 01:30 | 4.9505 | 0 | N/A | 0 | 0
2021-05-17 02:00 | 4.5423 | 0 | N/A | 0 | 0
2021-05-17 02:30 | 3.9185 | 0 | N/A | 0 | 0
2021-05-17 03:00 | 3.4829 | 0 | N/A | 0 | 0
2021-05-17 03:30 | 3.2986 | 0 | N/A | 0 | 0
2021-05-17 04:00 | 3.1314 | 0 | N/A | 0 | 0
2021-05-17 04:30 | 3.0339 | 0 | N/A | 0 | 0
2021-05-17 05:00 | 3.0574 | 0 | N/A | 0 | 0
2021-05-17 05:30 | 3.4604 | 0 | N/A | 0 | 0
2021-05-17 06:00 | 3.8338 | 0 | N/A | 0 | 0
2021-05-17 06:30 | 4.6312 | 0 | N/A | 0 | 0
2021-05-17 07:00 | 5.4895 | 0 | N/A | 0 | 0
2021-05-17 07:30 | 5.9267 | 0 | N/A | 0 | 0
2021-05-17 08:00 | 6.4835 | 0 | N/A | 0 | 0
2021-05-17 08:30 | 6.6684 | 0 | N/A | 0 | 0
2021-05-17 09:00 | 6.4055 | 0 | N/A | 0 | 0
2021-05-17 09:30 | 6.3444 | 0 | N/A | 0 | 0
2021-05-17 10:00 | 5.7848 | 0 | N/A | 0 | 0
2021-05-17 10:30 | 5.5965 | 0 | N/A | 0 | 0
2021-05-17 11:00 | 4.8102 | 0 | N/A | 0 | 0
2021-05-17 11:30 | 4.7566 | 0 | N/A | 0 | 0
2021-05-17 12:00 | 4.271 | 0 | N/A | 0 | 0
2021-05-17 12:30 | 3.8515 | 0 | N/A | 0 | 0
2021-05-17 13:00 | 4.6428 | 0 | N/A | 0 | 0
2021-05-17 13:30 | 4.3413 | 0 | N/A | 0 | 0
2021-05-17 14:00 | 3.9016 | 0 | N/A | 0 | 0
2021-05-17 14:30 | 4.5019 | 0 | N/A | 0 | 0
2021-05-17 15:00 | 4.4141 | 0 | N/A | 0 | 0
2021-05-17 15:30 | 4.6133 | 0 | N/A | 0 | 0
2021-05-17 16:00 | 4.2941 | 0 | N/A | 0 | 0
2021-05-17 16:30 | 5.1793 | 0 | N/A | 0 | 0
2021-05-17 17:00 | 5.9458 | 0 | N/A | 0 | 0
2021-05-17 17:30 | 6.8272 | 0 | N/A | 0 | 0
2021-05-17 18:00 | 7.7935 | 0 | N/A | 0 | 0
2021-05-17 18:30 | 8.08 | 0 | N/A | 0 | 0
2021-05-17 19:00 | 7.8067 | 0 | N/A | 0 | 0
2021-05-17 19:30 | 7.587 | 0 | N/A | 0 | 0
2021-05-17 20:00 | 7.1907 | 0 | N/A | 0 | 0
2021-05-17 20:30 | 6.7105 | 0 | N/A | 0 | 0
2021-05-17 21:00 | 6.3339 | 0 | N/A | 0 | 0
2021-05-17 21:30 | 6.6414 | 0 | N/A | 0 | 0
2021-05-17 22:00 | 6.7006 | 0 | N/A | 0 | 0
2021-05-17 22:30 | 6.2102 | 0 | N/A | 0 | 0
2021-05-17 23:00 | 6.03 | 0 | N/A | 0 | 0
2021-05-17 23:30 | 6.1036 | 0 | N/A | 0 | 0
2021-05-18 | 6.3309 | 0 | N/A | 0 | 0
2021-05-18 00:30 | 5.7233 | 0 | N/A | 0 | 0
2021-05-18 01:00 | 4.947 | 0 | N/A | 0 | 0
2021-05-18 01:30 | 4.6832 | 0 | N/A | 0 | 0
2021-05-18 02:00 | 4.2393 | 0 | N/A | 0 | 0
2021-05-18 02:30 | 3.7077 | 0 | N/A | 0 | 0
2021-05-18 03:00 | 3.3688 | 0 | N/A | 0 | 0
2021-05-18 03:30 | 3.2058 | 0 | N/A | 0 | 0
2021-05-18 04:00 | 3.0503 | 0 | N/A | 0 | 0
2021-05-18 04:30 | 3.0435 | 0 | N/A | 0 | 0
2021-05-18 05:00 | 3.1361 | 0 | N/A | 0 | 0
2021-05-18 05:30 | 3.4923 | 0 | N/A | 0 | 0
2021-05-18 06:00 | 3.9913 | 0 | N/A | 0 | 0
2021-05-18 06:30 | 4.7709 | 0 | N/A | 0 | 0
2021-05-18 07:00 | 5.6851 | 0 | N/A | 0 | 0
2021-05-18 07:30 | 6.0867 | 0 | N/A | 0 | 0
2021-05-18 08:00 | 6.6241 | 0 | N/A | 0 | 0
2021-05-18 08:30 | 6.659 | 0 | N/A | 0 | 0
2021-05-18 09:00 | 6.1507 | 0 | N/A | 0 | 0
2021-05-18 09:30 | 5.8609 | 0 | N/A | 0 | 0
2021-05-18 10:00 | 5.4481 | 0 | N/A | 0 | 0
2021-05-18 10:30 | 4.6954 | 0 | N/A | 0 | 0
2021-05-18 11:00 | 4.6717 | 0 | N/A | 0 | 0
2021-05-18 11:30 | 4.9073 | 0 | N/A | 0 | 0
2021-05-18 12:00 | 4.7155 | 0 | N/A | 0 | 0
2021-05-18 12:30 | 4.8745 | 0 | N/A | 0 | 0
2021-05-18 13:00 | 5.0636 | 0 | N/A | 0 | 0
2021-05-18 13:30 | 4.9669 | 0 | N/A | 0 | 0
2021-05-18 14:00 | 4.8636 | 0 | N/A | 0 | 0
2021-05-18 14:30 | 4.6435 | 0 | N/A | 0 | 0
2021-05-18 15:00 | 4.5478 | 0 | N/A | 0 | 0
2021-05-18 15:30 | 4.5678 | 0 | N/A | 0 | 0
2021-05-18 16:00 | 4.5484 | 0 | N/A | 0 | 0
2021-05-18 16:30 | 4.8976 | 0 | N/A | 0 | 0
2021-05-18 17:00 | 5.795 | 0 | N/A | 0 | 0
2021-05-18 17:30 | 6.6055 | 0 | N/A | 0 | 0
2021-05-18 18:00 | 7.5138 | 0 | N/A | 0 | 0
2021-05-18 18:30 | 7.8233 | 0 | N/A | 0 | 0
2021-05-18 19:00 | 7.5838 | 0 | N/A | 0 | 0
2021-05-18 19:30 | 7.2308 | 0 | N/A | 0 | 0
2021-05-18 20:00 | 6.8978 | 0 | N/A | 0 | 0
2021-05-18 20:30 | 6.396 | 0 | N/A | 0 | 0
2021-05-18 21:00 | 6.0352 | 0 | N/A | 0 | 0
2021-05-18 21:30 | 6.3937 | 0 | N/A | 0 | 0
2021-05-18 22:00 | 6.5665 | 0 | N/A | 0 | 0
2021-05-18 22:30 | 5.9785 | 0 | N/A | 0 | 0
2021-05-18 23:00 | 5.8408 | 0 | N/A | 0 | 0
2021-05-18 23:30 | 5.9912 | 0 | N/A | 0 | 0
2021-05-19 | 6.3156 | 0 | N/A | 0 | 0
2021-05-19 00:30 | 5.5967 | 0 | N/A | 0 | 0
2021-05-19 01:00 | 4.7657 | 0 | N/A | 0 | 0
2021-05-19 01:30 | 4.6278 | 0 | N/A | 0 | 0
2021-05-19 02:00 | 4.2174 | 0 | N/A | 0 | 0
2021-05-19 02:30 | 3.7107 | 0 | N/A | 0 | 0
2021-05-19 03:00 | 3.3965 | 0 | N/A | 0 | 0
2021-05-19 03:30 | 3.1852 | 0 | N/A | 0 | 0
2021-05-19 04:00 | 3.0239 | 0 | N/A | 0 | 0
2021-05-19 04:30 | 3.0238 | 0 | N/A | 0 | 0
2021-05-19 05:00 | 3.1583 | 0 | N/A | 0 | 0
2021-05-19 05:30 | 3.6665 | 0 | N/A | 0 | 0
2021-05-19 06:00 | 4.2399 | 0 | N/A | 0 | 0
2021-05-19 06:30 | 5.0127 | 0 | N/A | 0 | 0
2021-05-19 07:00 | 5.7711 | 0 | N/A | 0 | 0
2021-05-19 07:30 | 6.23 | 0 | N/A | 0 | 0
2021-05-19 08:00 | 6.6672 | 0 | N/A | 0 | 0
2021-05-19 08:30 | 6.5174 | 0 | N/A | 0 | 0
2021-05-19 09:00 | 5.8591 | 0 | N/A | 0 | 0
2021-05-19 09:30 | 5.1142 | 0 | N/A | 0 | 0
2021-05-19 10:00 | 4.44 | 0 | N/A | 0 | 0
2021-05-19 10:30 | 3.7168 | 0 | N/A | 0 | 0
2021-05-19 11:00 | 3.0718 | 0 | N/A | 0 | 0
2021-05-19 11:30 | 2.6207 | 0 | N/A | 0 | 0
2021-05-19 12:00 | 2.5072 | 0 | N/A | 0 | 0
2021-05-19 12:30 | 2.2823 | 0 | N/A | 0 | 0
2021-05-19 13:00 | 1.7807 | 0 | N/A | 0 | 0
2021-05-19 13:30 | 2.3874 | 0 | N/A | 0 | 0
2021-05-19 14:00 | 2.9741 | 0 | N/A | 0 | 0
2021-05-19 14:30 | 3.7278 | 0 | N/A | 0 | 0
2021-05-19 15:00 | 3.7403 | 0 | N/A | 0 | 0
2021-05-19 15:30 | 4.4267 | 0 | N/A | 0 | 0
2021-05-19 16:00 | 4.9167 | 0 | N/A | 0 | 0
2021-05-19 16:30 | 5.2718 | 0 | N/A | 0 | 0
2021-05-19 17:00 | 5.7205 | 0 | N/A | 0 | 0
2021-05-19 17:30 | 6.6523 | 0 | N/A | 0 | 0
2021-05-19 18:00 | 7.5102 | 0 | N/A | 0 | 0
2021-05-19 18:30 | 7.8467 | 0 | N/A | 0 | 0
2021-05-19 19:00 | 7.5234 | 0 | N/A | 0 | 0
2021-05-19 19:30 | 7.2902 | 0 | N/A | 0 | 0
2021-05-19 20:00 | 7.0239 | 0 | N/A | 0 | 0
2021-05-19 20:30 | 6.6032 | 0 | N/A | 0 | 0
2021-05-19 21:00 | 6.1718 | 0 | N/A | 0 | 0
2021-05-19 21:30 | 6.4268 | 0 | N/A | 0 | 0
2021-05-19 22:00 | 6.5312 | 0 | N/A | 0 | 0
2021-05-19 22:30 | 6.0161 | 0 | N/A | 0 | 0
2021-05-19 23:00 | 5.8243 | 0 | N/A | 0 | 0
2021-05-19 23:30 | 5.9422 | 0 | N/A | 0 | 0
2021-05-20 | 6.1877 | 0 | N/A | 0 | 0
2021-05-20 00:30 | 5.3751 | 0 | N/A | 0 | 0
2021-05-20 01:00 | 4.6573 | 0 | N/A | 0 | 0
2021-05-20 01:30 | 4.6018 | 0 | N/A | 0 | 0
2021-05-20 02:00 | 4.1904 | 0 | N/A | 0 | 0
2021-05-20 02:30 | 3.6282 | 0 | N/A | 0 | 0
2021-05-20 03:00 | 3.309 | 0 | N/A | 0 | 0
2021-05-20 03:30 | 3.0963 | 0 | N/A | 0 | 0
2021-05-20 04:00 | 2.9088 | 0 | N/A | 0 | 0
2021-05-20 04:30 | 2.8514 | 0 | N/A | 0 | 0
2021-05-20 05:00 | 2.8561 | 0 | N/A | 0 | 0
2021-05-20 05:30 | 3.2371 | 0 | N/A | 0 | 0
2021-05-20 06:00 | 3.9203 | 0 | N/A | 0 | 0
2021-05-20 06:30 | 4.669 | 0 | N/A | 0 | 0
2021-05-20 07:00 | 5.5237 | 0 | N/A | 0 | 0
2021-05-20 07:30 | 6.2235 | 0 | N/A | 0 | 0
2021-05-20 08:00 | 6.7405 | 0 | N/A | 0 | 0
2021-05-20 08:30 | 6.6617 | 0 | N/A | 0 | 0
2021-05-20 09:00 | 6.2044 | 0 | N/A | 0 | 0
2021-05-20 09:30 | 6.4375 | 0 | N/A | 0 | 0
2021-05-20 10:00 | 5.7969 | 0 | N/A | 0 | 0
2021-05-20 10:30 | 5.142 | 0 | N/A | 0 | 0
2021-05-20 11:00 | 5.2688 | 0 | N/A | 0 | 0
2021-05-20 11:30 | 5.1137 | 0 | N/A | 0 | 0
2021-05-20 12:00 | 4.773 | 0 | N/A | 0 | 0
2021-05-20 12:30 | 4.3368 | 0 | N/A | 0 | 0
2021-05-20 13:00 | 3.8139 | 0 | N/A | 0 | 0
2021-05-20 13:30 | 4.01 | 0 | N/A | 0 | 0
2021-05-20 14:00 | 3.8025 | 0 | N/A | 0 | 0
2021-05-20 14:30 | 3.9767 | 0 | N/A | 0 | 0
2021-05-20 15:00 | 4.2267 | 0 | N/A | 0 | 0
2021-05-20 15:30 | 4.26 | 0 | N/A | 0 | 0
2021-05-20 16:00 | 4.38 | 0 | N/A | 0 | 0
2021-05-20 16:30 | 4.5832 | 0 | N/A | 0 | 0
2021-05-20 17:00 | 5.2449 | 0 | N/A | 0 | 0
2021-05-20 17:30 | 6.015 | 0 | N/A | 0 | 0
2021-05-20 18:00 | 7.0955 | 0 | N/A | 0 | 0
2021-05-20 18:30 | 7.4641 | 0 | N/A | 0 | 0
2021-05-20 19:00 | 7.3614 | 0 | N/A | 0 | 0
2021-05-20 19:30 | 7.2943 | 0 | N/A | 0 | 0
2021-05-20 20:00 | 7.1618 | 0 | N/A | 0 | 0
2021-05-20 20:30 | 6.8857 | 0 | N/A | 0 | 0
2021-05-20 21:00 | 6.6065 | 0 | N/A | 0 | 0
2021-05-20 21:30 | 6.791 | 0 | N/A | 0 | 0
2021-05-20 22:00 | 7.0211 | 0 | N/A | 0 | 0
2021-05-20 22:30 | 6.3906 | 0 | N/A | 0 | 0
2021-05-20 23:00 | 6.2104 | 0 | N/A | 0 | 0
2021-05-20 23:30 | 6.3176 | 0 | N/A | 0 | 0
2021-05-21 | 6.7092 | 0 | N/A | 0 | 0
2021-05-21 00:30 | 5.9984 | 0 | N/A | 0 | 0
2021-05-21 01:00 | 5.2115 | 0 | N/A | 0 | 0
2021-05-21 01:30 | 5.0179 | 0 | N/A | 0 | 0
2021-05-21 02:00 | 4.6872 | 0 | N/A | 0 | 0
2021-05-21 02:30 | 4.1322 | 0 | N/A | 0 | 0
2021-05-21 03:00 | 3.7985 | 0 | N/A | 0 | 0
2021-05-21 03:30 | 3.5713 | 0 | N/A | 0 | 0
2021-05-21 04:00 | 3.4667 | 0 | N/A | 0 | 0
2021-05-21 04:30 | 3.4918 | 0 | N/A | 0 | 0
2021-05-21 05:00 | 3.6295 | 0 | N/A | 0 | 0
2021-05-21 05:30 | 4.0276 | 0 | N/A | 0 | 0
2021-05-21 06:00 | 4.5237 | 0 | N/A | 0 | 0
2021-05-21 06:30 | 5.5176 | 0 | N/A | 0 | 0
2021-05-21 07:00 | 6.3795 | 0 | N/A | 0 | 0
2021-05-21 07:30 | 6.8533 | 0 | N/A | 0 | 0
2021-05-21 08:00 | 7.9345 | 0 | N/A | 0 | 0
2021-05-21 08:30 | 7.9071 | 0 | N/A | 0 | 0
2021-05-21 09:00 | 7.058 | 0 | N/A | 0 | 0
2021-05-22 00:30 | 6.198 | 0 | N/A | 0 | 0
2021-05-22 01:00 | 5.2211 | 0 | N/A | 0 | 0
2021-05-22 01:30 | 5.1573 | 0 | N/A | 0 | 0
2021-05-22 02:00 | 4.8283 | 0 | N/A | 0 | 0
2021-05-22 02:30 | 4.2442 | 0 | N/A | 0 | 0
2021-05-22 03:00 | 3.8539 | 0 | N/A | 0 | 0
2021-05-22 03:30 | 3.7113 | 0 | N/A | 0 | 0
2021-05-22 04:00 | 3.5818 | 0 | N/A | 0 | 0
2021-05-22 04:30 | 3.4824 | 0 | N/A | 0 | 0
2021-05-22 05:00 | 3.5089 | 0 | N/A | 0 | 0
2021-05-22 05:30 | 3.7226 | 0 | N/A | 0 | 0
2021-05-22 06:00 | 4.0079 | 0 | N/A | 0 | 0
2021-05-22 06:30 | 4.548 | 0 | N/A | 0 | 0
2021-05-22 07:00 | 4.9025 | 0 | N/A | 0 | 0
2021-05-22 07:30 | 5.0022 | 0 | N/A | 0 | 0
2021-05-22 08:00 | 5.7435 | 0 | N/A | 0 | 0
2021-05-22 08:30 | 6.065 | 0 | N/A | 0 | 0
2021-05-22 09:00 | 5.7537 | 0 | N/A | 0 | 0
2021-05-22 09:30 | 5.0748 | 0 | N/A | 0 | 0
2021-05-22 10:00 | 4.2785 | 0 | N/A | 0 | 0
2021-05-22 10:30 | 3.349 | 0 | N/A | 0 | 0
2021-05-22 11:00 | 2.5561 | 0 | N/A | 0 | 0
2021-05-22 11:30 | 2.0503 | 0 | N/A | 0 | 0
2021-05-22 12:00 | 1.5876 | 0 | N/A | 0 | 0
2021-05-22 12:30 | 1.37 | 0 | N/A | 0 | 0
2021-05-22 13:00 | 1.3245 | 0 | N/A | 0 | 0
2021-05-22 13:30 | 1.2484 | 0 | N/A | 0 | 0
2021-05-22 14:00 | 1.2153 | 0 | N/A | 0 | 0
2021-05-22 14:30 | 1.3068 | 0 | N/A | 0 | 0
2021-05-22 15:00 | 1.749 | 0 | N/A | 0 | 0
2021-05-22 15:30 | 2.2724 | 0 | N/A | 0 | 0
2021-05-22 16:00 | 2.9337 | 0 | N/A | 0 | 0
2021-05-22 16:30 | 3.6403 | 0 | N/A | 0 | 0
2021-05-22 17:00 | 4.7497 | 0 | N/A | 0 | 0
2021-05-22 17:30 | 5.8561 | 0 | N/A | 0 | 0
2021-05-22 18:00 | 6.7281 | 0 | N/A | 0 | 0
2021-05-22 18:30 | 7.0765 | 0 | N/A | 0 | 0
2021-05-22 19:00 | 6.9669 | 0 | N/A | 0 | 0
2021-05-22 19:30 | 6.6335 | 0 | N/A | 0 | 0
2021-05-22 20:00 | 6.4958 | 0 | N/A | 0 | 0
2021-05-22 20:30 | 6.2139 | 0 | N/A | 0 | 0
2021-05-22 21:00 | 6.068 | 0 | N/A | 0 | 0
2021-05-22 21:30 | 6.4884 | 0 | N/A | 0 | 0
2021-05-22 22:00 | 6.666 | 0 | N/A | 0 | 0
2021-05-22 22:30 | 6.3983 | 0 | N/A | 0 | 0
2021-05-22 23:00 | 6.3096 | 0 | N/A | 0 | 0
2021-05-22 23:30 | 6.4126 | 0 | N/A | 0 | 0
2021-05-23 | 6.8067 | 0 | N/A | 0 | 0
2021-05-23 00:30 | 6.1779 | 0 | N/A | 0 | 0
2021-05-23 01:00 | 5.2905 | 0 | N/A | 0 | 0
2021-05-23 01:30 | 5.2002 | 0 | N/A | 0 | 0
2021-05-23 02:00 | 4.767 | 0 | N/A | 0 | 0
2021-05-23 02:30 | 4.2509 | 0 | N/A | 0 | 0
2021-05-23 03:00 | 3.9812 | 0 | N/A | 0 | 0
2021-05-23 03:30 | 3.7913 | 0 | N/A | 0 | 0
2021-05-23 04:00 | 3.5683 | 0 | N/A | 0 | 0
2021-05-23 04:30 | 3.5006 | 0 | N/A | 0 | 0
2021-05-23 05:00 | 3.5236 | 0 | N/A | 0 | 0
2021-05-23 05:30 | 3.6495 | 0 | N/A | 0 | 0
2021-05-23 06:00 | 3.872 | 0 | N/A | 0 | 0
2021-05-23 06:30 | 4.2377 | 0 | N/A | 0 | 0
2021-05-23 07:00 | 4.4696 | 0 | N/A | 0 | 0
2021-05-23 07:30 | 4.4583 | 0 | N/A | 0 | 0
2021-05-23 08:00 | 4.8833 | 0 | N/A | 0 | 0
2021-05-23 08:30 | 4.9469 | 0 | N/A | 0 | 0
2021-05-23 09:00 | 4.5959 | 0 | N/A | 0 | 0
2021-05-23 09:30 | 4.182 | 0 | N/A | 0 | 0
2021-05-23 10:00 | 4.011 | 0 | N/A | 0 | 0
2021-05-23 10:30 | 3.1084 | 0 | N/A | 0 | 0
2021-05-23 11:00 | 2.8131 | 0 | N/A | 0 | 0
2021-05-23 11:30 | 2.5356 | 0 | N/A | 0 | 0
2021-05-23 12:00 | 1.5797 | 0 | N/A | 0 | 0
2021-05-23 12:30 | 1.2776 | 0 | N/A | 0 | 0
2021-05-23 13:00 | 0.96799 | 0 | N/A | 0 | 0
2021-05-23 13:30 | 1.0411 | 0 | N/A | 0 | 0
2021-05-23 14:00 | 1.095 | 0 | N/A | 0 | 0
2021-05-23 14:30 | 1.3402 | 0 | N/A | 0 | 0
2021-05-23 15:00 | 2.0971 | 0 | N/A | 0 | 0
2021-05-23 15:30 | 3.0371 | 0 | N/A | 0 | 0
2021-05-23 16:00 | 3.3097 | 0 | N/A | 0 | 0
2021-05-23 16:30 | 4.1034 | 0 | N/A | 0 | 0
2021-05-23 17:00 | 5.1438 | 0 | N/A | 0 | 0
2021-05-23 17:30 | 6.3522 | 0 | N/A | 0 | 0
2021-05-23 18:00 | 7.3038 | 0 | N/A | 0 | 0
2021-05-23 18:30 | 7.642 | 0 | N/A | 0 | 0
2021-05-23 19:00 | 7.4227 | 0 | N/A | 0 | 0
2021-05-23 19:30 | 7.0851 | 0 | N/A | 0 | 0
2021-05-23 20:00 | 6.7338 | 0 | N/A | 0 | 0
2021-05-23 20:30 | 6.3231 | 0 | N/A | 0 | 0
2021-05-23 21:00 | 5.9575 | 0 | N/A | 0 | 0
2021-05-23 21:30 | 6.2971 | 0 | N/A | 0 | 0
2021-05-23 22:00 | 6.4536 | 0 | N/A | 0 | 0
2021-05-23 22:30 | 5.9178 | 0 | N/A | 0 | 0
2021-05-23 23:00 | 5.8044 | 0 | N/A | 0 | 0
2021-05-23 23:30 | 5.9034 | 0 | N/A | 0 | 0
2021-05-24 | 6.1988 | 0 | N/A | 0 | 0
2021-05-24 00:30 | 5.63 | 0 | N/A | 0 | 0
2021-05-24 01:00 | 4.9857 | 0 | N/A | 0 | 0
2021-05-24 01:30 | 4.876 | 0 | N/A | 0 | 0
2021-05-24 02:00 | 4.5117 | 0 | N/A | 0 | 0
2021-05-24 02:30 | 3.8351 | 0 | N/A | 0 | 0
2021-05-24 03:00 | 3.4513 | 0 | N/A | 0 | 0
2021-05-24 03:30 | 3.2536 | 0 | N/A | 0 | 0
2021-05-24 04:00 | 3.0412 | 0 | N/A | 0 | 0
2021-05-24 04:30 | 2.9639 | 0 | N/A | 0 | 0
2021-05-24 05:00 | 3.0542 | 0 | N/A | 0 | 0
2021-05-24 05:30 | 3.3721 | 0 | N/A | 0 | 0
2021-05-24 06:00 | 3.9534 | 0 | N/A | 0 | 0
2021-05-24 06:30 | 4.6236 | 0 | N/A | 0 | 0
2021-05-24 07:00 | 5.3948 | 0 | N/A | 0 | 0
2021-05-24 07:30 | 5.8243 | 0 | N/A | 0 | 0
2021-05-24 08:00 | 6.4602 | 0 | N/A | 0 | 0
2021-05-24 08:30 | 6.3207 | 0 | N/A | 0 | 0
2021-05-24 09:00 | 5.801 | 0 | N/A | 0 | 0
2021-05-24 09:30 | 4.7546 | 0 | N/A | 0 | 0
2021-05-24 10:00 | 3.9773 | 0 | N/A | 0 | 0
2021-05-24 10:30 | 3.5233 | 0 | N/A | 0 | 0
2021-05-24 11:00 | 3.3302 | 0 | N/A | 0 | 0
2021-05-24 11:30 | 2.2322 | 0 | N/A | 0 | 0
2021-05-24 12:00 | 2.6605 | 0 | N/A | 0 | 0
2021-05-24 12:30 | 4.2836 | 0 | N/A | 0 | 0
2021-05-24 13:00 | 3.8033 | 0 | N/A | 0 | 0
2021-05-24 13:30 | 3.5004 | 0 | N/A | 0 | 0
2021-05-24 14:00 | 1.857 | 0 | N/A | 0 | 0
2021-05-24 14:30 | 2.46 | 0 | N/A | 0 | 0
2021-05-24 15:00 | 2.5467 | 0 | N/A | 0 | 0
2021-05-24 15:30 | 2.7426 | 0 | N/A | 0 | 0
2021-05-24 16:00 | 3.8747 | 0 | N/A | 0 | 0
2021-05-24 16:30 | 4.3563 | 0 | N/A | 0 | 0
2021-05-24 17:00 | 5.2111 | 0 | N/A | 0 | 0
2021-05-24 17:30 | 6.1605 | 0 | N/A | 0 | 0
2021-05-24 18:00 | 7.2241 | 0 | N/A | 0 | 0
2021-05-24 18:30 | 7.3373 | 0 | N/A | 0 | 0
2021-05-24 19:00 | 7.1186 | 0 | N/A | 0 | 0
2021-05-24 19:30 | 6.7957 | 0 | N/A | 0 | 0
2021-05-24 20:00 | 6.4756 | 0 | N/A | 0 | 0
2021-05-24 20:30 | 5.9969 | 0 | N/A | 0 | 0
2021-05-24 21:00 | 5.5734 | 0 | N/A | 0 | 0
2021-05-24 21:30 | 5.8741 | 0 | N/A | 0 | 0
2021-05-24 22:00 | 6.01 | 0 | N/A | 0 | 0
2021-05-24 22:30 | 5.3995 | 0 | N/A | 0 | 0
2021-05-24 23:00 | 5.3395 | 0 | N/A | 0 | 0
2021-05-24 23:30 | 5.4341 | 0 | N/A | 0 | 0
2021-05-25 | 5.701 | 0 | N/A | 0 | 0
2021-05-25 00:30 | 4.9725 | 0 | N/A | 0 | 0
2021-05-25 01:00 | 4.2137 | 0 | N/A | 0 | 0
2021-05-25 01:30 | 4.1144 | 0 | N/A | 0 | 0
2021-05-25 02:00 | 3.8373 | 0 | N/A | 0 | 0
2021-05-25 02:30 | 3.2007 | 0 | N/A | 0 | 0
2021-05-25 03:00 | 2.8823 | 0 | N/A | 0 | 0
2021-05-25 03:30 | 2.647 | 0 | N/A | 0 | 0
2021-05-25 04:00 | 2.5077 | 0 | N/A | 0 | 0
2021-05-25 04:30 | 2.4754 | 0 | N/A | 0 | 0
2021-05-25 05:00 | 2.591 | 0 | N/A | 0 | 0
2021-05-25 05:30 | 2.9336 | 0 | N/A | 0 | 0
2021-05-25 06:00 | 3.3152 | 0 | N/A | 0 | 0
2021-05-25 06:30 | 4.0726 | 0 | N/A | 0 | 0
2021-05-25 07:00 | 4.6789 | 0 | N/A | 0 | 0
2021-05-25 07:30 | 5.0955 | 0 | N/A | 0 | 0
2021-05-25 08:00 | 5.8334 | 0 | N/A | 0 | 0
2021-05-25 08:30 | 6.0393 | 0 | N/A | 0 | 0
2021-05-25 09:00 | 5.4817 | 0 | N/A | 0 | 0
2021-05-25 09:30 | 5.1908 | 0 | N/A | 0 | 0
2021-05-25 10:00 | 4.132 | 0 | N/A | 0 | 0
2021-05-25 10:30 | 3.7012 | 0 | N/A | 0 | 0
2021-05-25 11:00 | 4.2557 | 0 | N/A | 0 | 0
2021-05-25 11:30 | 4.1908 | 0 | N/A | 0 | 0
2021-05-25 12:00 | 4.5027 | 0 | N/A | 0 | 0
2021-05-25 12:30 | 5.8573 | 0 | N/A | 0 | 0
2021-05-25 13:00 | 5.9668 | 0 | N/A | 0 | 0
2021-05-25 13:30 | 6.4278 | 0 | N/A | 0 | 0
2021-05-25 14:00 | 6.7897 | 0 | N/A | 0 | 0
2021-05-25 14:30 | 6.8756 | 0 | N/A | 0 | 0
2021-05-25 15:00 | 6.8087 | 0 | N/A | 0 | 0
2021-05-25 15:30 | 6.1426 | 0 | N/A | 0 | 0
2021-05-25 16:00 | 5.3534 | 0 | N/A | 0 | 0
2021-05-25 16:30 | 5.7614 | 0 | N/A | 0 | 0
2021-05-25 17:00 | 6.4549 | 0 | N/A | 0 | 0
2021-05-25 17:30 | 7.1142 | 0 | N/A | 0 | 0
2021-05-25 18:00 | 7.8867 | 0 | N/A | 0 | 0
2021-05-25 18:30 | 7.9933 | 0 | N/A | 0 | 0
2021-05-25 19:00 | 7.597 | 0 | N/A | 0 | 0
2021-05-25 19:30 | 7.1742 | 0 | N/A | 0 | 0
2021-05-25 20:00 | 6.8662 | 0 | N/A | 0 | 0
2021-05-25 20:30 | 6.5311 | 0 | N/A | 0 | 0
2021-05-25 21:00 | 6.169 | 0 | N/A | 0 | 0
2021-05-25 21:30 | 6.4656 | 0 | N/A | 0 | 0
2021-05-25 22:00 | 6.572 | 0 | N/A | 0 | 0
2021-05-25 22:30 | 5.8644 | 0 | N/A | 0 | 0
2021-05-25 23:00 | 5.7815 | 0 | N/A | 0 | 0
2021-05-25 23:30 | 5.9245 | 0 | N/A | 0 | 0
2021-05-26 | 6.2213 | 0 | N/A | 0 | 0
2021-05-26 00:30 | 5.5585 | 0 | N/A | 0 | 0
2021-05-26 01:00 | 4.7941 | 0 | N/A | 0 | 0
2021-05-26 01:30 | 4.6266 | 0 | N/A | 0 | 0
2021-05-26 02:00 | 4.2405 | 0 | N/A | 0 | 0
2021-05-26 02:30 | 3.7131 | 0 | N/A | 0 | 0
2021-05-26 03:00 | 3.3316 | 0 | N/A | 0 | 0
2021-05-26 03:30 | 3.2032 | 0 | N/A | 0 | 0
2021-05-26 04:00 | 3.0741 | 0 | N/A | 0 | 0
2021-05-26 04:30 | 3.0151 | 0 | N/A | 0 | 0
2021-05-26 05:00 | 3.0057 | 0 | N/A | 0 | 0
2021-05-27 00:30 | 5.8426 | 0 | N/A | 0 | 0
2021-05-27 01:00 | 4.9262 | 0 | N/A | 0 | 0
2021-05-27 01:30 | 4.7906 | 0 | N/A | 0 | 0
2021-05-27 02:00 | 4.4 | 0 | N/A | 0 | 0
2021-05-27 02:30 | 3.8014 | 0 | N/A | 0 | 0
2021-05-27 03:00 | 3.5128 | 0 | N/A | 0 | 0
2021-05-27 03:30 | 3.261 | 0 | N/A | 0 | 0
2021-05-27 04:00 | 3.0938 | 0 | N/A | 0 | 0
2021-05-27 04:30 | 3.0737 | 0 | N/A | 0 | 0
2021-05-27 05:00 | 3.2152 | 0 | N/A | 0 | 0
2021-05-27 05:30 | 3.5576 | 0 | N/A | 0 | 0
2021-05-27 06:00 | 3.9997 | 0 | N/A | 0 | 0
2021-05-27 06:30 | 4.6469 | 0 | N/A | 0 | 0
2021-05-27 07:00 | 5.5877 | 0 | N/A | 0 | 0
2021-05-27 07:30 | 6.36 | 0 | N/A | 0 | 0
2021-05-27 08:00 | 6.9479 | 0 | N/A | 0 | 0
2021-05-27 08:30 | 6.9949 | 0 | N/A | 0 | 0
2021-05-27 09:00 | 6.6611 | 0 | N/A | 0 | 0
2021-05-27 09:30 | 6.1983 | 0 | N/A | 0 | 0
2021-05-27 10:00 | 5.8276 | 0 | N/A | 0 | 0
2021-05-27 10:30 | 4.7056 | 0 | N/A | 0 | 0
2021-05-27 11:00 | 4.2203 | 0 | N/A | 0 | 0
2021-05-27 11:30 | 4.39 | 0 | N/A | 0 | 0
2021-05-27 12:00 | 4.0539 | 0 | N/A | 0 | 0
2021-05-27 12:30 | 4.389 | 0 | N/A | 0 | 0
2021-05-27 13:00 | 4.9933 | 0 | N/A | 0 | 0
2021-05-27 13:30 | 4.1338 | 0 | N/A | 0 | 0
2021-05-27 14:00 | 4.8804 | 0 | N/A | 0 | 0
2021-05-27 14:30 | 5.4538 | 0 | N/A | 0 | 0
2021-05-27 15:00 | 5.5701 | 0 | N/A | 0 | 0
2021-05-27 15:30 | 4.4407 | 0 | N/A | 0 | 0
2021-05-27 16:00 | 4.9133 | 0 | N/A | 0 | 0
2021-05-27 16:30 | 5.0405 | 0 | N/A | 0 | 0
2021-05-27 17:00 | 5.5264 | 0 | N/A | 0 | 0
2021-05-27 17:30 | 6.4348 | 0 | N/A | 0 | 0
2021-05-27 18:00 | 7.4911 | 0 | N/A | 0 | 0
2021-05-27 18:30 | 7.7473 | 0 | N/A | 0 | 0
2021-05-27 19:00 | 7.5909 | 0 | N/A | 0 | 0
2021-05-27 19:30 | 7.3017 | 0 | N/A | 0 | 0
2021-05-27 20:00 | 6.9895 | 0 | N/A | 0 | 0
2021-05-27 20:30 | 6.7532 | 0 | N/A | 0 | 0
2021-05-27 21:00 | 6.4403 | 0 | N/A | 0 | 0
2021-05-27 21:30 | 6.5499 | 0 | N/A | 0 | 0
2021-05-27 22:00 | 6.7117 | 0 | N/A | 0 | 0
2021-05-27 22:30 | 6.1686 | 0 | N/A | 0 | 0
2021-05-27 23:00 | 6.0337 | 0 | N/A | 0 | 0
2021-05-27 23:30 | 6.0678 | 0 | N/A | 0 | 0
2021-05-28 | 6.3222 | 0 | N/A | 0 | 0
2021-05-28 00:30 | 5.6403 | 0 | N/A | 0 | 0
2021-05-28 01:00 | 4.8394 | 0 | N/A | 0 | 0
2021-05-28 01:30 | 4.7358 | 0 | N/A | 0 | 0
2021-05-28 02:00 | 4.35 | 0 | N/A | 0 | 0
2021-05-28 02:30 | 3.7921 | 0 | N/A | 0 | 0
2021-05-28 03:00 | 3.4669 | 0 | N/A | 0 | 0
2021-05-28 03:30 | 3.2261 | 0 | N/A | 0 | 0
2021-05-28 04:00 | 3.0865 | 0 | N/A | 0 | 0
2021-05-28 04:30 | 3.1736 | 0 | N/A | 0 | 0
2021-05-28 05:00 | 3.1612 | 0 | N/A | 0 | 0
2021-05-28 05:30 | 3.4935 | 0 | N/A | 0 | 0
2021-05-28 06:00 | 3.8681 | 0 | N/A | 0 | 0
2021-05-28 06:30 | 4.5269 | 0 | N/A | 0 | 0
2021-05-28 07:00 | 5.4642 | 0 | N/A | 0 | 0
2021-05-28 07:30 | 5.8501 | 0 | N/A | 0 | 0
2021-05-28 08:00 | 6.4404 | 0 | N/A | 0 | 0
2021-05-28 08:30 | 6.7415 | 0 | N/A | 0 | 0
2021-05-28 09:00 | 6.6807 | 0 | N/A | 0 | 0
2021-05-28 09:30 | 6.5468 | 0 | N/A | 0 | 0
2021-05-28 10:00 | 6.314 | 0 | N/A | 0 | 0
2021-05-28 10:30 | 5.88 | 0 | N/A | 0 | 0
2021-05-28 11:00 | 5.6404 | 0 | N/A | 0 | 0
2021-05-28 11:30 | 5.831 | 0 | N/A | 0 | 0
2021-05-28 12:00 | 6.0043 | 0 | N/A | 0 | 0
2021-05-28 12:30 | 6.2033 | 0 | N/A | 0 | 0
2021-05-28 13:00 | 5.9911 | 0 | N/A | 0 | 0
2021-05-28 13:30 | 6.3343 | 0 | N/A | 0 | 0
2021-05-28 14:00 | 6.4167 | 0 | N/A | 0 | 0
2021-05-28 14:30 | 6.6567 | 0 | N/A | 0 | 0
2021-05-28 15:00 | 6.36 | 0 | N/A | 0 | 0
2021-05-29 00:30 | 6.1075 | 0 | N/A | 0 | 0
2021-05-29 01:00 | 5.3092 | 0 | N/A | 0 | 0
2021-05-29 01:30 | 5.0094 | 0 | N/A | 0 | 0
2021-05-29 02:00 | 4.6668 | 0 | N/A | 0 | 0
2021-05-29 02:30 | 4.0949 | 0 | N/A | 0 | 0
2021-05-29 03:00 | 3.7255 | 0 | N/A | 0 | 0
2021-05-29 03:30 | 3.4791 | 0 | N/A | 0 | 0
2021-05-29 04:00 | 3.3261 | 0 | N/A | 0 | 0
2021-05-29 04:30 | 3.2133 | 0 | N/A | 0 | 0
2021-05-29 05:00 | 3.1804 | 0 | N/A | 0 | 0
2021-05-29 05:30 | 3.3827 | 0 | N/A | 0 | 0
2021-05-29 06:00 | 3.5291 | 0 | N/A | 0 | 0
2021-05-29 06:30 | 3.969 | 0 | N/A | 0 | 0
2021-05-29 07:00 | 4.1123 | 0 | N/A | 0 | 0
2021-05-29 07:30 | 4.0778 | 0 | N/A | 0 | 0
2021-05-29 08:00 | 4.6139 | 0 | N/A | 0 | 0
2021-05-29 08:30 | 5.2812 | 0 | N/A | 0 | 0
2021-05-29 09:00 | 5.3261 | 0 | N/A | 0 | 0
2021-05-29 09:30 | 5.3052 | 0 | N/A | 0 | 0
2021-05-29 10:00 | 4.882 | 0 | N/A | 0 | 0
2021-05-29 10:30 | 4.3629 | 0 | N/A | 0 | 0
2021-05-29 11:00 | 3.931 | 0 | N/A | 0 | 0
2021-05-29 11:30 | 3.5272 | 0 | N/A | 0 | 0
2021-05-29 12:00 | 3.0649 | 0 | N/A | 0 | 0
2021-05-29 12:30 | 2.6894 | 0 | N/A | 0 | 0
2021-05-29 13:00 | 2.3707 | 0 | N/A | 0 | 0
2021-05-29 13:30 | 2.367 | 0 | N/A | 0 | 0
2021-05-29 14:00 | 2.3384 | 0 | N/A | 0 | 0
2021-05-29 14:30 | 2.3849 | 0 | N/A | 0 | 0
2021-05-29 15:00 | 2.7843 | 0 | N/A | 0 | 0
2021-05-29 15:30 | 3.3583 | 0 | N/A | 0 | 0
2021-05-29 16:00 | 4.0283 | 0 | N/A | 0 | 0
2021-05-29 16:30 | 4.9138 | 0 | N/A | 0 | 0
2021-05-29 17:00 | 6.023 | 0 | N/A | 0 | 0
2021-05-29 17:30 | 7.1772 | 0 | N/A | 0 | 0
2021-05-29 18:00 | 8.1987 | 0 | N/A | 0 | 0
2021-05-29 18:30 | 8.1517 | 0 | N/A | 0 | 0
2021-05-29 19:00 | 7.7655 | 0 | N/A | 0 | 0
2021-05-29 19:30 | 7.4122 | 0 | N/A | 0 | 0
2021-05-29 20:00 | 7.0142 | 0 | N/A | 0 | 0
2021-05-29 20:30 | 6.7373 | 0 | N/A | 0 | 0
2021-05-29 21:00 | 6.4519 | 0 | N/A | 0 | 0
2021-05-29 21:30 | 6.6462 | 0 | N/A | 0 | 0
2021-05-29 22:00 | 6.8424 | 0 | N/A | 0 | 0
2021-05-29 22:30 | 6.5558 | 0 | N/A | 0 | 0
2021-05-29 23:00 | 6.6031 | 0 | N/A | 0 | 0
2021-05-29 23:30 | 6.6387 | 0 | N/A | 0 | 0
2021-05-30 | 6.9571 | 0 | N/A | 0 | 0
2021-05-30 00:30 | 6.295 | 0 | N/A | 0 | 0
2021-05-30 01:00 | 5.4641 | 0 | N/A | 0 | 0
2021-05-30 01:30 | 5.4469 | 0 | N/A | 0 | 0
2021-05-30 02:00 | 5.0896 | 0 | N/A | 0 | 0
2021-05-30 02:30 | 4.4399 | 0 | N/A | 0 | 0
2021-05-30 03:00 | 4.1146 | 0 | N/A | 0 | 0
2021-05-30 03:30 | 3.8294 | 0 | N/A | 0 | 0
2021-05-30 04:00 | 3.5734 | 0 | N/A | 0 | 0
2021-05-30 04:30 | 3.4983 | 0 | N/A | 0 | 0
2021-05-30 05:00 | 3.4733 | 0 | N/A | 0 | 0
2021-05-30 05:30 | 3.5176 | 0 | N/A | 0 | 0
2021-05-30 06:00 | 3.7659 | 0 | N/A | 0 | 0
2021-05-30 06:30 | 4.0943 | 0 | N/A | 0 | 0
2021-05-30 07:00 | 4.2256 | 0 | N/A | 0 | 0
2021-05-30 07:30 | 4.1203 | 0 | N/A | 0 | 0
2021-05-30 08:00 | 4.6082 | 0 | N/A | 0 | 0
2021-05-30 08:30 | 4.8767 | 0 | N/A | 0 | 0
2021-05-30 09:00 | 4.9088 | 0 | N/A | 0 | 0
2021-05-30 09:30 | 4.694 | 0 | N/A | 0 | 0
2021-05-30 10:00 | 4.2491 | 0 | N/A | 0 | 0
2021-05-30 10:30 | 3.669 | 0 | N/A | 0 | 0
2021-05-30 11:00 | 3.1044 | 0 | N/A | 0 | 0
2021-05-30 11:30 | 2.507 | 0 | N/A | 0 | 0
2021-05-30 12:00 | 2.1028 | 0 | N/A | 0 | 0
2021-05-30 12:30 | 1.9291 | 0 | N/A | 0 | 0
2021-05-30 13:00 | 1.7774 | 0 | N/A | 0 | 0
2021-05-30 13:30 | 1.8173 | 0 | N/A | 0 | 0
2021-05-30 14:00 | 1.8069 | 0 | N/A | 0 | 0
2021-05-30 14:30 | 1.9831 | 0 | N/A | 0 | 0
2021-05-30 15:00 | 2.318 | 0 | N/A | 0 | 0
2021-05-30 15:30 | 2.8503 | 0 | N/A | 0 | 0
2021-05-30 16:00 | 3.5512 | 0 | N/A | 0 | 0
2021-05-30 16:30 | 4.5062 | 0 | N/A | 0 | 0
2021-05-30 17:00 | 5.6814 | 0 | N/A | 0 | 0
2021-05-30 17:30 | 7.0832 | 0 | N/A | 0 | 0
2021-05-30 18:00 | 8.1956 | 0 | N/A | 0 | 0
2021-05-30 18:30 | 8.4441 | 0 | N/A | 0 | 0
2021-05-30 19:00 | 8.1846 | 0 | N/A | 0 | 0
2021-05-30 19:30 | 7.6774 | 0 | N/A | 0 | 0
2021-05-30 20:00 | 7.3364 | 0 | N/A | 0 | 0
2021-05-30 20:30 | 6.8376 | 0 | N/A | 0 | 0
2021-05-30 21:00 | 6.5994 | 0 | N/A | 0 | 0
2021-05-30 21:30 | 6.8841 | 0 | N/A | 0 | 0
2021-05-30 22:00 | 6.8812 | 0 | N/A | 0 | 0
2021-05-30 22:30 | 6.5274 | 0 | N/A | 0 | 0
2021-05-30 23:00 | 6.5163 | 0 | N/A | 0 | 0
2021-05-30 23:30 | 6.575 | 0 | N/A | 0 | 0
2021-05-31 | 6.8596 | 0 | N/A | 0 | 0
2021-05-31 00:30 | 6.2548 | 0 | N/A | 0 | 0
2021-05-31 01:00 | 5.3971 | 0 | N/A | 0 | 0
2021-05-31 01:30 | 5.3071 | 0 | N/A | 0 | 0
2021-05-31 02:00 | 5.1089 | 0 | N/A | 0 | 0
2021-05-31 02:30 | 4.5181 | 0 | N/A | 0 | 0
2021-05-31 03:00 | 4.1401 | 0 | N/A | 0 | 0
2021-05-31 03:30 | 3.8469 | 0 | N/A | 0 | 0
2021-05-31 04:00 | 3.676 | 0 | N/A | 0 | 0
2021-05-31 04:30 | 3.588 | 0 | N/A | 0 | 0
2021-05-31 05:00 | 3.5685 | 0 | N/A | 0 | 0
2021-05-31 05:30 | 4.0296 | 0 | N/A | 0 | 0
2021-05-31 06:00 | 4.6106 | 0 | N/A | 0 | 0
2021-05-31 06:30 | 5.1969 | 0 | N/A | 0 | 0
2021-05-31 07:00 | 5.9619 | 0 | N/A | 0 | 0
2021-05-31 07:30 | 6.3836 | 0 | N/A | 0 | 0
2021-05-31 08:00 | 7.1135 | 0 | N/A | 0 | 0
2021-05-31 08:30 | 7.4645 | 0 | N/A | 0 | 0
2021-05-31 09:00 | 7.1131 | 0 | N/A | 0 | 0
2021-05-31 09:30 | 6.4461 | 0 | N/A | 0 | 0
2021-05-31 10:00 | 5.3967 | 0 | N/A | 0 | 0
2021-05-31 10:30 | 4.9216 | 0 | N/A | 0 | 0
2021-05-31 11:00 | 4.2646 | 0 | N/A | 0 | 0
2021-05-31 11:30 | 3.6316 | 0 | N/A | 0 | 0
2021-05-31 12:00 | 3.3815 | 0 | N/A | 0 | 0
2021-05-31 12:30 | 3.2539 | 0 | N/A | 0 | 0
2021-05-31 13:00 | 2.7639 | 0 | N/A | 0 | 0
2021-05-31 13:30 | 2.8381 | 0 | N/A | 0 | 0
2021-05-31 14:00 | 3.24 | 0 | N/A | 0 | 0
2021-05-31 14:30 | 3.4767 | 0 | N/A | 0 | 0
2021-05-31 15:00 | 3.889 | 0 | N/A | 0 | 0
2021-05-31 15:30 | 3.783 | 0 | N/A | 0 | 0
2021-05-31 16:00 | 4.4486 | 0 | N/A | 0 | 0
2021-05-31 16:30 | 5.341 | 0 | N/A | 0 | 0
2021-05-31 17:00 | 6.369 | 0 | N/A | 0 | 0
2021-05-31 17:30 | 7.5595 | 0 | N/A | 0 | 0
2021-05-31 18:00 | 8.617 | 0 | N/A | 0 | 0
2021-05-31 18:30 | 8.6739 | 0 | N/A | 0 | 0
2021-05-31 19:00 | 8.1514 | 0 | N/A | 0 | 0
2021-05-31 19:30 | 7.8476 | 0 | N/A | 0 | 0
2021-05-31 20:00 | 7.5084 | 0 | N/A | 0 | 0
2021-05-31 20:30 | 7.0647 | 0 | N/A | 0 | 0
2021-05-31 21:00 | 6.7726 | 0 | N/A | 0 | 0
2021-05-31 21:30 | 6.8464 | 0 | N/A | 0 | 0
2021-05-31 22:00 | 6.8472 | 0 | N/A | 0 | 0
2021-05-31 22:30 | 6.2342 | 0 | N/A | 0 | 0
2021-05-31 23:00 | 6.0768 | 0 | N/A | 0 | 0
2021-05-31 23:30 | 6.0751 | 0 | N/A | 0 | 0
2021-06-01 | 6.5902 | 0 | N/A | 0 | 0
2021-06-01 00:30 | 5.7557 | 0 | N/A | 0 | 0
2021-06-01 01:00 | 5.0377 | 0 | N/A | 0 | 0
2021-06-01 01:30 | 4.9232 | 0 | N/A | 0 | 0
2021-06-01 02:00 | 4.5786 | 0 | N/A | 0 | 0
2021-06-01 02:30 | 4.0545 | 0 | N/A | 0 | 0
2021-06-01 03:00 | 3.6746 | 0 | N/A | 0 | 0
2021-06-01 03:30 | 3.4495 | 0 | N/A | 0 | 0
2021-06-01 04:00 | 3.2664 | 0 | N/A | 0 | 0
2021-06-02 00:30 | 5.5861 | 0 | N/A | 0 | 0
2021-06-02 01:00 | 4.9203 | 0 | N/A | 0 | 0
2021-06-02 01:30 | 4.7139 | 0 | N/A | 0 | 0
2021-06-02 02:00 | 4.322 | 0 | N/A | 0 | 0
2021-06-02 02:30 | 3.7077 | 0 | N/A | 0 | 0
2021-06-02 03:00 | 3.3875 | 0 | N/A | 0 | 0
2021-06-02 03:30 | 3.1631 | 0 | N/A | 0 | 0
2021-06-02 04:00 | 2.9919 | 0 | N/A | 0 | 0
2021-06-02 04:30 | 2.9866 | 0 | N/A | 0 | 0
2021-06-02 05:00 | 3.0056 | 0 | N/A | 0 | 0
2021-06-02 05:30 | 3.3745 | 0 | N/A | 0 | 0
2021-06-02 06:00 | 3.7989 | 0 | N/A | 0 | 0
2021-06-02 06:30 | 4.3086 | 0 | N/A | 0 | 0
2021-06-02 07:00 | 4.7934 | 0 | N/A | 0 | 0
2021-06-02 07:30 | 5.0063 | 0 | N/A | 0 | 0
2021-06-02 08:00 | 5.6676 | 0 | N/A | 0 | 0
2021-06-02 08:30 | 5.9014 | 0 | N/A | 0 | 0
2021-06-02 09:00 | 5.4775 | 0 | N/A | 0 | 0
2021-06-02 09:30 | 4.7582 | 0 | N/A | 0 | 0
2021-06-02 10:00 | 4.0266 | 0 | N/A | 0 | 0
2021-06-02 10:30 | 3.2652 | 0 | N/A | 0 | 0
2021-06-02 11:00 | 3.2059 | 0 | N/A | 0 | 0
2021-06-02 11:30 | 3.7664 | 0 | N/A | 0 | 0
2021-06-02 12:00 | 3.9545 | 0 | N/A | 0 | 0
2021-06-02 12:30 | 3.3746 | 0 | N/A | 0 | 0
2021-06-02 13:00 | 2.3972 | 0 | N/A | 0 | 0
2021-06-02 13:30 | 2.7354 | 0 | N/A | 0 | 0
2021-06-02 14:00 | 2.6975 | 0 | N/A | 0 | 0
2021-06-02 14:30 | 3.0525 | 0 | N/A | 0 | 0
2021-06-02 15:00 | 3.5655 | 0 | N/A | 0 | 0
2021-06-02 15:30 | 3.5913 | 0 | N/A | 0 | 0
2021-06-02 16:00 | 4.1545 | 0 | N/A | 0 | 0
2021-06-02 16:30 | 4.8018 | 0 | N/A | 0 | 0
2021-06-02 17:00 | 5.6912 | 0 | N/A | 0 | 0
2021-06-02 17:30 | 6.5416 | 0 | N/A | 0 | 0
2021-06-02 18:00 | 7.4449 | 0 | N/A | 0 | 0
2021-06-02 18:30 | 7.4855 | 0 | N/A | 0 | 0
2021-06-02 19:00 | 7.3359 | 0 | N/A | 0 | 0
2021-06-02 19:30 | 6.9569 | 0 | N/A | 0 | 0
2021-06-03 00:30 | 5.3579 | 0 | N/A | 0 | 0
2021-06-03 01:00 | 4.6032 | 0 | N/A | 0 | 0
2021-06-03 01:30 | 4.4414 | 0 | N/A | 0 | 0
2021-06-03 02:00 | 4.1355 | 0 | N/A | 0 | 0
2021-06-03 02:30 | 3.6683 | 0 | N/A | 0 | 0
2021-06-03 03:00 | 3.3495 | 0 | N/A | 0 | 0
2021-06-03 03:30 | 3.0698 | 0 | N/A | 0 | 0
2021-06-03 04:00 | 2.9095 | 0 | N/A | 0 | 0
2021-06-03 04:30 | 2.8608 | 0 | N/A | 0 | 0
2021-06-03 05:00 | 2.8629 | 0 | N/A | 0 | 0
2021-06-03 05:30 | 3.2101 | 0 | N/A | 0 | 0
2021-06-03 06:00 | 3.6821 | 0 | N/A | 0 | 0
2021-06-03 06:30 | 4.1938 | 0 | N/A | 0 | 0
2021-06-03 07:00 | 4.6415 | 0 | N/A | 0 | 0
2021-06-03 07:30 | 4.8393 | 0 | N/A | 0 | 0
2021-06-03 08:00 | 5.3186 | 0 | N/A | 0 | 0
2021-06-03 08:30 | 5.9341 | 0 | N/A | 0 | 0
2021-06-03 09:00 | 5.5589 | 0 | N/A | 0 | 0
2021-06-03 09:30 | 4.6368 | 0 | N/A | 0 | 0
2021-06-03 10:00 | 3.7954 | 0 | N/A | 0 | 0
2021-06-03 10:30 | 3.186 | 0 | N/A | 0 | 0
2021-06-03 11:00 | 3.3182 | 0 | N/A | 0 | 0
2021-06-03 11:30 | 3.8081 | 0 | N/A | 0 | 0
2021-06-03 12:00 | 3.7602 | 0 | N/A | 0 | 0
2021-06-03 12:30 | 3.853 | 0 | N/A | 0 | 0
2021-06-03 13:00 | 3.8594 | 0 | N/A | 0 | 0
2021-06-03 13:30 | 3.1264 | 0 | N/A | 0 | 0
2021-06-03 14:00 | 3.7229 | 0 | N/A | 0 | 0
2021-06-03 14:30 | 4.8662 | 0 | N/A | 0 | 0
2021-06-03 15:00 | 5.312 | 0 | N/A | 0 | 0
2021-06-03 15:30 | 5.2602 | 0 | N/A | 0 | 0
2021-06-03 16:00 | 5.0119 | 0 | N/A | 0 | 0
2021-06-03 16:30 | 5.21 | 0 | N/A | 0 | 0
2021-06-03 17:00 | 5.6324 | 0 | N/A | 0 | 0
2021-06-03 17:30 | 6.3491 | 0 | N/A | 0 | 0
2021-06-03 18:00 | 7.2896 | 0 | N/A | 0 | 0
2021-06-03 18:30 | 7.4855 | 0 | N/A | 0 | 0
2021-06-03 19:00 | 7.1236 | 0 | N/A | 0 | 0
2021-06-03 19:30 | 6.7296 | 0 | N/A | 0 | 0
2021-06-03 20:00 | 6.404 | 0 | N/A | 0 | 0
2021-06-03 20:30 | 6.1445 | 0 | N/A | 0 | 0
2021-06-03 21:00 | 5.8014 | 0 | N/A | 0 | 0
2021-06-03 21:30 | 6.0111 | 0 | N/A | 0 | 0
2021-06-03 22:00 | 6.0216 | 0 | N/A | 0 | 0
2021-06-03 22:30 | 5.5227 | 0 | N/A | 0 | 0
2021-06-03 23:00 | 5.5069 | 0 | N/A | 0 | 0
2021-06-03 23:30 | 5.7266 | 0 | N/A | 0 | 0
2021-06-04 | 6.0256 | 0 | N/A | 0 | 0
2021-06-04 00:30 | 5.3397 | 0 | N/A | 0 | 0
2021-06-04 01:00 | 4.519 | 0 | N/A | 0 | 0
2021-06-04 01:30 | 4.3607 | 0 | N/A | 0 | 0
2021-06-04 02:00 | 4.1027 | 0 | N/A | 0 | 0
2021-06-04 02:30 | 3.5783 | 0 | N/A | 0 | 0
2021-06-04 03:00 | 3.2513 | 0 | N/A | 0 | 0
2021-06-04 03:30 | 3.0705 | 0 | N/A | 0 | 0
2021-06-04 04:00 | 2.9337 | 0 | N/A | 0 | 0
2021-06-04 04:30 | 2.9062 | 0 | N/A | 0 | 0
2021-06-04 05:00 | 2.9548 | 0 | N/A | 0 | 0
2021-06-04 05:30 | 3.2929 | 0 | N/A | 0 | 0
2021-06-04 06:00 | 3.7597 | 0 | N/A | 0 | 0
2021-06-04 06:30 | 4.4402 | 0 | N/A | 0 | 0
2021-06-04 07:00 | 5.1474 | 0 | N/A | 0 | 0
2021-06-04 07:30 | 5.4631 | 0 | N/A | 0 | 0
2021-06-04 08:00 | 6.0155 | 0 | N/A | 0 | 0
2021-06-04 08:30 | 6.191 | 0 | N/A | 0 | 0
2021-06-04 09:00 | 6.0404 | 0 | N/A | 0 | 0
2021-06-04 09:30 | 5.7301 | 0 | N/A | 0 | 0
2021-06-04 10:00 | 5.4433 | 0 | N/A | 0 | 0
2021-06-04 10:30 | 5.2967 | 0 | N/A | 0 | 0
2021-06-04 11:00 | 3.99 | 0 | N/A | 0 | 0
2021-06-04 11:30 | 3.79 | 0 | N/A | 0 | 0
2021-06-04 12:00 | 3.7748 | 0 | N/A | 0 | 0
2021-06-04 12:30 | 3.8866 | 0 | N/A | 0 | 0
2021-06-04 13:00 | 3.6441 | 0 | N/A | 0 | 0
2021-06-04 13:30 | 4.2388 | 0 | N/A | 0 | 0
2021-06-04 14:00 | 4.597 | 0 | N/A | 0 | 0
2021-06-04 14:30 | 4.5866 | 0 | N/A | 0 | 0
2021-06-04 15:00 | 4.3127 | 0 | N/A | 0 | 0
2021-06-04 15:30 | 4.8258 | 0 | N/A | 0 | 0
2021-06-04 16:00 | 5.0344 | 0 | N/A | 0 | 0
2021-06-04 16:30 | 5.3307 | 0 | N/A | 0 | 0
2021-06-04 17:00 | 5.9488 | 0 | N/A | 0 | 0
2021-06-04 17:30 | 6.9855 | 0 | N/A | 0 | 0
2021-06-04 18:00 | 7.8202 | 0 | N/A | 0 | 0
2021-06-04 18:30 | 8.0601 | 0 | N/A | 0 | 0
2021-06-04 19:00 | 8.0367 | 0 | N/A | 0 | 0
2021-06-04 19:30 | 7.7771 | 0 | N/A | 0 | 0
2021-06-04 20:00 | 7.6275 | 0 | N/A | 0 | 0
2021-06-04 20:30 | 7.3483 | 0 | N/A | 0 | 0
2021-06-04 21:00 | 7.1257 | 0 | N/A | 0 | 0
2021-06-04 21:30 | 7.4348 | 0 | N/A | 0 | 0
2021-06-04 22:00 | 7.5584 | 0 | N/A | 0 | 0
2021-06-04 22:30 | 6.9856 | 0 | N/A | 0 | 0
2021-06-04 23:00 | 6.8477 | 0 | N/A | 0 | 0
2021-06-04 23:30 | 7.0388 | 0 | N/A | 0 | 0
2021-06-05 | 7.2702 | 0 | N/A | 0 | 0
2021-06-05 00:30 | 6.5891 | 0 | N/A | 0 | 0
2021-06-05 01:00 | 5.6925 | 0 | N/A | 0 | 0
2021-06-05 01:30 | 5.5221 | 0 | N/A | 0 | 0
2021-06-05 02:00 | 5.1657 | 0 | N/A | 0 | 0
2021-06-05 02:30 | 4.5761 | 0 | N/A | 0 | 0
2021-06-05 03:00 | 4.2195 | 0 | N/A | 0 | 0
2021-06-05 03:30 | 3.9158 | 0 | N/A | 0 | 0
2021-06-05 04:00 | 3.778 | 0 | N/A | 0 | 0
2021-06-05 04:30 | 3.7725 | 0 | N/A | 0 | 0
2021-06-05 05:00 | 3.7391 | 0 | N/A | 0 | 0
2021-06-05 05:30 | 3.8691 | 0 | N/A | 0 | 0
2021-06-05 06:00 | 4.1662 | 0 | N/A | 0 | 0
2021-06-05 06:30 | 4.653 | 0 | N/A | 0 | 0
2021-06-05 07:00 | 4.9908 | 0 | N/A | 0 | 0
2021-06-05 07:30 | 5.137 | 0 | N/A | 0 | 0
2021-06-05 08:00 | 5.6193 | 0 | N/A | 0 | 0
2021-06-05 08:30 | 6.3299 | 0 | N/A | 0 | 0
2021-06-05 09:00 | 6.4998 | 0 | N/A | 0 | 0
2021-06-05 09:30 | 6.254 | 0 | N/A | 0 | 0
2021-06-05 10:00 | 5.9 | 0 | N/A | 0 | 0
2021-06-05 10:30 | 5.6312 | 0 | N/A | 0 | 0
2021-06-05 11:00 | 5.2525 | 0 | N/A | 0 | 0
2021-06-05 11:30 | 4.8591 | 0 | N/A | 0 | 0
2021-06-05 12:00 | 4.5783 | 0 | N/A | 0 | 0
2021-06-05 12:30 | 4.2586 | 0 | N/A | 0 | 0
2021-06-05 13:00 | 4.2708 | 0 | N/A | 0 | 0
2021-06-05 13:30 | 4.6694 | 0 | N/A | 0 | 0
2021-06-05 14:00 | 5.1129 | 0 | N/A | 0 | 0
2021-06-05 14:30 | 5.3401 | 0 | N/A | 0 | 0
2021-06-05 15:00 | 5.6761 | 0 | N/A | 0 | 0
2021-06-05 15:30 | 6.233 | 0 | N/A | 0 | 0
2021-06-05 16:00 | 6.4588 | 0 | N/A | 0 | 0
2021-06-05 16:30 | 6.6101 | 0 | N/A | 0 | 0
2021-06-05 17:00 | 6.9896 | 0 | N/A | 0 | 0
2021-06-05 17:30 | 7.6043 | 0 | N/A | 0 | 0
2021-06-05 18:00 | 8.4433 | 0 | N/A | 0 | 0
2021-06-05 18:30 | 8.41 | 0 | N/A | 0 | 0
2021-06-05 19:00 | 8.1634 | 0 | N/A | 0 | 0
2021-06-05 19:30 | 7.7079 | 0 | N/A | 0 | 0
2021-06-05 20:00 | 7.1196 | 0 | N/A | 0 | 0
2021-06-05 20:30 | 6.7603 | 0 | N/A | 0 | 0
2021-06-05 21:00 | 6.4081 | 0 | N/A | 0 | 0
2021-06-05 21:30 | 6.6213 | 0 | N/A | 0 | 0
2021-06-05 22:00 | 6.8034 | 0 | N/A | 0 | 0
2021-06-05 22:30 | 6.441 | 0 | N/A | 0 | 0
2021-06-05 23:00 | 6.4118 | 0 | N/A | 0 | 0
2021-06-05 23:30 | 6.4386 | 0 | N/A | 0 | 0
2021-06-06 | 6.7915 | 0 | N/A | 0 | 0
2021-06-06 00:30 | 6.1042 | 0 | N/A | 0 | 0
2021-06-06 01:00 | 5.3665 | 0 | N/A | 0 | 0
2021-06-06 01:30 | 5.1355 | 0 | N/A | 0 | 0
2021-06-06 02:00 | 4.7013 | 0 | N/A | 0 | 0
2021-06-06 02:30 | 4.1269 | 0 | N/A | 0 | 0
2021-06-06 03:00 | 3.6786 | 0 | N/A | 0 | 0
2021-06-06 03:30 | 3.3936 | 0 | N/A | 0 | 0
2021-06-06 04:00 | 3.1612 | 0 | N/A | 0 | 0
2021-06-06 04:30 | 3.0396 | 0 | N/A | 0 | 0
2021-06-06 05:00 | 3.0014 | 0 | N/A | 0 | 0
2021-06-06 05:30 | 2.9816 | 0 | N/A | 0 | 0
2021-06-06 06:00 | 3.1218 | 0 | N/A | 0 | 0
2021-06-06 06:30 | 3.364 | 0 | N/A | 0 | 0
2021-06-06 07:00 | 3.5613 | 0 | N/A | 0 | 0
2021-06-06 07:30 | 3.6705 | 0 | N/A | 0 | 0
2021-06-06 08:00 | 4.0691 | 0 | N/A | 0 | 0
2021-06-06 08:30 | 4.5673 | 0 | N/A | 0 | 0
2021-06-06 09:00 | 4.877 | 0 | N/A | 0 | 0
2021-06-06 09:30 | 5.3034 | 0 | N/A | 0 | 0
2021-06-06 10:00 | 5.1951 | 0 | N/A | 0 | 0
2021-06-06 10:30 | 5.3567 | 0 | N/A | 0 | 0
2021-06-06 11:00 | 5.3936 | 0 | N/A | 0 | 0
2021-06-06 11:30 | 5.3534 | 0 | N/A | 0 | 0
2021-06-06 12:00 | 5.5639 | 0 | N/A | 0 | 0
2021-06-06 12:30 | 4.7771 | 0 | N/A | 0 | 0
2021-06-06 13:00 | 3.9167 | 0 | N/A | 0 | 0
2021-06-06 13:30 | 3.7753 | 0 | N/A | 0 | 0
2021-06-06 14:00 | 3.5379 | 0 | N/A | 0 | 0
2021-06-06 14:30 | 3.4141 | 0 | N/A | 0 | 0
2021-06-06 15:00 | 4.0082 | 0 | N/A | 0 | 0
2021-06-06 15:30 | 4.3808 | 0 | N/A | 0 | 0
2021-06-06 16:00 | 4.1694 | 0 | N/A | 0 | 0
2021-06-06 16:30 | 4.9135 | 0 | N/A | 0 | 0
2021-06-06 17:00 | 5.8039 | 0 | N/A | 0 | 0
2021-06-06 17:30 | 6.9144 | 0 | N/A | 0 | 0
2021-06-06 18:00 | 7.9779 | 0 | N/A | 0 | 0
2021-06-06 18:30 | 7.975 | 0 | N/A | 0 | 0
2021-06-06 19:00 | 7.5172 | 0 | N/A | 0 | 0
2021-06-06 19:30 | 7.0208 | 0 | N/A | 0 | 0
2021-06-06 20:00 | 6.5965 | 0 | N/A | 0 | 0
2021-06-06 20:30 | 6.2325 | 0 | N/A | 0 | 0
2021-06-06 21:00 | 5.7437 | 0 | N/A | 0 | 0
2021-06-06 21:30 | 6.0512 | 0 | N/A | 0 | 0
2021-06-06 22:00 | 6.1963 | 0 | N/A | 0 | 0
2021-06-06 22:30 | 5.8916 | 0 | N/A | 0 | 0
2021-06-06 23:00 | 5.8326 | 0 | N/A | 0 | 0
2021-06-06 23:30 | 5.8323 | 0 | N/A | 0 | 0
2021-06-07 | 6.275 | 0 | N/A | 0 | 0
2021-06-07 00:30 | 5.6072 | 0 | N/A | 0 | 0
2021-06-07 01:00 | 4.9523 | 0 | N/A | 0 | 0
2021-06-07 01:30 | 4.8142 | 0 | N/A | 0 | 0
2021-06-07 02:00 | 4.3928 | 0 | N/A | 0 | 0
2021-06-07 02:30 | 3.8464 | 0 | N/A | 0 | 0
2021-06-07 03:00 | 3.5034 | 0 | N/A | 0 | 0
2021-06-07 03:30 | 3.2701 | 0 | N/A | 0 | 0
2021-06-07 04:00 | 3.045 | 0 | N/A | 0 | 0
2021-06-07 04:30 | 2.973 | 0 | N/A | 0 | 0
2021-06-07 05:00 | 3.0568 | 0 | N/A | 0 | 0
2021-06-07 05:30 | 3.4239 | 0 | N/A | 0 | 0
2021-06-07 06:00 | 3.8589 | 0 | N/A | 0 | 0
2021-06-07 06:30 | 4.5798 | 0 | N/A | 0 | 0
2021-06-07 07:00 | 5.2847 | 0 | N/A | 0 | 0
2021-06-07 07:30 | 6.0701 | 0 | N/A | 0 | 0
2021-06-07 08:00 | 6.7349 | 0 | N/A | 0 | 0
2021-06-07 08:30 | 6.9407 | 0 | N/A | 0 | 0
2021-06-07 09:00 | 6.5291 | 0 | N/A | 0 | 0
2021-06-07 09:30 | 5.8074 | 0 | N/A | 0 | 0
2021-06-07 10:00 | 5.068 | 0 | N/A | 0 | 0
2021-06-07 10:30 | 4.2701 | 0 | N/A | 0 | 0
2021-06-07 11:00 | 4.05 | 0 | N/A | 0 | 0
2021-06-07 11:30 | 4.1869 | 0 | N/A | 0 | 0
2021-06-07 12:00 | 4.328 | 0 | N/A | 0 | 0
2021-06-07 12:30 | 3.9972 | 0 | N/A | 0 | 0
2021-06-07 13:00 | 4.1418 | 0 | N/A | 0 | 0
2021-06-07 13:30 | 3.9709 | 0 | N/A | 0 | 0
2021-06-07 14:00 | 3.64 | 0 | N/A | 0 | 0
2021-06-07 14:30 | 3.9244 | 0 | N/A | 0 | 0
2021-06-07 15:00 | 4.2067 | 0 | N/A | 0 | 0
2021-06-07 15:30 | 4.6967 | 0 | N/A | 0 | 0
2021-06-07 16:00 | 4.7095 | 0 | N/A | 0 | 0
2021-06-07 16:30 | 5.0761 | 0 | N/A | 0 | 0
2021-06-07 17:00 | 5.8754 | 0 | N/A | 0 | 0
2021-06-07 17:30 | 6.9257 | 0 | N/A | 0 | 0
2021-06-07 18:00 | 7.9671 | 0 | N/A | 0 | 0
2021-06-07 18:30 | 8.1434 | 0 | N/A | 0 | 0
2021-06-07 19:00 | 7.8402 | 0 | N/A | 0 | 0
2021-06-07 19:30 | 7.3142 | 0 | N/A | 0 | 0
2021-06-07 20:00 | 7.0349 | 0 | N/A | 0 | 0
2021-06-07 20:30 | 6.6352 | 0 | N/A | 0 | 0
2021-06-07 21:00 | 6.2561 | 0 | N/A | 0 | 0
2021-06-07 21:30 | 6.4967 | 0 | N/A | 0 | 0
2021-06-07 22:00 | 6.6357 | 0 | N/A | 0 | 0
2021-06-07 22:30 | 6.2129 | 0 | N/A | 0 | 0
2021-06-07 23:00 | 6.0918 | 0 | N/A | 0 | 0
2021-06-07 23:30 | 6.107 | 0 | N/A | 0 | 0
2021-06-08 | 6.4466 | 0 | N/A | 0 | 0
2021-06-08 00:30 | 5.7488 | 0 | N/A | 0 | 0
2021-06-08 01:00 | 4.9175 | 0 | N/A | 0 | 0
2021-06-08 01:30 | 4.7627 | 0 | N/A | 0 | 0
2021-06-08 02:00 | 4.4432 | 0 | N/A | 0 | 0
2021-06-08 02:30 | 3.8952 | 0 | N/A | 0 | 0
2021-06-08 03:00 | 3.5057 | 0 | N/A | 0 | 0
2021-06-08 03:30 | 3.3317 | 0 | N/A | 0 | 0
2021-06-08 04:00 | 3.2266 | 0 | N/A | 0 | 0
2021-06-08 04:30 | 3.2069 | 0 | N/A | 0 | 0
2021-06-08 05:00 | 3.2298 | 0 | N/A | 0 | 0
2021-06-08 05:30 | 3.5968 | 0 | N/A | 0 | 0
2021-06-08 06:00 | 4.1111 | 0 | N/A | 0 | 0
2021-06-08 06:30 | 4.8304 | 0 | N/A | 0 | 0
2021-06-08 07:00 | 5.5386 | 0 | N/A | 0 | 0
2021-06-08 07:30 | 6.0588 | 0 | N/A | 0 | 0
2021-06-08 08:00 | 6.83 | 0 | N/A | 0 | 0
2021-06-08 08:30 | 7.3547 | 0 | N/A | 0 | 0
2021-06-08 09:00 | 7.2623 | 0 | N/A | 0 | 0
2021-06-08 09:30 | 6.796 | 0 | N/A | 0 | 0
2021-06-08 10:00 | 6.4825 | 0 | N/A | 0 | 0
2021-06-08 10:30 | 5.6477 | 0 | N/A | 0 | 0
2021-06-08 11:00 | 5.2463 | 0 | N/A | 0 | 0
2021-06-08 11:30 | 5.368 | 0 | N/A | 0 | 0
2021-06-08 12:00 | 5.5818 | 0 | N/A | 0 | 0
2021-06-08 12:30 | 4.6542 | 0 | N/A | 0 | 0
2021-06-08 13:00 | 5.357 | 0 | N/A | 0 | 0
2021-06-08 13:30 | 5.0701 | 0 | N/A | 0 | 0
2021-06-08 14:00 | 5.6504 | 0 | N/A | 0 | 0
2021-06-08 14:30 | 6.2309 | 0 | N/A | 0 | 0
2021-06-08 15:00 | 6.4451 | 0 | N/A | 0 | 0
2021-06-08 15:30 | 6.9308 | 0 | N/A | 0 | 0
2021-06-08 16:00 | 7.2878 | 0 | N/A | 0 | 0
2021-06-08 16:30 | 7.1776 | 0 | N/A | 0 | 0
2021-06-08 17:00 | 7.8573 | 0 | N/A | 0 | 0
2021-06-08 17:30 | 8.6503 | 0 | N/A | 0 | 0
2021-06-08 18:00 | 9.3038 | 0 | N/A | 0 | 0
2021-06-08 18:30 | 9.337 | 0 | N/A | 0 | 0
2021-06-08 19:00 | 9.0936 | 0 | N/A | 0 | 0
2021-06-08 19:30 | 8.4867 | 0 | N/A | 0 | 0
2021-06-08 20:00 | 8.0902 | 0 | N/A | 0 | 0
2021-06-08 20:30 | 7.6821 | 0 | N/A | 0 | 0
2021-06-08 21:00 | 7.2174 | 0 | N/A | 0 | 0
2021-06-08 21:30 | 7.3096 | 0 | N/A | 0 | 0
2021-06-08 22:00 | 7.4773 | 0 | N/A | 0 | 0
2021-06-08 22:30 | 6.6614 | 0 | N/A | 0 | 0
2021-06-08 23:00 | 6.4563 | 0 | N/A | 0 | 0
2021-06-08 23:30 | 6.6251 | 0 | N/A | 0 | 0
2021-06-09 | 6.9393 | 0 | N/A | 0 | 0
2021-06-09 00:30 | 6.3312 | 0 | N/A | 0 | 0
2021-06-09 01:00 | 5.5915 | 0 | N/A | 0 | 0
2021-06-09 01:30 | 5.4877 | 0 | N/A | 0 | 0
2021-06-09 02:00 | 4.9153 | 0 | N/A | 0 | 0
2021-06-09 02:30 | 4.2721 | 0 | N/A | 0 | 0
2021-06-09 03:00 | 3.9648 | 0 | N/A | 0 | 0
2021-06-09 03:30 | 3.7494 | 0 | N/A | 0 | 0
2021-06-09 04:00 | 3.6397 | 0 | N/A | 0 | 0
2021-06-09 04:30 | 3.5499 | 0 | N/A | 0 | 0
2021-06-09 05:00 | 3.6519 | 0 | N/A | 0 | 0
2021-06-09 05:30 | 4.027 | 0 | N/A | 0 | 0
2021-06-09 06:00 | 4.4733 | 0 | N/A | 0 | 0
2021-06-09 06:30 | 5.2789 | 0 | N/A | 0 | 0
2021-06-09 07:00 | 5.9988 | 0 | N/A | 0 | 0
2021-06-09 07:30 | 6.6869 | 0 | N/A | 0 | 0
2021-06-09 08:00 | 7.6524 | 0 | N/A | 0 | 0
2021-06-09 08:30 | 7.9645 | 0 | N/A | 0 | 0
2021-06-09 09:00 | 7.6377 | 0 | N/A | 0 | 0
2021-06-09 09:30 | 7.3434 | 0 | N/A | 0 | 0
2021-06-09 10:00 | 7.0351 | 0 | N/A | 0 | 0
2021-06-09 10:30 | 6.8023 | 0 | N/A | 0 | 0
2021-06-09 11:00 | 6.7609 | 0 | N/A | 0 | 0
2021-06-09 11:30 | 6.0483 | 0 | N/A | 0 | 0
2021-06-09 12:00 | 6.3194 | 0 | N/A | 0 | 0
2021-06-09 12:30 | 6.8816 | 0 | N/A | 0 | 0
2021-06-09 13:00 | 6.54 | 0 | N/A | 0 | 0
2021-06-09 13:30 | 6.5833 | 0 | N/A | 0 | 0
2021-06-09 14:00 | 7.055 | 0 | N/A | 0 | 0
2021-06-09 14:30 | 7.0367 | 0 | N/A | 0 | 0
2021-06-09 15:00 | 7.4162 | 0 | N/A | 0 | 0
2021-06-09 15:30 | 7.3678 | 0 | N/A | 0 | 0
2021-06-09 16:00 | 6.9833 | 0 | N/A | 0 | 0
2021-06-09 16:30 | 7.3867 | 0 | N/A | 0 | 0
2021-06-09 17:00 | 7.9133 | 0 | N/A | 0 | 0
2021-06-09 17:30 | 8.6967 | 0 | N/A | 0 | 0
2021-06-09 18:00 | 9.4477 | 0 | N/A | 0 | 0
2021-06-09 18:30 | 9.4044 | 0 | N/A | 0 | 0
2021-06-09 19:00 | 8.9536 | 0 | N/A | 0 | 0
2021-06-09 19:30 | 8.4067 | 0 | N/A | 0 | 0
2021-06-09 20:00 | 8.1868 | 0 | N/A | 0 | 0
2021-06-09 20:30 | 7.8838 | 0 | N/A | 0 | 0
2021-06-09 21:00 | 8.4934 | 0 | N/A | 0 | 0
2021-06-09 21:30 | 8.7214 | 0 | N/A | 0 | 0
2021-06-09 22:00 | 7.9954 | 0 | N/A | 0 | 0
2021-06-09 22:30 | 6.6457 | 0 | N/A | 0 | 0
2021-06-09 23:00 | 6.3689 | 0 | N/A | 0 | 0
2021-06-09 23:30 | 6.4793 | 0 | N/A | 0 | 0
2021-06-10 | 6.7677 | 0 | N/A | 0 | 0
2021-06-10 00:30 | 6.0911 | 0 | N/A | 0 | 0
2021-06-10 01:00 | 5.3053 | 0 | N/A | 0 | 0
2021-06-10 01:30 | 5.1992 | 0 | N/A | 0 | 0
2021-06-10 02:00 | 6.1439 | 0 | N/A | 0 | 0
2021-06-10 02:30 | 5.8421 | 0 | N/A | 0 | 0
2021-06-10 03:00 | 3.9898 | 0 | N/A | 0 | 0
2021-06-10 03:30 | 3.609 | 0 | N/A | 0 | 0
2021-06-10 04:00 | 3.483 | 0 | N/A | 0 | 0
2021-06-10 04:30 | 3.3056 | 0 | N/A | 0 | 0
2021-06-10 05:00 | 3.4367 | 0 | N/A | 0 | 0
2021-06-10 05:30 | 3.7363 | 0 | N/A | 0 | 0
2021-06-10 06:00 | 4.2284 | 0 | N/A | 0 | 0
2021-06-10 06:30 | 5.016 | 0 | N/A | 0 | 0
2021-06-10 07:00 | 5.7587 | 0 | N/A | 0 | 0
2021-06-10 07:30 | 6.63 | 0 | N/A | 0 | 0
2021-06-10 08:00 | 7.391 | 0 | N/A | 0 | 0
2021-06-10 08:30 | 7.7068 | 0 | N/A | 0 | 0
2021-06-10 09:00 | 7.589 | 0 | N/A | 0 | 0
2021-06-10 09:30 | 7.2768 | 0 | N/A | 0 | 0
2021-06-10 10:00 | 7.6748 | 0 | N/A | 0 | 0
2021-06-10 10:30 | 7.5456 | 0 | N/A | 0 | 0
2021-06-10 11:00 | 7.6181 | 0 | N/A | 0 | 0
2021-06-10 11:30 | 7.2591 | 0 | N/A | 0 | 0
2021-06-10 12:00 | 6.9274 | 0 | N/A | 0 | 0
2021-06-10 12:30 | 7.0271 | 0 | N/A | 0 | 0
2021-06-10 13:00 | 7.2545 | 0 | N/A | 0 | 0
2021-06-10 13:30 | 7.3321 | 0 | N/A | 0 | 0
2021-06-10 14:00 | 7.3111 | 0 | N/A | 0 | 0
2021-06-10 14:30 | 7.1664 | 0 | N/A | 0 | 0
2021-06-10 15:00 | 7.255 | 0 | N/A | 0 | 0
2021-06-10 15:30 | 7.2099 | 0 | N/A | 0 | 0
2021-06-10 16:00 | 6.8601 | 0 | N/A | 0 | 0
2021-06-10 16:30 | 7.0106 | 0 | N/A | 0 | 0
2021-06-10 17:00 | 7.5202 | 0 | N/A | 0 | 0
2021-06-10 17:30 | 8.24 | 0 | N/A | 0 | 0
2021-06-10 18:00 | 8.86 | 0 | N/A | 0 | 0
2021-06-10 18:30 | 8.9067 | 0 | N/A | 0 | 0
2021-06-10 19:00 | 8.6733 | 0 | N/A | 0 | 0
2021-06-10 19:30 | 8.2733 | 0 | N/A | 0 | 0
2021-06-10 20:00 | 7.8234 | 0 | N/A | 0 | 0
2021-06-10 20:30 | 7.3817 | 0 | N/A | 0 | 0
2021-06-10 21:00 | 7.0096 | 0 | N/A | 0 | 0
2021-06-10 21:30 | 7.1955 | 0 | N/A | 0 | 0
2021-06-10 22:00 | 7.1251 | 0 | N/A | 0 | 0
2021-06-10 22:30 | 6.4026 | 0 | N/A | 0 | 0
2021-06-10 23:00 | 6.1905 | 0 | N/A | 0 | 0
2021-06-10 23:30 | 6.3951 | 0 | N/A | 0 | 0
2021-06-11 | 6.7521 | 0 | N/A | 0 | 0
2021-06-11 00:30 | 5.9343 | 0 | N/A | 0 | 0
2021-06-11 01:00 | 5.2756 | 0 | N/A | 0 | 0
2021-06-11 01:30 | 5.1214 | 0 | N/A | 0 | 0
2021-06-11 02:00 | 4.7031 | 0 | N/A | 0 | 0
2021-06-11 02:30 | 4.1086 | 0 | N/A | 0 | 0
2021-06-11 03:00 | 3.8044 | 0 | N/A | 0 | 0
2021-06-11 03:30 | 3.4834 | 0 | N/A | 0 | 0
2021-06-11 04:00 | 3.3881 | 0 | N/A | 0 | 0
2021-06-11 04:30 | 3.4112 | 0 | N/A | 0 | 0
2021-06-11 05:00 | 3.4773 | 0 | N/A | 0 | 0
2021-06-11 05:30 | 3.7609 | 0 | N/A | 0 | 0
2021-06-11 06:00 | 4.239 | 0 | N/A | 0 | 0
2021-06-11 06:30 | 4.7941 | 0 | N/A | 0 | 0
2021-06-11 07:00 | 5.7567 | 0 | N/A | 0 | 0
2021-06-11 07:30 | 6.265 | 0 | N/A | 0 | 0
2021-06-11 08:00 | 6.9133 | 0 | N/A | 0 | 0
2021-06-11 08:30 | 7.1667 | 0 | N/A | 0 | 0
2021-06-11 09:00 | 6.6232 | 0 | N/A | 0 | 0
2021-06-11 09:30 | 5.9063 | 0 | N/A | 0 | 0
2021-06-11 10:00 | 5.2545 | 0 | N/A | 0 | 0
2021-06-11 10:30 | 4.5167 | 0 | N/A | 0 | 0
2021-06-11 11:00 | 3.6539 | 0 | N/A | 0 | 0
2021-06-11 11:30 | 3.1177 | 0 | N/A | 0 | 0
2021-06-11 12:00 | 2.831 | 0 | N/A | 0 | 0
2021-06-11 12:30 | 2.947 | 0 | N/A | 0 | 0
2021-06-11 13:00 | 2.7155 | 0 | N/A | 0 | 0
2021-06-11 13:30 | 3.7285 | 0 | N/A | 0 | 0
2021-06-11 14:00 | 4.3564 | 0 | N/A | 0 | 0
2021-06-11 14:30 | 3.7822 | 0 | N/A | 0 | 0
2021-06-11 15:00 | 3.3737 | 0 | N/A | 0 | 0
2021-06-11 15:30 | 3.6293 | 0 | N/A | 0 | 0
2021-06-11 16:00 | 4.4747 | 0 | N/A | 0 | 0
2021-06-11 16:30 | 4.6595 | 0 | N/A | 0 | 0
2021-06-11 17:00 | 5.4406 | 0 | N/A | 0 | 0
2021-06-11 17:30 | 6.3216 | 0 | N/A | 0 | 0
2021-06-11 18:00 | 7.1447 | 0 | N/A | 0 | 0
2021-06-11 18:30 | 7.3272 | 0 | N/A | 0 | 0
2021-06-11 19:00 | 7.2301 | 0 | N/A | 0 | 0
2021-06-11 19:30 | 7.0111 | 0 | N/A | 0 | 0
2021-06-11 20:00 | 6.8521 | 0 | N/A | 0 | 0
2021-06-11 20:30 | 6.6893 | 0 | N/A | 0 | 0
2021-06-11 21:00 | 6.3434 | 0 | N/A | 0 | 0
2021-06-11 21:30 | 6.7186 | 0 | N/A | 0 | 0
2021-06-11 22:00 | 6.7795 | 0 | N/A | 0 | 0
2021-06-11 22:30 | 6.3423 | 0 | N/A | 0 | 0
2021-06-11 23:00 | 6.1903 | 0 | N/A | 0 | 0
2021-06-11 23:30 | 6.2512 | 0 | N/A | 0 | 0
2021-06-12 | 6.5998 | 0 | N/A | 0 | 0
2021-06-12 00:30 | 5.8882 | 0 | N/A | 0 | 0
2021-06-12 01:00 | 5.1289 | 0 | N/A | 0 | 0
2021-06-12 01:30 | 4.9276 | 0 | N/A | 0 | 0
2021-06-12 02:00 | 4.4042 | 0 | N/A | 0 | 0
2021-06-12 02:30 | 3.7809 | 0 | N/A | 0 | 0
2021-06-12 03:00 | 3.4581 | 0 | N/A | 0 | 0
2021-06-12 03:30 | 3.2477 | 0 | N/A | 0 | 0
2021-06-12 04:00 | 3.0534 | 0 | N/A | 0 | 0
2021-06-12 04:30 | 2.9379 | 0 | N/A | 0 | 0
2021-06-12 05:00 | 2.9496 | 0 | N/A | 0 | 0
2021-06-12 05:30 | 3.0156 | 0 | N/A | 0 | 0
2021-06-12 06:00 | 3.289 | 0 | N/A | 0 | 0
2021-06-12 06:30 | 3.5568 | 0 | N/A | 0 | 0
2021-06-12 07:00 | 3.7825 | 0 | N/A | 0 | 0
2021-06-12 07:30 | 3.7955 | 0 | N/A | 0 | 0
2021-06-12 08:00 | 4.3506 | 0 | N/A | 0 | 0
2021-06-12 08:30 | 4.9103 | 0 | N/A | 0 | 0
2021-06-12 09:00 | 5.1954 | 0 | N/A | 0 | 0
2021-06-12 09:30 | 5.024 | 0 | N/A | 0 | 0
2021-06-12 10:00 | 4.6403 | 0 | N/A | 0 | 0
2021-06-12 10:30 | 4.4427 | 0 | N/A | 0 | 0
2021-06-12 11:00 | 3.8455 | 0 | N/A | 0 | 0
2021-06-12 11:30 | 3.9505 | 0 | N/A | 0 | 0
2021-06-12 12:00 | 4.2034 | 0 | N/A | 0 | 0
2021-06-12 12:30 | 4.4519 | 0 | N/A | 0 | 0
2021-06-12 13:00 | 4.2053 | 0 | N/A | 0 | 0
2021-06-12 13:30 | 4.305 | 0 | N/A | 0 | 0
2021-06-12 14:00 | 4.092 | 0 | N/A | 0 | 0
2021-06-12 14:30 | 3.8808 | 0 | N/A | 0 | 0
2021-06-12 15:00 | 4.6018 | 0 | N/A | 0 | 0
2021-06-12 15:30 | 4.8583 | 0 | N/A | 0 | 0
2021-06-12 16:00 | 5.1049 | 0 | N/A | 0 | 0
2021-06-12 16:30 | 5.4397 | 0 | N/A | 0 | 0
2021-06-12 17:00 | 5.8614 | 0 | N/A | 0 | 0
2021-06-12 17:30 | 6.4859 | 0 | N/A | 0 | 0
2021-06-12 18:00 | 7.108 | 0 | N/A | 0 | 0
2021-06-12 18:30 | 7.2152 | 0 | N/A | 0 | 0
2021-06-12 19:00 | 6.8884 | 0 | N/A | 0 | 0
2021-06-12 19:30 | 6.4711 | 0 | N/A | 0 | 0
2021-06-12 20:00 | 6.2443 | 0 | N/A | 0 | 0
2021-06-12 20:30 | 5.9279 | 0 | N/A | 0 | 0
2021-06-12 21:00 | 5.6275 | 0 | N/A | 0 | 0
2021-06-12 21:30 | 6.102 | 0 | N/A | 0 | 0
2021-06-12 22:00 | 6.2477 | 0 | N/A | 0 | 0
2021-06-12 22:30 | 5.8976 | 0 | N/A | 0 | 0
2021-06-12 23:00 | 5.9735 | 0 | N/A | 0 | 0
2021-06-12 23:30 | 6.0764 | 0 | N/A | 0 | 0
2021-06-13 | 6.3766 | 0 | N/A | 0 | 0
2021-06-13 00:30 | 5.6167 | 0 | N/A | 0 | 0
2021-06-13 01:00 | 4.891 | 0 | N/A | 0 | 0
2021-06-13 01:30 | 4.6789 | 0 | N/A | 0 | 0
2021-06-13 02:00 | 4.2492 | 0 | N/A | 0 | 0
2021-06-13 02:30 | 3.6316 | 0 | N/A | 0 | 0
2021-06-13 03:00 | 3.3242 | 0 | N/A | 0 | 0
2021-06-13 03:30 | 3.1573 | 0 | N/A | 0 | 0
2021-06-13 04:00 | 2.9452 | 0 | N/A | 0 | 0
2021-06-13 04:30 | 2.8798 | 0 | N/A | 0 | 0
2021-06-13 05:00 | 2.8482 | 0 | N/A | 0 | 0
2021-06-13 05:30 | 2.865 | 0 | N/A | 0 | 0
2021-06-13 06:00 | 3.0323 | 0 | N/A | 0 | 0
2021-06-13 06:30 | 3.3649 | 0 | N/A | 0 | 0
2021-06-13 07:00 | 3.5072 | 0 | N/A | 0 | 0
2021-06-13 07:30 | 3.5668 | 0 | N/A | 0 | 0
2021-06-13 08:00 | 4.0413 | 0 | N/A | 0 | 0
2021-06-13 08:30 | 4.5079 | 0 | N/A | 0 | 0
2021-06-13 09:00 | 4.3881 | 0 | N/A | 0 | 0
2021-06-13 09:30 | 4.3968 | 0 | N/A | 0 | 0
2021-06-13 10:00 | 4.4137 | 0 | N/A | 0 | 0
2021-06-13 10:30 | 4.3405 | 0 | N/A | 0 | 0
2021-06-13 11:00 | 4.2945 | 0 | N/A | 0 | 0
2021-06-13 11:30 | 4.0786 | 0 | N/A | 0 | 0
2021-06-13 12:00 | 3.7216 | 0 | N/A | 0 | 0
2021-06-13 12:30 | 3.6492 | 0 | N/A | 0 | 0
2021-06-13 13:00 | 3.2796 | 0 | N/A | 0 | 0
2021-06-13 13:30 | 3.7571 | 0 | N/A | 0 | 0
2021-06-13 14:00 | 3.8109 | 0 | N/A | 0 | 0
2021-06-13 14:30 | 3.8184 | 0 | N/A | 0 | 0
2021-06-13 15:00 | 3.4394 | 0 | N/A | 0 | 0
2021-06-13 15:30 | 4.1007 | 0 | N/A | 0 | 0
2021-06-13 16:00 | 4.5873 | 0 | N/A | 0 | 0
2021-06-13 16:30 | 5.0564 | 0 | N/A | 0 | 0
2021-06-13 17:00 | 5.6651 | 0 | N/A | 0 | 0
2021-06-13 17:30 | 6.4246 | 0 | N/A | 0 | 0
2021-06-13 18:00 | 7.056 | 0 | N/A | 0 | 0
2021-06-13 18:30 | 7.1026 | 0 | N/A | 0 | 0
2021-06-13 19:00 | 6.8538 | 0 | N/A | 0 | 0
2021-06-13 19:30 | 6.6219 | 0 | N/A | 0 | 0
2021-06-13 20:00 | 6.1424 | 0 | N/A | 0 | 0
2021-06-13 20:30 | 5.8802 | 0 | N/A | 0 | 0
2021-06-13 21:00 | 5.5966 | 0 | N/A | 0 | 0
2021-06-13 21:30 | 5.9609 | 0 | N/A | 0 | 0
2021-06-13 22:00 | 6.1429 | 0 | N/A | 0 | 0
2021-06-13 22:30 | 5.902 | 0 | N/A | 0 | 0
2021-06-13 23:00 | 5.9046 | 0 | N/A | 0 | 0
2021-06-13 23:30 | 6.112 | 0 | N/A | 0 | 0
2021-06-14 | 6.363 | 0 | N/A | 0 | 0
2021-06-14 00:30 | 5.6729 | 0 | N/A | 0 | 0
2021-06-14 01:00 | 4.9019 | 0 | N/A | 0 | 0
2021-06-14 01:30 | 4.6789 | 0 | N/A | 0 | 0
2021-06-14 02:00 | 4.3336 | 0 | N/A | 0 | 0
2021-06-14 02:30 | 3.7423 | 0 | N/A | 0 | 0
2021-06-14 03:00 | 3.4398 | 0 | N/A | 0 | 0
2021-06-14 03:30 | 3.1139 | 0 | N/A | 0 | 0
2021-06-14 04:00 | 2.9536 | 0 | N/A | 0 | 0
2021-06-14 04:30 | 2.961 | 0 | N/A | 0 | 0
2021-06-14 05:00 | 2.9125 | 0 | N/A | 0 | 0
2021-06-14 05:30 | 3.0237 | 0 | N/A | 0 | 0
2021-06-14 06:00 | 3.2788 | 0 | N/A | 0 | 0
2021-06-14 06:30 | 3.4757 | 0 | N/A | 0 | 0
2021-06-14 07:00 | 3.5631 | 0 | N/A | 0 | 0
2021-06-14 07:30 | 3.581 | 0 | N/A | 0 | 0
2021-06-14 08:00 | 4.0682 | 0 | N/A | 0 | 0
2021-06-14 08:30 | 4.5594 | 0 | N/A | 0 | 0
2021-06-14 09:00 | 4.8767 | 0 | N/A | 0 | 0
2021-06-14 09:30 | 5.0684 | 0 | N/A | 0 | 0
2021-06-14 10:00 | 5.2466 | 0 | N/A | 0 | 0
2021-06-14 10:30 | 5.2622 | 0 | N/A | 0 | 0
2021-06-14 11:00 | 5.1467 | 0 | N/A | 0 | 0
2021-06-14 11:30 | 5.1144 | 0 | N/A | 0 | 0
2021-06-14 12:00 | 4.8904 | 0 | N/A | 0 | 0
2021-06-14 12:30 | 4.6916 | 0 | N/A | 0 | 0
2021-06-14 13:00 | 4.3895 | 0 | N/A | 0 | 0
2021-06-14 13:30 | 4.205 | 0 | N/A | 0 | 0
2021-06-14 14:00 | 3.5346 | 0 | N/A | 0 | 0
2021-06-14 14:30 | 3.2862 | 0 | N/A | 0 | 0
2021-06-14 15:00 | 3.1866 | 0 | N/A | 0 | 0
2021-06-14 15:30 | 3.7807 | 0 | N/A | 0 | 0
2021-06-14 16:00 | 4.3942 | 0 | N/A | 0 | 0
2021-06-14 16:30 | 5.0545 | 0 | N/A | 0 | 0
2021-06-14 17:00 | 5.9775 | 0 | N/A | 0 | 0
2021-06-14 17:30 | 6.9928 | 0 | N/A | 0 | 0
2021-06-14 18:00 | 7.9119 | 0 | N/A | 0 | 0
2021-06-14 18:30 | 8.2272 | 0 | N/A | 0 | 0
2021-06-14 19:00 | 8.0771 | 0 | N/A | 0 | 0
2021-06-14 19:30 | 7.6979 | 0 | N/A | 0 | 0
2021-06-14 20:00 | 7.2432 | 0 | N/A | 0 | 0
2021-06-14 20:30 | 6.9068 | 0 | N/A | 0 | 0
2021-06-14 21:00 | 6.6143 | 0 | N/A | 0 | 0
2021-06-14 21:30 | 6.7611 | 0 | N/A | 0 | 0
2021-06-14 22:00 | 6.8914 | 0 | N/A | 0 | 0
2021-06-14 22:30 | 6.4313 | 0 | N/A | 0 | 0
2021-06-14 23:00 | 6.1543 | 0 | N/A | 0 | 0
2021-06-14 23:30 | 6.1408 | 0 | N/A | 0 | 0
2021-06-15 | 6.4711 | 0 | N/A | 0 | 0
2021-06-15 00:30 | 5.9652 | 0 | N/A | 0 | 0
2021-06-15 01:00 | 5.2812 | 0 | N/A | 0 | 0
2021-06-15 01:30 | 5.211 | 0 | N/A | 0 | 0
2021-06-15 02:00 | 4.7533 | 0 | N/A | 0 | 0
2021-06-15 02:30 | 4.1969 | 0 | N/A | 0 | 0
2021-06-15 03:00 | 3.7109 | 0 | N/A | 0 | 0
2021-06-15 03:30 | 3.5051 | 0 | N/A | 0 | 0
2021-06-15 04:00 | 3.276 | 0 | N/A | 0 | 0
2021-06-15 04:30 | 3.2065 | 0 | N/A | 0 | 0
2021-06-15 05:00 | 3.2139 | 0 | N/A | 0 | 0
2021-06-15 05:30 | 3.5095 | 0 | N/A | 0 | 0
2021-06-15 06:00 | 3.9743 | 0 | N/A | 0 | 0
2021-06-15 06:30 | 4.6591 | 0 | N/A | 0 | 0
2021-06-15 07:00 | 5.3004 | 0 | N/A | 0 | 0
2021-06-15 07:30 | 5.6812 | 0 | N/A | 0 | 0
2021-06-15 08:00 | 6.3902 | 0 | N/A | 0 | 0
2021-06-15 08:30 | 6.8301 | 0 | N/A | 0 | 0
2021-06-15 09:00 | 6.6736 | 0 | N/A | 0 | 0
2021-06-15 09:30 | 6.467 | 0 | N/A | 0 | 0
2021-06-15 10:00 | 6.5301 | 0 | N/A | 0 | 0
2021-06-15 10:30 | 6.33 | 0 | N/A | 0 | 0
2021-06-15 11:00 | 6.1369 | 0 | N/A | 0 | 0
2021-06-15 11:30 | 6.1547 | 0 | N/A | 0 | 0
2021-06-15 12:00 | 5.6259 | 0 | N/A | 0 | 0
2021-06-15 12:30 | 5.8008 | 0 | N/A | 0 | 0
2021-06-15 13:00 | 5.5267 | 0 | N/A | 0 | 0
2021-06-15 13:30 | 5.5938 | 0 | N/A | 0 | 0
2021-06-15 14:00 | 5.26 | 0 | N/A | 0 | 0
2021-06-15 14:30 | 5.5601 | 0 | N/A | 0 | 0
2021-06-15 15:00 | 5.944 | 0 | N/A | 0 | 0
2021-06-15 15:30 | 6.2168 | 0 | N/A | 0 | 0
2021-06-15 16:00 | 6.2073 | 0 | N/A | 0 | 0
2021-06-15 16:30 | 6.4 | 0 | N/A | 0 | 0
2021-06-15 17:00 | 6.8995 | 0 | N/A | 0 | 0
2021-06-15 17:30 | 7.5819 | 0 | N/A | 0 | 0
2021-06-15 18:00 | 8.407 | 0 | N/A | 0 | 0
2021-06-15 18:30 | 8.7567 | 0 | N/A | 0 | 0
2021-06-15 19:00 | 8.4367 | 0 | N/A | 0 | 0
2021-06-15 19:30 | 7.9968 | 0 | N/A | 0 | 0
2021-06-15 20:00 | 7.6083 | 0 | N/A | 0 | 0
2021-06-15 20:30 | 7.2131 | 0 | N/A | 0 | 0
2021-06-15 21:00 | 6.7955 | 0 | N/A | 0 | 0
2021-06-15 21:30 | 6.8829 | 0 | N/A | 0 | 0
2021-06-15 22:00 | 6.8688 | 0 | N/A | 0 | 0
2021-06-15 22:30 | 6.2826 | 0 | N/A | 0 | 0
2021-06-15 23:00 | 6.0395 | 0 | N/A | 0 | 0
2021-06-15 23:30 | 6.1427 | 0 | N/A | 0 | 0
2021-06-16 | 6.476 | 0 | N/A | 0 | 0
2021-06-16 00:30 | 5.7184 | 0 | N/A | 0 | 0
2021-06-16 01:00 | 4.93 | 0 | N/A | 0 | 0
2021-06-16 01:30 | 4.7101 | 0 | N/A | 0 | 0
2021-06-16 02:00 | 4.4027 | 0 | N/A | 0 | 0
2021-06-16 02:30 | 3.8198 | 0 | N/A | 0 | 0
2021-06-16 03:00 | 3.4359 | 0 | N/A | 0 | 0
2021-06-16 03:30 | 3.2996 | 0 | N/A | 0 | 0
2021-06-16 04:00 | 3.1337 | 0 | N/A | 0 | 0
2021-06-16 04:30 | 3.1187 | 0 | N/A | 0 | 0
2021-06-16 05:00 | 3.1282 | 0 | N/A | 0 | 0
2021-06-16 05:30 | 3.4101 | 0 | N/A | 0 | 0
2021-06-16 06:00 | 3.8766 | 0 | N/A | 0 | 0
2021-06-16 06:30 | 4.66 | 0 | N/A | 0 | 0
2021-06-16 07:00 | 5.3995 | 0 | N/A | 0 | 0
2021-06-16 07:30 | 5.8323 | 0 | N/A | 0 | 0
2021-06-16 08:00 | 6.9604 | 0 | N/A | 0 | 0
2021-06-16 08:30 | 7.1722 | 0 | N/A | 0 | 0
2021-06-16 09:00 | 6.9831 | 0 | N/A | 0 | 0
2021-06-16 09:30 | 6.2447 | 0 | N/A | 0 | 0
2021-06-16 10:00 | 5.7614 | 0 | N/A | 0 | 0
2021-06-16 10:30 | 5.1245 | 0 | N/A | 0 | 0
2021-06-16 11:00 | 5.0882 | 0 | N/A | 0 | 0
2021-06-16 11:30 | 5.3954 | 0 | N/A | 0 | 0
2021-06-17 00:30 | 5.8978 | 0 | N/A | 0 | 0
2021-06-17 01:00 | 5.1473 | 0 | N/A | 0 | 0
2021-06-17 01:30 | 5.1309 | 0 | N/A | 0 | 0
2021-06-17 02:00 | 4.7994 | 0 | N/A | 0 | 0
2021-06-17 02:30 | 4.1669 | 0 | N/A | 0 | 0
2021-06-17 03:00 | 3.7095 | 0 | N/A | 0 | 0
2021-06-17 03:30 | 3.4684 | 0 | N/A | 0 | 0
2021-06-17 04:00 | 3.3288 | 0 | N/A | 0 | 0
2021-06-17 04:30 | 3.2591 | 0 | N/A | 0 | 0
2021-06-17 05:00 | 3.3366 | 0 | N/A | 0 | 0
2021-06-17 05:30 | 3.5841 | 0 | N/A | 0 | 0
2021-06-17 06:00 | 4.1682 | 0 | N/A | 0 | 0
2021-06-17 06:30 | 4.843 | 0 | N/A | 0 | 0
2021-06-17 07:00 | 5.6263 | 0 | N/A | 0 | 0
2021-06-17 07:30 | 6.147 | 0 | N/A | 0 | 0
2021-06-17 08:00 | 7.1871 | 0 | N/A | 0 | 0
2021-06-17 08:30 | 7.4993 | 0 | N/A | 0 | 0
2021-06-17 09:00 | 6.8248 | 0 | N/A | 0 | 0
2021-06-17 09:30 | 6.4144 | 0 | N/A | 0 | 0
2021-06-17 10:00 | 6.1549 | 0 | N/A | 0 | 0
2021-06-17 10:30 | 6.4155 | 0 | N/A | 0 | 0
2021-06-17 11:00 | 6.0905 | 0 | N/A | 0 | 0
2021-06-17 11:30 | 5.9921 | 0 | N/A | 0 | 0
2021-06-17 12:00 | 5.7115 | 0 | N/A | 0 | 0
2021-06-17 12:30 | 5.3747 | 0 | N/A | 0 | 0
2021-06-17 13:00 | 5.004 | 0 | N/A | 0 | 0
2021-06-17 13:30 | 5.2168 | 0 | N/A | 0 | 0
2021-06-17 14:00 | 5.4301 | 0 | N/A | 0 | 0
2021-06-17 14:30 | 5.567 | 0 | N/A | 0 | 0
2021-06-17 15:00 | 5.5533 | 0 | N/A | 0 | 0
2021-06-17 15:30 | 5.5933 | 0 | N/A | 0 | 0
2021-06-17 16:00 | 5.6736 | 0 | N/A | 0 | 0
2021-06-17 16:30 | 5.9028 | 0 | N/A | 0 | 0
2021-06-17 17:00 | 6.641 | 0 | N/A | 0 | 0
2021-06-17 17:30 | 7.534 | 0 | N/A | 0 | 0
2021-06-17 18:00 | 8.1367 | 0 | N/A | 0 | 0
2021-06-17 18:30 | 8.55 | 0 | N/A | 0 | 0
2021-06-17 19:00 | 8.3367 | 0 | N/A | 0 | 0
2021-06-17 19:30 | 8.0701 | 0 | N/A | 0 | 0
2021-06-17 20:00 | 7.8139 | 0 | N/A | 0 | 0
2021-06-17 20:30 | 7.3657 | 0 | N/A | 0 | 0
2021-06-17 21:00 | 6.9836 | 0 | N/A | 0 | 0
2021-06-17 21:30 | 7.0895 | 0 | N/A | 0 | 0
2021-06-17 22:00 | 7.1646 | 0 | N/A | 0 | 0
2021-06-17 22:30 | 6.5463 | 0 | N/A | 0 | 0
2021-06-17 23:00 | 6.269 | 0 | N/A | 0 | 0
2021-06-17 23:30 | 6.2887 | 0 | N/A | 0 | 0
2021-06-18 | 6.5298 | 0 | N/A | 0 | 0
2021-06-18 00:30 | 5.8243 | 0 | N/A | 0 | 0
2021-06-18 01:00 | 5.064 | 0 | N/A | 0 | 0
2021-06-18 01:30 | 4.9874 | 0 | N/A | 0 | 0
2021-06-18 02:00 | 4.5858 | 0 | N/A | 0 | 0
2021-06-18 02:30 | 3.865 | 0 | N/A | 0 | 0
2021-06-18 03:00 | 3.5054 | 0 | N/A | 0 | 0
2021-06-18 03:30 | 3.3036 | 0 | N/A | 0 | 0
2021-06-18 04:00 | 3.1311 | 0 | N/A | 0 | 0
2021-06-18 04:30 | 3.1034 | 0 | N/A | 0 | 0
2021-06-18 05:00 | 3.1672 | 0 | N/A | 0 | 0
2021-06-18 05:30 | 3.4982 | 0 | N/A | 0 | 0
2021-06-18 06:00 | 3.9583 | 0 | N/A | 0 | 0
2021-06-18 06:30 | 4.7311 | 0 | N/A | 0 | 0
2021-06-18 07:00 | 5.3517 | 0 | N/A | 0 | 0
2021-06-18 07:30 | 5.8952 | 0 | N/A | 0 | 0
2021-06-18 08:00 | 6.7435 | 0 | N/A | 0 | 0
2021-06-18 08:30 | 6.994 | 0 | N/A | 0 | 0
2021-06-18 09:00 | 6.544 | 0 | N/A | 0 | 0
2021-06-18 09:30 | 6.32 | 0 | N/A | 0 | 0
2021-06-18 10:00 | 6.0202 | 0 | N/A | 0 | 0
2021-06-18 10:30 | 5.39 | 0 | N/A | 0 | 0
2021-06-18 11:00 | 4.6933 | 0 | N/A | 0 | 0
2021-06-18 11:30 | 4.9402 | 0 | N/A | 0 | 0
2021-06-18 12:00 | 4.9469 | 0 | N/A | 0 | 0
2021-06-18 12:30 | 5.3133 | 0 | N/A | 0 | 0
2021-06-18 13:00 | 4.8368 | 0 | N/A | 0 | 0
2021-06-18 13:30 | 5.2721 | 0 | N/A | 0 | 0
2021-06-18 14:00 | 5.0544 | 0 | N/A | 0 | 0
2021-06-18 14:30 | 4.9446 | 0 | N/A | 0 | 0
2021-06-18 15:00 | 5.0167 | 0 | N/A | 0 | 0
2021-06-18 15:30 | 5.4919 | 0 | N/A | 0 | 0
2021-06-18 16:00 | 5.9639 | 0 | N/A | 0 | 0
2021-06-18 16:30 | 6.1214 | 0 | N/A | 0 | 0
2021-06-18 17:00 | 6.692 | 0 | N/A | 0 | 0
2021-06-18 17:30 | 7.2891 | 0 | N/A | 0 | 0
2021-06-18 18:00 | 7.8739 | 0 | N/A | 0 | 0
2021-06-18 18:30 | 8.1567 | 0 | N/A | 0 | 0
2021-06-18 19:00 | 7.9304 | 0 | N/A | 0 | 0
2021-06-18 19:30 | 7.7303 | 0 | N/A | 0 | 0
2021-06-18 20:00 | 7.3217 | 0 | N/A | 0 | 0
2021-06-18 20:30 | 7.1324 | 0 | N/A | 0 | 0
2021-06-18 21:00 | 6.7954 | 0 | N/A | 0 | 0
2021-06-18 21:30 | 7.1242 | 0 | N/A | 0 | 0
2021-06-18 22:00 | 7.176 | 0 | N/A | 0 | 0
2021-06-18 22:30 | 6.7186 | 0 | N/A | 0 | 0
2021-06-18 23:00 | 6.7363 | 0 | N/A | 0 | 0
2021-06-18 23:30 | 6.7627 | 0 | N/A | 0 | 0
2021-06-19 | 7.0029 | 0 | N/A | 0 | 0
2021-06-19 00:30 | 6.1019 | 0 | N/A | 0 | 0
2021-06-19 01:00 | 5.1143 | 0 | N/A | 0 | 0
2021-06-19 01:30 | 4.9931 | 0 | N/A | 0 | 0
2021-06-19 02:00 | 4.5781 | 0 | N/A | 0 | 0
2021-06-19 02:30 | 3.9109 | 0 | N/A | 0 | 0
2021-06-19 03:00 | 3.5888 | 0 | N/A | 0 | 0
2021-06-19 03:30 | 3.451 | 0 | N/A | 0 | 0
2021-06-19 04:00 | 3.2079 | 0 | N/A | 0 | 0
2021-06-19 04:30 | 3.1481 | 0 | N/A | 0 | 0
2021-06-19 05:00 | 3.1864 | 0 | N/A | 0 | 0
2021-06-19 05:30 | 3.2803 | 0 | N/A | 0 | 0
2021-06-19 06:00 | 3.4626 | 0 | N/A | 0 | 0
2021-06-19 06:30 | 3.7196 | 0 | N/A | 0 | 0
2021-06-19 07:00 | 4.0354 | 0 | N/A | 0 | 0
2021-06-19 07:30 | 4.1224 | 0 | N/A | 0 | 0
2021-06-19 08:00 | 4.8442 | 0 | N/A | 0 | 0
2021-06-19 08:30 | 5.4347 | 0 | N/A | 0 | 0
2021-06-19 09:00 | 5.6031 | 0 | N/A | 0 | 0
2021-06-19 09:30 | 5.8739 | 0 | N/A | 0 | 0
2021-06-19 10:00 | 5.8575 | 0 | N/A | 0 | 0
2021-06-19 10:30 | 5.5464 | 0 | N/A | 0 | 0
2021-06-19 11:00 | 5.1954 | 0 | N/A | 0 | 0
2021-06-19 11:30 | 5.2818 | 0 | N/A | 0 | 0
2021-06-19 12:00 | 5.0768 | 0 | N/A | 0 | 0
2021-06-19 12:30 | 4.9373 | 0 | N/A | 0 | 0
2021-06-19 13:00 | 5.0085 | 0 | N/A | 0 | 0
2021-06-19 13:30 | 4.8413 | 0 | N/A | 0 | 0
2021-06-19 14:00 | 4.054 | 0 | N/A | 0 | 0
2021-06-19 14:30 | 3.9086 | 0 | N/A | 0 | 0
2021-06-19 15:00 | 4.0439 | 0 | N/A | 0 | 0
2021-06-19 15:30 | 4.1251 | 0 | N/A | 0 | 0
2021-06-19 16:00 | 4.8581 | 0 | N/A | 0 | 0
2021-06-19 16:30 | 5.3096 | 0 | N/A | 0 | 0
2021-06-19 17:00 | 6.0798 | 0 | N/A | 0 | 0
2021-06-19 17:30 | 6.9149 | 0 | N/A | 0 | 0
2021-06-19 18:00 | 7.64 | 0 | N/A | 0 | 0
2021-06-19 18:30 | 7.682 | 0 | N/A | 0 | 0
2021-06-19 19:00 | 7.3863 | 0 | N/A | 0 | 0
2021-06-19 19:30 | 7.0275 | 0 | N/A | 0 | 0
2021-06-19 20:00 | 6.6349 | 0 | N/A | 0 | 0
2021-06-19 20:30 | 6.4019 | 0 | N/A | 0 | 0
2021-06-19 21:00 | 6.1273 | 0 | N/A | 0 | 0
2021-06-19 21:30 | 6.5693 | 0 | N/A | 0 | 0
2021-06-19 22:00 | 6.7674 | 0 | N/A | 0 | 0
2021-06-19 22:30 | 6.4993 | 0 | N/A | 0 | 0
2021-06-19 23:00 | 6.4875 | 0 | N/A | 0 | 0
2021-06-19 23:30 | 6.5542 | 0 | N/A | 0 | 0
2021-06-20 | 6.8989 | 0 | N/A | 0 | 0
2021-06-20 00:30 | 6.1684 | 0 | N/A | 0 | 0
2021-06-20 01:00 | 5.3543 | 0 | N/A | 0 | 0
2021-06-20 01:30 | 5.004 | 0 | N/A | 0 | 0
2021-06-20 02:00 | 4.524 | 0 | N/A | 0 | 0
2021-06-20 02:30 | 3.9561 | 0 | N/A | 0 | 0
2021-06-20 03:00 | 3.5831 | 0 | N/A | 0 | 0
2021-06-20 03:30 | 3.3536 | 0 | N/A | 0 | 0
2021-06-20 04:00 | 3.2056 | 0 | N/A | 0 | 0
2021-06-20 04:30 | 3.1257 | 0 | N/A | 0 | 0
2021-06-20 05:00 | 3.0896 | 0 | N/A | 0 | 0
2021-06-20 05:30 | 3.2165 | 0 | N/A | 0 | 0
2021-06-20 06:00 | 3.4499 | 0 | N/A | 0 | 0
2021-06-20 06:30 | 3.6835 | 0 | N/A | 0 | 0
2021-06-20 07:00 | 3.8936 | 0 | N/A | 0 | 0
2021-06-20 07:30 | 3.9158 | 0 | N/A | 0 | 0
2021-06-20 08:00 | 4.5019 | 0 | N/A | 0 | 0
2021-06-20 08:30 | 5.1522 | 0 | N/A | 0 | 0
2021-06-20 09:00 | 5.1078 | 0 | N/A | 0 | 0
2021-06-20 09:30 | 4.8108 | 0 | N/A | 0 | 0
2021-06-20 10:00 | 4.3592 | 0 | N/A | 0 | 0
2021-06-20 10:30 | 3.8397 | 0 | N/A | 0 | 0
2021-06-20 11:00 | 3.1833 | 0 | N/A | 0 | 0
2021-06-20 11:30 | 2.8043 | 0 | N/A | 0 | 0
2021-06-20 12:00 | 2.4568 | 0 | N/A | 0 | 0
2021-06-20 12:30 | 2.9722 | 0 | N/A | 0 | 0
2021-06-20 13:00 | 2.8804 | 0 | N/A | 0 | 0
2021-06-20 13:30 | 2.6867 | 0 | N/A | 0 | 0
2021-06-20 14:00 | 3.3326 | 0 | N/A | 0 | 0
2021-06-20 14:30 | 3.4286 | 0 | N/A | 0 | 0
2021-06-20 15:00 | 3.7934 | 0 | N/A | 0 | 0
2021-06-20 15:30 | 4.6646 | 0 | N/A | 0 | 0
2021-06-20 16:00 | 5.1309 | 0 | N/A | 0 | 0
2021-06-20 16:30 | 5.7346 | 0 | N/A | 0 | 0
2021-06-20 17:00 | 6.6308 | 0 | N/A | 0 | 0
2021-06-20 17:30 | 7.4294 | 0 | N/A | 0 | 0
2021-06-20 18:00 | 8.3109 | 0 | N/A | 0 | 0
2021-06-20 18:30 | 8.4172 | 0 | N/A | 0 | 0
2021-06-20 19:00 | 8.1281 | 0 | N/A | 0 | 0
2021-06-20 19:30 | 7.7193 | 0 | N/A | 0 | 0
2021-06-20 20:00 | 7.3219 | 0 | N/A | 0 | 0
2021-06-20 20:30 | 6.9504 | 0 | N/A | 0 | 0
2021-06-20 21:00 | 6.7127 | 0 | N/A | 0 | 0
2021-06-20 21:30 | 6.9319 | 0 | N/A | 0 | 0
2021-06-20 22:00 | 6.9881 | 0 | N/A | 0 | 0
2021-06-20 22:30 | 6.5482 | 0 | N/A | 0 | 0
2021-06-20 23:00 | 6.3737 | 0 | N/A | 0 | 0
2021-06-20 23:30 | 6.4253 | 0 | N/A | 0 | 0
2021-06-21 | 6.8723 | 0 | N/A | 0 | 0
2021-06-21 00:30 | 6.2953 | 0 | N/A | 0 | 0
2021-06-21 01:00 | 5.6432 | 0 | N/A | 0 | 0
2021-06-21 01:30 | 5.5221 | 0 | N/A | 0 | 0
2021-06-21 02:00 | 5.1176 | 0 | N/A | 0 | 0
2021-06-21 02:30 | 4.5684 | 0 | N/A | 0 | 0
2021-06-21 03:00 | 4.12 | 0 | N/A | 0 | 0
2021-06-21 03:30 | 3.9883 | 0 | N/A | 0 | 0
2021-06-21 04:00 | 3.7813 | 0 | N/A | 0 | 0
2021-06-21 04:30 | 3.7944 | 0 | N/A | 0 | 0
2021-06-21 05:00 | 3.8097 | 0 | N/A | 0 | 0
2021-06-21 05:30 | 4.1374 | 0 | N/A | 0 | 0
2021-06-21 06:00 | 4.6399 | 0 | N/A | 0 | 0
2021-06-21 06:30 | 5.5957 | 0 | N/A | 0 | 0
2021-06-21 07:00 | 6.5326 | 0 | N/A | 0 | 0
2021-06-21 07:30 | 6.9906 | 0 | N/A | 0 | 0
2021-06-21 08:00 | 8.0433 | 0 | N/A | 0 | 0
2021-06-21 08:30 | 8.3251 | 0 | N/A | 0 | 0
2021-06-21 09:00 | 7.6883 | 0 | N/A | 0 | 0
2021-06-21 09:30 | 6.9402 | 0 | N/A | 0 | 0
2021-06-21 10:00 | 6.0702 | 0 | N/A | 0 | 0
2021-06-21 10:30 | 5.1611 | 0 | N/A | 0 | 0
2021-06-21 11:00 | 4.3002 | 0 | N/A | 0 | 0
2021-06-21 11:30 | 3.8837 | 0 | N/A | 0 | 0
2021-06-21 12:00 | 3.8174 | 0 | N/A | 0 | 0
2021-06-21 12:30 | 3.6567 | 0 | N/A | 0 | 0
2021-06-21 13:00 | 3.3033 | 0 | N/A | 0 | 0
2021-06-21 13:30 | 3.2767 | 0 | N/A | 0 | 0
2021-06-21 14:00 | 3.0705 | 0 | N/A | 0 | 0
2021-06-21 14:30 | 3.2842 | 0 | N/A | 0 | 0
2021-06-21 15:00 | 3.6567 | 0 | N/A | 0 | 0
2021-06-21 15:30 | 4.0035 | 0 | N/A | 0 | 0
2021-06-21 16:00 | 4.3396 | 0 | N/A | 0 | 0
2021-06-21 16:30 | 4.9968 | 0 | N/A | 0 | 0
2021-06-21 17:00 | 6.0832 | 0 | N/A | 0 | 0
2021-06-21 17:30 | 7.4042 | 0 | N/A | 0 | 0
2021-06-21 18:00 | 8.8002 | 0 | N/A | 0 | 0
2021-06-21 18:30 | 9.2 | 0 | N/A | 0 | 0
2021-06-21 19:00 | 8.95 | 0 | N/A | 0 | 0
2021-06-21 19:30 | 8.68 | 0 | N/A | 0 | 0
2021-06-21 20:00 | 8.4134 | 0 | N/A | 0 | 0
2021-06-21 20:30 | 7.9976 | 0 | N/A | 0 | 0
2021-06-21 21:00 | 7.63 | 0 | N/A | 0 | 0
2021-06-21 21:30 | 7.8211 | 0 | N/A | 0 | 0
2021-06-21 22:00 | 7.8347 | 0 | N/A | 0 | 0
2021-06-21 22:30 | 7.0949 | 0 | N/A | 0 | 0
2021-06-21 23:00 | 6.8229 | 0 | N/A | 0 | 0
2021-06-21 23:30 | 6.8654 | 0 | N/A | 0 | 0
2021-06-22 | 7.1571 | 0 | N/A | 0 | 0
2021-06-22 00:30 | 6.579 | 0 | N/A | 0 | 0
2021-06-22 01:00 | 5.8744 | 0 | N/A | 0 | 0
2021-06-22 01:30 | 5.7106 | 0 | N/A | 0 | 0
2021-06-22 02:00 | 5.3316 | 0 | N/A | 0 | 0
2021-06-22 02:30 | 4.6526 | 0 | N/A | 0 | 0
2021-06-22 03:00 | 4.2669 | 0 | N/A | 0 | 0
2021-06-22 03:30 | 4.0624 | 0 | N/A | 0 | 0
2021-06-22 04:00 | 3.9298 | 0 | N/A | 0 | 0
2021-06-22 04:30 | 3.9418 | 0 | N/A | 0 | 0
2021-06-22 05:00 | 3.988 | 0 | N/A | 0 | 0
2021-06-22 05:30 | 4.3115 | 0 | N/A | 0 | 0
2021-06-22 06:00 | 4.8513 | 0 | N/A | 0 | 0
2021-06-22 06:30 | 5.5798 | 0 | N/A | 0 | 0
2021-06-22 07:00 | 6.4859 | 0 | N/A | 0 | 0
2021-06-22 07:30 | 6.9047 | 0 | N/A | 0 | 0
2021-06-22 08:00 | 7.6634 | 0 | N/A | 0 | 0
2021-06-22 08:30 | 7.6641 | 0 | N/A | 0 | 0
2021-06-22 09:00 | 7.2779 | 0 | N/A | 0 | 0
2021-06-22 09:30 | 6.8071 | 0 | N/A | 0 | 0
2021-06-22 10:00 | 6.5338 | 0 | N/A | 0 | 0
2021-06-22 10:30 | 6.1 | 0 | N/A | 0 | 0
2021-06-22 11:00 | 6.0207 | 0 | N/A | 0 | 0
2021-06-22 11:30 | 7.0972 | 0 | N/A | 0 | 0
2021-06-22 12:00 | 6.3433 | 0 | N/A | 0 | 0
2021-06-22 12:30 | 5.6601 | 0 | N/A | 0 | 0
2021-06-22 13:00 | 4.9134 | 0 | N/A | 0 | 0
2021-06-22 13:30 | 5.2471 | 0 | N/A | 0 | 0
2021-06-22 14:00 | 5.3367 | 0 | N/A | 0 | 0
2021-06-22 14:30 | 6.1967 | 0 | N/A | 0 | 0
2021-06-22 15:00 | 5.6834 | 0 | N/A | 0 | 0
2021-06-22 15:30 | 5.8 | 0 | N/A | 0 | 0
2021-06-22 16:00 | 5.926 | 0 | N/A | 0 | 0
2021-06-22 16:30 | 6.4433 | 0 | N/A | 0 | 0
2021-06-22 17:00 | 7.2829 | 0 | N/A | 0 | 0
2021-06-22 17:30 | 8.1769 | 0 | N/A | 0 | 0
2021-06-22 18:00 | 8.8867 | 0 | N/A | 0 | 0
2021-06-22 18:30 | 9.0333 | 0 | N/A | 0 | 0
2021-06-22 19:00 | 8.7733 | 0 | N/A | 0 | 0
2021-06-22 19:30 | 8.4067 | 0 | N/A | 0 | 0
2021-06-22 20:00 | 7.8884 | 0 | N/A | 0 | 0
2021-06-22 20:30 | 7.437 | 0 | N/A | 0 | 0
2021-06-22 21:00 | 6.9866 | 0 | N/A | 0 | 0
2021-06-22 21:30 | 7.157 | 0 | N/A | 0 | 0
2021-06-22 22:00 | 7.2212 | 0 | N/A | 0 | 0
2021-06-22 22:30 | 6.4316 | 0 | N/A | 0 | 0
2021-06-22 23:00 | 6.24 | 0 | N/A | 0 | 0
2021-06-22 23:30 | 6.3297 | 0 | N/A | 0 | 0
2021-06-23 | 6.6436 | 0 | N/A | 0 | 0
2021-06-23 00:30 | 6.0293 | 0 | N/A | 0 | 0
2021-06-23 01:00 | 5.1388 | 0 | N/A | 0 | 0
2021-06-23 01:30 | 4.9771 | 0 | N/A | 0 | 0
2021-06-23 02:00 | 4.5297 | 0 | N/A | 0 | 0
2021-06-23 02:30 | 3.9544 | 0 | N/A | 0 | 0
2021-06-23 03:00 | 3.6345 | 0 | N/A | 0 | 0
2021-06-23 03:30 | 3.408 | 0 | N/A | 0 | 0
2021-06-23 04:00 | 3.1827 | 0 | N/A | 0 | 0
2021-06-23 04:30 | 3.0855 | 0 | N/A | 0 | 0
2021-06-23 05:00 | 3.2087 | 0 | N/A | 0 | 0
2021-06-23 05:30 | 3.4975 | 0 | N/A | 0 | 0
2021-06-23 06:00 | 3.9439 | 0 | N/A | 0 | 0
2021-06-23 06:30 | 4.7166 | 0 | N/A | 0 | 0
2021-06-23 07:00 | 5.3893 | 0 | N/A | 0 | 0
2021-06-23 07:30 | 5.9554 | 0 | N/A | 0 | 0
2021-06-23 08:00 | 6.8973 | 0 | N/A | 0 | 0
2021-06-23 08:30 | 7.2133 | 0 | N/A | 0 | 0
2021-06-23 09:00 | 6.9741 | 0 | N/A | 0 | 0
2021-06-23 09:30 | 6.9645 | 0 | N/A | 0 | 0
2021-06-23 10:00 | 6.9504 | 0 | N/A | 0 | 0
2021-06-23 10:30 | 6.8822 | 0 | N/A | 0 | 0
2021-06-23 11:00 | 6.4827 | 0 | N/A | 0 | 0
2021-06-23 11:30 | 6.1996 | 0 | N/A | 0 | 0
2021-06-23 12:00 | 5.7902 | 0 | N/A | 0 | 0
2021-06-23 12:30 | 5.6017 | 0 | N/A | 0 | 0
2021-06-23 13:00 | 5.9509 | 0 | N/A | 0 | 0
2021-06-23 13:30 | 6.6079 | 0 | N/A | 0 | 0
2021-06-23 14:00 | 6.5981 | 0 | N/A | 0 | 0
2021-06-23 14:30 | 6.9385 | 0 | N/A | 0 | 0
2021-06-23 15:00 | 7.1461 | 0 | N/A | 0 | 0
2021-06-23 15:30 | 7.1872 | 0 | N/A | 0 | 0
2021-06-23 16:00 | 7.1209 | 0 | N/A | 0 | 0
2021-06-23 16:30 | 7.0774 | 0 | N/A | 0 | 0
2021-06-23 17:00 | 7.6167 | 0 | N/A | 0 | 0
2021-06-23 17:30 | 8.1805 | 0 | N/A | 0 | 0
2021-06-23 18:00 | 8.99 | 0 | N/A | 0 | 0
2021-06-23 18:30 | 8.9468 | 0 | N/A | 0 | 0
2021-06-23 19:00 | 8.6133 | 0 | N/A | 0 | 0
2021-06-23 19:30 | 8.1067 | 0 | N/A | 0 | 0
2021-06-23 20:00 | 7.6606 | 0 | N/A | 0 | 0
2021-06-23 20:30 | 7.3486 | 0 | N/A | 0 | 0
2021-06-23 21:00 | 6.9411 | 0 | N/A | 0 | 0
2021-06-23 21:30 | 7.1338 | 0 | N/A | 0 | 0
2021-06-23 22:00 | 7.0224 | 0 | N/A | 0 | 0
2021-06-23 22:30 | 6.3658 | 0 | N/A | 0 | 0
2021-06-23 23:00 | 6.0439 | 0 | N/A | 0 | 0
2021-06-23 23:30 | 6.1065 | 0 | N/A | 0 | 0
2021-06-24 | 6.5714 | 0 | N/A | 0 | 0
2021-06-24 00:30 | 5.7713 | 0 | N/A | 0 | 0
2021-06-24 01:00 | 5.0195 | 0 | N/A | 0 | 0
2021-06-24 01:30 | 5.0082 | 0 | N/A | 0 | 0
2021-06-24 02:00 | 4.5774 | 0 | N/A | 0 | 0
2021-06-24 02:30 | 3.952 | 0 | N/A | 0 | 0
2021-06-24 03:00 | 3.5087 | 0 | N/A | 0 | 0
2021-06-24 03:30 | 3.3037 | 0 | N/A | 0 | 0
2021-06-24 04:00 | 3.0989 | 0 | N/A | 0 | 0
2021-06-24 04:30 | 3.1287 | 0 | N/A | 0 | 0
2021-06-24 05:00 | 3.1364 | 0 | N/A | 0 | 0
2021-06-24 05:30 | 3.527 | 0 | N/A | 0 | 0
2021-06-24 06:00 | 4.0473 | 0 | N/A | 0 | 0
2021-06-24 06:30 | 4.7919 | 0 | N/A | 0 | 0
2021-06-24 07:00 | 5.5148 | 0 | N/A | 0 | 0
2021-06-24 07:30 | 6.2334 | 0 | N/A | 0 | 0
2021-06-24 08:00 | 7.1217 | 0 | N/A | 0 | 0
2021-06-24 08:30 | 7.6557 | 0 | N/A | 0 | 0
2021-06-24 09:00 | 7.3883 | 0 | N/A | 0 | 0
2021-06-24 09:30 | 7.1113 | 0 | N/A | 0 | 0
2021-06-24 10:00 | 6.5805 | 0 | N/A | 0 | 0
2021-06-24 10:30 | 5.9234 | 0 | N/A | 0 | 0
2021-06-24 11:00 | 5.2839 | 0 | N/A | 0 | 0
2021-06-24 11:30 | 5.3608 | 0 | N/A | 0 | 0
2021-06-24 12:00 | 4.86 | 0 | N/A | 0 | 0
2021-06-24 12:30 | 5.0067 | 0 | N/A | 0 | 0
2021-06-24 13:00 | 4.827 | 0 | N/A | 0 | 0
2021-06-24 13:30 | 4.3667 | 0 | N/A | 0 | 0
2021-06-24 14:00 | 4.0134 | 0 | N/A | 0 | 0
2021-06-24 14:30 | 5.2903 | 0 | N/A | 0 | 0
2021-06-24 15:00 | 5.3001 | 0 | N/A | 0 | 0
2021-06-24 15:30 | 5.9667 | 0 | N/A | 0 | 0
2021-06-24 16:00 | 5.997 | 0 | N/A | 0 | 0
2021-06-24 16:30 | 6.4902 | 0 | N/A | 0 | 0
2021-06-24 17:00 | 7.1746 | 0 | N/A | 0 | 0
2021-06-24 17:30 | 7.8973 | 0 | N/A | 0 | 0
2021-06-24 18:00 | 8.62 | 0 | N/A | 0 | 0
2021-06-24 18:30 | 8.7167 | 0 | N/A | 0 | 0
2021-06-24 19:00 | 8.5801 | 0 | N/A | 0 | 0
2021-06-24 19:30 | 8.3467 | 0 | N/A | 0 | 0
2021-06-24 20:00 | 8.0436 | 0 | N/A | 0 | 0
2021-06-24 20:30 | 7.7439 | 0 | N/A | 0 | 0
2021-06-24 21:00 | 7.3582 | 0 | N/A | 0 | 0
2021-06-24 21:30 | 7.244 | 0 | N/A | 0 | 0
2021-06-24 22:00 | 7.1871 | 0 | N/A | 0 | 0
2021-06-24 22:30 | 6.4895 | 0 | N/A | 0 | 0
2021-06-24 23:00 | 6.3945 | 0 | N/A | 0 | 0
2021-06-24 23:30 | 6.4821 | 0 | N/A | 0 | 0
2021-06-25 | 6.7365 | 0 | N/A | 0 | 0
2021-06-25 00:30 | 5.9683 | 0 | N/A | 0 | 0
2021-06-25 01:00 | 5.07 | 0 | N/A | 0 | 0
2021-06-25 01:30 | 4.9135 | 0 | N/A | 0 | 0
2021-06-25 02:00 | 4.6262 | 0 | N/A | 0 | 0
2021-06-25 02:30 | 4.0472 | 0 | N/A | 0 | 0
2021-06-25 03:00 | 3.7512 | 0 | N/A | 0 | 0
2021-06-25 03:30 | 3.47 | 0 | N/A | 0 | 0
2021-06-25 04:00 | 3.3056 | 0 | N/A | 0 | 0
2021-06-25 04:30 | 3.2756 | 0 | N/A | 0 | 0
2021-06-25 05:00 | 3.3284 | 0 | N/A | 0 | 0
2021-06-25 05:30 | 3.7007 | 0 | N/A | 0 | 0
2021-06-25 06:00 | 4.0912 | 0 | N/A | 0 | 0
2021-06-25 06:30 | 4.8126 | 0 | N/A | 0 | 0
2021-06-25 07:00 | 5.5459 | 0 | N/A | 0 | 0
2021-06-25 07:30 | 5.7904 | 0 | N/A | 0 | 0
2021-06-25 08:00 | 6.5577 | 0 | N/A | 0 | 0
2021-06-25 08:30 | 6.95 | 0 | N/A | 0 | 0
2021-06-25 09:00 | 6.6637 | 0 | N/A | 0 | 0
2021-06-25 09:30 | 6.5208 | 0 | N/A | 0 | 0
2021-06-25 10:00 | 6.4105 | 0 | N/A | 0 | 0
2021-06-25 10:30 | 6.1341 | 0 | N/A | 0 | 0
2021-06-25 11:00 | 6.1571 | 0 | N/A | 0 | 0
2021-06-25 11:30 | 5.7639 | 0 | N/A | 0 | 0
2021-06-25 12:00 | 5.55 | 0 | N/A | 0 | 0
2021-06-25 12:30 | 5.6751 | 0 | N/A | 0 | 0
2021-06-25 13:00 | 5.5872 | 0 | N/A | 0 | 0
2021-06-25 13:30 | 5.4933 | 0 | N/A | 0 | 0
2021-06-25 14:00 | 5.2235 | 0 | N/A | 0 | 0
2021-06-25 14:30 | 4.5124 | 0 | N/A | 0 | 0
2021-06-25 15:00 | 4.7474 | 0 | N/A | 0 | 0
2021-06-25 15:30 | 4.8393 | 0 | N/A | 0 | 0
2021-06-25 16:00 | 5.3666 | 0 | N/A | 0 | 0
2021-06-25 16:30 | 5.2543 | 0 | N/A | 0 | 0
2021-06-25 17:00 | 5.9521 | 0 | N/A | 0 | 0
2021-06-25 17:30 | 7.0228 | 0 | N/A | 0 | 0
2021-06-25 18:00 | 7.8934 | 0 | N/A | 0 | 0
2021-06-25 18:30 | 8.0768 | 0 | N/A | 0 | 0
2021-06-25 19:00 | 7.8672 | 0 | N/A | 0 | 0
2021-06-25 19:30 | 7.641 | 0 | N/A | 0 | 0
2021-06-25 20:00 | 7.458 | 0 | N/A | 0 | 0
2021-06-25 20:30 | 7.1289 | 0 | N/A | 0 | 0
2021-06-25 21:00 | 6.7717 | 0 | N/A | 0 | 0
2021-06-25 21:30 | 7.0555 | 0 | N/A | 0 | 0
2021-06-25 22:00 | 7.1797 | 0 | N/A | 0 | 0
2021-06-25 22:30 | 6.6522 | 0 | N/A | 0 | 0
2021-06-25 23:00 | 6.4685 | 0 | N/A | 0 | 0
2021-06-25 23:30 | 6.6517 | 0 | N/A | 0 | 0
2021-06-26 | 6.9263 | 0 | N/A | 0 | 0
2021-06-26 00:30 | 6.1543 | 0 | N/A | 0 | 0
2021-06-26 01:00 | 5.2387 | 0 | N/A | 0 | 0
2021-06-26 01:30 | 5.0334 | 0 | N/A | 0 | 0
2021-06-26 02:00 | 4.6454 | 0 | N/A | 0 | 0
2021-06-26 02:30 | 4.0433 | 0 | N/A | 0 | 0
2021-06-26 03:00 | 3.6615 | 0 | N/A | 0 | 0
2021-06-26 03:30 | 3.4115 | 0 | N/A | 0 | 0
2021-06-26 04:00 | 3.2701 | 0 | N/A | 0 | 0
2021-06-26 04:30 | 3.2088 | 0 | N/A | 0 | 0
2021-06-26 05:00 | 3.2129 | 0 | N/A | 0 | 0
2021-06-26 05:30 | 3.3546 | 0 | N/A | 0 | 0
2021-06-26 06:00 | 3.5475 | 0 | N/A | 0 | 0
2021-06-26 06:30 | 3.8821 | 0 | N/A | 0 | 0
2021-06-26 07:00 | 4.1418 | 0 | N/A | 0 | 0
2021-06-26 07:30 | 4.2382 | 0 | N/A | 0 | 0
2021-06-26 08:00 | 4.8013 | 0 | N/A | 0 | 0
2021-06-26 08:30 | 5.5487 | 0 | N/A | 0 | 0
2021-06-26 09:00 | 5.6048 | 0 | N/A | 0 | 0
2021-06-26 09:30 | 5.5602 | 0 | N/A | 0 | 0
2021-06-26 10:00 | 5.6283 | 0 | N/A | 0 | 0
2021-06-26 10:30 | 5.6067 | 0 | N/A | 0 | 0
2021-06-26 11:00 | 5.0287 | 0 | N/A | 0 | 0
2021-06-26 11:30 | 4.8289 | 0 | N/A | 0 | 0
2021-06-26 12:00 | 4.389 | 0 | N/A | 0 | 0
2021-06-26 12:30 | 3.6528 | 0 | N/A | 0 | 0
2021-06-26 13:00 | 3.8817 | 0 | N/A | 0 | 0
2021-06-26 13:30 | 3.9738 | 0 | N/A | 0 | 0
2021-06-26 14:00 | 4.1644 | 0 | N/A | 0 | 0
2021-06-26 14:30 | 4.3443 | 0 | N/A | 0 | 0
2021-06-26 15:00 | 5.0674 | 0 | N/A | 0 | 0
2021-06-26 15:30 | 5.3514 | 0 | N/A | 0 | 0
2021-06-26 16:00 | 5.3972 | 0 | N/A | 0 | 0
2021-06-26 16:30 | 5.961 | 0 | N/A | 0 | 0
2021-06-26 17:00 | 6.5837 | 0 | N/A | 0 | 0
2021-06-26 17:30 | 7.384 | 0 | N/A | 0 | 0
2021-06-26 18:00 | 8.0874 | 0 | N/A | 0 | 0
2021-06-26 18:30 | 8.1142 | 0 | N/A | 0 | 0
2021-06-26 19:00 | 7.9016 | 0 | N/A | 0 | 0
2021-06-26 19:30 | 7.5931 | 0 | N/A | 0 | 0
2021-06-26 20:00 | 7.1674 | 0 | N/A | 0 | 0
2021-06-26 20:30 | 6.8765 | 0 | N/A | 0 | 0
2021-06-26 21:00 | 6.5355 | 0 | N/A | 0 | 0
2021-06-26 21:30 | 6.9417 | 0 | N/A | 0 | 0
2021-06-26 22:00 | 7.0274 | 0 | N/A | 0 | 0
2021-06-26 22:30 | 6.5968 | 0 | N/A | 0 | 0
2021-06-26 23:00 | 6.5322 | 0 | N/A | 0 | 0
2021-06-26 23:30 | 6.6597 | 0 | N/A | 0 | 0
2021-06-27 | 7.0244 | 0 | N/A | 0 | 0
2021-06-27 00:30 | 6.3062 | 0 | N/A | 0 | 0
2021-06-27 01:00 | 5.5238 | 0 | N/A | 0 | 0
2021-06-27 01:30 | 5.3571 | 0 | N/A | 0 | 0
2021-06-27 02:00 | 4.9315 | 0 | N/A | 0 | 0
2021-06-27 02:30 | 4.2813 | 0 | N/A | 0 | 0
2021-06-27 03:00 | 3.8846 | 0 | N/A | 0 | 0
2021-06-27 03:30 | 3.5913 | 0 | N/A | 0 | 0
2021-06-27 04:00 | 3.3595 | 0 | N/A | 0 | 0
2021-06-27 04:30 | 3.2175 | 0 | N/A | 0 | 0
2021-06-27 05:00 | 3.1267 | 0 | N/A | 0 | 0
2021-06-27 05:30 | 3.2087 | 0 | N/A | 0 | 0
2021-06-27 06:00 | 3.329 | 0 | N/A | 0 | 0
2021-06-27 06:30 | 3.623 | 0 | N/A | 0 | 0
2021-06-27 07:00 | 3.8311 | 0 | N/A | 0 | 0
2021-06-27 07:30 | 3.8309 | 0 | N/A | 0 | 0
2021-06-27 08:00 | 4.2848 | 0 | N/A | 0 | 0
2021-06-27 08:30 | 4.8797 | 0 | N/A | 0 | 0
2021-06-27 09:00 | 5.0516 | 0 | N/A | 0 | 0
2021-06-27 09:30 | 4.8262 | 0 | N/A | 0 | 0
2021-06-27 10:00 | 4.8841 | 0 | N/A | 0 | 0
2021-06-27 10:30 | 5.0119 | 0 | N/A | 0 | 0
2021-06-27 11:00 | 4.5723 | 0 | N/A | 0 | 0
2021-06-27 11:30 | 3.8228 | 0 | N/A | 0 | 0
2021-06-27 12:00 | 3.1165 | 0 | N/A | 0 | 0
2021-06-27 12:30 | 3.4659 | 0 | N/A | 0 | 0
2021-06-27 13:00 | 2.7778 | 0 | N/A | 0 | 0
2021-06-27 13:30 | 2.6101 | 0 | N/A | 0 | 0
2021-06-27 14:00 | 2.9404 | 0 | N/A | 0 | 0
2021-06-27 14:30 | 3.2584 | 0 | N/A | 0 | 0
2021-06-27 15:00 | 3.0862 | 0 | N/A | 0 | 0
2021-06-27 15:30 | 3.2732 | 0 | N/A | 0 | 0
2021-06-27 16:00 | 3.8482 | 0 | N/A | 0 | 0
2021-06-27 16:30 | 4.6373 | 0 | N/A | 0 | 0
2021-06-27 17:00 | 5.6386 | 0 | N/A | 0 | 0
2021-06-27 17:30 | 6.8588 | 0 | N/A | 0 | 0
2021-06-27 18:00 | 7.6985 | 0 | N/A | 0 | 0
2021-06-27 18:30 | 8.1245 | 0 | N/A | 0 | 0
2021-06-27 19:00 | 7.9425 | 0 | N/A | 0 | 0
2021-06-27 19:30 | 7.6797 | 0 | N/A | 0 | 0
2021-06-27 20:00 | 7.3247 | 0 | N/A | 0 | 0
2021-06-27 20:30 | 6.9086 | 0 | N/A | 0 | 0
2021-06-27 21:00 | 6.5296 | 0 | N/A | 0 | 0
2021-06-27 21:30 | 6.9351 | 0 | N/A | 0 | 0
2021-06-27 22:00 | 7.0393 | 0 | N/A | 0 | 0
2021-06-27 22:30 | 6.5966 | 0 | N/A | 0 | 0
2021-06-27 23:00 | 6.5436 | 0 | N/A | 0 | 0
2021-06-27 23:30 | 6.6253 | 0 | N/A | 0 | 0
2021-06-28 | 6.9595 | 0 | N/A | 0 | 0
2021-06-28 00:30 | 6.3425 | 0 | N/A | 0 | 0
2021-06-28 01:00 | 5.6242 | 0 | N/A | 0 | 0
2021-06-28 01:30 | 5.5637 | 0 | N/A | 0 | 0
2021-06-28 02:00 | 5.1905 | 0 | N/A | 0 | 0
2021-06-28 02:30 | 4.6007 | 0 | N/A | 0 | 0
2021-06-28 03:00 | 4.2444 | 0 | N/A | 0 | 0
2021-06-28 03:30 | 4.049 | 0 | N/A | 0 | 0
2021-06-28 04:00 | 3.8063 | 0 | N/A | 0 | 0
2021-06-28 04:30 | 3.7205 | 0 | N/A | 0 | 0
2021-06-28 05:00 | 3.7917 | 0 | N/A | 0 | 0
2021-06-28 05:30 | 4.1152 | 0 | N/A | 0 | 0
2021-06-28 06:00 | 4.5912 | 0 | N/A | 0 | 0
2021-06-28 06:30 | 5.3988 | 0 | N/A | 0 | 0
2021-06-28 07:00 | 6.053 | 0 | N/A | 0 | 0
2021-06-28 07:30 | 6.2722 | 0 | N/A | 0 | 0
2021-06-28 08:00 | 7.2734 | 0 | N/A | 0 | 0
2021-06-28 08:30 | 8.0753 | 0 | N/A | 0 | 0
2021-06-28 09:00 | 7.854 | 0 | N/A | 0 | 0
2021-06-28 09:30 | 7.3795 | 0 | N/A | 0 | 0
2021-06-28 10:00 | 6.682 | 0 | N/A | 0 | 0
2021-06-28 10:30 | 6.1917 | 0 | N/A | 0 | 0
2021-06-28 11:00 | 6.2282 | 0 | N/A | 0 | 0
2021-06-28 11:30 | 5.8449 | 0 | N/A | 0 | 0
2021-06-28 12:00 | 5.4768 | 0 | N/A | 0 | 0
2021-06-28 12:30 | 4.635 | 0 | N/A | 0 | 0
2021-06-28 13:00 | 4.3472 | 0 | N/A | 0 | 0
2021-06-28 13:30 | 4.8667 | 0 | N/A | 0 | 0
2021-06-28 14:00 | 5.5733 | 0 | N/A | 0 | 0
2021-06-28 14:30 | 5.4433 | 0 | N/A | 0 | 0
2021-06-28 15:00 | 5.42 | 0 | N/A | 0 | 0
2021-06-28 15:30 | 5.0867 | 0 | N/A | 0 | 0
2021-06-28 16:00 | 5.3776 | 0 | N/A | 0 | 0
2021-06-28 16:30 | 5.5943 | 0 | N/A | 0 | 0
2021-06-28 17:00 | 6.2426 | 0 | N/A | 0 | 0
2021-06-28 17:30 | 7.4749 | 0 | N/A | 0 | 0
2021-06-28 18:00 | 8.6867 | 0 | N/A | 0 | 0
2021-06-28 18:30 | 9.0733 | 0 | N/A | 0 | 0
2021-06-28 19:00 | 8.7734 | 0 | N/A | 0 | 0
2021-06-28 19:30 | 8.4335 | 0 | N/A | 0 | 0
2021-06-28 20:00 | 8.1837 | 0 | N/A | 0 | 0
2021-06-28 20:30 | 7.8773 | 0 | N/A | 0 | 0
2021-06-28 21:00 | 7.4954 | 0 | N/A | 0 | 0
2021-06-28 21:30 | 7.7242 | 0 | N/A | 0 | 0
2021-06-28 22:00 | 7.8079 | 0 | N/A | 0 | 0
2021-06-28 22:30 | 7.1894 | 0 | N/A | 0 | 0
2021-06-28 23:00 | 6.9915 | 0 | N/A | 0 | 0
2021-06-28 23:30 | 7.0211 | 0 | N/A | 0 | 0
2021-06-29 | 7.1857 | 0 | N/A | 0 | 0
2021-06-29 00:30 | 6.6532 | 0 | N/A | 0 | 0
2021-06-29 01:00 | 5.7647 | 0 | N/A | 0 | 0
2021-06-29 01:30 | 5.6655 | 0 | N/A | 0 | 0
2021-06-29 02:00 | 5.285 | 0 | N/A | 0 | 0
2021-06-29 02:30 | 4.7075 | 0 | N/A | 0 | 0
2021-06-29 03:00 | 4.2969 | 0 | N/A | 0 | 0
2021-06-29 03:30 | 4.019 | 0 | N/A | 0 | 0
2021-06-29 04:00 | 3.8339 | 0 | N/A | 0 | 0
2021-06-29 04:30 | 3.7143 | 0 | N/A | 0 | 0
2021-06-29 05:00 | 3.8017 | 0 | N/A | 0 | 0
2021-06-29 05:30 | 4.1054 | 0 | N/A | 0 | 0
2021-06-29 06:00 | 4.6421 | 0 | N/A | 0 | 0
2021-06-29 06:30 | 5.4246 | 0 | N/A | 0 | 0
2021-06-29 07:00 | 5.9578 | 0 | N/A | 0 | 0
2021-06-29 07:30 | 6.0888 | 0 | N/A | 0 | 0
2021-06-29 08:00 | 6.6883 | 0 | N/A | 0 | 0
2021-06-29 08:30 | 7.2767 | 0 | N/A | 0 | 0
2021-06-29 09:00 | 7.4033 | 0 | N/A | 0 | 0
2021-06-29 09:30 | 7.08 | 0 | N/A | 0 | 0
2021-06-29 10:00 | 6.5771 | 0 | N/A | 0 | 0
2021-06-29 10:30 | 5.9667 | 0 | N/A | 0 | 0
2021-06-29 11:00 | 5.6933 | 0 | N/A | 0 | 0
2021-06-29 11:30 | 4.8367 | 0 | N/A | 0 | 0
2021-06-29 12:00 | 4.7233 | 0 | N/A | 0 | 0
2021-06-29 12:30 | 4.7934 | 0 | N/A | 0 | 0
2021-06-29 13:00 | 4.4838 | 0 | N/A | 0 | 0
2021-06-29 13:30 | 3.8581 | 0 | N/A | 0 | 0
2021-06-29 14:00 | 3.2663 | 0 | N/A | 0 | 0
2021-06-29 14:30 | 3.5248 | 0 | N/A | 0 | 0
2021-06-29 15:00 | 4.7629 | 0 | N/A | 0 | 0
2021-06-29 15:30 | 5.1389 | 0 | N/A | 0 | 0
2021-06-29 16:00 | 5.234 | 0 | N/A | 0 | 0
2021-06-29 16:30 | 5.5823 | 0 | N/A | 0 | 0
2021-06-29 17:00 | 6.3169 | 0 | N/A | 0 | 0
2021-06-29 17:30 | 7.3338 | 0 | N/A | 0 | 0
2021-06-29 18:00 | 8.3473 | 0 | N/A | 0 | 0
2021-06-29 18:30 | 8.7233 | 0 | N/A | 0 | 0
2021-06-29 19:00 | 8.6334 | 0 | N/A | 0 | 0
2021-06-29 19:30 | 8.2539 | 0 | N/A | 0 | 0
2021-06-29 20:00 | 7.8308 | 0 | N/A | 0 | 0
2021-06-29 20:30 | 7.4659 | 0 | N/A | 0 | 0
2021-06-29 21:00 | 7.0874 | 0 | N/A | 0 | 0
2021-06-29 21:30 | 7.2805 | 0 | N/A | 0 | 0
2021-06-29 22:00 | 7.2222 | 0 | N/A | 0 | 0
2021-06-29 22:30 | 6.6588 | 0 | N/A | 0 | 0
2021-06-29 23:00 | 6.4386 | 0 | N/A | 0 | 0
2021-06-29 23:30 | 6.4715 | 0 | N/A | 0 | 0
2021-06-30 | 6.7754 | 0 | N/A | 0 | 0
2021-06-30 00:30 | 6.0529 | 0 | N/A | 0 | 0
2021-06-30 01:00 | 5.308 | 0 | N/A | 0 | 0
2021-06-30 01:30 | 5.1281 | 0 | N/A | 0 | 0
2021-06-30 02:00 | 4.9018 | 0 | N/A | 0 | 0
2021-06-30 02:30 | 4.2049 | 0 | N/A | 0 | 0
2021-06-30 03:00 | 3.8265 | 0 | N/A | 0 | 0
2021-06-30 03:30 | 3.6098 | 0 | N/A | 0 | 0
2021-06-30 04:00 | 3.3852 | 0 | N/A | 0 | 0
2021-06-30 04:30 | 3.3338 | 0 | N/A | 0 | 0
2021-06-30 05:00 | 3.4357 | 0 | N/A | 0 | 0
2021-06-30 05:30 | 3.7772 | 0 | N/A | 0 | 0
2021-06-30 06:00 | 4.3201 | 0 | N/A | 0 | 0
2021-06-30 06:30 | 4.9427 | 0 | N/A | 0 | 0
2021-06-30 07:00 | 5.4996 | 0 | N/A | 0 | 0
2021-06-30 07:30 | 5.6446 | 0 | N/A | 0 | 0
2021-06-30 08:00 | 6.2965 | 0 | N/A | 0 | 0
2021-06-30 08:30 | 6.6669 | 0 | N/A | 0 | 0
2021-06-30 09:00 | 6.2302 | 0 | N/A | 0 | 0
2021-06-30 09:30 | 5.5767 | 0 | N/A | 0 | 0
2021-06-30 10:00 | 4.6551 | 0 | N/A | 0 | 0
2021-06-30 10:30 | 4.0548 | 0 | N/A | 0 | 0
2021-06-30 11:00 | 3.4775 | 0 | N/A | 0 | 0
2021-06-30 11:30 | 3.3563 | 0 | N/A | 0 | 0
2021-06-30 12:00 | 3.9705 | 0 | N/A | 0 | 0
2021-06-30 12:30 | 4.3997 | 0 | N/A | 0 | 0
2021-06-30 13:00 | 4.2309 | 0 | N/A | 0 | 0
2021-06-30 13:30 | 4.6875 | 0 | N/A | 0 | 0
2021-06-30 14:00 | 4.7083 | 0 | N/A | 0 | 0
2021-06-30 14:30 | 4.5307 | 0 | N/A | 0 | 0
2021-06-30 15:00 | 4.0177 | 0 | N/A | 0 | 0
2021-06-30 15:30 | 3.7869 | 0 | N/A | 0 | 0
2021-06-30 16:00 | 4.1103 | 0 | N/A | 0 | 0
2021-06-30 16:30 | 4.6933 | 0 | N/A | 0 | 0
2021-06-30 17:00 | 5.6907 | 0 | N/A | 0 | 0
2021-06-30 17:30 | 6.744 | 0 | N/A | 0 | 0
2021-06-30 18:00 | 7.7554 | 0 | N/A | 0 | 0
2021-06-30 18:30 | 8.1173 | 0 | N/A | 0 | 0
2021-06-30 19:00 | 8.0706 | 0 | N/A | 0 | 0
2021-06-30 19:30 | 7.7521 | 0 | N/A | 0 | 0
2021-06-30 20:00 | 7.549 | 0 | N/A | 0 | 0
2021-06-30 20:30 | 7.1808 | 0 | N/A | 0 | 0
2021-06-30 21:00 | 6.8042 | 0 | N/A | 0 | 0
2021-06-30 21:30 | 6.9795 | 0 | N/A | 0 | 0
2021-06-30 22:00 | 7.0048 | 0 | N/A | 0 | 0
2021-06-30 22:30 | 6.371 | 0 | N/A | 0 | 0
2021-06-30 23:00 | 6.2045 | 0 | N/A | 0 | 0
2021-06-30 23:30 | 6.3574 | 0 | N/A | 0 | 0
2021-07-01 | 6.7098 | 0 | N/A | 0 | 0
2021-07-01 00:30 | 5.988 | 0 | N/A | 0 | 0
2021-07-01 01:00 | 5.1329 | 0 | N/A | 0 | 0
2021-07-01 01:30 | 4.9589 | 0 | N/A | 0 | 0
2021-07-01 02:00 | 4.6395 | 0 | N/A | 0 | 0
2021-07-01 02:30 | 4.0401 | 0 | N/A | 0 | 0
2021-07-01 03:00 | 3.588 | 0 | N/A | 0 | 0
2021-07-01 03:30 | 3.4109 | 0 | N/A | 0 | 0
2021-07-01 04:00 | 3.2028 | 0 | N/A | 0 | 0
2021-07-01 04:30 | 3.12 | 0 | N/A | 0 | 0
2021-07-01 05:00 | 3.2387 | 0 | N/A | 0 | 0
2021-07-01 05:30 | 3.499 | 0 | N/A | 0 | 0
2021-07-01 06:00 | 3.9923 | 0 | N/A | 0 | 0
2021-07-01 06:30 | 4.5174 | 0 | N/A | 0 | 0
2021-07-01 07:00 | 5.0929 | 0 | N/A | 0 | 0
2021-07-01 07:30 | 5.3287 | 0 | N/A | 0 | 0
2021-07-01 08:00 | 6.0311 | 0 | N/A | 0 | 0
2021-07-01 08:30 | 6.62 | 0 | N/A | 0 | 0
2021-07-01 09:00 | 6.2033 | 0 | N/A | 0 | 0
2021-07-01 09:30 | 5.8167 | 0 | N/A | 0 | 0
2021-07-01 10:00 | 5.33 | 0 | N/A | 0 | 0
2021-07-01 10:30 | 4.6867 | 0 | N/A | 0 | 0
2021-07-01 11:00 | 4.1368 | 0 | N/A | 0 | 0
2021-07-01 11:30 | 4.3033 | 0 | N/A | 0 | 0
2021-07-01 12:00 | 3.98 | 0 | N/A | 0 | 0
2021-07-01 12:30 | 4.0936 | 0 | N/A | 0 | 0
2021-07-01 13:00 | 4.1378 | 0 | N/A | 0 | 0
2021-07-01 13:30 | 3.7777 | 0 | N/A | 0 | 0
2021-07-01 14:00 | 3.7469 | 0 | N/A | 0 | 0
2021-07-01 14:30 | 3.6205 | 0 | N/A | 0 | 0
2021-07-01 15:00 | 3.754 | 0 | N/A | 0 | 0
2021-07-01 15:30 | 4.6775 | 0 | N/A | 0 | 0
2021-07-01 16:00 | 4.9685 | 0 | N/A | 0 | 0
2021-07-01 16:30 | 5.2922 | 0 | N/A | 0 | 0
2021-07-01 17:00 | 5.9584 | 0 | N/A | 0 | 0
2021-07-01 17:30 | 6.8927 | 0 | N/A | 0 | 0
2021-07-01 18:00 | 7.8644 | 0 | N/A | 0 | 0
2021-07-01 18:30 | 7.9707 | 0 | N/A | 0 | 0
2021-07-01 19:00 | 7.7943 | 0 | N/A | 0 | 0
2021-07-01 19:30 | 7.5852 | 0 | N/A | 0 | 0
2021-07-01 20:00 | 7.1962 | 0 | N/A | 0 | 0
2021-07-01 20:30 | 6.9221 | 0 | N/A | 0 | 0
2021-07-01 21:00 | 6.5317 | 0 | N/A | 0 | 0
2021-07-01 21:30 | 6.7245 | 0 | N/A | 0 | 0
2021-07-01 22:00 | 6.7797 | 0 | N/A | 0 | 0
2021-07-01 22:30 | 6.2796 | 0 | N/A | 0 | 0
2021-07-01 23:00 | 6.193 | 0 | N/A | 0 | 0
2021-07-01 23:30 | 6.2446 | 0 | N/A | 0 | 0
2021-07-02 | 6.5232 | 0 | N/A | 0 | 0
2021-07-02 00:30 | 5.5799 | 0 | N/A | 0 | 0
2021-07-02 01:00 | 4.7742 | 0 | N/A | 0 | 0
2021-07-02 01:30 | 4.6455 | 0 | N/A | 0 | 0
2021-07-02 02:00 | 4.3633 | 0 | N/A | 0 | 0
2021-07-02 02:30 | 3.8111 | 0 | N/A | 0 | 0
2021-07-02 03:00 | 3.4659 | 0 | N/A | 0 | 0
2021-07-02 03:30 | 3.2665 | 0 | N/A | 0 | 0
2021-07-02 04:00 | 3.0396 | 0 | N/A | 0 | 0
2021-07-02 04:30 | 3.0178 | 0 | N/A | 0 | 0
2021-07-02 05:00 | 3.0756 | 0 | N/A | 0 | 0
2021-07-02 05:30 | 3.3159 | 0 | N/A | 0 | 0
2021-07-02 06:00 | 3.7338 | 0 | N/A | 0 | 0
2021-07-02 06:30 | 4.3561 | 0 | N/A | 0 | 0
2021-07-02 07:00 | 4.7567 | 0 | N/A | 0 | 0
2021-07-02 07:30 | 5.0418 | 0 | N/A | 0 | 0
2021-07-02 08:00 | 5.6874 | 0 | N/A | 0 | 0
2021-07-02 08:30 | 6.3134 | 0 | N/A | 0 | 0
2021-07-02 09:00 | 6.3301 | 0 | N/A | 0 | 0
2021-07-02 09:30 | 6.2106 | 0 | N/A | 0 | 0
2021-07-02 10:00 | 5.9236 | 0 | N/A | 0 | 0
2021-07-02 10:30 | 5.47 | 0 | N/A | 0 | 0
2021-07-02 11:00 | 4.4901 | 0 | N/A | 0 | 0
2021-07-02 11:30 | 3.9638 | 0 | N/A | 0 | 0
2021-07-02 12:00 | 3.5702 | 0 | N/A | 0 | 0
2021-07-02 12:30 | 3.9267 | 0 | N/A | 0 | 0
2021-07-02 13:00 | 2.9313 | 0 | N/A | 0 | 0
2021-07-02 13:30 | 2.6661 | 0 | N/A | 0 | 0
2021-07-02 14:00 | 3.575 | 0 | N/A | 0 | 0
2021-07-02 14:30 | 3.862 | 0 | N/A | 0 | 0
2021-07-02 15:00 | 4.2554 | 0 | N/A | 0 | 0
2021-07-02 15:30 | 4.8402 | 0 | N/A | 0 | 0
2021-07-02 16:00 | 5.8313 | 0 | N/A | 0 | 0
2021-07-02 16:30 | 6.3164 | 0 | N/A | 0 | 0
2021-07-02 17:00 | 7.0292 | 0 | N/A | 0 | 0
2021-07-02 17:30 | 7.6583 | 0 | N/A | 0 | 0
2021-07-02 18:00 | 8.1705 | 0 | N/A | 0 | 0
2021-07-02 18:30 | 8.2035 | 0 | N/A | 0 | 0
2021-07-02 19:00 | 8.0702 | 0 | N/A | 0 | 0
2021-07-02 19:30 | 7.8303 | 0 | N/A | 0 | 0
2021-07-02 20:00 | 7.5439 | 0 | N/A | 0 | 0
2021-07-02 20:30 | 7.2551 | 0 | N/A | 0 | 0
2021-07-02 21:00 | 6.9397 | 0 | N/A | 0 | 0
2021-07-02 21:30 | 7.4068 | 0 | N/A | 0 | 0
2021-07-02 22:00 | 7.4255 | 0 | N/A | 0 | 0
2021-07-02 22:30 | 6.9573 | 0 | N/A | 0 | 0
2021-07-02 23:00 | 6.8509 | 0 | N/A | 0 | 0
2021-07-02 23:30 | 6.8611 | 0 | N/A | 0 | 0
2021-07-03 | 7.2519 | 0 | N/A | 0 | 0
2021-07-03 00:30 | 6.544 | 0 | N/A | 0 | 0
2021-07-03 01:00 | 5.8503 | 0 | N/A | 0 | 0
2021-07-03 01:30 | 5.6163 | 0 | N/A | 0 | 0
2021-07-03 02:00 | 5.1049 | 0 | N/A | 0 | 0
2021-07-03 02:30 | 4.4596 | 0 | N/A | 0 | 0
2021-07-03 03:00 | 4.1577 | 0 | N/A | 0 | 0
2021-07-03 03:30 | 4.0407 | 0 | N/A | 0 | 0
2021-07-03 04:00 | 3.7768 | 0 | N/A | 0 | 0
2021-07-03 04:30 | 3.7252 | 0 | N/A | 0 | 0
2021-07-03 05:00 | 3.7055 | 0 | N/A | 0 | 0
2021-07-03 05:30 | 3.7576 | 0 | N/A | 0 | 0
2021-07-03 06:00 | 4.0184 | 0 | N/A | 0 | 0
2021-07-03 06:30 | 4.3741 | 0 | N/A | 0 | 0
2021-07-03 07:00 | 4.6054 | 0 | N/A | 0 | 0
2021-07-03 07:30 | 4.708 | 0 | N/A | 0 | 0
2021-07-03 08:00 | 5.3903 | 0 | N/A | 0 | 0
2021-07-03 08:30 | 6.2714 | 0 | N/A | 0 | 0
2021-07-03 09:00 | 6.6074 | 0 | N/A | 0 | 0
2021-07-03 09:30 | 6.6285 | 0 | N/A | 0 | 0
2021-07-03 10:00 | 6.7661 | 0 | N/A | 0 | 0
2021-07-03 10:30 | 6.8809 | 0 | N/A | 0 | 0
2021-07-03 11:00 | 6.8508 | 0 | N/A | 0 | 0
2021-07-03 11:30 | 6.5809 | 0 | N/A | 0 | 0
2021-07-03 12:00 | 6.2474 | 0 | N/A | 0 | 0
2021-07-03 12:30 | 5.9242 | 0 | N/A | 0 | 0
2021-07-03 13:00 | 6.1102 | 0 | N/A | 0 | 0
2021-07-03 13:30 | 6.3358 | 0 | N/A | 0 | 0
2021-07-03 14:00 | 6.4112 | 0 | N/A | 0 | 0
2021-07-03 14:30 | 6.3731 | 0 | N/A | 0 | 0
2021-07-03 15:00 | 6.2084 | 0 | N/A | 0 | 0
2021-07-03 15:30 | 6.3332 | 0 | N/A | 0 | 0
2021-07-03 16:00 | 6.9319 | 0 | N/A | 0 | 0
2021-07-03 16:30 | 6.9182 | 0 | N/A | 0 | 0
2021-07-03 17:00 | 7.4267 | 0 | N/A | 0 | 0
2021-07-03 17:30 | 8.1491 | 0 | N/A | 0 | 0
2021-07-03 18:00 | 8.8834 | 0 | N/A | 0 | 0
2021-07-03 18:30 | 8.87 | 0 | N/A | 0 | 0
2021-07-03 19:00 | 8.49 | 0 | N/A | 0 | 0
2021-07-03 19:30 | 8.1205 | 0 | N/A | 0 | 0
2021-07-03 20:00 | 7.7608 | 0 | N/A | 0 | 0
2021-07-03 20:30 | 7.4593 | 0 | N/A | 0 | 0
2021-07-03 21:00 | 7.1604 | 0 | N/A | 0 | 0
2021-07-03 21:30 | 7.5338 | 0 | N/A | 0 | 0
2021-07-03 22:00 | 7.7631 | 0 | N/A | 0 | 0
2021-07-03 22:30 | 7.2664 | 0 | N/A | 0 | 0
2021-07-03 23:00 | 7.2377 | 0 | N/A | 0 | 0
2021-07-03 23:30 | 7.3752 | 0 | N/A | 0 | 0
2021-07-04 | 7.5168 | 0 | N/A | 0 | 0
2021-07-04 00:30 | 6.9139 | 0 | N/A | 0 | 0
2021-07-04 01:00 | 6.2359 | 0 | N/A | 0 | 0
2021-07-04 01:30 | 6.0374 | 0 | N/A | 0 | 0
2021-07-04 02:00 | 5.5187 | 0 | N/A | 0 | 0
2021-07-04 02:30 | 4.7331 | 0 | N/A | 0 | 0
2021-07-04 03:00 | 4.3562 | 0 | N/A | 0 | 0
2021-07-04 03:30 | 4.1204 | 0 | N/A | 0 | 0
2021-07-04 04:00 | 3.8856 | 0 | N/A | 0 | 0
2021-07-04 04:30 | 3.7757 | 0 | N/A | 0 | 0
2021-07-04 05:00 | 3.7414 | 0 | N/A | 0 | 0
2021-07-04 05:30 | 3.7648 | 0 | N/A | 0 | 0
2021-07-04 06:00 | 3.9917 | 0 | N/A | 0 | 0
2021-07-04 06:30 | 4.2376 | 0 | N/A | 0 | 0
2021-07-04 07:00 | 4.3064 | 0 | N/A | 0 | 0
2021-07-04 07:30 | 4.2525 | 0 | N/A | 0 | 0
2021-07-04 08:00 | 4.7591 | 0 | N/A | 0 | 0
2021-07-04 08:30 | 5.5658 | 0 | N/A | 0 | 0
2021-07-04 09:00 | 6.1079 | 0 | N/A | 0 | 0
2021-07-04 09:30 | 6.5113 | 0 | N/A | 0 | 0
2021-07-04 10:00 | 6.6123 | 0 | N/A | 0 | 0
2021-07-04 10:30 | 6.8287 | 0 | N/A | 0 | 0
2021-07-04 11:00 | 6.7834 | 0 | N/A | 0 | 0
2021-07-04 11:30 | 6.5112 | 0 | N/A | 0 | 0
2021-07-04 12:00 | 5.9864 | 0 | N/A | 0 | 0
2021-07-04 12:30 | 5.1497 | 0 | N/A | 0 | 0
2021-07-04 13:00 | 5.7142 | 0 | N/A | 0 | 0
2021-07-04 13:30 | 6.4337 | 0 | N/A | 0 | 0
2021-07-04 14:00 | 6.3373 | 0 | N/A | 0 | 0
2021-07-04 14:30 | 5.4518 | 0 | N/A | 0 | 0
2021-07-04 15:00 | 6.4231 | 0 | N/A | 0 | 0
2021-07-04 15:30 | 6.2433 | 0 | N/A | 0 | 0
2021-07-04 16:00 | 6.8162 | 0 | N/A | 0 | 0
2021-07-04 16:30 | 7.0114 | 0 | N/A | 0 | 0
2021-07-04 17:00 | 7.4336 | 0 | N/A | 0 | 0
2021-07-04 17:30 | 7.9743 | 0 | N/A | 0 | 0
2021-07-04 18:00 | 8.9501 | 0 | N/A | 0 | 0
2021-07-04 18:30 | 9.1133 | 0 | N/A | 0 | 0
2021-07-04 19:00 | 8.7267 | 0 | N/A | 0 | 0
2021-07-04 19:30 | 8.2709 | 0 | N/A | 0 | 0
2021-07-04 20:00 | 7.8621 | 0 | N/A | 0 | 0
2021-07-04 20:30 | 7.4054 | 0 | N/A | 0 | 0
2021-07-04 21:00 | 7.1068 | 0 | N/A | 0 | 0
2021-07-04 21:30 | 7.2779 | 0 | N/A | 0 | 0
2021-07-04 22:00 | 7.3707 | 0 | N/A | 0 | 0
2021-07-04 22:30 | 6.8863 | 0 | N/A | 0 | 0
2021-07-04 23:00 | 6.7713 | 0 | N/A | 0 | 0
2021-07-04 23:30 | 6.8264 | 0 | N/A | 0 | 0
2021-07-05 | 7.1206 | 0 | N/A | 0 | 0
2021-07-05 00:30 | 6.4399 | 0 | N/A | 0 | 0
2021-07-05 01:00 | 5.7106 | 0 | N/A | 0 | 0
2021-07-05 01:30 | 5.5754 | 0 | N/A | 0 | 0
2021-07-05 02:00 | 5.2322 | 0 | N/A | 0 | 0
2021-07-05 02:30 | 4.6833 | 0 | N/A | 0 | 0
2021-07-05 03:00 | 4.3394 | 0 | N/A | 0 | 0
2021-07-05 03:30 | 3.9868 | 0 | N/A | 0 | 0
2021-07-05 04:00 | 3.6874 | 0 | N/A | 0 | 0
2021-07-05 04:30 | 3.5857 | 0 | N/A | 0 | 0
2021-07-05 05:00 | 3.6656 | 0 | N/A | 0 | 0
2021-07-05 05:30 | 3.942 | 0 | N/A | 0 | 0
2021-07-05 06:00 | 4.3937 | 0 | N/A | 0 | 0
2021-07-05 06:30 | 4.9602 | 0 | N/A | 0 | 0
2021-07-05 07:00 | 5.5015 | 0 | N/A | 0 | 0
2021-07-05 07:30 | 5.5909 | 0 | N/A | 0 | 0
2021-07-05 08:00 | 6.2704 | 0 | N/A | 0 | 0
2021-07-05 08:30 | 6.9005 | 0 | N/A | 0 | 0
2021-07-05 09:00 | 6.9967 | 0 | N/A | 0 | 0
2021-07-05 09:30 | 6.9367 | 0 | N/A | 0 | 0
2021-07-05 10:00 | 6.8101 | 0 | N/A | 0 | 0
2021-07-05 10:30 | 6.6635 | 0 | N/A | 0 | 0
2021-07-05 11:00 | 6.5233 | 0 | N/A | 0 | 0
2021-07-05 11:30 | 5.9533 | 0 | N/A | 0 | 0
2021-07-05 12:00 | 5.1567 | 0 | N/A | 0 | 0
2021-07-05 12:30 | 5.7337 | 0 | N/A | 0 | 0
2021-07-05 13:00 | 5.5641 | 0 | N/A | 0 | 0
2021-07-05 13:30 | 5.63 | 0 | N/A | 0 | 0
2021-07-05 14:00 | 5.5533 | 0 | N/A | 0 | 0
2021-07-05 14:30 | 5.6067 | 0 | N/A | 0 | 0
2021-07-05 15:00 | 6.1535 | 0 | N/A | 0 | 0
2021-07-05 15:30 | 5.9871 | 0 | N/A | 0 | 0
2021-07-05 16:00 | 5.7011 | 0 | N/A | 0 | 0
2021-07-05 16:30 | 5.7814 | 0 | N/A | 0 | 0
2021-07-05 17:00 | 6.8643 | 0 | N/A | 0 | 0
2021-07-05 17:30 | 7.8978 | 0 | N/A | 0 | 0
2021-07-05 18:00 | 8.7667 | 0 | N/A | 0 | 0
2021-07-05 18:30 | 8.97 | 0 | N/A | 0 | 0
2021-07-05 19:00 | 8.6033 | 0 | N/A | 0 | 0
2021-07-05 19:30 | 8.3 | 0 | N/A | 0 | 0
2021-07-05 20:00 | 8.0204 | 0 | N/A | 0 | 0
2021-07-05 20:30 | 7.6849 | 0 | N/A | 0 | 0
2021-07-05 21:00 | 7.2966 | 0 | N/A | 0 | 0
2021-07-05 21:30 | 7.6147 | 0 | N/A | 0 | 0
2021-07-05 22:00 | 7.4844 | 0 | N/A | 0 | 0
2021-07-05 22:30 | 6.7493 | 0 | N/A | 0 | 0
2021-07-05 23:00 | 6.6647 | 0 | N/A | 0 | 0
2021-07-05 23:30 | 6.6704 | 0 | N/A | 0 | 0
2021-07-06 | 6.9592 | 0 | N/A | 0 | 0
2021-07-06 00:30 | 6.2886 | 0 | N/A | 0 | 0
2021-07-06 01:00 | 5.5878 | 0 | N/A | 0 | 0
2021-07-06 01:30 | 5.3952 | 0 | N/A | 0 | 0
2021-07-06 02:00 | 4.9931 | 0 | N/A | 0 | 0
2021-07-06 02:30 | 4.4514 | 0 | N/A | 0 | 0
2021-07-06 03:00 | 4.1051 | 0 | N/A | 0 | 0
2021-07-06 03:30 | 3.8332 | 0 | N/A | 0 | 0
2021-07-06 04:00 | 3.5678 | 0 | N/A | 0 | 0
2021-07-06 04:30 | 3.509 | 0 | N/A | 0 | 0
2021-07-06 05:00 | 3.5308 | 0 | N/A | 0 | 0
2021-07-06 05:30 | 3.946 | 0 | N/A | 0 | 0
2021-07-06 06:00 | 4.4192 | 0 | N/A | 0 | 0
2021-07-06 06:30 | 5.037 | 0 | N/A | 0 | 0
2021-07-06 07:00 | 5.546 | 0 | N/A | 0 | 0
2021-07-06 07:30 | 5.7055 | 0 | N/A | 0 | 0
2021-07-06 08:00 | 6.4627 | 0 | N/A | 0 | 0
2021-07-06 08:30 | 7.0203 | 0 | N/A | 0 | 0
2021-07-06 09:00 | 6.827 | 0 | N/A | 0 | 0
2021-07-06 09:30 | 6.6136 | 0 | N/A | 0 | 0
2021-07-06 10:00 | 6.2602 | 0 | N/A | 0 | 0
2021-07-06 10:30 | 5.2975 | 0 | N/A | 0 | 0
2021-07-06 11:00 | 4.2105 | 0 | N/A | 0 | 0
2021-07-06 11:30 | 3.6779 | 0 | N/A | 0 | 0
2021-07-06 12:00 | 3.2941 | 0 | N/A | 0 | 0
2021-07-06 12:30 | 3.4828 | 0 | N/A | 0 | 0
2021-07-06 13:00 | 4.5096 | 0 | N/A | 0 | 0
2021-07-06 13:30 | 5.2713 | 0 | N/A | 0 | 0
2021-07-06 14:00 | 5.4179 | 0 | N/A | 0 | 0
2021-07-06 14:30 | 5.5331 | 0 | N/A | 0 | 0
2021-07-06 15:00 | 5.9702 | 0 | N/A | 0 | 0
2021-07-06 15:30 | 6.2222 | 0 | N/A | 0 | 0
2021-07-06 16:00 | 6.2487 | 0 | N/A | 0 | 0
2021-07-06 16:30 | 6.4518 | 0 | N/A | 0 | 0
2021-07-06 17:00 | 7.0603 | 0 | N/A | 0 | 0
2021-07-06 17:30 | 7.8972 | 0 | N/A | 0 | 0
2021-07-06 18:00 | 8.59 | 0 | N/A | 0 | 0
2021-07-06 18:30 | 8.8234 | 0 | N/A | 0 | 0
2021-07-06 19:00 | 8.6067 | 0 | N/A | 0 | 0
2021-07-06 19:30 | 8.2767 | 0 | N/A | 0 | 0
2021-07-06 20:00 | 7.9767 | 0 | N/A | 0 | 0
2021-07-06 20:30 | 7.439 | 0 | N/A | 0 | 0
2021-07-06 21:00 | 7.1297 | 0 | N/A | 0 | 0
2021-07-06 21:30 | 7.2625 | 0 | N/A | 0 | 0
2021-07-06 22:00 | 7.1689 | 0 | N/A | 0 | 0
2021-07-06 22:30 | 6.7265 | 0 | N/A | 0 | 0
2021-07-06 23:00 | 6.5086 | 0 | N/A | 0 | 0
2021-07-06 23:30 | 6.5814 | 0 | N/A | 0 | 0
2021-07-07 | 6.8305 | 0 | N/A | 0 | 0
2021-07-07 00:30 | 6.1716 | 0 | N/A | 0 | 0
2021-07-07 01:00 | 5.4383 | 0 | N/A | 0 | 0
2021-07-07 01:30 | 5.2676 | 0 | N/A | 0 | 0
2021-07-07 02:00 | 4.9163 | 0 | N/A | 0 | 0
2021-07-07 02:30 | 4.327 | 0 | N/A | 0 | 0
2021-07-07 03:00 | 3.9474 | 0 | N/A | 0 | 0
2021-07-07 03:30 | 3.6995 | 0 | N/A | 0 | 0
2021-07-07 04:00 | 3.5629 | 0 | N/A | 0 | 0
2021-07-07 04:30 | 3.5218 | 0 | N/A | 0 | 0
2021-07-07 05:00 | 3.5744 | 0 | N/A | 0 | 0
2021-07-07 05:30 | 3.9457 | 0 | N/A | 0 | 0
2021-07-07 06:00 | 4.4599 | 0 | N/A | 0 | 0
2021-07-07 06:30 | 5.0258 | 0 | N/A | 0 | 0
2021-07-07 07:00 | 5.556 | 0 | N/A | 0 | 0
2021-07-07 07:30 | 5.7869 | 0 | N/A | 0 | 0
2021-07-07 08:00 | 6.5363 | 0 | N/A | 0 | 0
2021-07-07 08:30 | 7.0768 | 0 | N/A | 0 | 0
2021-07-07 09:00 | 6.9267 | 0 | N/A | 0 | 0
2021-07-07 09:30 | 7.3967 | 0 | N/A | 0 | 0
2021-07-07 10:00 | 7.21 | 0 | N/A | 0 | 0
2021-07-07 10:30 | 6.86 | 0 | N/A | 0 | 0
2021-07-07 11:00 | 6.5333 | 0 | N/A | 0 | 0
2021-07-07 11:30 | 5.76 | 0 | N/A | 0 | 0
2021-07-07 12:00 | 5.9033 | 0 | N/A | 0 | 0
2021-07-07 12:30 | 4.4869 | 0 | N/A | 0 | 0
2021-07-07 13:00 | 4.907 | 0 | N/A | 0 | 0
2021-07-07 13:30 | 5.2734 | 0 | N/A | 0 | 0
2021-07-07 14:00 | 5.7701 | 0 | N/A | 0 | 0
2021-07-07 14:30 | 5.8574 | 0 | N/A | 0 | 0
2021-07-07 15:00 | 5.5134 | 0 | N/A | 0 | 0
2021-07-07 15:30 | 4.3883 | 0 | N/A | 0 | 0
2021-07-07 16:00 | 4.7898 | 0 | N/A | 0 | 0
2021-07-07 16:30 | 5.5804 | 0 | N/A | 0 | 0
2021-07-07 17:00 | 6.391 | 0 | N/A | 0 | 0
2021-07-07 17:30 | 7.3425 | 0 | N/A | 0 | 0
2021-07-07 18:00 | 8.3268 | 0 | N/A | 0 | 0
2021-07-07 18:30 | 8.81 | 0 | N/A | 0 | 0
2021-07-07 19:00 | 8.7834 | 0 | N/A | 0 | 0
2021-07-07 19:30 | 8.47 | 0 | N/A | 0 | 0
2021-07-07 20:00 | 8.356 | 0 | N/A | 0 | 0
2021-07-07 20:30 | 8.0369 | 0 | N/A | 0 | 0
2021-07-07 21:00 | 7.7108 | 0 | N/A | 0 | 0
2021-07-07 21:30 | 7.8422 | 0 | N/A | 0 | 0
2021-07-07 22:00 | 7.9227 | 0 | N/A | 0 | 0
2021-07-07 22:30 | 7.3048 | 0 | N/A | 0 | 0
2021-07-07 23:00 | 6.918 | 0 | N/A | 0 | 0
2021-07-07 23:30 | 6.9905 | 0 | N/A | 0 | 0
2021-07-08 | 7.4879 | 0 | N/A | 0 | 0
2021-07-08 00:30 | 6.915 | 0 | N/A | 0 | 0
2021-07-08 01:00 | 6.2147 | 0 | N/A | 0 | 0
2021-07-08 01:30 | 6.0632 | 0 | N/A | 0 | 0
2021-07-08 02:00 | 5.6185 | 0 | N/A | 0 | 0
2021-07-08 02:30 | 5.0937 | 0 | N/A | 0 | 0
2021-07-08 03:00 | 4.6553 | 0 | N/A | 0 | 0
2021-07-08 03:30 | 4.4453 | 0 | N/A | 0 | 0
2021-07-08 04:00 | 4.2244 | 0 | N/A | 0 | 0
2021-07-08 04:30 | 4.2231 | 0 | N/A | 0 | 0
2021-07-08 05:00 | 4.269 | 0 | N/A | 0 | 0
2021-07-08 05:30 | 4.664 | 0 | N/A | 0 | 0
2021-07-08 06:00 | 5.1903 | 0 | N/A | 0 | 0
2021-07-08 06:30 | 6.0536 | 0 | N/A | 0 | 0
2021-07-08 07:00 | 6.6637 | 0 | N/A | 0 | 0
2021-07-08 07:30 | 6.9949 | 0 | N/A | 0 | 0
2021-07-08 08:00 | 8.1717 | 0 | N/A | 0 | 0
2021-07-08 08:30 | 8.5718 | 0 | N/A | 0 | 0
2021-07-08 09:00 | 8.3775 | 0 | N/A | 0 | 0
2021-07-08 09:30 | 7.3009 | 0 | N/A | 0 | 0
2021-07-08 10:00 | 6.5474 | 0 | N/A | 0 | 0
2021-07-08 10:30 | 6.05 | 0 | N/A | 0 | 0
2021-07-08 11:00 | 5.18 | 0 | N/A | 0 | 0
2021-07-08 11:30 | 4.4824 | 0 | N/A | 0 | 0
2021-07-08 12:00 | 4.0078 | 0 | N/A | 0 | 0
2021-07-08 12:30 | 3.6584 | 0 | N/A | 0 | 0
2021-07-08 13:00 | 3.3439 | 0 | N/A | 0 | 0
2021-07-08 13:30 | 3.8806 | 0 | N/A | 0 | 0
2021-07-08 14:00 | 4.2703 | 0 | N/A | 0 | 0
2021-07-08 14:30 | 4.0834 | 0 | N/A | 0 | 0
2021-07-08 15:00 | 3.7746 | 0 | N/A | 0 | 0
2021-07-08 15:30 | 4.2527 | 0 | N/A | 0 | 0
2021-07-08 16:00 | 4.6524 | 0 | N/A | 0 | 0
2021-07-08 16:30 | 5.3945 | 0 | N/A | 0 | 0
2021-07-08 17:00 | 6.4565 | 0 | N/A | 0 | 0
2021-07-08 17:30 | 7.5994 | 0 | N/A | 0 | 0
2021-07-08 18:00 | 8.67 | 0 | N/A | 0 | 0
2021-07-08 18:30 | 9.0633 | 0 | N/A | 0 | 0
2021-07-08 19:00 | 9.12 | 0 | N/A | 0 | 0
2021-07-08 19:30 | 8.97 | 0 | N/A | 0 | 0
2021-07-08 20:00 | 8.7633 | 0 | N/A | 0 | 0
2021-07-08 20:30 | 8.6233 | 0 | N/A | 0 | 0
2021-07-08 21:00 | 8.2701 | 0 | N/A | 0 | 0
2021-07-08 21:30 | 8.4375 | 0 | N/A | 0 | 0
2021-07-08 22:00 | 8.3477 | 0 | N/A | 0 | 0
2021-07-08 22:30 | 7.6791 | 0 | N/A | 0 | 0
2021-07-08 23:00 | 7.2769 | 0 | N/A | 0 | 0
2021-07-08 23:30 | 7.4268 | 0 | N/A | 0 | 0
2021-07-09 | 7.5609 | 0 | N/A | 0 | 0
2021-07-09 00:30 | 6.8504 | 0 | N/A | 0 | 0
2021-07-09 01:00 | 6.1419 | 0 | N/A | 0 | 0
2021-07-09 01:30 | 6.1499 | 0 | N/A | 0 | 0
2021-07-09 02:00 | 5.8304 | 0 | N/A | 0 | 0
2021-07-09 02:30 | 5.2337 | 0 | N/A | 0 | 0
2021-07-09 03:00 | 4.7156 | 0 | N/A | 0 | 0
2021-07-09 03:30 | 4.4617 | 0 | N/A | 0 | 0
2021-07-09 04:00 | 4.2952 | 0 | N/A | 0 | 0
2021-07-09 04:30 | 4.174 | 0 | N/A | 0 | 0
2021-07-09 05:00 | 4.2408 | 0 | N/A | 0 | 0
2021-07-09 05:30 | 4.6898 | 0 | N/A | 0 | 0
2021-07-09 06:00 | 5.3373 | 0 | N/A | 0 | 0
2021-07-09 06:30 | 6.1151 | 0 | N/A | 0 | 0
2021-07-09 07:00 | 6.6505 | 0 | N/A | 0 | 0
2021-07-09 07:30 | 7.0833 | 0 | N/A | 0 | 0
2021-07-09 08:00 | 8.1379 | 0 | N/A | 0 | 0
2021-07-09 08:30 | 8.6625 | 0 | N/A | 0 | 0
2021-07-09 09:00 | 8.2574 | 0 | N/A | 0 | 0
2021-07-09 09:30 | 7.8973 | 0 | N/A | 0 | 0
2021-07-09 10:00 | 7.5777 | 0 | N/A | 0 | 0
2021-07-09 10:30 | 6.8401 | 0 | N/A | 0 | 0
2021-07-09 11:00 | 6.1601 | 0 | N/A | 0 | 0
2021-07-09 11:30 | 5.5434 | 0 | N/A | 0 | 0
2021-07-09 12:00 | 4.81 | 0 | N/A | 0 | 0
2021-07-09 12:30 | 4.0638 | 0 | N/A | 0 | 0
2021-07-09 13:00 | 3.4655 | 0 | N/A | 0 | 0
2021-07-09 13:30 | 3.3966 | 0 | N/A | 0 | 0
2021-07-09 14:00 | 3.1135 | 0 | N/A | 0 | 0
2021-07-09 14:30 | 3.1819 | 0 | N/A | 0 | 0
2021-07-09 15:00 | 3.5012 | 0 | N/A | 0 | 0
2021-07-09 15:30 | 3.8707 | 0 | N/A | 0 | 0
2021-07-09 16:00 | 4.3533 | 0 | N/A | 0 | 0
2021-07-09 16:30 | 4.9232 | 0 | N/A | 0 | 0
2021-07-09 17:00 | 5.8165 | 0 | N/A | 0 | 0
2021-07-09 17:30 | 6.9556 | 0 | N/A | 0 | 0
2021-07-09 18:00 | 7.9349 | 0 | N/A | 0 | 0
2021-07-09 18:30 | 8.4334 | 0 | N/A | 0 | 0
2021-07-09 19:00 | 8.6 | 0 | N/A | 0 | 0
2021-07-09 19:30 | 8.4267 | 0 | N/A | 0 | 0
2021-07-09 20:00 | 8.2434 | 0 | N/A | 0 | 0
2021-07-09 20:30 | 8.0904 | 0 | N/A | 0 | 0
2021-07-09 21:00 | 7.8906 | 0 | N/A | 0 | 0
2021-07-09 21:30 | 8.1747 | 0 | N/A | 0 | 0
2021-07-09 22:00 | 8.3088 | 0 | N/A | 0 | 0
2021-07-09 22:30 | 7.7743 | 0 | N/A | 0 | 0
2021-07-09 23:00 | 7.5659 | 0 | N/A | 0 | 0
2021-07-09 23:30 | 7.6876 | 0 | N/A | 0 | 0
2021-07-10 | 7.9804 | 0 | N/A | 0 | 0
2021-07-10 00:30 | 7.2413 | 0 | N/A | 0 | 0
2021-07-10 01:00 | 6.4965 | 0 | N/A | 0 | 0
2021-07-10 01:30 | 6.4542 | 0 | N/A | 0 | 0
2021-07-10 02:00 | 6.0888 | 0 | N/A | 0 | 0
2021-07-10 02:30 | 5.4139 | 0 | N/A | 0 | 0
2021-07-10 03:00 | 4.9019 | 0 | N/A | 0 | 0
2021-07-10 03:30 | 4.6756 | 0 | N/A | 0 | 0
2021-07-10 04:00 | 4.4647 | 0 | N/A | 0 | 0
2021-07-10 04:30 | 4.3159 | 0 | N/A | 0 | 0
2021-07-10 05:00 | 4.3126 | 0 | N/A | 0 | 0
2021-07-10 05:30 | 4.3669 | 0 | N/A | 0 | 0
2021-07-10 06:00 | 4.6071 | 0 | N/A | 0 | 0
2021-07-10 06:30 | 5.0245 | 0 | N/A | 0 | 0
2021-07-10 07:00 | 5.2658 | 0 | N/A | 0 | 0
2021-07-10 07:30 | 5.3248 | 0 | N/A | 0 | 0
2021-07-10 08:00 | 5.9636 | 0 | N/A | 0 | 0
2021-07-10 08:30 | 6.6363 | 0 | N/A | 0 | 0
2021-07-10 09:00 | 6.6726 | 0 | N/A | 0 | 0
2021-07-10 09:30 | 6.2755 | 0 | N/A | 0 | 0
2021-07-10 10:00 | 5.6122 | 0 | N/A | 0 | 0
2021-07-10 10:30 | 4.8419 | 0 | N/A | 0 | 0
2021-07-10 11:00 | 3.9068 | 0 | N/A | 0 | 0
2021-07-10 11:30 | 3.1806 | 0 | N/A | 0 | 0
2021-07-10 12:00 | 2.7144 | 0 | N/A | 0 | 0
2021-07-10 12:30 | 2.3139 | 0 | N/A | 0 | 0
2021-07-10 13:00 | 1.9446 | 0 | N/A | 0 | 0
2021-07-10 13:30 | 1.9652 | 0 | N/A | 0 | 0
2021-07-10 14:00 | 2.0437 | 0 | N/A | 0 | 0
2021-07-10 14:30 | 2.1896 | 0 | N/A | 0 | 0
2021-07-10 15:00 | 2.6843 | 0 | N/A | 0 | 0
2021-07-10 15:30 | 3.2426 | 0 | N/A | 0 | 0
2021-07-10 16:00 | 3.9675 | 0 | N/A | 0 | 0
2021-07-10 16:30 | 4.6798 | 0 | N/A | 0 | 0
2021-07-10 17:00 | 5.6519 | 0 | N/A | 0 | 0
2021-07-10 17:30 | 6.8335 | 0 | N/A | 0 | 0
2021-07-10 18:00 | 7.7348 | 0 | N/A | 0 | 0
2021-07-10 18:30 | 8.0472 | 0 | N/A | 0 | 0
2021-07-10 19:00 | 7.8941 | 0 | N/A | 0 | 0
2021-07-10 19:30 | 7.5557 | 0 | N/A | 0 | 0
2021-07-10 20:00 | 7.2497 | 0 | N/A | 0 | 0
2021-07-10 20:30 | 6.953 | 0 | N/A | 0 | 0
2021-07-10 21:00 | 6.5573 | 0 | N/A | 0 | 0
2021-07-10 21:30 | 6.9852 | 0 | N/A | 0 | 0
2021-07-10 22:00 | 7.1984 | 0 | N/A | 0 | 0
2021-07-10 22:30 | 6.9608 | 0 | N/A | 0 | 0
2021-07-10 23:00 | 7.0796 | 0 | N/A | 0 | 0
2021-07-10 23:30 | 7.1472 | 0 | N/A | 0 | 0
2021-07-11 | 7.503 | 0 | N/A | 0 | 0
2021-07-11 00:30 | 6.9731 | 0 | N/A | 0 | 0
2021-07-11 01:00 | 6.2309 | 0 | N/A | 0 | 0
2021-07-11 01:30 | 6.2353 | 0 | N/A | 0 | 0
2021-07-11 02:00 | 5.6742 | 0 | N/A | 0 | 0
2021-07-11 02:30 | 5.0769 | 0 | N/A | 0 | 0
2021-07-11 03:00 | 4.6424 | 0 | N/A | 0 | 0
2021-07-11 03:30 | 4.3335 | 0 | N/A | 0 | 0
2021-07-11 04:00 | 4.092 | 0 | N/A | 0 | 0
2021-07-11 04:30 | 3.9985 | 0 | N/A | 0 | 0
2021-07-11 05:00 | 3.9603 | 0 | N/A | 0 | 0
2021-07-11 05:30 | 3.9366 | 0 | N/A | 0 | 0
2021-07-11 06:00 | 4.174 | 0 | N/A | 0 | 0
2021-07-11 06:30 | 4.4844 | 0 | N/A | 0 | 0
2021-07-11 07:00 | 4.6192 | 0 | N/A | 0 | 0
2021-07-11 07:30 | 4.5999 | 0 | N/A | 0 | 0
2021-07-11 08:00 | 4.9594 | 0 | N/A | 0 | 0
2021-07-11 08:30 | 5.3185 | 0 | N/A | 0 | 0
2021-07-11 09:00 | 5.3746 | 0 | N/A | 0 | 0
2021-07-11 09:30 | 5.3712 | 0 | N/A | 0 | 0
2021-07-11 10:00 | 5.0409 | 0 | N/A | 0 | 0
2021-07-11 10:30 | 4.354 | 0 | N/A | 0 | 0
2021-07-11 11:00 | 3.6876 | 0 | N/A | 0 | 0
2021-07-11 11:30 | 3.3918 | 0 | N/A | 0 | 0
2021-07-11 12:00 | 3.4735 | 0 | N/A | 0 | 0
2021-07-11 12:30 | 4.4277 | 0 | N/A | 0 | 0
2021-07-11 13:00 | 3.7803 | 0 | N/A | 0 | 0
2021-07-11 13:30 | 4.008 | 0 | N/A | 0 | 0
2021-07-11 14:00 | 3.5924 | 0 | N/A | 0 | 0
2021-07-11 14:30 | 3.6126 | 0 | N/A | 0 | 0
2021-07-11 15:00 | 4.5943 | 0 | N/A | 0 | 0
2021-07-11 15:30 | 5.1403 | 0 | N/A | 0 | 0
2021-07-11 16:00 | 5.5677 | 0 | N/A | 0 | 0
2021-07-11 16:30 | 5.7659 | 0 | N/A | 0 | 0
2021-07-11 17:00 | 6.8604 | 0 | N/A | 0 | 0
2021-07-11 17:30 | 7.8576 | 0 | N/A | 0 | 0
2021-07-11 18:00 | 8.7434 | 0 | N/A | 0 | 0
2021-07-11 18:30 | 8.8833 | 0 | N/A | 0 | 0
2021-07-11 19:00 | 8.6368 | 0 | N/A | 0 | 0
2021-07-11 19:30 | 8.2745 | 0 | N/A | 0 | 0
2021-07-11 20:00 | 7.8061 | 0 | N/A | 0 | 0
2021-07-11 20:30 | 7.3922 | 0 | N/A | 0 | 0
2021-07-11 21:00 | 6.9748 | 0 | N/A | 0 | 0
2021-07-11 21:30 | 7.1712 | 0 | N/A | 0 | 0
2021-07-11 22:00 | 7.1638 | 0 | N/A | 0 | 0
2021-07-11 22:30 | 6.6158 | 0 | N/A | 0 | 0
2021-07-11 23:00 | 6.4453 | 0 | N/A | 0 | 0
2021-07-11 23:30 | 6.3601 | 0 | N/A | 0 | 0
2021-07-12 | 6.6506 | 0 | N/A | 0 | 0
2021-07-12 00:30 | 5.9972 | 0 | N/A | 0 | 0
2021-07-12 01:00 | 5.2727 | 0 | N/A | 0 | 0
2021-07-12 01:30 | 5.2656 | 0 | N/A | 0 | 0
2021-07-12 02:00 | 5.008 | 0 | N/A | 0 | 0
2021-07-12 02:30 | 4.4656 | 0 | N/A | 0 | 0
2021-07-12 03:00 | 4.0581 | 0 | N/A | 0 | 0
2021-07-12 03:30 | 3.7909 | 0 | N/A | 0 | 0
2021-07-12 04:00 | 3.4922 | 0 | N/A | 0 | 0
2021-07-12 04:30 | 3.4012 | 0 | N/A | 0 | 0
2021-07-12 05:00 | 3.5343 | 0 | N/A | 0 | 0
2021-07-12 05:30 | 3.9537 | 0 | N/A | 0 | 0
2021-07-12 06:00 | 4.457 | 0 | N/A | 0 | 0
2021-07-12 06:30 | 5.2484 | 0 | N/A | 0 | 0
2021-07-12 07:00 | 6.0263 | 0 | N/A | 0 | 0
2021-07-12 07:30 | 6.3774 | 0 | N/A | 0 | 0
2021-07-12 08:00 | 7.4937 | 0 | N/A | 0 | 0
2021-07-12 08:30 | 7.5839 | 0 | N/A | 0 | 0
2021-07-12 09:00 | 7.1539 | 0 | N/A | 0 | 0
2021-07-12 09:30 | 6.5611 | 0 | N/A | 0 | 0
2021-07-12 10:00 | 6.6367 | 0 | N/A | 0 | 0
2021-07-12 10:30 | 6.3218 | 0 | N/A | 0 | 0
2021-07-12 11:00 | 5.0039 | 0 | N/A | 0 | 0
2021-07-12 11:30 | 3.5747 | 0 | N/A | 0 | 0
2021-07-12 12:00 | 3.7657 | 0 | N/A | 0 | 0
2021-07-12 12:30 | 2.8972 | 0 | N/A | 0 | 0
2021-07-12 13:00 | 2.7056 | 0 | N/A | 0 | 0
2021-07-12 13:30 | 2.2739 | 0 | N/A | 0 | 0
2021-07-12 14:00 | 2.5067 | 0 | N/A | 0 | 0
2021-07-12 14:30 | 2.5485 | 0 | N/A | 0 | 0
2021-07-12 15:00 | 3.25 | 0 | N/A | 0 | 0
2021-07-12 15:30 | 3.8533 | 0 | N/A | 0 | 0
2021-07-12 16:00 | 4.4576 | 0 | N/A | 0 | 0
2021-07-12 16:30 | 5.0528 | 0 | N/A | 0 | 0
2021-07-12 17:00 | 6.3121 | 0 | N/A | 0 | 0
2021-07-12 17:30 | 7.3392 | 0 | N/A | 0 | 0
2021-07-12 18:00 | 8.3902 | 0 | N/A | 0 | 0
2021-07-12 18:30 | 8.7833 | 0 | N/A | 0 | 0
2021-07-12 19:00 | 8.4367 | 0 | N/A | 0 | 0
2021-07-12 19:30 | 8.0401 | 0 | N/A | 0 | 0
2021-07-12 20:00 | 7.6777 | 0 | N/A | 0 | 0
2021-07-12 20:30 | 7.199 | 0 | N/A | 0 | 0
2021-07-12 21:00 | 6.7875 | 0 | N/A | 0 | 0
2021-07-12 21:30 | 6.9212 | 0 | N/A | 0 | 0
2021-07-12 22:00 | 6.8681 | 0 | N/A | 0 | 0
2021-07-12 22:30 | 6.4389 | 0 | N/A | 0 | 0
2021-07-12 23:00 | 6.1794 | 0 | N/A | 0 | 0
2021-07-12 23:30 | 6.1172 | 0 | N/A | 0 | 0
2021-07-13 | 6.4356 | 0 | N/A | 0 | 0
2021-07-13 00:30 | 5.8021 | 0 | N/A | 0 | 0
2021-07-13 01:00 | 5.0586 | 0 | N/A | 0 | 0
2021-07-13 01:30 | 5.0446 | 0 | N/A | 0 | 0
2021-07-13 02:00 | 4.6711 | 0 | N/A | 0 | 0
2021-07-13 02:30 | 4.1126 | 0 | N/A | 0 | 0
2021-07-13 03:00 | 3.7521 | 0 | N/A | 0 | 0
2021-07-13 03:30 | 3.5517 | 0 | N/A | 0 | 0
2021-07-13 04:00 | 3.3586 | 0 | N/A | 0 | 0
2021-07-13 04:30 | 3.3013 | 0 | N/A | 0 | 0
2021-07-13 05:00 | 3.3884 | 0 | N/A | 0 | 0
2021-07-13 05:30 | 3.803 | 0 | N/A | 0 | 0
2021-07-13 06:00 | 4.2828 | 0 | N/A | 0 | 0
2021-07-13 06:30 | 5.0756 | 0 | N/A | 0 | 0
2021-07-13 07:00 | 5.7443 | 0 | N/A | 0 | 0
2021-07-13 07:30 | 6.1063 | 0 | N/A | 0 | 0
2021-07-13 08:00 | 6.7328 | 0 | N/A | 0 | 0
2021-07-13 08:30 | 6.927 | 0 | N/A | 0 | 0
2021-07-13 09:00 | 6.7167 | 0 | N/A | 0 | 0
2021-07-13 09:30 | 6.3133 | 0 | N/A | 0 | 0
2021-07-13 10:00 | 6.0033 | 0 | N/A | 0 | 0
2021-07-13 10:30 | 5.6434 | 0 | N/A | 0 | 0
2021-07-13 11:00 | 5.4705 | 0 | N/A | 0 | 0
2021-07-13 11:30 | 5.9103 | 0 | N/A | 0 | 0
2021-07-13 12:00 | 5.6467 | 0 | N/A | 0 | 0
2021-07-13 12:30 | 5.23 | 0 | N/A | 0 | 0
2021-07-13 13:00 | 4.6304 | 0 | N/A | 0 | 0
2021-07-13 13:30 | 4.9075 | 0 | N/A | 0 | 0
2021-07-13 14:00 | 4.1167 | 0 | N/A | 0 | 0
2021-07-13 14:30 | 4.1917 | 0 | N/A | 0 | 0
2021-07-13 15:00 | 5.108 | 0 | N/A | 0 | 0
2021-07-13 15:30 | 5.3195 | 0 | N/A | 0 | 0
2021-07-13 16:00 | 5.6744 | 0 | N/A | 0 | 0
2021-07-13 16:30 | 5.9999 | 0 | N/A | 0 | 0
2021-07-13 17:00 | 6.6093 | 0 | N/A | 0 | 0
2021-07-13 17:30 | 7.3501 | 0 | N/A | 0 | 0
2021-07-13 18:00 | 8.2633 | 0 | N/A | 0 | 0
2021-07-13 18:30 | 8.5833 | 0 | N/A | 0 | 0
2021-07-13 19:00 | 8.4733 | 0 | N/A | 0 | 0
2021-07-13 19:30 | 8.0401 | 0 | N/A | 0 | 0
2021-07-13 20:00 | 7.7009 | 0 | N/A | 0 | 0
2021-07-13 20:30 | 7.3485 | 0 | N/A | 0 | 0
2021-07-13 21:00 | 6.8123 | 0 | N/A | 0 | 0
2021-07-13 21:30 | 6.8012 | 0 | N/A | 0 | 0
2021-07-13 22:00 | 6.8856 | 0 | N/A | 0 | 0
2021-07-13 22:30 | 6.429 | 0 | N/A | 0 | 0
2021-07-13 23:00 | 6.2204 | 0 | N/A | 0 | 0
2021-07-13 23:30 | 6.1637 | 0 | N/A | 0 | 0
2021-07-14 | 6.5621 | 0 | N/A | 0 | 0
2021-07-14 00:30 | 5.8702 | 0 | N/A | 0 | 0
2021-07-14 01:00 | 4.9596 | 0 | N/A | 0 | 0
2021-07-14 01:30 | 4.8087 | 0 | N/A | 0 | 0
2021-07-14 02:00 | 4.5256 | 0 | N/A | 0 | 0
2021-07-14 02:30 | 4.008 | 0 | N/A | 0 | 0
2021-07-14 03:00 | 3.6154 | 0 | N/A | 0 | 0
2021-07-14 03:30 | 3.4191 | 0 | N/A | 0 | 0
2021-07-14 04:00 | 3.1973 | 0 | N/A | 0 | 0
2021-07-14 04:30 | 3.1283 | 0 | N/A | 0 | 0
2021-07-14 05:00 | 3.2756 | 0 | N/A | 0 | 0
2021-07-14 05:30 | 3.8845 | 0 | N/A | 0 | 0
2021-07-14 06:00 | 4.4557 | 0 | N/A | 0 | 0
2021-07-14 06:30 | 5.3815 | 0 | N/A | 0 | 0
2021-07-14 07:00 | 6.1529 | 0 | N/A | 0 | 0
2021-07-14 07:30 | 6.8016 | 0 | N/A | 0 | 0
2021-07-14 08:00 | 8.1137 | 0 | N/A | 0 | 0
2021-07-14 08:30 | 7.6923 | 0 | N/A | 0 | 0
2021-07-14 09:00 | 7.4202 | 0 | N/A | 0 | 0
2021-07-14 09:30 | 7.3601 | 0 | N/A | 0 | 0
2021-07-14 10:00 | 7.1534 | 0 | N/A | 0 | 0
2021-07-14 10:30 | 7.1643 | 0 | N/A | 0 | 0
2021-07-14 11:00 | 6.8174 | 0 | N/A | 0 | 0
2021-07-14 11:30 | 6.3943 | 0 | N/A | 0 | 0
2021-07-14 12:00 | 6.356 | 0 | N/A | 0 | 0
2021-07-14 12:30 | 6.277 | 0 | N/A | 0 | 0
2021-07-14 13:00 | 5.0012 | 0 | N/A | 0 | 0
2021-07-14 13:30 | 5.7116 | 0 | N/A | 0 | 0
2021-07-14 14:00 | 6.0032 | 0 | N/A | 0 | 0
2021-07-14 14:30 | 6.0744 | 0 | N/A | 0 | 0
2021-07-14 15:00 | 6.4998 | 0 | N/A | 0 | 0
2021-07-14 15:30 | 6.2629 | 0 | N/A | 0 | 0
2021-07-14 16:00 | 6.33 | 0 | N/A | 0 | 0
2021-07-14 16:30 | 6.5409 | 0 | N/A | 0 | 0
2021-07-14 17:00 | 7.0438 | 0 | N/A | 0 | 0
2021-07-14 17:30 | 7.5104 | 0 | N/A | 0 | 0
2021-07-14 18:00 | 8.3567 | 0 | N/A | 0 | 0
2021-07-14 18:30 | 8.5267 | 0 | N/A | 0 | 0
2021-07-14 19:00 | 8.3933 | 0 | N/A | 0 | 0
2021-07-14 19:30 | 8.0033 | 0 | N/A | 0 | 0
2021-07-14 20:00 | 7.677 | 0 | N/A | 0 | 0
2021-07-14 20:30 | 7.232 | 0 | N/A | 0 | 0
2021-07-14 21:00 | 6.7635 | 0 | N/A | 0 | 0
2021-07-14 21:30 | 6.9866 | 0 | N/A | 0 | 0
2021-07-14 22:00 | 6.9858 | 0 | N/A | 0 | 0
2021-07-14 22:30 | 6.3084 | 0 | N/A | 0 | 0
2021-07-14 23:00 | 6.1591 | 0 | N/A | 0 | 0
2021-07-14 23:30 | 6.3188 | 0 | N/A | 0 | 0
2021-07-15 | 6.6488 | 0 | N/A | 0 | 0
2021-07-15 00:30 | 5.7474 | 0 | N/A | 0 | 0
2021-07-15 01:00 | 4.9733 | 0 | N/A | 0 | 0
2021-07-15 01:30 | 4.8856 | 0 | N/A | 0 | 0
2021-07-15 02:00 | 4.6854 | 0 | N/A | 0 | 0
2021-07-15 02:30 | 4.0048 | 0 | N/A | 0 | 0
2021-07-15 03:00 | 3.732 | 0 | N/A | 0 | 0
2021-07-15 03:30 | 3.4723 | 0 | N/A | 0 | 0
2021-07-15 04:00 | 3.293 | 0 | N/A | 0 | 0
2021-07-15 04:30 | 3.2188 | 0 | N/A | 0 | 0
2021-07-15 05:00 | 3.2282 | 0 | N/A | 0 | 0
2021-07-15 05:30 | 3.6448 | 0 | N/A | 0 | 0
2021-07-15 06:00 | 4.3199 | 0 | N/A | 0 | 0
2021-07-15 06:30 | 4.9726 | 0 | N/A | 0 | 0
2021-07-15 07:00 | 5.5788 | 0 | N/A | 0 | 0
2021-07-15 07:30 | 6.1798 | 0 | N/A | 0 | 0
2021-07-15 08:00 | 7.1808 | 0 | N/A | 0 | 0
2021-07-15 08:30 | 7.502 | 0 | N/A | 0 | 0
2021-07-15 09:00 | 6.7787 | 0 | N/A | 0 | 0
2021-07-15 09:30 | 6.5562 | 0 | N/A | 0 | 0
2021-07-15 10:00 | 6.4365 | 0 | N/A | 0 | 0
2021-07-15 10:30 | 5.8054 | 0 | N/A | 0 | 0
2021-07-15 11:00 | 5.8111 | 0 | N/A | 0 | 0
2021-07-15 11:30 | 5.2428 | 0 | N/A | 0 | 0
2021-07-15 12:00 | 4.915 | 0 | N/A | 0 | 0
2021-07-15 12:30 | 3.5922 | 0 | N/A | 0 | 0
2021-07-15 13:00 | 3.4769 | 0 | N/A | 0 | 0
2021-07-15 13:30 | 4.1568 | 0 | N/A | 0 | 0
2021-07-15 14:00 | 3.1824 | 0 | N/A | 0 | 0
2021-07-15 14:30 | 3.3069 | 0 | N/A | 0 | 0
2021-07-15 15:00 | 3.4233 | 0 | N/A | 0 | 0
2021-07-15 15:30 | 3.9367 | 0 | N/A | 0 | 0
2021-07-15 16:00 | 4.7312 | 0 | N/A | 0 | 0
2021-07-15 16:30 | 5.1308 | 0 | N/A | 0 | 0
2021-07-15 17:00 | 5.8324 | 0 | N/A | 0 | 0
2021-07-15 17:30 | 6.8156 | 0 | N/A | 0 | 0
2021-07-15 18:00 | 7.6204 | 0 | N/A | 0 | 0
2021-07-15 18:30 | 8.05 | 0 | N/A | 0 | 0
2021-07-15 19:00 | 7.9733 | 0 | N/A | 0 | 0
2021-07-15 19:30 | 7.6336 | 0 | N/A | 0 | 0
2021-07-15 20:00 | 7.4872 | 0 | N/A | 0 | 0
2021-07-15 20:30 | 7.1977 | 0 | N/A | 0 | 0
2021-07-15 21:00 | 6.9161 | 0 | N/A | 0 | 0
2021-07-15 21:30 | 7.0478 | 0 | N/A | 0 | 0
2021-07-15 22:00 | 7.2232 | 0 | N/A | 0 | 0
2021-07-15 22:30 | 6.5849 | 0 | N/A | 0 | 0
2021-07-15 23:00 | 6.4453 | 0 | N/A | 0 | 0
2021-07-15 23:30 | 6.472 | 0 | N/A | 0 | 0
2021-07-16 | 6.7746 | 0 | N/A | 0 | 0
2021-07-16 00:30 | 5.9808 | 0 | N/A | 0 | 0
2021-07-16 01:00 | 5.0756 | 0 | N/A | 0 | 0
2021-07-16 01:30 | 4.9093 | 0 | N/A | 0 | 0
2021-07-16 02:00 | 4.5435 | 0 | N/A | 0 | 0
2021-07-16 02:30 | 3.9002 | 0 | N/A | 0 | 0
2021-07-16 03:00 | 3.566 | 0 | N/A | 0 | 0
2021-07-16 03:30 | 3.3095 | 0 | N/A | 0 | 0
2021-07-16 04:00 | 3.2193 | 0 | N/A | 0 | 0
2021-07-16 04:30 | 3.164 | 0 | N/A | 0 | 0
2021-07-16 05:00 | 3.2797 | 0 | N/A | 0 | 0
2021-07-16 05:30 | 3.556 | 0 | N/A | 0 | 0
2021-07-16 06:00 | 4.0609 | 0 | N/A | 0 | 0
2021-07-16 06:30 | 4.5465 | 0 | N/A | 0 | 0
2021-07-16 07:00 | 5.0038 | 0 | N/A | 0 | 0
2021-07-16 07:30 | 5.3007 | 0 | N/A | 0 | 0
2021-07-16 08:00 | 6.1567 | 0 | N/A | 0 | 0
2021-07-16 08:30 | 7.1044 | 0 | N/A | 0 | 0
2021-07-16 09:00 | 7.2142 | 0 | N/A | 0 | 0
2021-07-16 09:30 | 7.3932 | 0 | N/A | 0 | 0
2021-07-16 10:00 | 7.1962 | 0 | N/A | 0 | 0
2021-07-16 10:30 | 7.4731 | 0 | N/A | 0 | 0
2021-07-16 11:00 | 7.421 | 0 | N/A | 0 | 0
2021-07-16 11:30 | 7.3604 | 0 | N/A | 0 | 0
2021-07-16 12:00 | 6.86 | 0 | N/A | 0 | 0
2021-07-16 12:30 | 6.2846 | 0 | N/A | 0 | 0
2021-07-16 13:00 | 6.3417 | 0 | N/A | 0 | 0
2021-07-16 13:30 | 6.0841 | 0 | N/A | 0 | 0
2021-07-16 14:00 | 4.7214 | 0 | N/A | 0 | 0
2021-07-16 14:30 | 3.8619 | 0 | N/A | 0 | 0
2021-07-16 15:00 | 4.7911 | 0 | N/A | 0 | 0
2021-07-16 15:30 | 6.1903 | 0 | N/A | 0 | 0
2021-07-16 16:00 | 6.3672 | 0 | N/A | 0 | 0
2021-07-16 16:30 | 6.3032 | 0 | N/A | 0 | 0
2021-07-16 17:00 | 6.5675 | 0 | N/A | 0 | 0
2021-07-16 17:30 | 7.38 | 0 | N/A | 0 | 0
2021-07-16 18:00 | 8.1702 | 0 | N/A | 0 | 0
2021-07-16 18:30 | 8.5001 | 0 | N/A | 0 | 0
2021-07-16 19:00 | 8.2601 | 0 | N/A | 0 | 0
2021-07-16 19:30 | 7.8139 | 0 | N/A | 0 | 0
2021-07-16 20:00 | 7.6014 | 0 | N/A | 0 | 0
2021-07-16 20:30 | 7.2492 | 0 | N/A | 0 | 0
2021-07-16 21:00 | 6.9398 | 0 | N/A | 0 | 0
2021-07-16 21:30 | 7.065 | 0 | N/A | 0 | 0
2021-07-16 22:00 | 7.3265 | 0 | N/A | 0 | 0
2021-07-16 22:30 | 6.8732 | 0 | N/A | 0 | 0
2021-07-16 23:00 | 6.8447 | 0 | N/A | 0 | 0
2021-07-16 23:30 | 6.8426 | 0 | N/A | 0 | 0
2021-07-17 | 7.0554 | 0 | N/A | 0 | 0
2021-07-17 00:30 | 6.4366 | 0 | N/A | 0 | 0
2021-07-17 01:00 | 5.5548 | 0 | N/A | 0 | 0
2021-07-17 01:30 | 5.4458 | 0 | N/A | 0 | 0
2021-07-17 02:00 | 5.0022 | 0 | N/A | 0 | 0
2021-07-17 02:30 | 4.4262 | 0 | N/A | 0 | 0
2021-07-17 03:00 | 4.066 | 0 | N/A | 0 | 0
2021-07-17 03:30 | 3.9063 | 0 | N/A | 0 | 0
2021-07-17 04:00 | 3.6671 | 0 | N/A | 0 | 0
2021-07-17 04:30 | 3.6316 | 0 | N/A | 0 | 0
2021-07-17 05:00 | 3.5976 | 0 | N/A | 0 | 0
2021-07-17 05:30 | 3.8181 | 0 | N/A | 0 | 0
2021-07-17 06:00 | 3.9943 | 0 | N/A | 0 | 0
2021-07-17 06:30 | 4.2936 | 0 | N/A | 0 | 0
2021-07-17 07:00 | 4.4807 | 0 | N/A | 0 | 0
2021-07-17 07:30 | 4.4058 | 0 | N/A | 0 | 0
2021-07-17 08:00 | 4.9726 | 0 | N/A | 0 | 0
2021-07-17 08:30 | 5.6911 | 0 | N/A | 0 | 0
2021-07-17 09:00 | 6.3911 | 0 | N/A | 0 | 0
2021-07-17 09:30 | 6.7601 | 0 | N/A | 0 | 0
2021-07-17 10:00 | 6.9621 | 0 | N/A | 0 | 0
2021-07-17 10:30 | 7.1004 | 0 | N/A | 0 | 0
2021-07-17 11:00 | 6.8692 | 0 | N/A | 0 | 0
2021-07-17 11:30 | 7.042 | 0 | N/A | 0 | 0
2021-07-17 12:00 | 8.0462 | 0 | N/A | 0 | 0
2021-07-17 12:30 | 7.5694 | 0 | N/A | 0 | 0
2021-07-17 13:00 | 7.7762 | 0 | N/A | 0 | 0
2021-07-17 13:30 | 7.902 | 0 | N/A | 0 | 0
2021-07-17 14:00 | 8.2276 | 0 | N/A | 0 | 0
2021-07-17 14:30 | 7.5747 | 0 | N/A | 0 | 0
2021-07-17 15:00 | 7.2984 | 0 | N/A | 0 | 0
2021-07-17 15:30 | 7.6043 | 0 | N/A | 0 | 0
2021-07-17 16:00 | 7.662 | 0 | N/A | 0 | 0
2021-07-17 16:30 | 7.2425 | 0 | N/A | 0 | 0
2021-07-17 17:00 | 7.9577 | 0 | N/A | 0 | 0
2021-07-17 17:30 | 8.4403 | 0 | N/A | 0 | 0
2021-07-17 18:00 | 9.19 | 0 | N/A | 0 | 0
2021-07-17 18:30 | 9.21 | 0 | N/A | 0 | 0
2021-07-17 19:00 | 9.0368 | 0 | N/A | 0 | 0
2021-07-17 19:30 | 8.5072 | 0 | N/A | 0 | 0
2021-07-17 20:00 | 7.9912 | 0 | N/A | 0 | 0
2021-07-17 20:30 | 7.5232 | 0 | N/A | 0 | 0
2021-07-17 21:00 | 7.1263 | 0 | N/A | 0 | 0
2021-07-17 21:30 | 7.3796 | 0 | N/A | 0 | 0
2021-07-17 22:00 | 7.4424 | 0 | N/A | 0 | 0
2021-07-17 22:30 | 7.1034 | 0 | N/A | 0 | 0
2021-07-17 23:00 | 7.0763 | 0 | N/A | 0 | 0
2021-07-17 23:30 | 7.095 | 0 | N/A | 0 | 0
2021-07-18 | 7.5085 | 0 | N/A | 0 | 0
2021-07-18 00:30 | 6.8162 | 0 | N/A | 0 | 0
2021-07-18 01:00 | 5.945 | 0 | N/A | 0 | 0
2021-07-18 01:30 | 5.7446 | 0 | N/A | 0 | 0
2021-07-18 02:00 | 5.2936 | 0 | N/A | 0 | 0
2021-07-18 02:30 | 4.7442 | 0 | N/A | 0 | 0
2021-07-18 03:00 | 4.3087 | 0 | N/A | 0 | 0
2021-07-18 03:30 | 4.0162 | 0 | N/A | 0 | 0
2021-07-18 04:00 | 3.769 | 0 | N/A | 0 | 0
2021-07-18 04:30 | 3.6204 | 0 | N/A | 0 | 0
2021-07-18 05:00 | 3.5324 | 0 | N/A | 0 | 0
2021-07-18 05:30 | 3.6535 | 0 | N/A | 0 | 0
2021-07-18 06:00 | 3.8552 | 0 | N/A | 0 | 0
2021-07-18 06:30 | 4.0681 | 0 | N/A | 0 | 0
2021-07-18 07:00 | 4.1754 | 0 | N/A | 0 | 0
2021-07-18 07:30 | 4.1409 | 0 | N/A | 0 | 0
2021-07-18 08:00 | 4.5248 | 0 | N/A | 0 | 0
2021-07-18 08:30 | 5.0945 | 0 | N/A | 0 | 0
2021-07-18 09:00 | 5.2604 | 0 | N/A | 0 | 0
2021-07-18 09:30 | 5.5735 | 0 | N/A | 0 | 0
2021-07-18 10:00 | 4.803 | 0 | N/A | 0 | 0
2021-07-18 10:30 | 5.1101 | 0 | N/A | 0 | 0
2021-07-18 11:00 | 5.007 | 0 | N/A | 0 | 0
2021-07-18 11:30 | 4.3111 | 0 | N/A | 0 | 0
2021-07-18 12:00 | 4.4501 | 0 | N/A | 0 | 0
2021-07-18 12:30 | 5.5329 | 0 | N/A | 0 | 0
2021-07-18 13:00 | 5.4054 | 0 | N/A | 0 | 0
2021-07-18 13:30 | 5.2243 | 0 | N/A | 0 | 0
2021-07-18 14:00 | 5.1031 | 0 | N/A | 0 | 0
2021-07-18 14:30 | 4.7767 | 0 | N/A | 0 | 0
2021-07-18 15:00 | 5.4925 | 0 | N/A | 0 | 0
2021-07-18 15:30 | 6.1459 | 0 | N/A | 0 | 0
2021-07-18 16:00 | 6.0184 | 0 | N/A | 0 | 0
2021-07-18 16:30 | 6.3631 | 0 | N/A | 0 | 0
2021-07-18 17:00 | 7.327 | 0 | N/A | 0 | 0
2021-07-18 17:30 | 8.2231 | 0 | N/A | 0 | 0
2021-07-18 18:00 | 8.9477 | 0 | N/A | 0 | 0
2021-07-18 18:30 | 9.0514 | 0 | N/A | 0 | 0
2021-07-18 19:00 | 8.6711 | 0 | N/A | 0 | 0
2021-07-18 19:30 | 8.0796 | 0 | N/A | 0 | 0
2021-07-18 20:00 | 7.5355 | 0 | N/A | 0 | 0
2021-07-18 20:30 | 7.0643 | 0 | N/A | 0 | 0
2021-07-18 21:00 | 6.7427 | 0 | N/A | 0 | 0
2021-07-18 21:30 | 7.0682 | 0 | N/A | 0 | 0
2021-07-18 22:00 | 7.0698 | 0 | N/A | 0 | 0
2021-07-18 22:30 | 6.5844 | 0 | N/A | 0 | 0
2021-07-18 23:00 | 6.5442 | 0 | N/A | 0 | 0
2021-07-18 23:30 | 6.6809 | 0 | N/A | 0 | 0
2021-07-19 | 6.9537 | 0 | N/A | 0 | 0
2021-07-19 00:30 | 6.3756 | 0 | N/A | 0 | 0
2021-07-19 01:00 | 5.6635 | 0 | N/A | 0 | 0
2021-07-19 01:30 | 5.5084 | 0 | N/A | 0 | 0
2021-07-19 02:00 | 5.1515 | 0 | N/A | 0 | 0
2021-07-19 02:30 | 4.5298 | 0 | N/A | 0 | 0
2021-07-19 03:00 | 4.1806 | 0 | N/A | 0 | 0
2021-07-19 03:30 | 3.8824 | 0 | N/A | 0 | 0
2021-07-19 04:00 | 3.6519 | 0 | N/A | 0 | 0
2021-07-19 04:30 | 3.5317 | 0 | N/A | 0 | 0
2021-07-19 05:00 | 3.6332 | 0 | N/A | 0 | 0
2021-07-19 05:30 | 3.9652 | 0 | N/A | 0 | 0
2021-07-19 06:00 | 4.4259 | 0 | N/A | 0 | 0
2021-07-19 06:30 | 5.078 | 0 | N/A | 0 | 0
2021-07-19 07:00 | 5.6475 | 0 | N/A | 0 | 0
2021-07-19 07:30 | 5.9583 | 0 | N/A | 0 | 0
2021-07-19 08:00 | 7.1242 | 0 | N/A | 0 | 0
2021-07-19 08:30 | 7.5112 | 0 | N/A | 0 | 0
2021-07-19 09:00 | 7.5488 | 0 | N/A | 0 | 0
2021-07-19 09:30 | 7.6927 | 0 | N/A | 0 | 0
2021-07-19 10:00 | 7.2334 | 0 | N/A | 0 | 0
2021-07-19 10:30 | 6.7743 | 0 | N/A | 0 | 0
2021-07-19 11:00 | 6.9445 | 0 | N/A | 0 | 0
2021-07-19 11:30 | 7.07 | 0 | N/A | 0 | 0
2021-07-19 12:00 | 7.212 | 0 | N/A | 0 | 0
2021-07-19 12:30 | 7.1715 | 0 | N/A | 0 | 0
2021-07-19 13:00 | 7.0945 | 0 | N/A | 0 | 0
2021-07-19 13:30 | 7.4613 | 0 | N/A | 0 | 0
2021-07-19 14:00 | 6.7494 | 0 | N/A | 0 | 0
2021-07-19 14:30 | 6.4029 | 0 | N/A | 0 | 0
2021-07-19 15:00 | 7.133 | 0 | N/A | 0 | 0
2021-07-19 15:30 | 6.9254 | 0 | N/A | 0 | 0
2021-07-19 16:00 | 6.6333 | 0 | N/A | 0 | 0
2021-07-19 16:30 | 6.0987 | 0 | N/A | 0 | 0
2021-07-19 17:00 | 6.6764 | 0 | N/A | 0 | 0
2021-07-19 17:30 | 7.7003 | 0 | N/A | 0 | 0
2021-07-19 18:00 | 8.5903 | 0 | N/A | 0 | 0
2021-07-19 18:30 | 8.9202 | 0 | N/A | 0 | 0
2021-07-19 19:00 | 8.7303 | 0 | N/A | 0 | 0
2021-07-19 19:30 | 8.3005 | 0 | N/A | 0 | 0
2021-07-19 20:00 | 7.841 | 0 | N/A | 0 | 0
2021-07-19 20:30 | 7.526 | 0 | N/A | 0 | 0
2021-07-19 21:00 | 7.1117 | 0 | N/A | 0 | 0
2021-07-19 21:30 | 7.2369 | 0 | N/A | 0 | 0
2021-07-19 22:00 | 7.2083 | 0 | N/A | 0 | 0
2021-07-19 22:30 | 6.5486 | 0 | N/A | 0 | 0
2021-07-19 23:00 | 6.3602 | 0 | N/A | 0 | 0
2021-07-19 23:30 | 6.4664 | 0 | N/A | 0 | 0
2021-07-20 | 6.8158 | 0 | N/A | 0 | 0
2021-07-20 00:30 | 6.2246 | 0 | N/A | 0 | 0
2021-07-20 01:00 | 5.3699 | 0 | N/A | 0 | 0
2021-07-20 01:30 | 5.2214 | 0 | N/A | 0 | 0
2021-07-20 02:00 | 4.869 | 0 | N/A | 0 | 0
2021-07-20 02:30 | 4.2598 | 0 | N/A | 0 | 0
2021-07-20 03:00 | 3.8701 | 0 | N/A | 0 | 0
2021-07-20 03:30 | 3.5831 | 0 | N/A | 0 | 0
2021-07-20 04:00 | 3.4036 | 0 | N/A | 0 | 0
2021-07-20 04:30 | 3.2706 | 0 | N/A | 0 | 0
2021-07-20 05:00 | 3.3586 | 0 | N/A | 0 | 0
2021-07-20 05:30 | 3.8484 | 0 | N/A | 0 | 0
2021-07-20 06:00 | 4.1985 | 0 | N/A | 0 | 0
2021-07-20 06:30 | 4.8621 | 0 | N/A | 0 | 0
2021-07-20 07:00 | 5.2959 | 0 | N/A | 0 | 0
2021-07-20 07:30 | 5.6285 | 0 | N/A | 0 | 0
2021-07-20 08:00 | 6.62 | 0 | N/A | 0 | 0
2021-07-20 08:30 | 7.5127 | 0 | N/A | 0 | 0
2021-07-20 09:00 | 7.4872 | 0 | N/A | 0 | 0
2021-07-20 09:30 | 7.0933 | 0 | N/A | 0 | 0
2021-07-20 10:00 | 7.02 | 0 | N/A | 0 | 0
2021-07-20 10:30 | 6.8733 | 0 | N/A | 0 | 0
2021-07-20 11:00 | 7.3767 | 0 | N/A | 0 | 0
2021-07-20 11:30 | 7.7535 | 0 | N/A | 0 | 0
2021-07-20 12:00 | 8.0574 | 0 | N/A | 0 | 0
2021-07-20 12:30 | 8.7872 | 0 | N/A | 0 | 0
2021-07-20 13:00 | 9.1602 | 0 | N/A | 0 | 0
2021-07-20 13:30 | 8.6968 | 0 | N/A | 0 | 0
2021-07-20 14:00 | 7.9767 | 0 | N/A | 0 | 0
2021-07-20 14:30 | 7.8533 | 0 | N/A | 0 | 0
2021-07-20 15:00 | 6.74 | 0 | N/A | 0 | 0
2021-07-20 15:30 | 6.9001 | 0 | N/A | 0 | 0
2021-07-20 16:00 | 6.9544 | 0 | N/A | 0 | 0
2021-07-20 16:30 | 7.4417 | 0 | N/A | 0 | 0
2021-07-20 17:00 | 8.4177 | 0 | N/A | 0 | 0
2021-07-20 17:30 | 9.5336 | 0 | N/A | 0 | 0
2021-07-20 18:00 | 10.4867 | 0 | N/A | 0 | 0
2021-07-20 18:30 | 11.0319 | 0 | N/A | 0 | 0
2021-07-20 19:00 | 10.7682 | 0 | N/A | 0 | 0
2021-07-20 19:30 | 10.2136 | 0 | N/A | 0 | 0
2021-07-20 20:00 | 9.7167 | 0 | N/A | 0 | 0
2021-07-20 20:30 | 9.2301 | 0 | N/A | 0 | 0
2021-07-20 21:00 | 8.8009 | 0 | N/A | 0 | 0
2021-07-20 21:30 | 9.0477 | 0 | N/A | 0 | 0
2021-07-20 22:00 | 8.9258 | 0 | N/A | 0 | 0
2021-07-20 22:30 | 8.2262 | 0 | N/A | 0 | 0
2021-07-20 23:00 | 8.0515 | 0 | N/A | 0 | 0
2021-07-20 23:30 | 7.9883 | 0 | N/A | 0 | 0
2021-07-21 | 8.3381 | 0 | N/A | 0 | 0
2021-07-21 00:30 | 7.7944 | 0 | N/A | 0 | 0
2021-07-21 01:00 | 7.1098 | 0 | N/A | 0 | 0
2021-07-21 01:30 | 6.9666 | 0 | N/A | 0 | 0
2021-07-21 02:00 | 6.3974 | 0 | N/A | 0 | 0
2021-07-21 02:30 | 5.746 | 0 | N/A | 0 | 0
2021-07-21 03:00 | 5.4457 | 0 | N/A | 0 | 0
2021-07-21 03:30 | 5.1914 | 0 | N/A | 0 | 0
2021-07-21 04:00 | 5.0649 | 0 | N/A | 0 | 0
2021-07-21 04:30 | 4.9548 | 0 | N/A | 0 | 0
2021-07-21 05:00 | 4.9645 | 0 | N/A | 0 | 0
2021-07-21 05:30 | 5.3729 | 0 | N/A | 0 | 0
2021-07-21 06:00 | 5.9573 | 0 | N/A | 0 | 0
2021-07-21 06:30 | 6.8243 | 0 | N/A | 0 | 0
2021-07-21 07:00 | 7.3234 | 0 | N/A | 0 | 0
2021-07-21 07:30 | 7.3391 | 0 | N/A | 0 | 0
2021-07-21 08:00 | 8.1739 | 0 | N/A | 0 | 0
2021-07-21 08:30 | 8.7568 | 0 | N/A | 0 | 0
2021-07-21 09:00 | 9.1039 | 0 | N/A | 0 | 0
2021-07-21 09:30 | 8.7235 | 0 | N/A | 0 | 0
2021-07-21 10:00 | 8.4667 | 0 | N/A | 0 | 0
2021-07-21 10:30 | 8.45 | 0 | N/A | 0 | 0
2021-07-21 11:00 | 8.3968 | 0 | N/A | 0 | 0
2021-07-21 11:30 | 8.0434 | 0 | N/A | 0 | 0
2021-07-21 12:00 | 8.0334 | 0 | N/A | 0 | 0
2021-07-21 12:30 | 7.3767 | 0 | N/A | 0 | 0
2021-07-21 13:00 | 6.7968 | 0 | N/A | 0 | 0
2021-07-21 13:30 | 6.98 | 0 | N/A | 0 | 0
2021-07-21 14:00 | 7.4267 | 0 | N/A | 0 | 0
2021-07-21 14:30 | 7.23 | 0 | N/A | 0 | 0
2021-07-21 15:00 | 7.1567 | 0 | N/A | 0 | 0
2021-07-21 15:30 | 7.297 | 0 | N/A | 0 | 0
2021-07-21 16:00 | 6.7168 | 0 | N/A | 0 | 0
2021-07-21 16:30 | 6.8909 | 0 | N/A | 0 | 0
2021-07-21 17:00 | 7.5602 | 0 | N/A | 0 | 0
2021-07-21 17:30 | 8.5163 | 0 | N/A | 0 | 0
2021-07-21 18:00 | 9.5242 | 0 | N/A | 0 | 0
2021-07-21 18:30 | 9.8067 | 0 | N/A | 0 | 0
2021-07-21 19:00 | 8.9567 | 0 | N/A | 0 | 0
2021-07-21 19:30 | 8.4533 | 0 | N/A | 0 | 0
2021-07-21 20:00 | 7.9673 | 0 | N/A | 0 | 0
2021-07-21 20:30 | 7.5489 | 0 | N/A | 0 | 0
2021-07-21 21:00 | 7.1412 | 0 | N/A | 0 | 0
2021-07-21 21:30 | 7.2782 | 0 | N/A | 0 | 0
2021-07-21 22:00 | 7.3497 | 0 | N/A | 0 | 0
2021-07-21 22:30 | 6.6861 | 0 | N/A | 0 | 0
2021-07-21 23:00 | 6.6406 | 0 | N/A | 0 | 0
2021-07-21 23:30 | 6.6662 | 0 | N/A | 0 | 0
2021-07-22 | 6.988 | 0 | N/A | 0 | 0
2021-07-22 00:30 | 6.3974 | 0 | N/A | 0 | 0
2021-07-22 01:00 | 5.5734 | 0 | N/A | 0 | 0
2021-07-22 01:30 | 5.3302 | 0 | N/A | 0 | 0
2021-07-22 02:00 | 4.9787 | 0 | N/A | 0 | 0
2021-07-22 02:30 | 4.4483 | 0 | N/A | 0 | 0
2021-07-22 03:00 | 4.1825 | 0 | N/A | 0 | 0
2021-07-22 03:30 | 3.9443 | 0 | N/A | 0 | 0
2021-07-22 04:00 | 3.7683 | 0 | N/A | 0 | 0
2021-07-22 04:30 | 3.7189 | 0 | N/A | 0 | 0
2021-07-22 05:00 | 3.7554 | 0 | N/A | 0 | 0
2021-07-22 05:30 | 4.2931 | 0 | N/A | 0 | 0
2021-07-22 06:00 | 4.7954 | 0 | N/A | 0 | 0
2021-07-22 06:30 | 5.5424 | 0 | N/A | 0 | 0
2021-07-22 07:00 | 6.0724 | 0 | N/A | 0 | 0
2021-07-22 07:30 | 6.3234 | 0 | N/A | 0 | 0
2021-07-22 08:00 | 7.2537 | 0 | N/A | 0 | 0
2021-07-22 08:30 | 8.1207 | 0 | N/A | 0 | 0
2021-07-22 09:00 | 8.3787 | 0 | N/A | 0 | 0
2021-07-22 09:30 | 8.2831 | 0 | N/A | 0 | 0
2021-07-22 10:00 | 7.751 | 0 | N/A | 0 | 0
2021-07-22 10:30 | 7.2033 | 0 | N/A | 0 | 0
2021-07-22 11:00 | 7.0067 | 0 | N/A | 0 | 0
2021-07-22 11:30 | 6.6403 | 0 | N/A | 0 | 0
2021-07-22 12:00 | 7.427 | 0 | N/A | 0 | 0
2021-07-22 12:30 | 7.361 | 0 | N/A | 0 | 0
2021-07-22 13:00 | 6.8939 | 0 | N/A | 0 | 0
2021-07-22 13:30 | 6.8872 | 0 | N/A | 0 | 0
2021-07-22 14:00 | 6.9194 | 0 | N/A | 0 | 0
2021-07-22 14:30 | 7.7812 | 0 | N/A | 0 | 0
2021-07-22 15:00 | 7.7041 | 0 | N/A | 0 | 0
2021-07-22 15:30 | 7.6535 | 0 | N/A | 0 | 0
2021-07-22 16:00 | 7.5133 | 0 | N/A | 0 | 0
2021-07-22 16:30 | 7.481 | 0 | N/A | 0 | 0
2021-07-22 17:00 | 7.9973 | 0 | N/A | 0 | 0
2021-07-22 17:30 | 8.7335 | 0 | N/A | 0 | 0
2021-07-22 18:00 | 9.59 | 0 | N/A | 0 | 0
2021-07-22 18:30 | 9.831 | 0 | N/A | 0 | 0
2021-07-22 19:00 | 9.6875 | 0 | N/A | 0 | 0
2021-07-22 19:30 | 9.1267 | 0 | N/A | 0 | 0
2021-07-22 20:00 | 8.6467 | 0 | N/A | 0 | 0
2021-07-22 20:30 | 8.2005 | 0 | N/A | 0 | 0
2021-07-22 21:00 | 7.7884 | 0 | N/A | 0 | 0
2021-07-22 21:30 | 7.9189 | 0 | N/A | 0 | 0
2021-07-22 22:00 | 7.7649 | 0 | N/A | 0 | 0
2021-07-22 22:30 | 7.2013 | 0 | N/A | 0 | 0
2021-07-22 23:00 | 6.9407 | 0 | N/A | 0 | 0
2021-07-22 23:30 | 7.0917 | 0 | N/A | 0 | 0
2021-07-23 | 7.4074 | 0 | N/A | 0 | 0
2021-07-23 00:30 | 6.8037 | 0 | N/A | 0 | 0
2021-07-23 01:00 | 6.013 | 0 | N/A | 0 | 0
2021-07-23 01:30 | 5.8956 | 0 | N/A | 0 | 0
2021-07-23 02:00 | 5.4472 | 0 | N/A | 0 | 0
2021-07-23 02:30 | 4.7692 | 0 | N/A | 0 | 0
2021-07-23 03:00 | 4.4254 | 0 | N/A | 0 | 0
2021-07-23 03:30 | 4.1073 | 0 | N/A | 0 | 0
2021-07-23 04:00 | 3.8541 | 0 | N/A | 0 | 0
2021-07-23 04:30 | 3.7639 | 0 | N/A | 0 | 0
2021-07-23 05:00 | 3.9257 | 0 | N/A | 0 | 0
2021-07-23 05:30 | 4.2796 | 0 | N/A | 0 | 0
2021-07-23 06:00 | 4.7586 | 0 | N/A | 0 | 0
2021-07-23 06:30 | 5.433 | 0 | N/A | 0 | 0
2021-07-23 07:00 | 5.9315 | 0 | N/A | 0 | 0
2021-07-23 07:30 | 6.3667 | 0 | N/A | 0 | 0
2021-07-23 08:00 | 7.2435 | 0 | N/A | 0 | 0
2021-07-23 08:30 | 7.8187 | 0 | N/A | 0 | 0
2021-07-23 09:00 | 8.0968 | 0 | N/A | 0 | 0
2021-07-23 09:30 | 7.8355 | 0 | N/A | 0 | 0
2021-07-23 10:00 | 7.14 | 0 | N/A | 0 | 0
2021-07-23 10:30 | 7.4793 | 0 | N/A | 0 | 0
2021-07-23 11:00 | 7.6192 | 0 | N/A | 0 | 0
2021-07-23 11:30 | 7.6612 | 0 | N/A | 0 | 0
2021-07-23 12:00 | 7.5822 | 0 | N/A | 0 | 0
2021-07-23 12:30 | 7.2411 | 0 | N/A | 0 | 0
2021-07-23 13:00 | 6.6095 | 0 | N/A | 0 | 0
2021-07-23 13:30 | 6.5367 | 0 | N/A | 0 | 0
2021-07-23 14:00 | 6.4033 | 0 | N/A | 0 | 0
2021-07-23 14:30 | 6.5674 | 0 | N/A | 0 | 0
2021-07-23 15:00 | 6.8678 | 0 | N/A | 0 | 0
2021-07-23 15:30 | 6.76 | 0 | N/A | 0 | 0
2021-07-23 16:00 | 6.8824 | 0 | N/A | 0 | 0
2021-07-23 16:30 | 6.9328 | 0 | N/A | 0 | 0
2021-07-23 17:00 | 7.5048 | 0 | N/A | 0 | 0
2021-07-23 17:30 | 7.998 | 0 | N/A | 0 | 0
2021-07-23 18:00 | 8.5642 | 0 | N/A | 0 | 0
2021-07-23 18:30 | 8.9901 | 0 | N/A | 0 | 0
2021-07-23 19:00 | 8.697 | 0 | N/A | 0 | 0
2021-07-23 19:30 | 8.4868 | 0 | N/A | 0 | 0
2021-07-23 20:00 | 8.1671 | 0 | N/A | 0 | 0
2021-07-23 20:30 | 7.788 | 0 | N/A | 0 | 0
2021-07-23 21:00 | 7.45 | 0 | N/A | 0 | 0
2021-07-23 21:30 | 7.5838 | 0 | N/A | 0 | 0
2021-07-23 22:00 | 7.734 | 0 | N/A | 0 | 0
2021-07-23 22:30 | 8.0071 | 0 | N/A | 0 | 0
2021-07-23 23:00 | 8.5907 | 0 | N/A | 0 | 0
2021-07-23 23:30 | 8.6794 | 0 | N/A | 0 | 0
2021-07-24 | 9.0802 | 0 | N/A | 0 | 0
2021-07-24 00:30 | 8.3719 | 0 | N/A | 0 | 0
2021-07-24 01:00 | 7.5721 | 0 | N/A | 0 | 0
2021-07-24 01:30 | 7.2389 | 0 | N/A | 0 | 0
2021-07-24 02:00 | 6.8177 | 0 | N/A | 0 | 0
2021-07-24 02:30 | 5.6173 | 0 | N/A | 0 | 0
2021-07-24 03:00 | 4.4111 | 0 | N/A | 0 | 0
2021-07-24 03:30 | 3.9818 | 0 | N/A | 0 | 0
2021-07-24 04:00 | 3.7751 | 0 | N/A | 0 | 0
2021-07-24 04:30 | 3.6761 | 0 | N/A | 0 | 0
2021-07-24 05:00 | 3.6154 | 0 | N/A | 0 | 0
2021-07-24 05:30 | 3.6917 | 0 | N/A | 0 | 0
2021-07-24 06:00 | 3.9706 | 0 | N/A | 0 | 0
2021-07-24 06:30 | 4.2155 | 0 | N/A | 0 | 0
2021-07-24 07:00 | 4.412 | 0 | N/A | 0 | 0
2021-07-24 07:30 | 4.36 | 0 | N/A | 0 | 0
2021-07-24 08:00 | 4.8734 | 0 | N/A | 0 | 0
2021-07-24 08:30 | 5.675 | 0 | N/A | 0 | 0
2021-07-24 09:00 | 6.277 | 0 | N/A | 0 | 0
2021-07-24 09:30 | 6.4138 | 0 | N/A | 0 | 0
2021-07-24 10:00 | 7.1479 | 0 | N/A | 0 | 0
2021-07-24 10:30 | 7.1502 | 0 | N/A | 0 | 0
2021-07-24 11:00 | 6.76 | 0 | N/A | 0 | 0
2021-07-24 11:30 | 5.5669 | 0 | N/A | 0 | 0
2021-07-24 12:00 | 5.1026 | 0 | N/A | 0 | 0
2021-07-24 12:30 | 4.1416 | 0 | N/A | 0 | 0
2021-07-24 13:00 | 4.1285 | 0 | N/A | 0 | 0
2021-07-24 13:30 | 4.9258 | 0 | N/A | 0 | 0
2021-07-24 14:00 | 4.4527 | 0 | N/A | 0 | 0
2021-07-24 14:30 | 4.0196 | 0 | N/A | 0 | 0
2021-07-24 15:00 | 5.7086 | 0 | N/A | 0 | 0
2021-07-24 15:30 | 6.2265 | 0 | N/A | 0 | 0
2021-07-24 16:00 | 6.3505 | 0 | N/A | 0 | 0
2021-07-25 00:30 | 7.1311 | 0 | N/A | 0 | 0
2021-07-25 01:00 | 6.3952 | 0 | N/A | 0 | 0
2021-07-25 01:30 | 6.1454 | 0 | N/A | 0 | 0
2021-07-25 02:00 | 5.7395 | 0 | N/A | 0 | 0
2021-07-25 02:30 | 5.1185 | 0 | N/A | 0 | 0
2021-07-25 03:00 | 4.698 | 0 | N/A | 0 | 0
2021-07-25 03:30 | 4.4591 | 0 | N/A | 0 | 0
2021-07-25 04:00 | 4.1589 | 0 | N/A | 0 | 0
2021-07-25 04:30 | 4.1618 | 0 | N/A | 0 | 0
2021-07-25 05:00 | 4.138 | 0 | N/A | 0 | 0
2021-07-25 05:30 | 4.1152 | 0 | N/A | 0 | 0
2021-07-25 06:00 | 4.3394 | 0 | N/A | 0 | 0
2021-07-25 06:30 | 4.7303 | 0 | N/A | 0 | 0
2021-07-25 07:00 | 4.8205 | 0 | N/A | 0 | 0
2021-07-25 07:30 | 4.7576 | 0 | N/A | 0 | 0
2021-07-25 08:00 | 5.2513 | 0 | N/A | 0 | 0
2021-07-25 08:30 | 5.6943 | 0 | N/A | 0 | 0
2021-07-25 09:00 | 5.6659 | 0 | N/A | 0 | 0
2021-07-25 09:30 | 5.4582 | 0 | N/A | 0 | 0
2021-07-25 10:00 | 5.1008 | 0 | N/A | 0 | 0
2021-07-25 10:30 | 5.5305 | 0 | N/A | 0 | 0
2021-07-25 11:00 | 4.8127 | 0 | N/A | 0 | 0
2021-07-25 11:30 | 4.3186 | 0 | N/A | 0 | 0
2021-07-25 12:00 | 5.1555 | 0 | N/A | 0 | 0
2021-07-25 12:30 | 5.5398 | 0 | N/A | 0 | 0
2021-07-25 13:00 | 5.6802 | 0 | N/A | 0 | 0
2021-07-25 13:30 | 5.6178 | 0 | N/A | 0 | 0
2021-07-25 14:00 | 5.4245 | 0 | N/A | 0 | 0
2021-07-25 14:30 | 5.8517 | 0 | N/A | 0 | 0
2021-07-25 15:00 | 5.6644 | 0 | N/A | 0 | 0
2021-07-25 15:30 | 6.4453 | 0 | N/A | 0 | 0
2021-07-25 16:00 | 6.6892 | 0 | N/A | 0 | 0
2021-07-25 16:30 | 6.9748 | 0 | N/A | 0 | 0
2021-07-25 17:00 | 7.7337 | 0 | N/A | 0 | 0
2021-07-25 17:30 | 8.6516 | 0 | N/A | 0 | 0
2021-07-25 18:00 | 9.3767 | 0 | N/A | 0 | 0
2021-07-25 18:30 | 9.63 | 0 | N/A | 0 | 0
2021-07-25 19:00 | 9.1167 | 0 | N/A | 0 | 0
2021-07-25 19:30 | 8.5494 | 0 | N/A | 0 | 0
2021-07-26 00:30 | 6.5261 | 0 | N/A | 0 | 0
2021-07-26 01:00 | 5.7518 | 0 | N/A | 0 | 0
2021-07-26 01:30 | 5.6508 | 0 | N/A | 0 | 0
2021-07-26 02:00 | 5.377 | 0 | N/A | 0 | 0
2021-07-26 02:30 | 4.773 | 0 | N/A | 0 | 0
2021-07-26 03:00 | 4.4244 | 0 | N/A | 0 | 0
2021-07-26 03:30 | 4.0447 | 0 | N/A | 0 | 0
2021-07-26 04:00 | 3.7294 | 0 | N/A | 0 | 0
2021-07-26 04:30 | 3.548 | 0 | N/A | 0 | 0
2021-07-26 05:00 | 3.5624 | 0 | N/A | 0 | 0
2021-07-26 05:30 | 3.9641 | 0 | N/A | 0 | 0
2021-07-26 06:00 | 4.3663 | 0 | N/A | 0 | 0
2021-07-26 06:30 | 4.9978 | 0 | N/A | 0 | 0
2021-07-26 07:00 | 5.4712 | 0 | N/A | 0 | 0
2021-07-26 07:30 | 5.7369 | 0 | N/A | 0 | 0
2021-07-26 08:00 | 6.7001 | 0 | N/A | 0 | 0
2021-07-26 08:30 | 7.2611 | 0 | N/A | 0 | 0
2021-07-26 09:00 | 7.5563 | 0 | N/A | 0 | 0
2021-07-26 09:30 | 7.589 | 0 | N/A | 0 | 0
2021-07-26 10:00 | 6.9817 | 0 | N/A | 0 | 0
2021-07-26 10:30 | 6.1936 | 0 | N/A | 0 | 0
2021-07-26 11:00 | 6.8143 | 0 | N/A | 0 | 0
2021-07-26 11:30 | 6.4623 | 0 | N/A | 0 | 0
2021-07-26 12:00 | 6.1326 | 0 | N/A | 0 | 0
2021-07-26 12:30 | 5.494 | 0 | N/A | 0 | 0
2021-07-26 13:00 | 5.0433 | 0 | N/A | 0 | 0
2021-07-26 13:30 | 5.2269 | 0 | N/A | 0 | 0
2021-07-26 14:00 | 6.0642 | 0 | N/A | 0 | 0
2021-07-26 14:30 | 6.2667 | 0 | N/A | 0 | 0
2021-07-26 15:00 | 5.16 | 0 | N/A | 0 | 0
2021-07-26 15:30 | 5.245 | 0 | N/A | 0 | 0
2021-07-26 16:00 | 5.3695 | 0 | N/A | 0 | 0
2021-07-27 00:30 | 6.0255 | 0 | N/A | 0 | 0
2021-07-27 01:00 | 5.3344 | 0 | N/A | 0 | 0
2021-07-27 01:30 | 5.0795 | 0 | N/A | 0 | 0
2021-07-27 02:00 | 4.7627 | 0 | N/A | 0 | 0
2021-07-27 02:30 | 4.0845 | 0 | N/A | 0 | 0
2021-07-27 03:00 | 3.6923 | 0 | N/A | 0 | 0
2021-07-27 03:30 | 3.5001 | 0 | N/A | 0 | 0
2021-07-27 04:00 | 3.3168 | 0 | N/A | 0 | 0
2021-07-27 04:30 | 3.3081 | 0 | N/A | 0 | 0
2021-07-27 05:00 | 3.3379 | 0 | N/A | 0 | 0
2021-07-27 05:30 | 3.8274 | 0 | N/A | 0 | 0
2021-07-27 06:00 | 4.358 | 0 | N/A | 0 | 0
2021-07-27 06:30 | 5.1533 | 0 | N/A | 0 | 0
2021-07-27 07:00 | 5.5116 | 0 | N/A | 0 | 0
2021-07-27 07:30 | 5.7072 | 0 | N/A | 0 | 0
2021-07-27 08:00 | 6.4801 | 0 | N/A | 0 | 0
2021-07-27 08:30 | 7.001 | 0 | N/A | 0 | 0
2021-07-27 09:00 | 6.9322 | 0 | N/A | 0 | 0
2021-07-27 09:30 | 6.0564 | 0 | N/A | 0 | 0
2021-07-27 10:00 | 5.7205 | 0 | N/A | 0 | 0
2021-07-27 10:30 | 5.0736 | 0 | N/A | 0 | 0
2021-07-27 11:00 | 4.6449 | 0 | N/A | 0 | 0
2021-07-27 11:30 | 5.1018 | 0 | N/A | 0 | 0
2021-07-27 12:00 | 4.9783 | 0 | N/A | 0 | 0
2021-07-27 12:30 | 4.1374 | 0 | N/A | 0 | 0
2021-07-27 13:00 | 4.6146 | 0 | N/A | 0 | 0
2021-07-27 13:30 | 4.7201 | 0 | N/A | 0 | 0
2021-07-27 14:00 | 4.0813 | 0 | N/A | 0 | 0
2021-07-27 14:30 | 3.504 | 0 | N/A | 0 | 0
2021-07-27 15:00 | 3.4262 | 0 | N/A | 0 | 0
2021-07-27 15:30 | 4.2039 | 0 | N/A | 0 | 0
2021-07-27 16:00 | 3.8104 | 0 | N/A | 0 | 0
2021-07-27 16:30 | 4.6373 | 0 | N/A | 0 | 0
2021-07-27 17:00 | 5.5554 | 0 | N/A | 0 | 0
2021-07-27 17:30 | 7.0595 | 0 | N/A | 0 | 0
2021-07-27 18:00 | 7.8412 | 0 | N/A | 0 | 0
2021-07-28 00:30 | 5.8612 | 0 | N/A | 0 | 0
2021-07-28 01:00 | 5.1006 | 0 | N/A | 0 | 0
2021-07-28 01:30 | 4.9591 | 0 | N/A | 0 | 0
2021-07-28 02:00 | 4.6268 | 0 | N/A | 0 | 0
2021-07-28 02:30 | 4.2068 | 0 | N/A | 0 | 0
2021-07-28 03:00 | 3.7457 | 0 | N/A | 0 | 0
2021-07-28 03:30 | 3.4042 | 0 | N/A | 0 | 0
2021-07-28 04:00 | 3.2678 | 0 | N/A | 0 | 0
2021-07-28 04:30 | 3.1535 | 0 | N/A | 0 | 0
2021-07-28 05:00 | 3.217 | 0 | N/A | 0 | 0
2021-07-28 05:30 | 3.504 | 0 | N/A | 0 | 0
2021-07-28 06:00 | 3.9367 | 0 | N/A | 0 | 0
2021-07-28 06:30 | 4.6271 | 0 | N/A | 0 | 0
2021-07-28 07:00 | 5.3833 | 0 | N/A | 0 | 0
2021-07-28 07:30 | 5.8564 | 0 | N/A | 0 | 0
2021-07-28 08:00 | 6.691 | 0 | N/A | 0 | 0
2021-07-28 08:30 | 7.3372 | 0 | N/A | 0 | 0
2021-07-28 09:00 | 7.2341 | 0 | N/A | 0 | 0
2021-07-28 09:30 | 6.1301 | 0 | N/A | 0 | 0
2021-07-28 10:00 | 4.8315 | 0 | N/A | 0 | 0
2021-07-28 10:30 | 4.3784 | 0 | N/A | 0 | 0
2021-07-28 11:00 | 3.1021 | 0 | N/A | 0 | 0
2021-07-28 11:30 | 3.5248 | 0 | N/A | 0 | 0
2021-07-28 12:00 | 4.0728 | 0 | N/A | 0 | 0
2021-07-28 12:30 | 3.8359 | 0 | N/A | 0 | 0
2021-07-28 13:00 | 3.204 | 0 | N/A | 0 | 0
2021-07-29 00:30 | 6.8084 | 0 | N/A | 0 | 0
2021-07-29 01:00 | 5.9844 | 0 | N/A | 0 | 0
2021-07-29 01:30 | 5.7983 | 0 | N/A | 0 | 0
2021-07-29 02:00 | 5.425 | 0 | N/A | 0 | 0
2021-07-29 02:30 | 4.8492 | 0 | N/A | 0 | 0
2021-07-29 03:00 | 4.4859 | 0 | N/A | 0 | 0
2021-07-29 03:30 | 4.3172 | 0 | N/A | 0 | 0
2021-07-29 04:00 | 4.1224 | 0 | N/A | 0 | 0
2021-07-29 04:30 | 4.0454 | 0 | N/A | 0 | 0
2021-07-29 05:00 | 4.1043 | 0 | N/A | 0 | 0
2021-07-29 05:30 | 4.4835 | 0 | N/A | 0 | 0
2021-07-29 06:00 | 5.0329 | 0 | N/A | 0 | 0
2021-07-29 06:30 | 5.8283 | 0 | N/A | 0 | 0
2021-07-29 07:00 | 6.6362 | 0 | N/A | 0 | 0
2021-07-29 07:30 | 7.142 | 0 | N/A | 0 | 0
2021-07-29 08:00 | 7.9068 | 0 | N/A | 0 | 0
2021-07-29 08:30 | 8.0337 | 0 | N/A | 0 | 0
2021-07-29 09:00 | 7.1069 | 0 | N/A | 0 | 0
2021-07-29 09:30 | 6.14 | 0 | N/A | 0 | 0
2021-07-29 10:00 | 5.1534 | 0 | N/A | 0 | 0
2021-07-29 10:30 | 4.4968 | 0 | N/A | 0 | 0
2021-07-29 11:00 | 3.637 | 0 | N/A | 0 | 0
2021-07-29 11:30 | 3.0301 | 0 | N/A | 0 | 0
2021-07-29 12:00 | 3.3904 | 0 | N/A | 0 | 0
2021-07-30 00:30 | 6.5026 | 0 | N/A | 0 | 0
2021-07-30 01:00 | 5.5769 | 0 | N/A | 0 | 0
2021-07-30 01:30 | 5.54 | 0 | N/A | 0 | 0
2021-07-30 02:00 | 5.1976 | 0 | N/A | 0 | 0
2021-07-30 02:30 | 4.6362 | 0 | N/A | 0 | 0
2021-07-30 03:00 | 4.2727 | 0 | N/A | 0 | 0
2021-07-30 03:30 | 4.0548 | 0 | N/A | 0 | 0
2021-07-30 04:00 | 3.932 | 0 | N/A | 0 | 0
2021-07-30 04:30 | 3.9305 | 0 | N/A | 0 | 0
2021-07-30 05:00 | 3.9945 | 0 | N/A | 0 | 0
2021-07-30 05:30 | 4.3119 | 0 | N/A | 0 | 0
2021-07-30 06:00 | 4.8498 | 0 | N/A | 0 | 0
2021-07-30 06:30 | 5.7795 | 0 | N/A | 0 | 0
2021-07-30 07:00 | 6.5873 | 0 | N/A | 0 | 0
2021-07-30 07:30 | 6.937 | 0 | N/A | 0 | 0
2021-07-30 08:00 | 7.557 | 0 | N/A | 0 | 0
2021-07-30 08:30 | 7.5934 | 0 | N/A | 0 | 0
2021-07-30 09:00 | 6.9342 | 0 | N/A | 0 | 0
2021-07-30 09:30 | 6.3507 | 0 | N/A | 0 | 0
2021-07-30 10:00 | 5.7636 | 0 | N/A | 0 | 0
2021-07-30 10:30 | 4.3175 | 0 | N/A | 0 | 0
2021-07-30 11:00 | 3.7035 | 0 | N/A | 0 | 0
2021-07-30 11:30 | 4.6303 | 0 | N/A | 0 | 0
2021-07-30 12:00 | 4.8602 | 0 | N/A | 0 | 0
2021-07-30 12:30 | 4.8744 | 0 | N/A | 0 | 0
2021-07-30 13:00 | 4.7002 | 0 | N/A | 0 | 0
2021-07-30 13:30 | 3.8861 | 0 | N/A | 0 | 0
2021-07-30 14:00 | 4.1262 | 0 | N/A | 0 | 0
2021-07-30 14:30 | 5.2168 | 0 | N/A | 0 | 0
2021-07-30 15:00 | 5.3634 | 0 | N/A | 0 | 0
2021-07-30 15:30 | 5.3298 | 0 | N/A | 0 | 0
2021-07-30 16:00 | 5.6397 | 0 | N/A | 0 | 0
2021-07-30 16:30 | 5.5897 | 0 | N/A | 0 | 0
2021-07-30 17:00 | 6.5615 | 0 | N/A | 0 | 0
2021-07-30 17:30 | 7.3992 | 0 | N/A | 0 | 0
2021-07-30 18:00 | 8.2075 | 0 | N/A | 0 | 0
2021-07-30 18:30 | 8.6304 | 0 | N/A | 0 | 0
2021-07-30 19:00 | 8.6435 | 0 | N/A | 0 | 0
2021-07-30 19:30 | 8.4535 | 0 | N/A | 0 | 0
2021-07-30 20:00 | 8.0606 | 0 | N/A | 0 | 0
2021-07-30 20:30 | 7.8074 | 0 | N/A | 0 | 0
2021-07-30 21:00 | 7.5283 | 0 | N/A | 0 | 0
2021-07-30 21:30 | 7.7499 | 0 | N/A | 0 | 0
2021-07-30 22:00 | 7.8306 | 0 | N/A | 0 | 0
2021-07-30 22:30 | 7.3341 | 0 | N/A | 0 | 0
2021-07-30 23:00 | 7.1535 | 0 | N/A | 0 | 0
2021-07-30 23:30 | 7.1751 | 0 | N/A | 0 | 0
2021-07-31 | 7.4555 | 0 | N/A | 0 | 0
2021-07-31 00:30 | 6.802 | 0 | N/A | 0 | 0
2021-07-31 01:00 | 5.9058 | 0 | N/A | 0 | 0
2021-07-31 01:30 | 5.6725 | 0 | N/A | 0 | 0
2021-07-31 02:00 | 5.2907 | 0 | N/A | 0 | 0
2021-07-31 02:30 | 4.6859 | 0 | N/A | 0 | 0
2021-07-31 03:00 | 4.2539 | 0 | N/A | 0 | 0
2021-07-31 03:30 | 3.9727 | 0 | N/A | 0 | 0
2021-07-31 04:00 | 3.7814 | 0 | N/A | 0 | 0
2021-07-31 04:30 | 3.6761 | 0 | N/A | 0 | 0
2021-07-31 05:00 | 3.6332 | 0 | N/A | 0 | 0
2021-07-31 05:30 | 3.7352 | 0 | N/A | 0 | 0
2021-07-31 06:00 | 3.9224 | 0 | N/A | 0 | 0
2021-07-31 06:30 | 4.3216 | 0 | N/A | 0 | 0
2021-07-31 07:00 | 4.567 | 0 | N/A | 0 | 0
2021-07-31 07:30 | 4.5886 | 0 | N/A | 0 | 0
2021-07-31 08:00 | 5.1011 | 0 | N/A | 0 | 0
2021-07-31 08:30 | 5.32 | 0 | N/A | 0 | 0
2021-07-31 09:00 | 5.1215 | 0 | N/A | 0 | 0
2021-07-31 09:30 | 4.4897 | 0 | N/A | 0 | 0
2021-07-31 10:00 | 3.7578 | 0 | N/A | 0 | 0
2021-07-31 10:30 | 2.9961 | 0 | N/A | 0 | 0
2021-07-31 11:00 | 2.3081 | 0 | N/A | 0 | 0
2021-07-31 11:30 | 1.6855 | 0 | N/A | 0 | 0
2021-07-31 12:00 | 1.4125 | 0 | N/A | 0 | 0
2021-07-31 12:30 | 2.2999 | 0 | N/A | 0 | 0
2021-07-31 13:00 | 2.1635 | 0 | N/A | 0 | 0
2021-07-31 13:30 | 2.6103 | 0 | N/A | 0 | 0
2021-07-31 14:00 | 3.6828 | 0 | N/A | 0 | 0
2021-07-31 14:30 | 3.579 | 0 | N/A | 0 | 0
2021-07-31 15:00 | 2.8195 | 0 | N/A | 0 | 0
2021-07-31 15:30 | 4.5114 | 0 | N/A | 0 | 0
2021-07-31 16:00 | 5.642 | 0 | N/A | 0 | 0
2021-07-31 16:30 | 6.283 | 0 | N/A | 0 | 0
2021-07-31 17:00 | 6.8026 | 0 | N/A | 0 | 0
2021-07-31 17:30 | 7.2906 | 0 | N/A | 0 | 0
2021-07-31 18:00 | 8.0379 | 0 | N/A | 0 | 0
2021-07-31 18:30 | 8.1535 | 0 | N/A | 0 | 0
2021-07-31 19:00 | 7.7745 | 0 | N/A | 0 | 0
2021-07-31 19:30 | 7.5505 | 0 | N/A | 0 | 0
2021-08-01 00:30 | 6.3643 | 0 | N/A | 0 | 0
2021-08-01 01:00 | 5.5132 | 0 | N/A | 0 | 0
2021-08-01 01:30 | 5.2728 | 0 | N/A | 0 | 0
2021-08-01 02:00 | 4.9309 | 0 | N/A | 0 | 0
2021-08-01 02:30 | 4.3375 | 0 | N/A | 0 | 0
2021-08-01 03:00 | 4.1091 | 0 | N/A | 0 | 0
2021-08-01 03:30 | 3.9048 | 0 | N/A | 0 | 0
2021-08-01 04:00 | 3.7011 | 0 | N/A | 0 | 0
2021-08-02 00:30 | 6.4538 | 0 | N/A | 0 | 0
2021-08-02 01:00 | 5.7987 | 0 | N/A | 0 | 0
2021-08-02 01:30 | 5.6684 | 0 | N/A | 0 | 0
2021-08-02 02:00 | 5.3387 | 0 | N/A | 0 | 0
2021-08-02 02:30 | 4.7029 | 0 | N/A | 0 | 0
2021-08-02 03:00 | 4.3671 | 0 | N/A | 0 | 0
2021-08-02 03:30 | 4.0505 | 0 | N/A | 0 | 0
2021-08-02 04:00 | 3.8273 | 0 | N/A | 0 | 0
2021-08-02 04:30 | 3.7423 | 0 | N/A | 0 | 0
2021-08-02 05:00 | 3.8128 | 0 | N/A | 0 | 0
2021-08-02 05:30 | 4.2002 | 0 | N/A | 0 | 0
2021-08-02 06:00 | 4.7962 | 0 | N/A | 0 | 0
2021-08-02 06:30 | 5.5684 | 0 | N/A | 0 | 0
2021-08-02 07:00 | 6.2389 | 0 | N/A | 0 | 0
2021-08-02 07:30 | 6.7303 | 0 | N/A | 0 | 0
2021-08-02 08:00 | 7.5005 | 0 | N/A | 0 | 0
2021-08-02 08:30 | 7.948 | 0 | N/A | 0 | 0
2021-08-02 09:00 | 7.5567 | 0 | N/A | 0 | 0
2021-08-02 09:30 | 7.0756 | 0 | N/A | 0 | 0
2021-08-02 10:00 | 6.8711 | 0 | N/A | 0 | 0
2021-08-02 10:30 | 5.8767 | 0 | N/A | 0 | 0
2021-08-02 11:00 | 5.3352 | 0 | N/A | 0 | 0
2021-08-02 11:30 | 4.2557 | 0 | N/A | 0 | 0
2021-08-02 12:00 | 3.5101 | 0 | N/A | 0 | 0
2021-08-02 12:30 | 2.9067 | 0 | N/A | 0 | 0
2021-08-02 13:00 | 2.7924 | 0 | N/A | 0 | 0
2021-08-02 13:30 | 3.0749 | 0 | N/A | 0 | 0
2021-08-02 14:00 | 4.0769 | 0 | N/A | 0 | 0
2021-08-02 14:30 | 4.1945 | 0 | N/A | 0 | 0
2021-08-02 15:00 | 4.6894 | 0 | N/A | 0 | 0
2021-08-02 15:30 | 5.3996 | 0 | N/A | 0 | 0
2021-08-02 16:00 | 4.5343 | 0 | N/A | 0 | 0
2021-08-02 16:30 | 5.1936 | 0 | N/A | 0 | 0
2021-08-02 17:00 | 5.959 | 0 | N/A | 0 | 0
2021-08-02 17:30 | 7.2327 | 0 | N/A | 0 | 0
2021-08-02 18:00 | 8.2803 | 0 | N/A | 0 | 0
2021-08-02 18:30 | 8.77 | 0 | N/A | 0 | 0
2021-08-02 19:00 | 8.6667 | 0 | N/A | 0 | 0
2021-08-02 19:30 | 8.2634 | 0 | N/A | 0 | 0
2021-08-02 20:00 | 8.0002 | 0 | N/A | 0 | 0
2021-08-02 20:30 | 7.575 | 0 | N/A | 0 | 0
2021-08-02 21:00 | 7.1404 | 0 | N/A | 0 | 0
2021-08-02 21:30 | 7.1496 | 0 | N/A | 0 | 0
2021-08-02 22:00 | 7.2124 | 0 | N/A | 0 | 0
2021-08-02 22:30 | 6.5575 | 0 | N/A | 0 | 0
2021-08-02 23:00 | 6.3571 | 0 | N/A | 0 | 0
2021-08-02 23:30 | 6.4873 | 0 | N/A | 0 | 0
2021-08-03 | 6.9879 | 0 | N/A | 0 | 0
2021-08-04 00:30 | 6.6809 | 0 | N/A | 0 | 0
2021-08-04 01:00 | 5.941 | 0 | N/A | 0 | 0
2021-08-04 01:30 | 5.6961 | 0 | N/A | 0 | 0
2021-08-04 02:00 | 5.3627 | 0 | N/A | 0 | 0
2021-08-04 02:30 | 4.8054 | 0 | N/A | 0 | 0
2021-08-04 03:00 | 4.3826 | 0 | N/A | 0 | 0
2021-08-04 03:30 | 4.1956 | 0 | N/A | 0 | 0
2021-08-04 04:00 | 3.98 | 0 | N/A | 0 | 0
2021-08-04 04:30 | 3.8857 | 0 | N/A | 0 | 0
2021-08-04 05:00 | 3.941 | 0 | N/A | 0 | 0
2021-08-04 05:30 | 4.1688 | 0 | N/A | 0 | 0
2021-08-04 06:00 | 4.7575 | 0 | N/A | 0 | 0
2021-08-04 06:30 | 5.5613 | 0 | N/A | 0 | 0
2021-08-04 07:00 | 6.2439 | 0 | N/A | 0 | 0
2021-08-04 07:30 | 6.7252 | 0 | N/A | 0 | 0
2021-08-04 08:00 | 7.4633 | 0 | N/A | 0 | 0
2021-08-04 08:30 | 7.7059 | 0 | N/A | 0 | 0
2021-08-04 09:00 | 7.3699 | 0 | N/A | 0 | 0
2021-08-04 09:30 | 7.7913 | 0 | N/A | 0 | 0
2021-08-04 10:00 | 7.7248 | 0 | N/A | 0 | 0
2021-08-04 10:30 | 6.9469 | 0 | N/A | 0 | 0
2021-08-04 11:00 | 6.7441 | 0 | N/A | 0 | 0
2021-08-04 11:30 | 5.9975 | 0 | N/A | 0 | 0
2021-08-04 12:00 | 6.4608 | 0 | N/A | 0 | 0
2021-08-04 12:30 | 5.8767 | 0 | N/A | 0 | 0
2021-08-04 13:00 | 5.71 | 0 | N/A | 0 | 0
2021-08-04 13:30 | 5.0803 | 0 | N/A | 0 | 0
2021-08-04 14:00 | 4.6968 | 0 | N/A | 0 | 0
2021-08-04 14:30 | 5.0435 | 0 | N/A | 0 | 0
2021-08-04 15:00 | 4.9605 | 0 | N/A | 0 | 0
2021-08-04 15:30 | 5.2641 | 0 | N/A | 0 | 0
2021-08-04 16:00 | 5.619 | 0 | N/A | 0 | 0
2021-08-04 16:30 | 5.9561 | 0 | N/A | 0 | 0
2021-08-04 17:00 | 7.0176 | 0 | N/A | 0 | 0
2021-08-04 17:30 | 7.7954 | 0 | N/A | 0 | 0
2021-08-04 18:00 | 8.574 | 0 | N/A | 0 | 0
2021-08-04 18:30 | 9.0133 | 0 | N/A | 0 | 0
2021-08-04 19:00 | 8.9033 | 0 | N/A | 0 | 0
2021-08-04 19:30 | 8.6233 | 0 | N/A | 0 | 0
2021-08-04 20:00 | 8.3133 | 0 | N/A | 0 | 0
2021-08-04 20:30 | 7.8546 | 0 | N/A | 0 | 0
2021-08-04 21:00 | 7.4335 | 0 | N/A | 0 | 0
2021-08-04 21:30 | 7.5223 | 0 | N/A | 0 | 0
2021-08-04 22:00 | 7.617 | 0 | N/A | 0 | 0
2021-08-04 22:30 | 6.8841 | 0 | N/A | 0 | 0
2021-08-04 23:00 | 6.7025 | 0 | N/A | 0 | 0
2021-08-04 23:30 | 6.7762 | 0 | N/A | 0 | 0
2021-08-05 | 7.0091 | 0 | N/A | 0 | 0
2021-08-05 00:30 | 6.3158 | 0 | N/A | 0 | 0
2021-08-05 01:00 | 5.4989 | 0 | N/A | 0 | 0
2021-08-05 01:30 | 5.3475 | 0 | N/A | 0 | 0
2021-08-05 02:00 | 5.018 | 0 | N/A | 0 | 0
2021-08-05 02:30 | 4.4179 | 0 | N/A | 0 | 0
2021-08-05 03:00 | 4.0668 | 0 | N/A | 0 | 0
2021-08-05 03:30 | 3.8387 | 0 | N/A | 0 | 0
2021-08-05 04:00 | 3.6227 | 0 | N/A | 0 | 0
2021-08-05 04:30 | 3.4559 | 0 | N/A | 0 | 0
2021-08-05 05:00 | 3.6267 | 0 | N/A | 0 | 0
2021-08-05 05:30 | 4.0466 | 0 | N/A | 0 | 0
2021-08-05 06:00 | 4.5774 | 0 | N/A | 0 | 0
2021-08-05 06:30 | 5.2989 | 0 | N/A | 0 | 0
2021-08-05 07:00 | 6.0378 | 0 | N/A | 0 | 0
2021-08-05 07:30 | 6.3754 | 0 | N/A | 0 | 0
2021-08-05 08:00 | 7.1473 | 0 | N/A | 0 | 0
2021-08-05 08:30 | 7.3537 | 0 | N/A | 0 | 0
2021-08-05 09:00 | 7.0507 | 0 | N/A | 0 | 0
2021-08-05 09:30 | 6.7838 | 0 | N/A | 0 | 0
2021-08-05 10:00 | 6.34 | 0 | N/A | 0 | 0
2021-08-05 10:30 | 5.8936 | 0 | N/A | 0 | 0
2021-08-05 11:00 | 5.4152 | 0 | N/A | 0 | 0
2021-08-05 11:30 | 5.4177 | 0 | N/A | 0 | 0
2021-08-05 12:00 | 5.1552 | 0 | N/A | 0 | 0
2021-08-05 12:30 | 4.9404 | 0 | N/A | 0 | 0
2021-08-05 13:00 | 4.5838 | 0 | N/A | 0 | 0
2021-08-05 13:30 | 5.1667 | 0 | N/A | 0 | 0
2021-08-05 14:00 | 4.9767 | 0 | N/A | 0 | 0
2021-08-05 14:30 | 5.2633 | 0 | N/A | 0 | 0
2021-08-05 15:00 | 5.2934 | 0 | N/A | 0 | 0
2021-08-05 15:30 | 5.0438 | 0 | N/A | 0 | 0
2021-08-05 16:00 | 5.1025 | 0 | N/A | 0 | 0
2021-08-05 16:30 | 5.3773 | 0 | N/A | 0 | 0
2021-08-05 17:00 | 6.0424 | 0 | N/A | 0 | 0
2021-08-05 17:30 | 6.7903 | 0 | N/A | 0 | 0
2021-08-05 18:00 | 7.5312 | 0 | N/A | 0 | 0
2021-08-05 18:30 | 8.0636 | 0 | N/A | 0 | 0
2021-08-05 19:00 | 8.2034 | 0 | N/A | 0 | 0
2021-08-05 19:30 | 7.967 | 0 | N/A | 0 | 0
2021-08-05 20:00 | 7.7075 | 0 | N/A | 0 | 0
2021-08-05 20:30 | 7.5644 | 0 | N/A | 0 | 0
2021-08-05 21:00 | 7.2 | 0 | N/A | 0 | 0
2021-08-05 21:30 | 7.3898 | 0 | N/A | 0 | 0
2021-08-05 22:00 | 7.2644 | 0 | N/A | 0 | 0
2021-08-05 22:30 | 6.7519 | 0 | N/A | 0 | 0
2021-08-05 23:00 | 6.5814 | 0 | N/A | 0 | 0
2021-08-05 23:30 | 6.7206 | 0 | N/A | 0 | 0
2021-08-06 | 6.8989 | 0 | N/A | 0 | 0
2021-08-06 00:30 | 6.1567 | 0 | N/A | 0 | 0
2021-08-06 01:00 | 5.3372 | 0 | N/A | 0 | 0
2021-08-06 01:30 | 5.1537 | 0 | N/A | 0 | 0
2021-08-06 02:00 | 4.806 | 0 | N/A | 0 | 0
2021-08-06 02:30 | 4.1269 | 0 | N/A | 0 | 0
2021-08-06 03:00 | 3.7542 | 0 | N/A | 0 | 0
2021-08-06 03:30 | 3.6235 | 0 | N/A | 0 | 0
2021-08-06 04:00 | 3.3691 | 0 | N/A | 0 | 0
2021-08-06 04:30 | 3.3209 | 0 | N/A | 0 | 0
2021-08-06 05:00 | 3.46 | 0 | N/A | 0 | 0
2021-08-06 05:30 | 3.7296 | 0 | N/A | 0 | 0
2021-08-06 06:00 | 4.1545 | 0 | N/A | 0 | 0
2021-08-06 06:30 | 4.8348 | 0 | N/A | 0 | 0
2021-08-06 07:00 | 5.3475 | 0 | N/A | 0 | 0
2021-08-06 07:30 | 5.4631 | 0 | N/A | 0 | 0
2021-08-06 08:00 | 5.9979 | 0 | N/A | 0 | 0
2021-08-06 08:30 | 6.2713 | 0 | N/A | 0 | 0
2021-08-06 09:00 | 6.4791 | 0 | N/A | 0 | 0
2021-08-06 09:30 | 6.6936 | 0 | N/A | 0 | 0
2021-08-06 10:00 | 6.5542 | 0 | N/A | 0 | 0
2021-08-06 10:30 | 6.5508 | 0 | N/A | 0 | 0
2021-08-06 11:00 | 6.214 | 0 | N/A | 0 | 0
2021-08-06 11:30 | 5.1701 | 0 | N/A | 0 | 0
2021-08-06 12:00 | 4.4649 | 0 | N/A | 0 | 0
2021-08-06 12:30 | 4.4703 | 0 | N/A | 0 | 0
2021-08-06 13:00 | 5.6492 | 0 | N/A | 0 | 0
2021-08-06 13:30 | 5.9026 | 0 | N/A | 0 | 0
2021-08-06 14:00 | 5.3564 | 0 | N/A | 0 | 0
2021-08-06 14:30 | 5.0004 | 0 | N/A | 0 | 0
2021-08-06 15:00 | 5.549 | 0 | N/A | 0 | 0
2021-08-06 15:30 | 5.259 | 0 | N/A | 0 | 0
2021-08-06 16:00 | 5.7811 | 0 | N/A | 0 | 0
2021-08-06 16:30 | 5.8138 | 0 | N/A | 0 | 0
2021-08-06 17:00 | 6.4523 | 0 | N/A | 0 | 0
2021-08-06 17:30 | 7.1763 | 0 | N/A | 0 | 0
2021-08-06 18:00 | 7.9375 | 0 | N/A | 0 | 0
2021-08-06 18:30 | 8.4533 | 0 | N/A | 0 | 0
2021-08-06 19:00 | 8.3833 | 0 | N/A | 0 | 0
2021-08-06 19:30 | 7.9404 | 0 | N/A | 0 | 0
2021-08-06 20:00 | 7.6178 | 0 | N/A | 0 | 0
2021-08-06 20:30 | 7.2028 | 0 | N/A | 0 | 0
2021-08-06 21:00 | 6.8202 | 0 | N/A | 0 | 0
2021-08-06 21:30 | 6.9676 | 0 | N/A | 0 | 0
2021-08-06 22:00 | 7.1482 | 0 | N/A | 0 | 0
2021-08-06 22:30 | 6.821 | 0 | N/A | 0 | 0
2021-08-06 23:00 | 6.5729 | 0 | N/A | 0 | 0
2021-08-06 23:30 | 6.7463 | 0 | N/A | 0 | 0
2021-08-07 | 7.095 | 0 | N/A | 0 | 0
2021-08-07 00:30 | 6.1083 | 0 | N/A | 0 | 0
2021-08-07 01:00 | 5.3713 | 0 | N/A | 0 | 0
2021-08-07 01:30 | 5.2447 | 0 | N/A | 0 | 0
2021-08-07 02:00 | 4.9243 | 0 | N/A | 0 | 0
2021-08-07 02:30 | 4.331 | 0 | N/A | 0 | 0
2021-08-07 03:00 | 3.9207 | 0 | N/A | 0 | 0
2021-08-07 03:30 | 3.6639 | 0 | N/A | 0 | 0
2021-08-07 04:00 | 3.5212 | 0 | N/A | 0 | 0
2021-08-07 04:30 | 3.3925 | 0 | N/A | 0 | 0
2021-08-07 05:00 | 3.403 | 0 | N/A | 0 | 0
2021-08-07 05:30 | 3.5548 | 0 | N/A | 0 | 0
2021-08-07 06:00 | 3.6479 | 0 | N/A | 0 | 0
2021-08-07 06:30 | 4.0001 | 0 | N/A | 0 | 0
2021-08-07 07:00 | 4.0976 | 0 | N/A | 0 | 0
2021-08-07 07:30 | 3.9905 | 0 | N/A | 0 | 0
2021-08-07 08:00 | 4.503 | 0 | N/A | 0 | 0
2021-08-07 08:30 | 5.1702 | 0 | N/A | 0 | 0
2021-08-07 09:00 | 5.5562 | 0 | N/A | 0 | 0
2021-08-07 09:30 | 5.6502 | 0 | N/A | 0 | 0
2021-08-07 10:00 | 5.5478 | 0 | N/A | 0 | 0
2021-08-07 10:30 | 5.628 | 0 | N/A | 0 | 0
2021-08-07 11:00 | 5.0027 | 0 | N/A | 0 | 0
2021-08-07 11:30 | 4.7535 | 0 | N/A | 0 | 0
2021-08-07 12:00 | 4.6002 | 0 | N/A | 0 | 0
2021-08-07 12:30 | 4.1533 | 0 | N/A | 0 | 0
2021-08-07 13:00 | 3.7894 | 0 | N/A | 0 | 0
2021-08-07 13:30 | 4.1904 | 0 | N/A | 0 | 0
2021-08-07 14:00 | 4.1169 | 0 | N/A | 0 | 0
2021-08-07 14:30 | 4.6105 | 0 | N/A | 0 | 0
2021-08-07 15:00 | 3.2033 | 0 | N/A | 0 | 0
2021-08-07 15:30 | 3.2963 | 0 | N/A | 0 | 0
2021-08-07 16:00 | 4.5341 | 0 | N/A | 0 | 0
2021-08-07 16:30 | 4.5533 | 0 | N/A | 0 | 0
2021-08-07 17:00 | 5.7034 | 0 | N/A | 0 | 0
2021-08-07 17:30 | 6.6121 | 0 | N/A | 0 | 0
2021-08-07 18:00 | 7.5068 | 0 | N/A | 0 | 0
2021-08-07 18:30 | 8.021 | 0 | N/A | 0 | 0
2021-08-07 19:00 | 7.9249 | 0 | N/A | 0 | 0
2021-08-07 19:30 | 7.5735 | 0 | N/A | 0 | 0
2021-08-07 20:00 | 7.1924 | 0 | N/A | 0 | 0
2021-08-07 20:30 | 6.6899 | 0 | N/A | 0 | 0
2021-08-07 21:00 | 6.362 | 0 | N/A | 0 | 0
2021-08-07 21:30 | 6.6863 | 0 | N/A | 0 | 0
2021-08-07 22:00 | 7.007 | 0 | N/A | 0 | 0
2021-08-07 22:30 | 6.7938 | 0 | N/A | 0 | 0
2021-08-07 23:00 | 6.7951 | 0 | N/A | 0 | 0
2021-08-07 23:30 | 6.9011 | 0 | N/A | 0 | 0
2021-08-08 | 7.2957 | 0 | N/A | 0 | 0
2021-08-08 00:30 | 6.6002 | 0 | N/A | 0 | 0
2021-08-08 01:00 | 5.7266 | 0 | N/A | 0 | 0
2021-08-08 01:30 | 5.588 | 0 | N/A | 0 | 0
2021-08-08 02:00 | 5.2678 | 0 | N/A | 0 | 0
2021-08-08 02:30 | 4.7083 | 0 | N/A | 0 | 0
2021-08-08 03:00 | 4.3433 | 0 | N/A | 0 | 0
2021-08-08 03:30 | 4.0841 | 0 | N/A | 0 | 0
2021-08-08 04:00 | 3.9019 | 0 | N/A | 0 | 0
2021-08-08 04:30 | 3.8023 | 0 | N/A | 0 | 0
2021-08-08 05:00 | 3.7528 | 0 | N/A | 0 | 0
2021-08-08 05:30 | 3.9344 | 0 | N/A | 0 | 0
2021-08-08 06:00 | 4.0614 | 0 | N/A | 0 | 0
2021-08-08 06:30 | 4.4042 | 0 | N/A | 0 | 0
2021-08-08 07:00 | 4.4638 | 0 | N/A | 0 | 0
2021-08-08 07:30 | 4.4212 | 0 | N/A | 0 | 0
2021-08-08 08:00 | 4.8021 | 0 | N/A | 0 | 0
2021-08-08 08:30 | 5.0644 | 0 | N/A | 0 | 0
2021-08-08 09:00 | 5.0255 | 0 | N/A | 0 | 0
2021-08-08 09:30 | 4.694 | 0 | N/A | 0 | 0
2021-08-08 10:00 | 4.913 | 0 | N/A | 0 | 0
2021-08-08 10:30 | 4.7512 | 0 | N/A | 0 | 0
2021-08-08 11:00 | 4.183 | 0 | N/A | 0 | 0
2021-08-08 11:30 | 3.5577 | 0 | N/A | 0 | 0
2021-08-08 12:00 | 3.635 | 0 | N/A | 0 | 0
2021-08-08 12:30 | 3.3275 | 0 | N/A | 0 | 0
2021-08-08 13:00 | 3.6978 | 0 | N/A | 0 | 0
2021-08-08 13:30 | 3.5673 | 0 | N/A | 0 | 0
2021-08-08 14:00 | 4.1517 | 0 | N/A | 0 | 0
2021-08-08 14:30 | 2.9437 | 0 | N/A | 0 | 0
2021-08-08 15:00 | 3.2844 | 0 | N/A | 0 | 0
2021-08-08 15:30 | 3.9538 | 0 | N/A | 0 | 0
2021-08-08 16:00 | 5.0335 | 0 | N/A | 0 | 0
2021-08-08 16:30 | 5.5617 | 0 | N/A | 0 | 0
2021-08-08 17:00 | 6.2562 | 0 | N/A | 0 | 0
2021-08-08 17:30 | 7.0447 | 0 | N/A | 0 | 0
2021-08-08 18:00 | 8.1164 | 0 | N/A | 0 | 0
2021-08-08 18:30 | 8.4376 | 0 | N/A | 0 | 0
2021-08-08 19:00 | 8.165 | 0 | N/A | 0 | 0
2021-08-08 19:30 | 7.7714 | 0 | N/A | 0 | 0
2021-08-08 20:00 | 7.205 | 0 | N/A | 0 | 0
2021-08-08 20:30 | 6.7688 | 0 | N/A | 0 | 0
2021-08-08 21:00 | 6.509 | 0 | N/A | 0 | 0
2021-08-08 21:30 | 6.7909 | 0 | N/A | 0 | 0
2021-08-08 22:00 | 6.9415 | 0 | N/A | 0 | 0
2021-08-08 22:30 | 6.6362 | 0 | N/A | 0 | 0
2021-08-08 23:00 | 6.629 | 0 | N/A | 0 | 0
2021-08-08 23:30 | 6.5637 | 0 | N/A | 0 | 0
2021-08-09 | 6.9099 | 0 | N/A | 0 | 0
2021-08-09 00:30 | 6.3439 | 0 | N/A | 0 | 0
2021-08-09 01:00 | 5.7743 | 0 | N/A | 0 | 0
2021-08-09 01:30 | 5.6488 | 0 | N/A | 0 | 0
2021-08-09 02:00 | 5.3665 | 0 | N/A | 0 | 0
2021-08-09 02:30 | 4.8449 | 0 | N/A | 0 | 0
2021-08-09 03:00 | 4.4028 | 0 | N/A | 0 | 0
2021-08-09 03:30 | 4.0295 | 0 | N/A | 0 | 0
2021-08-09 04:00 | 3.7982 | 0 | N/A | 0 | 0
2021-08-09 04:30 | 3.6785 | 0 | N/A | 0 | 0
2021-08-09 05:00 | 3.706 | 0 | N/A | 0 | 0
2021-08-09 05:30 | 4.0002 | 0 | N/A | 0 | 0
2021-08-09 06:00 | 4.3332 | 0 | N/A | 0 | 0
2021-08-09 06:30 | 5.071 | 0 | N/A | 0 | 0
2021-08-09 07:00 | 5.5897 | 0 | N/A | 0 | 0
2021-08-09 07:30 | 5.7582 | 0 | N/A | 0 | 0
2021-08-09 08:00 | 6.4883 | 0 | N/A | 0 | 0
2021-08-09 08:30 | 7.1011 | 0 | N/A | 0 | 0
2021-08-09 09:00 | 7.2869 | 0 | N/A | 0 | 0
2021-08-09 09:30 | 7.2133 | 0 | N/A | 0 | 0
2021-08-09 10:00 | 7 | 0 | N/A | 0 | 0
2021-08-09 10:30 | 6.75 | 0 | N/A | 0 | 0
2021-08-09 11:00 | 6.0333 | 0 | N/A | 0 | 0
2021-08-09 11:30 | 5.4171 | 0 | N/A | 0 | 0
2021-08-09 12:00 | 4.8878 | 0 | N/A | 0 | 0
2021-08-09 12:30 | 4.6546 | 0 | N/A | 0 | 0
2021-08-09 13:00 | 3.3455 | 0 | N/A | 0 | 0
2021-08-09 13:30 | 3.3812 | 0 | N/A | 0 | 0
2021-08-09 14:00 | 3.9118 | 0 | N/A | 0 | 0
2021-08-09 14:30 | 3.9863 | 0 | N/A | 0 | 0
2021-08-09 15:00 | 4.4306 | 0 | N/A | 0 | 0
2021-08-09 15:30 | 4.5287 | 0 | N/A | 0 | 0
2021-08-09 16:00 | 5.5073 | 0 | N/A | 0 | 0
2021-08-09 16:30 | 5.9453 | 0 | N/A | 0 | 0
2021-08-09 17:00 | 6.4769 | 0 | N/A | 0 | 0
2021-08-09 17:30 | 7.3119 | 0 | N/A | 0 | 0
2021-08-09 18:00 | 8.1866 | 0 | N/A | 0 | 0
2021-08-09 18:30 | 8.664 | 0 | N/A | 0 | 0
2021-08-09 19:00 | 8.3843 | 0 | N/A | 0 | 0
2021-08-09 19:30 | 8.0582 | 0 | N/A | 0 | 0
2021-08-09 20:00 | 7.6788 | 0 | N/A | 0 | 0
2021-08-09 20:30 | 7.3749 | 0 | N/A | 0 | 0
2021-08-09 21:00 | 7.03 | 0 | N/A | 0 | 0
2021-08-09 21:30 | 7.2924 | 0 | N/A | 0 | 0
2021-08-09 22:00 | 7.3332 | 0 | N/A | 0 | 0
2021-08-09 22:30 | 6.6935 | 0 | N/A | 0 | 0
2021-08-09 23:00 | 6.5866 | 0 | N/A | 0 | 0
2021-08-09 23:30 | 6.6846 | 0 | N/A | 0 | 0
2021-08-10 | 6.8651 | 0 | N/A | 0 | 0
2021-08-10 00:30 | 6.3115 | 0 | N/A | 0 | 0
2021-08-10 01:00 | 5.5047 | 0 | N/A | 0 | 0
2021-08-10 01:30 | 5.4334 | 0 | N/A | 0 | 0
2021-08-10 02:00 | 5.1269 | 0 | N/A | 0 | 0
2021-08-10 02:30 | 4.5658 | 0 | N/A | 0 | 0
2021-08-10 03:00 | 4.1389 | 0 | N/A | 0 | 0
2021-08-10 03:30 | 3.9345 | 0 | N/A | 0 | 0
2021-08-10 04:00 | 3.7319 | 0 | N/A | 0 | 0
2021-08-10 04:30 | 3.7003 | 0 | N/A | 0 | 0
2021-08-10 05:00 | 3.7885 | 0 | N/A | 0 | 0
2021-08-10 05:30 | 4.1389 | 0 | N/A | 0 | 0
2021-08-10 06:00 | 4.7221 | 0 | N/A | 0 | 0
2021-08-10 06:30 | 5.5393 | 0 | N/A | 0 | 0
2021-08-10 07:00 | 6.3237 | 0 | N/A | 0 | 0
2021-08-10 07:30 | 6.6269 | 0 | N/A | 0 | 0
2021-08-10 08:00 | 6.9094 | 0 | N/A | 0 | 0
2021-08-10 08:30 | 6.74 | 0 | N/A | 0 | 0
2021-08-10 09:00 | 6.2433 | 0 | N/A | 0 | 0
2021-08-10 09:30 | 6.06 | 0 | N/A | 0 | 0
2021-08-10 10:00 | 5.1133 | 0 | N/A | 0 | 0
2021-08-10 10:30 | 4.5704 | 0 | N/A | 0 | 0
2021-08-10 11:00 | 4.6378 | 0 | N/A | 0 | 0
2021-08-10 11:30 | 3.2606 | 0 | N/A | 0 | 0
2021-08-10 12:00 | 2.9674 | 0 | N/A | 0 | 0
2021-08-10 12:30 | 1.7736 | 0 | N/A | 0 | 0
2021-08-10 13:00 | 2.2293 | 0 | N/A | 0 | 0
2021-08-10 13:30 | 1.599 | 0 | N/A | 0 | 0
2021-08-10 14:00 | 2.119 | 0 | N/A | 0 | 0
2021-08-10 14:30 | 3.6786 | 0 | N/A | 0 | 0
2021-08-10 15:00 | 3.6395 | 0 | N/A | 0 | 0
2021-08-10 15:30 | 3.7127 | 0 | N/A | 0 | 0
2021-08-10 16:00 | 4.0273 | 0 | N/A | 0 | 0
2021-08-10 16:30 | 4.8054 | 0 | N/A | 0 | 0
2021-08-10 17:00 | 5.6569 | 0 | N/A | 0 | 0
2021-08-10 17:30 | 6.4745 | 0 | N/A | 0 | 0
2021-08-10 18:00 | 7.4537 | 0 | N/A | 0 | 0
2021-08-10 18:30 | 8.1678 | 0 | N/A | 0 | 0
2021-08-10 19:00 | 8.1605 | 0 | N/A | 0 | 0
2021-08-10 19:30 | 7.924 | 0 | N/A | 0 | 0
2021-08-10 20:00 | 7.6054 | 0 | N/A | 0 | 0
2021-08-10 20:30 | 7.2771 | 0 | N/A | 0 | 0
2021-08-10 21:00 | 6.8446 | 0 | N/A | 0 | 0
2021-08-10 21:30 | 6.9766 | 0 | N/A | 0 | 0
2021-08-10 22:00 | 6.9999 | 0 | N/A | 0 | 0
2021-08-10 22:30 | 6.4191 | 0 | N/A | 0 | 0
2021-08-10 23:00 | 6.1999 | 0 | N/A | 0 | 0
2021-08-10 23:30 | 6.2797 | 0 | N/A | 0 | 0
2021-08-11 | 6.521 | 0 | N/A | 0 | 0
2021-08-11 00:30 | 5.9276 | 0 | N/A | 0 | 0
2021-08-11 01:00 | 5.0736 | 0 | N/A | 0 | 0
2021-08-11 01:30 | 4.9836 | 0 | N/A | 0 | 0
2021-08-11 02:00 | 4.5934 | 0 | N/A | 0 | 0
2021-08-11 02:30 | 3.958 | 0 | N/A | 0 | 0
2021-08-11 03:00 | 3.5887 | 0 | N/A | 0 | 0
2021-08-11 03:30 | 3.3925 | 0 | N/A | 0 | 0
2021-08-11 04:00 | 3.276 | 0 | N/A | 0 | 0
2021-08-11 04:30 | 3.2308 | 0 | N/A | 0 | 0
2021-08-11 05:00 | 3.2953 | 0 | N/A | 0 | 0
2021-08-11 05:30 | 3.6895 | 0 | N/A | 0 | 0
2021-08-11 06:00 | 4.1586 | 0 | N/A | 0 | 0
2021-08-11 06:30 | 4.9281 | 0 | N/A | 0 | 0
2021-08-11 07:00 | 5.7666 | 0 | N/A | 0 | 0
2021-08-11 07:30 | 6.0404 | 0 | N/A | 0 | 0
2021-08-11 08:00 | 6.579 | 0 | N/A | 0 | 0
2021-08-11 08:30 | 6.7868 | 0 | N/A | 0 | 0
2021-08-11 09:00 | 6.4901 | 0 | N/A | 0 | 0
2021-08-11 09:30 | 6.1968 | 0 | N/A | 0 | 0
2021-08-11 10:00 | 5.4534 | 0 | N/A | 0 | 0
2021-08-11 10:30 | 5.3201 | 0 | N/A | 0 | 0
2021-08-11 11:00 | 5.25 | 0 | N/A | 0 | 0
2021-08-11 11:30 | 5.8433 | 0 | N/A | 0 | 0
2021-08-11 12:00 | 5.9667 | 0 | N/A | 0 | 0
2021-08-11 12:30 | 6.2669 | 0 | N/A | 0 | 0
2021-08-11 13:00 | 6.5303 | 0 | N/A | 0 | 0
2021-08-11 13:30 | 6.9934 | 0 | N/A | 0 | 0
2021-08-11 14:00 | 6.9833 | 0 | N/A | 0 | 0
2021-08-11 14:30 | 6.8302 | 0 | N/A | 0 | 0
2021-08-11 15:00 | 6.95 | 0 | N/A | 0 | 0
2021-08-11 15:30 | 6.8234 | 0 | N/A | 0 | 0
2021-08-11 16:00 | 6.8143 | 0 | N/A | 0 | 0
2021-08-11 16:30 | 7.2139 | 0 | N/A | 0 | 0
2021-08-11 17:00 | 7.8335 | 0 | N/A | 0 | 0
2021-08-11 17:30 | 8.3667 | 0 | N/A | 0 | 0
2021-08-11 18:00 | 8.75 | 0 | N/A | 0 | 0
2021-08-11 18:30 | 9.0833 | 0 | N/A | 0 | 0
2021-08-11 19:00 | 9.05 | 0 | N/A | 0 | 0
2021-08-11 19:30 | 8.7933 | 0 | N/A | 0 | 0
2021-08-11 20:00 | 8.4767 | 0 | N/A | 0 | 0
2021-08-11 20:30 | 8.0842 | 0 | N/A | 0 | 0
2021-08-11 21:00 | 7.7223 | 0 | N/A | 0 | 0
2021-08-11 21:30 | 7.9152 | 0 | N/A | 0 | 0
2021-08-11 22:00 | 7.8836 | 0 | N/A | 0 | 0
2021-08-11 22:30 | 7.2238 | 0 | N/A | 0 | 0
2021-08-11 23:00 | 6.887 | 0 | N/A | 0 | 0
2021-08-11 23:30 | 6.9548 | 0 | N/A | 0 | 0
2021-08-12 | 7.3057 | 0 | N/A | 0 | 0
2021-08-12 00:30 | 6.7893 | 0 | N/A | 0 | 0
2021-08-12 01:00 | 5.9103 | 0 | N/A | 0 | 0
2021-08-12 01:30 | 5.679 | 0 | N/A | 0 | 0
2021-08-12 02:00 | 5.3929 | 0 | N/A | 0 | 0
2021-08-12 02:30 | 4.7351 | 0 | N/A | 0 | 0
2021-08-12 03:00 | 4.363 | 0 | N/A | 0 | 0
2021-08-12 03:30 | 4.1459 | 0 | N/A | 0 | 0
2021-08-12 04:00 | 3.9067 | 0 | N/A | 0 | 0
2021-08-12 04:30 | 3.8871 | 0 | N/A | 0 | 0
2021-08-12 05:00 | 3.9855 | 0 | N/A | 0 | 0
2021-08-12 05:30 | 4.3335 | 0 | N/A | 0 | 0
2021-08-12 06:00 | 4.7906 | 0 | N/A | 0 | 0
2021-08-12 06:30 | 5.6121 | 0 | N/A | 0 | 0
2021-08-12 07:00 | 6.3871 | 0 | N/A | 0 | 0
2021-08-12 07:30 | 6.6801 | 0 | N/A | 0 | 0
2021-08-12 08:00 | 7.24 | 0 | N/A | 0 | 0
2021-08-12 08:30 | 7.137 | 0 | N/A | 0 | 0
2021-08-12 09:00 | 5.9708 | 0 | N/A | 0 | 0
2021-08-12 09:30 | 5.5502 | 0 | N/A | 0 | 0
2021-08-12 10:00 | 4.8467 | 0 | N/A | 0 | 0
2021-08-12 10:30 | 4.866 | 0 | N/A | 0 | 0
2021-08-12 11:00 | 4.635 | 0 | N/A | 0 | 0
2021-08-12 11:30 | 4.5849 | 0 | N/A | 0 | 0
2021-08-12 12:00 | 4.2753 | 0 | N/A | 0 | 0
2021-08-12 12:30 | 4.3235 | 0 | N/A | 0 | 0
2021-08-12 13:00 | 3.4694 | 0 | N/A | 0 | 0
2021-08-12 13:30 | 3.3477 | 0 | N/A | 0 | 0
2021-08-12 14:00 | 3.5451 | 0 | N/A | 0 | 0
2021-08-12 14:30 | 3.5167 | 0 | N/A | 0 | 0
2021-08-12 15:00 | 3.701 | 0 | N/A | 0 | 0
2021-08-12 15:30 | 4.3083 | 0 | N/A | 0 | 0
2021-08-12 16:00 | 4.1069 | 0 | N/A | 0 | 0
2021-08-12 16:30 | 4.789 | 0 | N/A | 0 | 0
2021-08-12 17:00 | 5.7553 | 0 | N/A | 0 | 0
2021-08-12 17:30 | 6.6278 | 0 | N/A | 0 | 0
2021-08-12 18:00 | 7.5086 | 0 | N/A | 0 | 0
2021-08-12 18:30 | 8.224 | 0 | N/A | 0 | 0
2021-08-12 19:00 | 8.3769 | 0 | N/A | 0 | 0
2021-08-12 19:30 | 8.2003 | 0 | N/A | 0 | 0
2021-08-12 20:00 | 7.848 | 0 | N/A | 0 | 0
2021-08-12 20:30 | 7.6325 | 0 | N/A | 0 | 0
2021-08-12 21:00 | 7.2765 | 0 | N/A | 0 | 0
2021-08-12 21:30 | 7.3199 | 0 | N/A | 0 | 0
2021-08-12 22:00 | 7.2886 | 0 | N/A | 0 | 0
2021-08-12 22:30 | 6.7621 | 0 | N/A | 0 | 0
2021-08-12 23:00 | 6.4522 | 0 | N/A | 0 | 0
2021-08-12 23:30 | 6.5892 | 0 | N/A | 0 | 0
2021-08-13 | 6.8557 | 0 | N/A | 0 | 0
2021-08-13 00:30 | 6.1654 | 0 | N/A | 0 | 0
2021-08-13 01:00 | 5.3981 | 0 | N/A | 0 | 0
2021-08-13 01:30 | 5.3099 | 0 | N/A | 0 | 0
2021-08-13 02:00 | 4.8531 | 0 | N/A | 0 | 0
2021-08-13 02:30 | 4.2878 | 0 | N/A | 0 | 0
2021-08-13 03:00 | 3.9345 | 0 | N/A | 0 | 0
2021-08-13 03:30 | 3.7092 | 0 | N/A | 0 | 0
2021-08-13 04:00 | 3.5485 | 0 | N/A | 0 | 0
2021-08-13 04:30 | 3.4752 | 0 | N/A | 0 | 0
2021-08-13 05:00 | 3.565 | 0 | N/A | 0 | 0
2021-08-13 05:30 | 3.9001 | 0 | N/A | 0 | 0
2021-08-13 06:00 | 4.4116 | 0 | N/A | 0 | 0
2021-08-13 06:30 | 5.1776 | 0 | N/A | 0 | 0
2021-08-13 07:00 | 5.8625 | 0 | N/A | 0 | 0
2021-08-13 07:30 | 6.1992 | 0 | N/A | 0 | 0
2021-08-13 08:00 | 6.9279 | 0 | N/A | 0 | 0
2021-08-13 08:30 | 6.78 | 0 | N/A | 0 | 0
2021-08-13 09:00 | 6.3701 | 0 | N/A | 0 | 0
2021-08-13 09:30 | 5.43 | 0 | N/A | 0 | 0
2021-08-13 10:00 | 4.4737 | 0 | N/A | 0 | 0
2021-08-13 10:30 | 3.6893 | 0 | N/A | 0 | 0
2021-08-13 11:00 | 3.8821 | 0 | N/A | 0 | 0
2021-08-13 11:30 | 3.5807 | 0 | N/A | 0 | 0
2021-08-13 12:00 | 2.4216 | 0 | N/A | 0 | 0
2021-08-13 12:30 | 2.2042 | 0 | N/A | 0 | 0
2021-08-13 13:00 | 1.5898 | 0 | N/A | 0 | 0
2021-08-13 13:30 | 1.6592 | 0 | N/A | 0 | 0
2021-08-13 14:00 | 1.8378 | 0 | N/A | 0 | 0
2021-08-13 14:30 | 1.8045 | 0 | N/A | 0 | 0
2021-08-13 15:00 | 1.9492 | 0 | N/A | 0 | 0
2021-08-13 15:30 | 2.5874 | 0 | N/A | 0 | 0
2021-08-13 16:00 | 2.6711 | 0 | N/A | 0 | 0
2021-08-13 16:30 | 3.2037 | 0 | N/A | 0 | 0
2021-08-13 17:00 | 4.2165 | 0 | N/A | 0 | 0
2021-08-13 17:30 | 5.3211 | 0 | N/A | 0 | 0
2021-08-13 18:00 | 6.4626 | 0 | N/A | 0 | 0
2021-08-13 18:30 | 7.3706 | 0 | N/A | 0 | 0
2021-08-13 19:00 | 7.6791 | 0 | N/A | 0 | 0
2021-08-13 19:30 | 7.5491 | 0 | N/A | 0 | 0
2021-08-13 20:00 | 7.3831 | 0 | N/A | 0 | 0
2021-08-13 20:30 | 7.1878 | 0 | N/A | 0 | 0
2021-08-13 21:00 | 7.0711 | 0 | N/A | 0 | 0
2021-08-13 21:30 | 7.3704 | 0 | N/A | 0 | 0
2021-08-13 22:00 | 7.485 | 0 | N/A | 0 | 0
2021-08-13 22:30 | 7.0045 | 0 | N/A | 0 | 0
2021-08-13 23:00 | 6.8661 | 0 | N/A | 0 | 0
2021-08-13 23:30 | 6.9974 | 0 | N/A | 0 | 0
2021-08-14 | 7.1392 | 0 | N/A | 0 | 0
2021-08-14 00:30 | 6.4044 | 0 | N/A | 0 | 0
2021-08-14 01:00 | 5.5692 | 0 | N/A | 0 | 0
2021-08-14 01:30 | 5.4556 | 0 | N/A | 0 | 0
2021-08-14 02:00 | 5.0584 | 0 | N/A | 0 | 0
2021-08-14 02:30 | 4.5771 | 0 | N/A | 0 | 0
2021-08-14 03:00 | 4.2428 | 0 | N/A | 0 | 0
2021-08-14 03:30 | 3.997 | 0 | N/A | 0 | 0
2021-08-14 04:00 | 3.7844 | 0 | N/A | 0 | 0
2021-08-14 04:30 | 3.7326 | 0 | N/A | 0 | 0
2021-08-14 05:00 | 3.7496 | 0 | N/A | 0 | 0
2021-08-14 05:30 | 3.8952 | 0 | N/A | 0 | 0
2021-08-14 06:00 | 4.1106 | 0 | N/A | 0 | 0
2021-08-14 06:30 | 4.5786 | 0 | N/A | 0 | 0
2021-08-14 07:00 | 4.8608 | 0 | N/A | 0 | 0
2021-08-14 07:30 | 4.9177 | 0 | N/A | 0 | 0
2021-08-14 08:00 | 5.3581 | 0 | N/A | 0 | 0
2021-08-14 08:30 | 5.5897 | 0 | N/A | 0 | 0
2021-08-14 09:00 | 5.1954 | 0 | N/A | 0 | 0
2021-08-14 09:30 | 4.3917 | 0 | N/A | 0 | 0
2021-08-14 10:00 | 3.4465 | 0 | N/A | 0 | 0
2021-08-14 10:30 | 2.5117 | 0 | N/A | 0 | 0
2021-08-14 11:00 | 2.0874 | 0 | N/A | 0 | 0
2021-08-14 11:30 | 3.0217 | 0 | N/A | 0 | 0
2021-08-14 12:00 | 2.8678 | 0 | N/A | 0 | 0
2021-08-14 12:30 | 2.604 | 0 | N/A | 0 | 0
2021-08-14 13:00 | 3.0774 | 0 | N/A | 0 | 0
2021-08-14 13:30 | 2.8843 | 0 | N/A | 0 | 0
2021-08-14 14:00 | 2.6757 | 0 | N/A | 0 | 0
2021-08-14 14:30 | 2.5638 | 0 | N/A | 0 | 0
2021-08-14 15:00 | 2.2143 | 0 | N/A | 0 | 0
2021-08-14 15:30 | 3.1877 | 0 | N/A | 0 | 0
2021-08-14 16:00 | 3.8108 | 0 | N/A | 0 | 0
2021-08-14 16:30 | 3.8442 | 0 | N/A | 0 | 0
2021-08-14 17:00 | 4.5521 | 0 | N/A | 0 | 0
2021-08-14 17:30 | 5.7646 | 0 | N/A | 0 | 0
2021-08-14 18:00 | 6.7585 | 0 | N/A | 0 | 0
2021-08-14 18:30 | 7.4273 | 0 | N/A | 0 | 0
2021-08-14 19:00 | 7.6595 | 0 | N/A | 0 | 0
2021-08-14 19:30 | 7.4131 | 0 | N/A | 0 | 0
2021-08-14 20:00 | 6.8985 | 0 | N/A | 0 | 0
2021-08-14 20:30 | 6.7158 | 0 | N/A | 0 | 0
2021-08-14 21:00 | 6.4056 | 0 | N/A | 0 | 0
2021-08-14 21:30 | 6.8411 | 0 | N/A | 0 | 0
2021-08-14 22:00 | 6.8864 | 0 | N/A | 0 | 0
2021-08-14 22:30 | 6.4528 | 0 | N/A | 0 | 0
2021-08-14 23:00 | 6.5548 | 0 | N/A | 0 | 0
2021-08-14 23:30 | 6.6939 | 0 | N/A | 0 | 0
2021-08-15 | 6.8995 | 0 | N/A | 0 | 0
2021-08-15 00:30 | 6.3726 | 0 | N/A | 0 | 0
2021-08-15 01:00 | 5.5487 | 0 | N/A | 0 | 0
2021-08-15 01:30 | 5.4023 | 0 | N/A | 0 | 0
2021-08-15 02:00 | 5.0182 | 0 | N/A | 0 | 0
2021-08-15 02:30 | 4.4074 | 0 | N/A | 0 | 0
2021-08-15 03:00 | 3.9883 | 0 | N/A | 0 | 0
2021-08-15 03:30 | 3.8 | 0 | N/A | 0 | 0
2021-08-15 04:00 | 3.5268 | 0 | N/A | 0 | 0
2021-08-15 04:30 | 3.3841 | 0 | N/A | 0 | 0
2021-08-15 05:00 | 3.3114 | 0 | N/A | 0 | 0
2021-08-15 05:30 | 3.4603 | 0 | N/A | 0 | 0
2021-08-15 06:00 | 3.6397 | 0 | N/A | 0 | 0
2021-08-15 06:30 | 4.0195 | 0 | N/A | 0 | 0
2021-08-15 07:00 | 4.233 | 0 | N/A | 0 | 0
2021-08-15 07:30 | 4.2933 | 0 | N/A | 0 | 0
2021-08-15 08:00 | 4.4997 | 0 | N/A | 0 | 0
2021-08-15 08:30 | 4.505 | 0 | N/A | 0 | 0
2021-08-15 09:00 | 4.1292 | 0 | N/A | 0 | 0
2021-08-15 09:30 | 4.045 | 0 | N/A | 0 | 0
2021-08-15 10:00 | 3.1831 | 0 | N/A | 0 | 0
2021-08-15 10:30 | 2.2137 | 0 | N/A | 0 | 0
2021-08-15 11:00 | 1.5129 | 0 | N/A | 0 | 0
2021-08-15 11:30 | 1.0626 | 0 | N/A | 0 | 0
2021-08-15 12:00 | 0.7153 | 0 | N/A | 0 | 0
2021-08-15 12:30 | 0.64788 | 0 | N/A | 0 | 0
2021-08-15 13:00 | 0.57975 | 0 | N/A | 0 | 0
2021-08-15 13:30 | 0.59237 | 0 | N/A | 0 | 0
2021-08-15 14:00 | 0.67602 | 0 | N/A | 0 | 0
2021-08-15 14:30 | 0.79872 | 0 | N/A | 0 | 0
2021-08-15 15:00 | 1.1917 | 0 | N/A | 0 | 0
2021-08-15 15:30 | 1.7361 | 0 | N/A | 0 | 0
2021-08-15 16:00 | 2.7197 | 0 | N/A | 0 | 0
2021-08-15 16:30 | 4.1466 | 0 | N/A | 0 | 0
2021-08-15 17:00 | 5.1238 | 0 | N/A | 0 | 0
2021-08-15 17:30 | 6.2811 | 0 | N/A | 0 | 0
2021-08-15 18:00 | 7.3058 | 0 | N/A | 0 | 0
2021-08-15 18:30 | 7.7552 | 0 | N/A | 0 | 0
2021-08-15 19:00 | 7.959 | 0 | N/A | 0 | 0
2021-08-15 19:30 | 7.4541 | 0 | N/A | 0 | 0
2021-08-15 20:00 | 7.1292 | 0 | N/A | 0 | 0
2021-08-15 20:30 | 6.6822 | 0 | N/A | 0 | 0
2021-08-15 21:00 | 6.2216 | 0 | N/A | 0 | 0
2021-08-15 21:30 | 6.4451 | 0 | N/A | 0 | 0
2021-08-15 22:00 | 6.5205 | 0 | N/A | 0 | 0
2021-08-15 22:30 | 5.9682 | 0 | N/A | 0 | 0
2021-08-15 23:00 | 5.9 | 0 | N/A | 0 | 0
2021-08-15 23:30 | 6.0513 | 0 | N/A | 0 | 0
2021-08-16 | 6.445 | 0 | N/A | 0 | 0
2021-08-16 00:30 | 5.7763 | 0 | N/A | 0 | 0
2021-08-16 01:00 | 5.1046 | 0 | N/A | 0 | 0
2021-08-16 01:30 | 5.1142 | 0 | N/A | 0 | 0
2021-08-16 02:00 | 4.7846 | 0 | N/A | 0 | 0
2021-08-16 02:30 | 4.1799 | 0 | N/A | 0 | 0
2021-08-16 03:00 | 3.6914 | 0 | N/A | 0 | 0
2021-08-16 03:30 | 3.4615 | 0 | N/A | 0 | 0
2021-08-16 04:00 | 3.37 | 0 | N/A | 0 | 0
2021-08-16 04:30 | 3.2541 | 0 | N/A | 0 | 0
2021-08-16 05:00 | 3.4071 | 0 | N/A | 0 | 0
2021-08-16 05:30 | 3.6965 | 0 | N/A | 0 | 0
2021-08-16 06:00 | 4.1258 | 0 | N/A | 0 | 0
2021-08-16 06:30 | 5.0639 | 0 | N/A | 0 | 0
2021-08-16 07:00 | 5.691 | 0 | N/A | 0 | 0
2021-08-16 07:30 | 6.1296 | 0 | N/A | 0 | 0
2021-08-16 08:00 | 6.7645 | 0 | N/A | 0 | 0
2021-08-16 08:30 | 6.8435 | 0 | N/A | 0 | 0
2021-08-16 09:00 | 6.3835 | 0 | N/A | 0 | 0
2021-08-16 09:30 | 6.3333 | 0 | N/A | 0 | 0
2021-08-16 10:00 | 6.3067 | 0 | N/A | 0 | 0
2021-08-16 10:30 | 6.2568 | 0 | N/A | 0 | 0
2021-08-16 11:00 | 6.18 | 0 | N/A | 0 | 0
2021-08-16 11:30 | 5.0901 | 0 | N/A | 0 | 0
2021-08-16 12:00 | 4.5435 | 0 | N/A | 0 | 0
2021-08-16 12:30 | 4.7246 | 0 | N/A | 0 | 0
2021-08-16 13:00 | 4.2169 | 0 | N/A | 0 | 0
2021-08-16 13:30 | 4.7324 | 0 | N/A | 0 | 0
2021-08-16 14:00 | 4.7938 | 0 | N/A | 0 | 0
2021-08-16 14:30 | 4.371 | 0 | N/A | 0 | 0
2021-08-16 15:00 | 4.1225 | 0 | N/A | 0 | 0
2021-08-16 15:30 | 4.6887 | 0 | N/A | 0 | 0
2021-08-16 16:00 | 5.2484 | 0 | N/A | 0 | 0
2021-08-16 16:30 | 5.6358 | 0 | N/A | 0 | 0
2021-08-16 17:00 | 6.6869 | 0 | N/A | 0 | 0
2021-08-16 17:30 | 7.5253 | 0 | N/A | 0 | 0
2021-08-16 18:00 | 8.5254 | 0 | N/A | 0 | 0
2021-08-16 18:30 | 9.0769 | 0 | N/A | 0 | 0
2021-08-16 19:00 | 8.9101 | 0 | N/A | 0 | 0
2021-08-16 19:30 | 8.5034 | 0 | N/A | 0 | 0
2021-08-16 20:00 | 8.0607 | 0 | N/A | 0 | 0
2021-08-16 20:30 | 7.6083 | 0 | N/A | 0 | 0
2021-08-16 21:00 | 7.151 | 0 | N/A | 0 | 0
2021-08-16 21:30 | 7.2736 | 0 | N/A | 0 | 0
2021-08-16 22:00 | 7.2176 | 0 | N/A | 0 | 0
2021-08-16 22:30 | 6.5589 | 0 | N/A | 0 | 0
2021-08-16 23:00 | 6.4253 | 0 | N/A | 0 | 0
2021-08-16 23:30 | 6.642 | 0 | N/A | 0 | 0
2021-08-17 | 6.836 | 0 | N/A | 0 | 0
2021-08-17 00:30 | 6.1412 | 0 | N/A | 0 | 0
2021-08-17 01:00 | 5.4014 | 0 | N/A | 0 | 0
2021-08-17 01:30 | 5.2102 | 0 | N/A | 0 | 0
2021-08-17 02:00 | 4.8888 | 0 | N/A | 0 | 0
2021-08-17 02:30 | 4.2997 | 0 | N/A | 0 | 0
2021-08-17 03:00 | 3.8903 | 0 | N/A | 0 | 0
2021-08-17 03:30 | 3.6866 | 0 | N/A | 0 | 0
2021-08-17 04:00 | 3.5001 | 0 | N/A | 0 | 0
2021-08-17 04:30 | 3.443 | 0 | N/A | 0 | 0
2021-08-17 05:00 | 3.5687 | 0 | N/A | 0 | 0
2021-08-17 05:30 | 3.9427 | 0 | N/A | 0 | 0
2021-08-17 06:00 | 4.4557 | 0 | N/A | 0 | 0
2021-08-17 06:30 | 5.2731 | 0 | N/A | 0 | 0
2021-08-17 07:00 | 5.8346 | 0 | N/A | 0 | 0
2021-08-17 07:30 | 6.2727 | 0 | N/A | 0 | 0
2021-08-17 08:00 | 6.896 | 0 | N/A | 0 | 0
2021-08-17 08:30 | 7.0467 | 0 | N/A | 0 | 0
2021-08-17 09:00 | 6.6068 | 0 | N/A | 0 | 0
2021-08-17 09:30 | 6.3737 | 0 | N/A | 0 | 0
2021-08-17 10:00 | 6.0069 | 0 | N/A | 0 | 0
2021-08-17 10:30 | 5.6735 | 0 | N/A | 0 | 0
2021-08-17 11:00 | 5.2734 | 0 | N/A | 0 | 0
2021-08-17 11:30 | 5.41 | 0 | N/A | 0 | 0
2021-08-17 12:00 | 4.7133 | 0 | N/A | 0 | 0
2021-08-17 12:30 | 4.2298 | 0 | N/A | 0 | 0
2021-08-17 13:00 | 3.9631 | 0 | N/A | 0 | 0
2021-08-17 13:30 | 3.8059 | 0 | N/A | 0 | 0
2021-08-17 14:00 | 4.4904 | 0 | N/A | 0 | 0
2021-08-17 14:30 | 4.6151 | 0 | N/A | 0 | 0
2021-08-17 15:00 | 4.6636 | 0 | N/A | 0 | 0
2021-08-17 15:30 | 4.5318 | 0 | N/A | 0 | 0
2021-08-17 16:00 | 5.2364 | 0 | N/A | 0 | 0
2021-08-17 16:30 | 5.771 | 0 | N/A | 0 | 0
2021-08-17 17:00 | 6.2391 | 0 | N/A | 0 | 0
2021-08-17 17:30 | 7.024 | 0 | N/A | 0 | 0
2021-08-17 18:00 | 7.9034 | 0 | N/A | 0 | 0
2021-08-17 18:30 | 8.4175 | 0 | N/A | 0 | 0
2021-08-17 19:00 | 8.2773 | 0 | N/A | 0 | 0
2021-08-17 19:30 | 8.0009 | 0 | N/A | 0 | 0
2021-08-17 20:00 | 7.7787 | 0 | N/A | 0 | 0
2021-08-17 20:30 | 7.4535 | 0 | N/A | 0 | 0
2021-08-17 21:00 | 7.1068 | 0 | N/A | 0 | 0
2021-08-17 21:30 | 7.2689 | 0 | N/A | 0 | 0
2021-08-17 22:00 | 7.3766 | 0 | N/A | 0 | 0
2021-08-17 22:30 | 6.7299 | 0 | N/A | 0 | 0
2021-08-17 23:00 | 6.5781 | 0 | N/A | 0 | 0
2021-08-17 23:30 | 6.6946 | 0 | N/A | 0 | 0
2021-08-18 | 7.0373 | 0 | N/A | 0 | 0
2021-08-18 00:30 | 6.3818 | 0 | N/A | 0 | 0
2021-08-18 01:00 | 5.6842 | 0 | N/A | 0 | 0
2021-08-18 01:30 | 5.6521 | 0 | N/A | 0 | 0
2021-08-18 02:00 | 5.1852 | 0 | N/A | 0 | 0
2021-08-18 02:30 | 4.556 | 0 | N/A | 0 | 0
2021-08-18 03:00 | 4.1304 | 0 | N/A | 0 | 0
2021-08-18 03:30 | 3.9336 | 0 | N/A | 0 | 0
2021-08-18 04:00 | 3.7302 | 0 | N/A | 0 | 0
2021-08-18 04:30 | 3.6834 | 0 | N/A | 0 | 0
2021-08-18 05:00 | 3.8232 | 0 | N/A | 0 | 0
2021-08-18 05:30 | 4.1302 | 0 | N/A | 0 | 0
2021-08-18 06:00 | 4.664 | 0 | N/A | 0 | 0
2021-08-18 06:30 | 5.5636 | 0 | N/A | 0 | 0
2021-08-18 07:00 | 6.2968 | 0 | N/A | 0 | 0
2021-08-18 07:30 | 6.7052 | 0 | N/A | 0 | 0
2021-08-18 08:00 | 7.227 | 0 | N/A | 0 | 0
2021-08-18 08:30 | 7.29 | 0 | N/A | 0 | 0
2021-08-18 09:00 | 6.6633 | 0 | N/A | 0 | 0
2021-08-18 09:30 | 6.1033 | 0 | N/A | 0 | 0
2021-08-18 10:00 | 4.5768 | 0 | N/A | 0 | 0
2021-08-18 10:30 | 4.5245 | 0 | N/A | 0 | 0
2021-08-18 11:00 | 4.7718 | 0 | N/A | 0 | 0
2021-08-18 11:30 | 5.1544 | 0 | N/A | 0 | 0
2021-08-18 12:00 | 4.527 | 0 | N/A | 0 | 0
2021-08-18 12:30 | 4.2256 | 0 | N/A | 0 | 0
2021-08-18 13:00 | 3.9892 | 0 | N/A | 0 | 0
2021-08-18 13:30 | 4.1439 | 0 | N/A | 0 | 0
2021-08-18 14:00 | 3.7174 | 0 | N/A | 0 | 0
2021-08-18 14:30 | 3.4047 | 0 | N/A | 0 | 0
2021-08-18 15:00 | 2.9682 | 0 | N/A | 0 | 0
2021-08-18 15:30 | 3.6964 | 0 | N/A | 0 | 0
2021-08-18 16:00 | 4.1411 | 0 | N/A | 0 | 0
2021-08-18 16:30 | 4.2362 | 0 | N/A | 0 | 0
2021-08-18 17:00 | 5.0715 | 0 | N/A | 0 | 0
2021-08-18 17:30 | 6.2539 | 0 | N/A | 0 | 0
2021-08-18 18:00 | 7.1839 | 0 | N/A | 0 | 0
2021-08-18 18:30 | 7.866 | 0 | N/A | 0 | 0
2021-08-18 19:00 | 8.0941 | 0 | N/A | 0 | 0
2021-08-18 19:30 | 7.8807 | 0 | N/A | 0 | 0
2021-08-18 20:00 | 7.638 | 0 | N/A | 0 | 0
2021-08-18 20:30 | 7.3665 | 0 | N/A | 0 | 0
2021-08-18 21:00 | 6.9591 | 0 | N/A | 0 | 0
2021-08-18 21:30 | 7.1467 | 0 | N/A | 0 | 0
2021-08-18 22:00 | 7.2678 | 0 | N/A | 0 | 0
2021-08-18 22:30 | 6.6023 | 0 | N/A | 0 | 0
2021-08-18 23:00 | 6.308 | 0 | N/A | 0 | 0
2021-08-18 23:30 | 6.4271 | 0 | N/A | 0 | 0
2021-08-19 | 6.6777 | 0 | N/A | 0 | 0
2021-08-19 00:30 | 6.0565 | 0 | N/A | 0 | 0
2021-08-19 01:00 | 5.3493 | 0 | N/A | 0 | 0
2021-08-19 01:30 | 5.2298 | 0 | N/A | 0 | 0
2021-08-19 02:00 | 4.8213 | 0 | N/A | 0 | 0
2021-08-19 02:30 | 4.3115 | 0 | N/A | 0 | 0
2021-08-19 03:00 | 3.9978 | 0 | N/A | 0 | 0
2021-08-19 03:30 | 3.7792 | 0 | N/A | 0 | 0
2021-08-19 04:00 | 3.6146 | 0 | N/A | 0 | 0
2021-08-19 04:30 | 3.5317 | 0 | N/A | 0 | 0
2021-08-19 05:00 | 3.6558 | 0 | N/A | 0 | 0
2021-08-19 05:30 | 4.0191 | 0 | N/A | 0 | 0
2021-08-19 06:00 | 4.6465 | 0 | N/A | 0 | 0
2021-08-19 06:30 | 5.4637 | 0 | N/A | 0 | 0
2021-08-19 07:00 | 6.2234 | 0 | N/A | 0 | 0
2021-08-19 07:30 | 6.6584 | 0 | N/A | 0 | 0
2021-08-19 08:00 | 6.889 | 0 | N/A | 0 | 0
2021-08-19 08:30 | 7.0602 | 0 | N/A | 0 | 0
2021-08-19 09:00 | 6.0767 | 0 | N/A | 0 | 0
2021-08-19 09:30 | 4.9938 | 0 | N/A | 0 | 0
2021-08-19 10:00 | 3.8153 | 0 | N/A | 0 | 0
2021-08-19 10:30 | 2.8462 | 0 | N/A | 0 | 0
2021-08-19 11:00 | 2.0495 | 0 | N/A | 0 | 0
2021-08-19 11:30 | 1.4746 | 0 | N/A | 0 | 0
2021-08-19 12:00 | 1.1895 | 0 | N/A | 0 | 0
2021-08-19 12:30 | 0.96538 | 0 | N/A | 0 | 0
2021-08-19 13:00 | 0.90613 | 0 | N/A | 0 | 0
2021-08-19 13:30 | 1.0227 | 0 | N/A | 0 | 0
2021-08-19 14:00 | 1.1341 | 0 | N/A | 0 | 0
2021-08-19 14:30 | 1.4165 | 0 | N/A | 0 | 0
2021-08-19 15:00 | 1.6163 | 0 | N/A | 0 | 0
2021-08-19 15:30 | 1.9633 | 0 | N/A | 0 | 0
2021-08-19 16:00 | 2.3501 | 0 | N/A | 0 | 0
2021-08-19 16:30 | 2.9973 | 0 | N/A | 0 | 0
2021-08-19 17:00 | 4.0726 | 0 | N/A | 0 | 0
2021-08-19 17:30 | 5.4045 | 0 | N/A | 0 | 0
2021-08-19 18:00 | 6.6293 | 0 | N/A | 0 | 0
2021-08-19 18:30 | 7.4586 | 0 | N/A | 0 | 0
2021-08-19 19:00 | 7.6645 | 0 | N/A | 0 | 0
2021-08-19 19:30 | 7.5921 | 0 | N/A | 0 | 0
2021-08-19 20:00 | 7.3016 | 0 | N/A | 0 | 0
2021-08-19 20:30 | 7.0671 | 0 | N/A | 0 | 0
2021-08-19 21:00 | 6.7097 | 0 | N/A | 0 | 0
2021-08-19 21:30 | 6.9978 | 0 | N/A | 0 | 0
2021-08-19 22:00 | 6.804 | 0 | N/A | 0 | 0
2021-08-19 22:30 | 6.2123 | 0 | N/A | 0 | 0
2021-08-19 23:00 | 6.0143 | 0 | N/A | 0 | 0
2021-08-19 23:30 | 6.2051 | 0 | N/A | 0 | 0
2021-08-20 | 6.5083 | 0 | N/A | 0 | 0
2021-08-20 00:30 | 5.7595 | 0 | N/A | 0 | 0
2021-08-20 01:00 | 4.8789 | 0 | N/A | 0 | 0
2021-08-20 01:30 | 4.8301 | 0 | N/A | 0 | 0
2021-08-20 02:00 | 4.5918 | 0 | N/A | 0 | 0
2021-08-20 02:30 | 4.0106 | 0 | N/A | 0 | 0
2021-08-20 03:00 | 3.6544 | 0 | N/A | 0 | 0
2021-08-20 03:30 | 3.416 | 0 | N/A | 0 | 0
2021-08-20 04:00 | 3.2472 | 0 | N/A | 0 | 0
2021-08-20 04:30 | 3.2298 | 0 | N/A | 0 | 0
2021-08-20 05:00 | 3.3638 | 0 | N/A | 0 | 0
2021-08-20 05:30 | 3.6737 | 0 | N/A | 0 | 0
2021-08-20 06:00 | 4.2217 | 0 | N/A | 0 | 0
2021-08-20 06:30 | 5.0065 | 0 | N/A | 0 | 0
2021-08-20 07:00 | 5.6908 | 0 | N/A | 0 | 0
2021-08-20 07:30 | 6.0568 | 0 | N/A | 0 | 0
2021-08-20 08:00 | 6.8636 | 0 | N/A | 0 | 0
2021-08-20 08:30 | 7.0702 | 0 | N/A | 0 | 0
2021-08-20 09:00 | 6.0036 | 0 | N/A | 0 | 0
2021-08-20 09:30 | 5.2867 | 0 | N/A | 0 | 0
2021-08-20 10:00 | 6.0234 | 0 | N/A | 0 | 0
2021-08-20 10:30 | 4.957 | 0 | N/A | 0 | 0
2021-08-20 11:00 | 4.1635 | 0 | N/A | 0 | 0
2021-08-20 11:30 | 3.5636 | 0 | N/A | 0 | 0
2021-08-20 12:00 | 2.527 | 0 | N/A | 0 | 0
2021-08-20 12:30 | 1.2977 | 0 | N/A | 0 | 0
2021-08-20 13:00 | 0.86555 | 0 | N/A | 0 | 0
2021-08-20 13:30 | 0.69619 | 0 | N/A | 0 | 0
2021-08-20 14:00 | 0.72777 | 0 | N/A | 0 | 0
2021-08-20 14:30 | 0.93143 | 0 | N/A | 0 | 0
2021-08-20 15:00 | 1.3448 | 0 | N/A | 0 | 0
2021-08-20 15:30 | 2.1394 | 0 | N/A | 0 | 0
2021-08-20 16:00 | 3.7852 | 0 | N/A | 0 | 0
2021-08-20 16:30 | 4.0957 | 0 | N/A | 0 | 0
2021-08-20 17:00 | 4.9209 | 0 | N/A | 0 | 0
2021-08-20 17:30 | 5.9284 | 0 | N/A | 0 | 0
2021-08-20 18:00 | 6.7901 | 0 | N/A | 0 | 0
2021-08-20 18:30 | 7.255 | 0 | N/A | 0 | 0
2021-08-20 19:00 | 7.2687 | 0 | N/A | 0 | 0
2021-08-20 19:30 | 7.1085 | 0 | N/A | 0 | 0
2021-08-20 20:00 | 6.8457 | 0 | N/A | 0 | 0
2021-08-20 20:30 | 6.6812 | 0 | N/A | 0 | 0
2021-08-20 21:00 | 6.438 | 0 | N/A | 0 | 0
2021-08-20 21:30 | 6.6766 | 0 | N/A | 0 | 0
2021-08-20 22:00 | 6.7302 | 0 | N/A | 0 | 0
2021-08-20 22:30 | 6.2658 | 0 | N/A | 0 | 0
2021-08-20 23:00 | 6.1945 | 0 | N/A | 0 | 0
2021-08-20 23:30 | 6.3982 | 0 | N/A | 0 | 0
2021-08-21 | 6.5681 | 0 | N/A | 0 | 0
2021-08-21 00:30 | 5.755 | 0 | N/A | 0 | 0
2021-08-21 01:00 | 4.95 | 0 | N/A | 0 | 0
2021-08-21 01:30 | 4.7966 | 0 | N/A | 0 | 0
2021-08-21 02:00 | 4.406 | 0 | N/A | 0 | 0
2021-08-21 02:30 | 3.8686 | 0 | N/A | 0 | 0
2021-08-21 03:00 | 3.5443 | 0 | N/A | 0 | 0
2021-08-21 03:30 | 3.3361 | 0 | N/A | 0 | 0
2021-08-21 04:00 | 3.2312 | 0 | N/A | 0 | 0
2021-08-21 04:30 | 3.2834 | 0 | N/A | 0 | 0
2021-08-21 05:00 | 3.2632 | 0 | N/A | 0 | 0
2021-08-21 05:30 | 3.3876 | 0 | N/A | 0 | 0
2021-08-21 06:00 | 3.5253 | 0 | N/A | 0 | 0
2021-08-21 06:30 | 3.9877 | 0 | N/A | 0 | 0
2021-08-21 07:00 | 4.2199 | 0 | N/A | 0 | 0
2021-08-21 07:30 | 4.2319 | 0 | N/A | 0 | 0
2021-08-21 08:00 | 4.5117 | 0 | N/A | 0 | 0
2021-08-21 08:30 | 4.5652 | 0 | N/A | 0 | 0
2021-08-21 09:00 | 3.9836 | 0 | N/A | 0 | 0
2021-08-21 09:30 | 3.2815 | 0 | N/A | 0 | 0
2021-08-21 10:00 | 2.4776 | 0 | N/A | 0 | 0
2021-08-21 10:30 | 1.6835 | 0 | N/A | 0 | 0
2021-08-21 11:00 | 1.2703 | 0 | N/A | 0 | 0
2021-08-21 11:30 | 1.0467 | 0 | N/A | 0 | 0
2021-08-21 12:00 | 1.1315 | 0 | N/A | 0 | 0
2021-08-21 12:30 | 1.8511 | 0 | N/A | 0 | 0
2021-08-21 13:00 | 3.1876 | 0 | N/A | 0 | 0
2021-08-21 13:30 | 2.8331 | 0 | N/A | 0 | 0
2021-08-21 14:00 | 2.9672 | 0 | N/A | 0 | 0
2021-08-21 14:30 | 3.353 | 0 | N/A | 0 | 0
2021-08-21 15:00 | 2.7924 | 0 | N/A | 0 | 0
2021-08-21 15:30 | 2.3216 | 0 | N/A | 0 | 0
2021-08-21 16:00 | 3.2626 | 0 | N/A | 0 | 0
2021-08-21 16:30 | 4.4679 | 0 | N/A | 0 | 0
2021-08-21 17:00 | 5.1857 | 0 | N/A | 0 | 0
2021-08-21 17:30 | 5.9597 | 0 | N/A | 0 | 0
2021-08-21 18:00 | 6.576 | 0 | N/A | 0 | 0
2021-08-21 18:30 | 7.0932 | 0 | N/A | 0 | 0
2021-08-21 19:00 | 7.2271 | 0 | N/A | 0 | 0
2021-08-21 19:30 | 6.8226 | 0 | N/A | 0 | 0
2021-08-21 20:00 | 6.3461 | 0 | N/A | 0 | 0
2021-08-21 20:30 | 5.9853 | 0 | N/A | 0 | 0
2021-08-21 21:00 | 5.747 | 0 | N/A | 0 | 0
2021-08-21 21:30 | 6.1809 | 0 | N/A | 0 | 0
2021-08-21 22:00 | 6.4078 | 0 | N/A | 0 | 0
2021-08-21 22:30 | 6.0857 | 0 | N/A | 0 | 0
2021-08-21 23:00 | 6.0432 | 0 | N/A | 0 | 0
2021-08-21 23:30 | 6.2012 | 0 | N/A | 0 | 0
2021-08-22 | 6.4731 | 0 | N/A | 0 | 0
2021-08-22 00:30 | 5.7706 | 0 | N/A | 0 | 0
2021-08-22 01:00 | 4.9728 | 0 | N/A | 0 | 0
2021-08-22 01:30 | 4.8629 | 0 | N/A | 0 | 0
2021-08-22 02:00 | 4.5443 | 0 | N/A | 0 | 0
2021-08-22 02:30 | 3.9659 | 0 | N/A | 0 | 0
2021-08-22 03:00 | 3.6025 | 0 | N/A | 0 | 0
2021-08-22 03:30 | 3.4237 | 0 | N/A | 0 | 0
2021-08-22 04:00 | 3.2376 | 0 | N/A | 0 | 0
2021-08-22 04:30 | 3.1608 | 0 | N/A | 0 | 0
2021-08-22 05:00 | 3.1321 | 0 | N/A | 0 | 0
2021-08-22 05:30 | 3.2647 | 0 | N/A | 0 | 0
2021-08-22 06:00 | 3.3943 | 0 | N/A | 0 | 0
2021-08-22 06:30 | 3.6528 | 0 | N/A | 0 | 0
2021-08-22 07:00 | 3.7945 | 0 | N/A | 0 | 0
2021-08-22 07:30 | 3.7624 | 0 | N/A | 0 | 0
2021-08-22 08:00 | 3.9108 | 0 | N/A | 0 | 0
2021-08-22 08:30 | 3.9108 | 0 | N/A | 0 | 0
2021-08-22 09:00 | 3.4642 | 0 | N/A | 0 | 0
2021-08-22 09:30 | 3.0034 | 0 | N/A | 0 | 0
2021-08-22 10:00 | 2.3955 | 0 | N/A | 0 | 0
2021-08-22 10:30 | 1.8226 | 0 | N/A | 0 | 0
2021-08-22 11:00 | 1.2512 | 0 | N/A | 0 | 0
2021-08-22 11:30 | 0.79686 | 0 | N/A | 0 | 0
2021-08-22 12:00 | 0.60052 | 0 | N/A | 0 | 0
2021-08-22 12:30 | 0.54741 | 0 | N/A | 0 | 0
2021-08-22 13:00 | -0.56337 | 0 | N/A | 0 | 0
2021-08-22 13:30 | 0.59337 | 0 | N/A | 0 | 0
2021-08-22 14:00 | 0.59393 | 0 | N/A | 0 | 0
2021-08-22 14:30 | 0.66804 | 0 | N/A | 0 | 0
2021-08-22 15:00 | 0.92472 | 0 | N/A | 0 | 0
2021-08-22 15:30 | 1.4269 | 0 | N/A | 0 | 0
2021-08-22 16:00 | 2.027 | 0 | N/A | 0 | 0
2021-08-22 16:30 | 2.7861 | 0 | N/A | 0 | 0
2021-08-22 17:00 | 3.8706 | 0 | N/A | 0 | 0
2021-08-22 17:30 | 5.1115 | 0 | N/A | 0 | 0
2021-08-22 18:00 | 6.2681 | 0 | N/A | 0 | 0
2021-08-22 18:30 | 6.9922 | 0 | N/A | 0 | 0
2021-08-22 19:00 | 7.0744 | 0 | N/A | 0 | 0
2021-08-22 19:30 | 6.7317 | 0 | N/A | 0 | 0
2021-08-22 20:00 | 6.3259 | 0 | N/A | 0 | 0
2021-08-22 20:30 | 5.8916 | 0 | N/A | 0 | 0
2021-08-22 21:00 | 5.5032 | 0 | N/A | 0 | 0
2021-08-22 21:30 | 5.7862 | 0 | N/A | 0 | 0
2021-08-22 22:00 | 5.9344 | 0 | N/A | 0 | 0
2021-08-22 22:30 | 5.5363 | 0 | N/A | 0 | 0
2021-08-22 23:00 | 5.5283 | 0 | N/A | 0 | 0
2021-08-22 23:30 | 5.6316 | 0 | N/A | 0 | 0
2021-08-23 | 5.9962 | 0 | N/A | 0 | 0
2021-08-23 00:30 | 5.2859 | 0 | N/A | 0 | 0
2021-08-23 01:00 | 4.6882 | 0 | N/A | 0 | 0
2021-08-23 01:30 | 4.5279 | 0 | N/A | 0 | 0
2021-08-23 02:00 | 4.305 | 0 | N/A | 0 | 0
2021-08-23 02:30 | 3.7064 | 0 | N/A | 0 | 0
2021-08-23 03:00 | 3.3018 | 0 | N/A | 0 | 0
2021-08-23 03:30 | 3.1292 | 0 | N/A | 0 | 0
2021-08-23 04:00 | 2.8545 | 0 | N/A | 0 | 0
2021-08-23 04:30 | 2.8935 | 0 | N/A | 0 | 0
2021-08-23 05:00 | 2.9599 | 0 | N/A | 0 | 0
2021-08-23 05:30 | 3.2509 | 0 | N/A | 0 | 0
2021-08-23 06:00 | 3.7297 | 0 | N/A | 0 | 0
2021-08-23 06:30 | 4.434 | 0 | N/A | 0 | 0
2021-08-23 07:00 | 4.9866 | 0 | N/A | 0 | 0
2021-08-23 07:30 | 5.0762 | 0 | N/A | 0 | 0
2021-08-23 08:00 | 5.4326 | 0 | N/A | 0 | 0
2021-08-23 08:30 | 5.6293 | 0 | N/A | 0 | 0
2021-08-23 09:00 | 5.6723 | 0 | N/A | 0 | 0
2021-08-23 09:30 | 4.8366 | 0 | N/A | 0 | 0
2021-08-23 10:00 | 4.3469 | 0 | N/A | 0 | 0
2021-08-23 10:30 | 3.7982 | 0 | N/A | 0 | 0
2021-08-23 11:00 | 3.9144 | 0 | N/A | 0 | 0
2021-08-23 11:30 | 3.9839 | 0 | N/A | 0 | 0
2021-08-23 12:00 | 3.6781 | 0 | N/A | 0 | 0
2021-08-23 12:30 | 3.841 | 0 | N/A | 0 | 0
2021-08-23 13:00 | 4.2418 | 0 | N/A | 0 | 0
2021-08-23 13:30 | 3.793 | 0 | N/A | 0 | 0
2021-08-23 14:00 | 3.4626 | 0 | N/A | 0 | 0
2021-08-23 14:30 | 4.4006 | 0 | N/A | 0 | 0
2021-08-23 15:00 | 5.1116 | 0 | N/A | 0 | 0
2021-08-23 15:30 | 4.7022 | 0 | N/A | 0 | 0
2021-08-23 16:00 | 5.1935 | 0 | N/A | 0 | 0
2021-08-23 16:30 | 5.1295 | 0 | N/A | 0 | 0
2021-08-23 17:00 | 6.1227 | 0 | N/A | 0 | 0
2021-08-23 17:30 | 7.1619 | 0 | N/A | 0 | 0
2021-08-23 18:00 | 8.2504 | 0 | N/A | 0 | 0
2021-08-23 18:30 | 8.8777 | 0 | N/A | 0 | 0
2021-08-23 19:00 | 8.7217 | 0 | N/A | 0 | 0
2021-08-23 19:30 | 8.3679 | 0 | N/A | 0 | 0
2021-08-23 20:00 | 8.0753 | 0 | N/A | 0 | 0
2021-08-23 20:30 | 7.7272 | 0 | N/A | 0 | 0
2021-08-23 21:00 | 7.3384 | 0 | N/A | 0 | 0
2021-08-23 21:30 | 7.5135 | 0 | N/A | 0 | 0
2021-08-23 22:00 | 7.4389 | 0 | N/A | 0 | 0
2021-08-23 22:30 | 6.8521 | 0 | N/A | 0 | 0
2021-08-23 23:00 | 6.7364 | 0 | N/A | 0 | 0
2021-08-23 23:30 | 6.8895 | 0 | N/A | 0 | 0
2021-08-24 | 7.1556 | 0 | N/A | 0 | 0
2021-08-24 00:30 | 6.5425 | 0 | N/A | 0 | 0
2021-08-24 01:00 | 5.7928 | 0 | N/A | 0 | 0
2021-08-24 01:30 | 5.6994 | 0 | N/A | 0 | 0
2021-08-24 02:00 | 5.3306 | 0 | N/A | 0 | 0
2021-08-24 02:30 | 4.8196 | 0 | N/A | 0 | 0
2021-08-24 03:00 | 4.4227 | 0 | N/A | 0 | 0
2021-08-24 03:30 | 4.2303 | 0 | N/A | 0 | 0
2021-08-24 04:00 | 3.966 | 0 | N/A | 0 | 0
2021-08-24 04:30 | 4.028 | 0 | N/A | 0 | 0
2021-08-24 05:00 | 4.1061 | 0 | N/A | 0 | 0
2021-08-24 05:30 | 4.4972 | 0 | N/A | 0 | 0
2021-08-24 06:00 | 5.0207 | 0 | N/A | 0 | 0
2021-08-24 06:30 | 5.8519 | 0 | N/A | 0 | 0
2021-08-24 07:00 | 6.5281 | 0 | N/A | 0 | 0
2021-08-24 07:30 | 6.5972 | 0 | N/A | 0 | 0
2021-08-24 08:00 | 6.8971 | 0 | N/A | 0 | 0
2021-08-24 08:30 | 6.8641 | 0 | N/A | 0 | 0
2021-08-24 09:00 | 6.2502 | 0 | N/A | 0 | 0
2021-08-24 09:30 | 5.8744 | 0 | N/A | 0 | 0
2021-08-24 10:00 | 4.9729 | 0 | N/A | 0 | 0
2021-08-24 10:30 | 4.5365 | 0 | N/A | 0 | 0
2021-08-24 11:00 | 4.1686 | 0 | N/A | 0 | 0
2021-08-24 11:30 | 3.9508 | 0 | N/A | 0 | 0
2021-08-24 12:00 | 4.1733 | 0 | N/A | 0 | 0
2021-08-24 12:30 | 2.998 | 0 | N/A | 0 | 0
2021-08-24 13:00 | 2.5065 | 0 | N/A | 0 | 0
2021-08-24 13:30 | 3.0173 | 0 | N/A | 0 | 0
2021-08-24 14:00 | 3.6604 | 0 | N/A | 0 | 0
2021-08-24 14:30 | 2.7895 | 0 | N/A | 0 | 0
2021-08-24 15:00 | 3.7597 | 0 | N/A | 0 | 0
2021-08-24 15:30 | 4.0295 | 0 | N/A | 0 | 0
2021-08-24 16:00 | 4.6107 | 0 | N/A | 0 | 0
2021-08-24 16:30 | 4.4884 | 0 | N/A | 0 | 0
2021-08-24 17:00 | 5.74 | 0 | N/A | 0 | 0
2021-08-24 17:30 | 6.8174 | 0 | N/A | 0 | 0
2021-08-24 18:00 | 7.9742 | 0 | N/A | 0 | 0
2021-08-24 18:30 | 8.5995 | 0 | N/A | 0 | 0
2021-08-24 19:00 | 8.6186 | 0 | N/A | 0 | 0
2021-08-24 19:30 | 8.2164 | 0 | N/A | 0 | 0
2021-08-24 20:00 | 7.7369 | 0 | N/A | 0 | 0
2021-08-24 20:30 | 7.4459 | 0 | N/A | 0 | 0
2021-08-24 21:00 | 7.053 | 0 | N/A | 0 | 0
2021-08-24 21:30 | 7.3526 | 0 | N/A | 0 | 0
2021-08-24 22:00 | 7.3146 | 0 | N/A | 0 | 0
2021-08-24 22:30 | 6.6478 | 0 | N/A | 0 | 0
2021-08-24 23:00 | 6.5738 | 0 | N/A | 0 | 0
2021-08-24 23:30 | 6.5278 | 0 | N/A | 0 | 0
2021-08-25 | 6.8997 | 0 | N/A | 0 | 0
2021-08-25 00:30 | 6.3391 | 0 | N/A | 0 | 0
2021-08-25 01:00 | 5.474 | 0 | N/A | 0 | 0
2021-08-25 01:30 | 5.4287 | 0 | N/A | 0 | 0
2021-08-25 02:00 | 5.1412 | 0 | N/A | 0 | 0
2021-08-25 02:30 | 4.5726 | 0 | N/A | 0 | 0
2021-08-25 03:00 | 4.2062 | 0 | N/A | 0 | 0
2021-08-25 03:30 | 3.9645 | 0 | N/A | 0 | 0
2021-08-25 04:00 | 3.7254 | 0 | N/A | 0 | 0
2021-08-25 04:30 | 3.6526 | 0 | N/A | 0 | 0
2021-08-25 05:00 | 3.6922 | 0 | N/A | 0 | 0
2021-08-25 05:30 | 4.0021 | 0 | N/A | 0 | 0
2021-08-25 06:00 | 4.4876 | 0 | N/A | 0 | 0
2021-08-25 06:30 | 5.196 | 0 | N/A | 0 | 0
2021-08-25 07:00 | 5.7681 | 0 | N/A | 0 | 0
2021-08-25 07:30 | 5.9353 | 0 | N/A | 0 | 0
2021-08-25 08:00 | 6.4231 | 0 | N/A | 0 | 0
2021-08-25 08:30 | 6.9275 | 0 | N/A | 0 | 0
2021-08-25 09:00 | 7.1 | 0 | N/A | 0 | 0
2021-08-25 09:30 | 6.9034 | 0 | N/A | 0 | 0
2021-08-25 10:00 | 5.7567 | 0 | N/A | 0 | 0
2021-08-25 10:30 | 5.38 | 0 | N/A | 0 | 0
2021-08-25 11:00 | 5.1 | 0 | N/A | 0 | 0
2021-08-25 11:30 | 5.2101 | 0 | N/A | 0 | 0
2021-08-25 12:00 | 4.6268 | 0 | N/A | 0 | 0
2021-08-25 12:30 | 4.7243 | 0 | N/A | 0 | 0
2021-08-25 13:00 | 5.1316 | 0 | N/A | 0 | 0
2021-08-25 13:30 | 5.1207 | 0 | N/A | 0 | 0
2021-08-25 14:00 | 4.997 | 0 | N/A | 0 | 0
2021-08-25 14:30 | 4.6941 | 0 | N/A | 0 | 0
2021-08-25 15:00 | 4.3507 | 0 | N/A | 0 | 0
2021-08-25 15:30 | 3.35 | 0 | N/A | 0 | 0
2021-08-25 16:00 | 4.211 | 0 | N/A | 0 | 0
2021-08-25 16:30 | 5.1702 | 0 | N/A | 0 | 0
2021-08-25 17:00 | 6.379 | 0 | N/A | 0 | 0
2021-08-25 17:30 | 7.5218 | 0 | N/A | 0 | 0
2021-08-25 18:00 | 8.5623 | 0 | N/A | 0 | 0
2021-08-25 18:30 | 8.8636 | 0 | N/A | 0 | 0
2021-08-25 19:00 | 8.6539 | 0 | N/A | 0 | 0
2021-08-25 19:30 | 8.3439 | 0 | N/A | 0 | 0
2021-08-25 20:00 | 8.0212 | 0 | N/A | 0 | 0
2021-08-25 20:30 | 7.7067 | 0 | N/A | 0 | 0
2021-08-25 21:00 | 7.2859 | 0 | N/A | 0 | 0
2021-08-25 21:30 | 7.3691 | 0 | N/A | 0 | 0
2021-08-25 22:00 | 7.4019 | 0 | N/A | 0 | 0
2021-08-25 22:30 | 6.8212 | 0 | N/A | 0 | 0
2021-08-25 23:00 | 6.6232 | 0 | N/A | 0 | 0
2021-08-25 23:30 | 6.8693 | 0 | N/A | 0 | 0
2021-08-26 | 7.2164 | 0 | N/A | 0 | 0
2021-08-26 00:30 | 6.5168 | 0 | N/A | 0 | 0
2021-08-26 01:00 | 5.7163 | 0 | N/A | 0 | 0
2021-08-26 01:30 | 5.6242 | 0 | N/A | 0 | 0
2021-08-26 02:00 | 5.3449 | 0 | N/A | 0 | 0
2021-08-26 02:30 | 4.8509 | 0 | N/A | 0 | 0
2021-08-26 03:00 | 4.4853 | 0 | N/A | 0 | 0
2021-08-26 03:30 | 4.2539 | 0 | N/A | 0 | 0
2021-08-26 04:00 | 4.0557 | 0 | N/A | 0 | 0
2021-08-26 04:30 | 3.9482 | 0 | N/A | 0 | 0
2021-08-26 05:00 | 4.0722 | 0 | N/A | 0 | 0
2021-08-26 05:30 | 4.3431 | 0 | N/A | 0 | 0
2021-08-26 06:00 | 4.8717 | 0 | N/A | 0 | 0
2021-08-26 06:30 | 5.7218 | 0 | N/A | 0 | 0
2021-08-26 07:00 | 6.2372 | 0 | N/A | 0 | 0
2021-08-26 07:30 | 6.4005 | 0 | N/A | 0 | 0
2021-08-26 08:00 | 6.8818 | 0 | N/A | 0 | 0
2021-08-26 08:30 | 7.3834 | 0 | N/A | 0 | 0
2021-08-26 09:00 | 7.42 | 0 | N/A | 0 | 0
2021-08-26 09:30 | 7.3167 | 0 | N/A | 0 | 0
2021-08-26 10:00 | 6.8733 | 0 | N/A | 0 | 0
2021-08-26 10:30 | 6.6433 | 0 | N/A | 0 | 0
2021-08-26 11:00 | 5.9033 | 0 | N/A | 0 | 0
2021-08-26 11:30 | 5.9667 | 0 | N/A | 0 | 0
2021-08-26 12:00 | 5.534 | 0 | N/A | 0 | 0
2021-08-26 12:30 | 5.1236 | 0 | N/A | 0 | 0
2021-08-26 13:00 | 5.3972 | 0 | N/A | 0 | 0
2021-08-26 13:30 | 5.5698 | 0 | N/A | 0 | 0
2021-08-26 14:00 | 5.6593 | 0 | N/A | 0 | 0
2021-08-26 14:30 | 5.3502 | 0 | N/A | 0 | 0
2021-08-26 15:00 | 5.6581 | 0 | N/A | 0 | 0
2021-08-26 15:30 | 5.9143 | 0 | N/A | 0 | 0
2021-08-26 16:00 | 6.3599 | 0 | N/A | 0 | 0
2021-08-26 16:30 | 6.5272 | 0 | N/A | 0 | 0
2021-08-26 17:00 | 7.1647 | 0 | N/A | 0 | 0
2021-08-26 17:30 | 7.8232 | 0 | N/A | 0 | 0
2021-08-26 18:00 | 8.4416 | 0 | N/A | 0 | 0
2021-08-26 18:30 | 8.777 | 0 | N/A | 0 | 0
2021-08-26 19:00 | 8.8867 | 0 | N/A | 0 | 0
2021-08-26 19:30 | 8.6033 | 0 | N/A | 0 | 0
2021-08-26 20:00 | 8.2938 | 0 | N/A | 0 | 0
2021-08-26 20:30 | 8.0445 | 0 | N/A | 0 | 0
2021-08-26 21:00 | 7.5995 | 0 | N/A | 0 | 0
2021-08-26 21:30 | 7.7185 | 0 | N/A | 0 | 0
2021-08-26 22:00 | 7.6893 | 0 | N/A | 0 | 0
2021-08-26 22:30 | 7.069 | 0 | N/A | 0 | 0
2021-08-26 23:00 | 6.9148 | 0 | N/A | 0 | 0
2021-08-26 23:30 | 6.8803 | 0 | N/A | 0 | 0
2021-08-27 | 7.3253 | 0 | N/A | 0 | 0
2021-08-27 00:30 | 6.7157 | 0 | N/A | 0 | 0
2021-08-27 01:00 | 5.9132 | 0 | N/A | 0 | 0
2021-08-27 01:30 | 5.8597 | 0 | N/A | 0 | 0
2021-08-27 02:00 | 5.609 | 0 | N/A | 0 | 0
2021-08-27 02:30 | 5.0676 | 0 | N/A | 0 | 0
2021-08-27 03:00 | 4.6335 | 0 | N/A | 0 | 0
2021-08-27 03:30 | 4.3917 | 0 | N/A | 0 | 0
2021-08-27 04:00 | 4.1362 | 0 | N/A | 0 | 0
2021-08-27 04:30 | 4.057 | 0 | N/A | 0 | 0
2021-08-27 05:00 | 4.1752 | 0 | N/A | 0 | 0
2021-08-27 05:30 | 4.4862 | 0 | N/A | 0 | 0
2021-08-27 06:00 | 4.9421 | 0 | N/A | 0 | 0
2021-08-27 06:30 | 5.8098 | 0 | N/A | 0 | 0
2021-08-27 07:00 | 6.4982 | 0 | N/A | 0 | 0
2021-08-27 07:30 | 6.5616 | 0 | N/A | 0 | 0
2021-08-27 08:00 | 6.9418 | 0 | N/A | 0 | 0
2021-08-27 08:30 | 7.0571 | 0 | N/A | 0 | 0
2021-08-27 09:00 | 6.4833 | 0 | N/A | 0 | 0
2021-08-27 09:30 | 5.4312 | 0 | N/A | 0 | 0
2021-08-27 10:00 | 4.2289 | 0 | N/A | 0 | 0
2021-08-27 10:30 | 3.2792 | 0 | N/A | 0 | 0
2021-08-27 11:00 | 2.4726 | 0 | N/A | 0 | 0
2021-08-27 11:30 | 2.581 | 0 | N/A | 0 | 0
2021-08-27 12:00 | 2.5425 | 0 | N/A | 0 | 0
2021-08-27 12:30 | 2.6621 | 0 | N/A | 0 | 0
2021-08-27 13:00 | 2.5243 | 0 | N/A | 0 | 0
2021-08-27 13:30 | 1.5402 | 0 | N/A | 0 | 0
2021-08-27 14:00 | 1.2111 | 0 | N/A | 0 | 0
2021-08-27 14:30 | 1.288 | 0 | N/A | 0 | 0
2021-08-27 15:00 | 1.8547 | 0 | N/A | 0 | 0
2021-08-27 15:30 | 2.5359 | 0 | N/A | 0 | 0
2021-08-27 16:00 | 2.9036 | 0 | N/A | 0 | 0
2021-08-27 16:30 | 3.6387 | 0 | N/A | 0 | 0
2021-08-27 17:00 | 4.5854 | 0 | N/A | 0 | 0
2021-08-27 17:30 | 5.773 | 0 | N/A | 0 | 0
2021-08-27 18:00 | 6.7677 | 0 | N/A | 0 | 0
2021-08-27 18:30 | 7.4804 | 0 | N/A | 0 | 0
2021-08-27 19:00 | 7.7828 | 0 | N/A | 0 | 0
2021-08-27 19:30 | 7.5967 | 0 | N/A | 0 | 0
2021-08-27 20:00 | 7.508 | 0 | N/A | 0 | 0
2021-08-27 20:30 | 7.2295 | 0 | N/A | 0 | 0
2021-08-27 21:00 | 6.9319 | 0 | N/A | 0 | 0
2021-08-27 21:30 | 7.2209 | 0 | N/A | 0 | 0
2021-08-27 22:00 | 7.4654 | 0 | N/A | 0 | 0
2021-08-27 22:30 | 7.0712 | 0 | N/A | 0 | 0
2021-08-27 23:00 | 6.9469 | 0 | N/A | 0 | 0
2021-08-27 23:30 | 6.9925 | 0 | N/A | 0 | 0
2021-08-28 | 7.2175 | 0 | N/A | 0 | 0
2021-08-28 00:30 | 6.6011 | 0 | N/A | 0 | 0
2021-08-28 01:00 | 5.8627 | 0 | N/A | 0 | 0
2021-08-28 01:30 | 5.8255 | 0 | N/A | 0 | 0
2021-08-28 02:00 | 5.3603 | 0 | N/A | 0 | 0
2021-08-28 02:30 | 4.7142 | 0 | N/A | 0 | 0
2021-08-28 03:00 | 4.3675 | 0 | N/A | 0 | 0
2021-08-28 03:30 | 4.1441 | 0 | N/A | 0 | 0
2021-08-28 04:00 | 3.9668 | 0 | N/A | 0 | 0
2021-08-28 04:30 | 3.9051 | 0 | N/A | 0 | 0
2021-08-28 05:00 | 3.8798 | 0 | N/A | 0 | 0
2021-08-28 05:30 | 3.978 | 0 | N/A | 0 | 0
2021-08-28 06:00 | 4.2658 | 0 | N/A | 0 | 0
2021-08-28 06:30 | 4.6697 | 0 | N/A | 0 | 0
2021-08-28 07:00 | 4.8898 | 0 | N/A | 0 | 0
2021-08-28 07:30 | 4.7884 | 0 | N/A | 0 | 0
2021-08-28 08:00 | 4.8947 | 0 | N/A | 0 | 0
2021-08-28 08:30 | 4.9318 | 0 | N/A | 0 | 0
2021-08-28 09:00 | 4.5753 | 0 | N/A | 0 | 0
2021-08-28 09:30 | 3.7259 | 0 | N/A | 0 | 0
2021-08-28 10:00 | 2.8412 | 0 | N/A | 0 | 0
2021-08-28 10:30 | 3.064 | 0 | N/A | 0 | 0
2021-08-28 11:00 | 2.5128 | 0 | N/A | 0 | 0
2021-08-28 11:30 | 1.8298 | 0 | N/A | 0 | 0
2021-08-28 12:00 | 1.0495 | 0 | N/A | 0 | 0
2021-08-28 12:30 | 0.74277 | 0 | N/A | 0 | 0
2021-08-28 13:00 | 0.70137 | 0 | N/A | 0 | 0
2021-08-28 13:30 | 0.70903 | 0 | N/A | 0 | 0
2021-08-28 14:00 | 0.74703 | 0 | N/A | 0 | 0
2021-08-28 14:30 | 0.8675 | 0 | N/A | 0 | 0
2021-08-28 15:00 | 1.4781 | 0 | N/A | 0 | 0
2021-08-28 15:30 | 1.5165 | 0 | N/A | 0 | 0
2021-08-28 16:00 | 2.8377 | 0 | N/A | 0 | 0
2021-08-28 16:30 | 2.4753 | 0 | N/A | 0 | 0
2021-08-28 17:00 | 3.6987 | 0 | N/A | 0 | 0
2021-08-28 17:30 | 5.3317 | 0 | N/A | 0 | 0
2021-08-28 18:00 | 6.5722 | 0 | N/A | 0 | 0
2021-08-28 18:30 | 7.4186 | 0 | N/A | 0 | 0
2021-08-28 19:00 | 7.8419 | 0 | N/A | 0 | 0
2021-08-28 19:30 | 7.5977 | 0 | N/A | 0 | 0
2021-08-28 20:00 | 7.17 | 0 | N/A | 0 | 0
2021-08-28 20:30 | 6.7372 | 0 | N/A | 0 | 0
2021-08-28 21:00 | 6.3237 | 0 | N/A | 0 | 0
2021-08-28 21:30 | 6.6007 | 0 | N/A | 0 | 0
2021-08-28 22:00 | 6.7854 | 0 | N/A | 0 | 0
2021-08-28 22:30 | 6.3901 | 0 | N/A | 0 | 0
2021-08-28 23:00 | 6.189 | 0 | N/A | 0 | 0
2021-08-28 23:30 | 6.3576 | 0 | N/A | 0 | 0
2021-08-29 | 6.6297 | 0 | N/A | 0 | 0
2021-08-29 00:30 | 6.0163 | 0 | N/A | 0 | 0
2021-08-29 01:00 | 5.2252 | 0 | N/A | 0 | 0
2021-08-29 01:30 | 5.0932 | 0 | N/A | 0 | 0
2021-08-29 02:00 | 4.7889 | 0 | N/A | 0 | 0
2021-08-29 02:30 | 4.2474 | 0 | N/A | 0 | 0
2021-08-29 03:00 | 3.6575 | 0 | N/A | 0 | 0
2021-08-29 03:30 | 3.4293 | 0 | N/A | 0 | 0
2021-08-29 04:00 | 3.3563 | 0 | N/A | 0 | 0
2021-08-29 04:30 | 3.2203 | 0 | N/A | 0 | 0
2021-08-29 05:00 | 3.26 | 0 | N/A | 0 | 0
2021-08-29 05:30 | 3.3595 | 0 | N/A | 0 | 0
2021-08-29 06:00 | 3.4353 | 0 | N/A | 0 | 0
2021-08-29 06:30 | 3.6203 | 0 | N/A | 0 | 0
2021-08-29 07:00 | 3.818 | 0 | N/A | 0 | 0
2021-08-29 07:30 | 3.8084 | 0 | N/A | 0 | 0
2021-08-29 08:00 | 4.0786 | 0 | N/A | 0 | 0
2021-08-29 08:30 | 4.1991 | 0 | N/A | 0 | 0
2021-08-29 09:00 | 4.4783 | 0 | N/A | 0 | 0
2021-08-29 09:30 | 4.8776 | 0 | N/A | 0 | 0
2021-08-29 10:00 | 4.7586 | 0 | N/A | 0 | 0
2021-08-29 10:30 | 4.699 | 0 | N/A | 0 | 0
2021-08-29 11:00 | 4.2069 | 0 | N/A | 0 | 0
2021-08-29 11:30 | 4.608 | 0 | N/A | 0 | 0
2021-08-29 12:00 | 4.6385 | 0 | N/A | 0 | 0
2021-08-29 12:30 | 4.3099 | 0 | N/A | 0 | 0
2021-08-29 13:00 | 4.0927 | 0 | N/A | 0 | 0
2021-08-29 13:30 | 3.5091 | 0 | N/A | 0 | 0
2021-08-29 14:00 | 3.3984 | 0 | N/A | 0 | 0
2021-08-29 14:30 | 2.4676 | 0 | N/A | 0 | 0
2021-08-29 15:00 | 2.7075 | 0 | N/A | 0 | 0
2021-08-29 15:30 | 2.6293 | 0 | N/A | 0 | 0
2021-08-29 16:00 | 3.0083 | 0 | N/A | 0 | 0
2021-08-29 16:30 | 3.6123 | 0 | N/A | 0 | 0
2021-08-29 17:00 | 4.5897 | 0 | N/A | 0 | 0
2021-08-29 17:30 | 5.6804 | 0 | N/A | 0 | 0
2021-08-29 18:00 | 6.9122 | 0 | N/A | 0 | 0
2021-08-29 18:30 | 7.9647 | 0 | N/A | 0 | 0
2021-08-29 19:00 | 8.3308 | 0 | N/A | 0 | 0
2021-08-29 19:30 | 7.8693 | 0 | N/A | 0 | 0
2021-08-29 20:00 | 7.3396 | 0 | N/A | 0 | 0
2021-08-29 20:30 | 6.9351 | 0 | N/A | 0 | 0
2021-08-29 21:00 | 6.5747 | 0 | N/A | 0 | 0
2021-08-29 21:30 | 6.9469 | 0 | N/A | 0 | 0
2021-08-29 22:00 | 7.1228 | 0 | N/A | 0 | 0
2021-08-29 22:30 | 6.7539 | 0 | N/A | 0 | 0
2021-08-29 23:00 | 6.6127 | 0 | N/A | 0 | 0
2021-08-29 23:30 | 6.3531 | 0 | N/A | 0 | 0
2021-08-30 | 6.719 | 0 | N/A | 0 | 0
2021-08-30 00:30 | 6.201 | 0 | N/A | 0 | 0
2021-08-30 01:00 | 5.5432 | 0 | N/A | 0 | 0
2021-08-30 01:30 | 5.4599 | 0 | N/A | 0 | 0
2021-08-30 02:00 | 5.1079 | 0 | N/A | 0 | 0
2021-08-30 02:30 | 4.5849 | 0 | N/A | 0 | 0
2021-08-30 03:00 | 4.2584 | 0 | N/A | 0 | 0
2021-08-30 03:30 | 3.9258 | 0 | N/A | 0 | 0
2021-08-30 04:00 | 3.6526 | 0 | N/A | 0 | 0
2021-08-30 04:30 | 3.6106 | 0 | N/A | 0 | 0
2021-08-30 05:00 | 3.6946 | 0 | N/A | 0 | 0
2021-08-30 05:30 | 3.9634 | 0 | N/A | 0 | 0
2021-08-30 06:00 | 4.6341 | 0 | N/A | 0 | 0
2021-08-30 06:30 | 5.3671 | 0 | N/A | 0 | 0
2021-08-30 07:00 | 5.8747 | 0 | N/A | 0 | 0
2021-08-30 07:30 | 5.9289 | 0 | N/A | 0 | 0
2021-08-30 08:00 | 6.4962 | 0 | N/A | 0 | 0
2021-08-30 08:30 | 6.742 | 0 | N/A | 0 | 0
2021-08-30 09:00 | 6.7277 | 0 | N/A | 0 | 0
2021-08-30 09:30 | 6.1702 | 0 | N/A | 0 | 0
2021-08-30 10:00 | 5.1503 | 0 | N/A | 0 | 0
2021-08-30 10:30 | 3.8054 | 0 | N/A | 0 | 0
2021-08-30 11:00 | 3.0025 | 0 | N/A | 0 | 0
2021-08-30 11:30 | 2.107 | 0 | N/A | 0 | 0
2021-08-30 12:00 | 1.5413 | 0 | N/A | 0 | 0
2021-08-30 12:30 | 1.1861 | 0 | N/A | 0 | 0
2021-08-30 13:00 | 1.0352 | 0 | N/A | 0 | 0
2021-08-30 13:30 | 1.4905 | 0 | N/A | 0 | 0
2021-08-30 14:00 | 2.2017 | 0 | N/A | 0 | 0
2021-08-30 14:30 | 2.4066 | 0 | N/A | 0 | 0
2021-08-30 15:00 | 3.4914 | 0 | N/A | 0 | 0
2021-08-30 15:30 | 2.5179 | 0 | N/A | 0 | 0
2021-08-30 16:00 | 3.0836 | 0 | N/A | 0 | 0
2021-08-30 16:30 | 3.9107 | 0 | N/A | 0 | 0
2021-08-30 17:00 | 4.5396 | 0 | N/A | 0 | 0
2021-08-30 17:30 | 5.6341 | 0 | N/A | 0 | 0
2021-08-30 18:00 | 6.8866 | 0 | N/A | 0 | 0
2021-08-30 18:30 | 7.7397 | 0 | N/A | 0 | 0
2021-08-30 19:00 | 7.9185 | 0 | N/A | 0 | 0
2021-08-30 19:30 | 7.6291 | 0 | N/A | 0 | 0
2021-08-30 20:00 | 7.3505 | 0 | N/A | 0 | 0
2021-08-30 20:30 | 6.839 | 0 | N/A | 0 | 0
2021-08-30 21:00 | 6.4469 | 0 | N/A | 0 | 0
2021-08-30 21:30 | 6.6315 | 0 | N/A | 0 | 0
2021-08-30 22:00 | 6.722 | 0 | N/A | 0 | 0
2021-08-30 22:30 | 6.3861 | 0 | N/A | 0 | 0
2021-08-30 23:00 | 6.2064 | 0 | N/A | 0 | 0
2021-08-30 23:30 | 6.221 | 0 | N/A | 0 | 0
2021-08-31 | 6.5551 | 0 | N/A | 0 | 0
2021-08-31 00:30 | 5.8834 | 0 | N/A | 0 | 0
2021-08-31 01:00 | 5.0625 | 0 | N/A | 0 | 0
2021-08-31 01:30 | 4.9612 | 0 | N/A | 0 | 0
2021-08-31 02:00 | 4.6876 | 0 | N/A | 0 | 0
2021-08-31 02:30 | 4.1596 | 0 | N/A | 0 | 0
2021-08-31 03:00 | 3.7874 | 0 | N/A | 0 | 0
2021-08-31 03:30 | 3.53 | 0 | N/A | 0 | 0
2021-08-31 04:00 | 3.3274 | 0 | N/A | 0 | 0
2021-08-31 04:30 | 3.2935 | 0 | N/A | 0 | 0
2021-08-31 05:00 | 3.4109 | 0 | N/A | 0 | 0
2021-08-31 05:30 | 3.7769 | 0 | N/A | 0 | 0
2021-08-31 06:00 | 4.3168 | 0 | N/A | 0 | 0
2021-08-31 06:30 | 4.8743 | 0 | N/A | 0 | 0
2021-08-31 07:00 | 5.3428 | 0 | N/A | 0 | 0
2021-08-31 07:30 | 5.4256 | 0 | N/A | 0 | 0
2021-08-31 08:00 | 5.9491 | 0 | N/A | 0 | 0
2021-08-31 08:30 | 6.6467 | 0 | N/A | 0 | 0
2021-08-31 09:00 | 6.8069 | 0 | N/A | 0 | 0
2021-08-31 09:30 | 5.7303 | 0 | N/A | 0 | 0
2021-08-31 10:00 | 3.87 | 0 | N/A | 0 | 0
2021-08-31 10:30 | 4.2372 | 0 | N/A | 0 | 0
2021-08-31 11:00 | 3.9038 | 0 | N/A | 0 | 0
2021-08-31 11:30 | 2.8251 | 0 | N/A | 0 | 0
2021-08-31 12:00 | 3.1136 | 0 | N/A | 0 | 0
2021-08-31 12:30 | 2.7367 | 0 | N/A | 0 | 0
2021-08-31 13:00 | 2.1067 | 0 | N/A | 0 | 0
2021-08-31 13:30 | 1.1903 | 0 | N/A | 0 | 0
2021-08-31 14:00 | 1.0039 | 0 | N/A | 0 | 0
2021-08-31 14:30 | 1.4512 | 0 | N/A | 0 | 0
2021-08-31 15:00 | 2.2471 | 0 | N/A | 0 | 0
2021-08-31 15:30 | 3.2438 | 0 | N/A | 0 | 0
2021-08-31 16:00 | 4.1428 | 0 | N/A | 0 | 0
2021-08-31 16:30 | 4.5642 | 0 | N/A | 0 | 0
2021-08-31 17:00 | 4.9809 | 0 | N/A | 0 | 0
2021-08-31 17:30 | 5.7449 | 0 | N/A | 0 | 0
2021-08-31 18:00 | 6.5216 | 0 | N/A | 0 | 0
2021-08-31 18:30 | 6.9487 | 0 | N/A | 0 | 0
2021-08-31 19:00 | 6.9874 | 0 | N/A | 0 | 0
2021-08-31 19:30 | 6.532 | 0 | N/A | 0 | 0
2021-08-31 20:00 | 6.2636 | 0 | N/A | 0 | 0
2021-08-31 20:30 | 5.9229 | 0 | N/A | 0 | 0
2021-08-31 21:00 | 5.6479 | 0 | N/A | 0 | 0
2021-08-31 21:30 | 5.9235 | 0 | N/A | 0 | 0
2021-08-31 22:00 | 5.946 | 0 | N/A | 0 | 0
2021-08-31 22:30 | 5.4056 | 0 | N/A | 0 | 0
2021-08-31 23:00 | 5.3826 | 0 | N/A | 0 | 0
2021-08-31 23:30 | 5.6932 | 0 | N/A | 0 | 0
2021-09-01 | 6.0906 | 0 | N/A | 0 | 0
2021-09-01 00:30 | 5.3628 | 0 | N/A | 0 | 0
2021-09-01 01:00 | 4.6934 | 0 | N/A | 0 | 0
2021-09-01 01:30 | 4.6939 | 0 | N/A | 0 | 0
2021-09-01 02:00 | 4.3199 | 0 | N/A | 0 | 0
2021-09-01 02:30 | 3.8532 | 0 | N/A | 0 | 0
2021-09-01 03:00 | 3.5006 | 0 | N/A | 0 | 0
2021-09-01 03:30 | 3.338 | 0 | N/A | 0 | 0
2021-09-01 04:00 | 3.2111 | 0 | N/A | 0 | 0
2021-09-01 04:30 | 3.1486 | 0 | N/A | 0 | 0
2021-09-01 05:00 | 3.2429 | 0 | N/A | 0 | 0
2021-09-01 05:30 | 3.5566 | 0 | N/A | 0 | 0
2021-09-01 06:00 | 4.1087 | 0 | N/A | 0 | 0
2021-09-01 06:30 | 4.7068 | 0 | N/A | 0 | 0
2021-09-01 07:00 | 5.1826 | 0 | N/A | 0 | 0
2021-09-01 07:30 | 5.3758 | 0 | N/A | 0 | 0
2021-09-01 08:00 | 5.6647 | 0 | N/A | 0 | 0
2021-09-01 08:30 | 5.1467 | 0 | N/A | 0 | 0
2021-09-01 09:00 | 4.4933 | 0 | N/A | 0 | 0
2021-09-01 09:30 | 3.4301 | 0 | N/A | 0 | 0
2021-09-01 10:00 | 2.5067 | 0 | N/A | 0 | 0
2021-09-01 10:30 | 1.7483 | 0 | N/A | 0 | 0
2021-09-01 11:00 | 0.84444 | 0 | N/A | 0 | 0
2021-09-01 11:30 | 0.76225 | 0 | N/A | 0 | 0
2021-09-01 12:00 | 0.52941 | 0 | N/A | 0 | 0
2021-09-01 12:30 | -0.25368 | 0 | N/A | 0 | 0
2021-09-01 13:00 | 0.24518 | 0 | N/A | 0 | 0
2021-09-01 13:30 | 0.22472 | 0 | N/A | 0 | 0
2021-09-01 14:00 | 0.34059 | 0 | N/A | 0 | 0
2021-09-01 14:30 | 0.65839 | 0 | N/A | 0 | 0
2021-09-01 15:00 | 0.77334 | 0 | N/A | 0 | 0
2021-09-01 15:30 | 1.3657 | 0 | N/A | 0 | 0
2021-09-01 16:00 | 1.5009 | 0 | N/A | 0 | 0
2021-09-01 16:30 | 2.0306 | 0 | N/A | 0 | 0
2021-09-01 17:00 | 3.027 | 0 | N/A | 0 | 0
2021-09-01 17:30 | 4.1004 | 0 | N/A | 0 | 0
2021-09-01 18:00 | 5.1367 | 0 | N/A | 0 | 0
2021-09-01 18:30 | 5.8318 | 0 | N/A | 0 | 0
2021-09-01 19:00 | 6.3071 | 0 | N/A | 0 | 0
2021-09-01 19:30 | 5.9413 | 0 | N/A | 0 | 0
2021-09-01 20:00 | 5.7085 | 0 | N/A | 0 | 0
2021-09-01 20:30 | 5.4531 | 0 | N/A | 0 | 0
2021-09-01 21:00 | 5.0848 | 0 | N/A | 0 | 0
2021-09-01 21:30 | 5.4336 | 0 | N/A | 0 | 0
2021-09-01 22:00 | 5.6953 | 0 | N/A | 0 | 0
2021-09-01 22:30 | 5.2152 | 0 | N/A | 0 | 0
2021-09-01 23:00 | 5.1199 | 0 | N/A | 0 | 0
2021-09-01 23:30 | 5.4381 | 0 | N/A | 0 | 0
2021-09-02 | 5.7483 | 0 | N/A | 0 | 0
2021-09-02 00:30 | 5.0625 | 0 | N/A | 0 | 0
2021-09-02 01:00 | 4.3486 | 0 | N/A | 0 | 0
2021-09-02 01:30 | 4.2704 | 0 | N/A | 0 | 0
2021-09-02 02:00 | 3.9271 | 0 | N/A | 0 | 0
2021-09-02 02:30 | 3.353 | 0 | N/A | 0 | 0
2021-09-02 03:00 | 3.0404 | 0 | N/A | 0 | 0
2021-09-02 03:30 | 2.942 | 0 | N/A | 0 | 0
2021-09-02 04:00 | 2.7454 | 0 | N/A | 0 | 0
2021-09-02 04:30 | 2.6873 | 0 | N/A | 0 | 0
2021-09-02 05:00 | 2.7568 | 0 | N/A | 0 | 0
2021-09-02 05:30 | 2.9453 | 0 | N/A | 0 | 0
2021-09-02 06:00 | 3.3375 | 0 | N/A | 0 | 0
2021-09-02 06:30 | 3.8969 | 0 | N/A | 0 | 0
2021-09-02 07:00 | 4.2113 | 0 | N/A | 0 | 0
2021-09-02 07:30 | 4.1292 | 0 | N/A | 0 | 0
2021-09-02 08:00 | 4.4715 | 0 | N/A | 0 | 0
2021-09-02 08:30 | 4.1325 | 0 | N/A | 0 | 0
2021-09-02 09:00 | 3.3743 | 0 | N/A | 0 | 0
2021-09-02 09:30 | 2.5004 | 0 | N/A | 0 | 0
2021-09-02 10:00 | 1.6399 | 0 | N/A | 0 | 0
2021-09-02 10:30 | 0.87598 | 0 | N/A | 0 | 0
2021-09-02 11:00 | 0.54992 | 0 | N/A | 0 | 0
2021-09-02 11:30 | 0.15206 | 0 | N/A | 0 | 0
2021-09-02 12:00 | 0.054263 | 0 | N/A | 0 | 0
2021-09-02 12:30 | -0.13308 | 0 | N/A | 0 | 0
2021-09-02 13:00 | -0.57998 | 0 | N/A | 0 | 0
2021-09-02 13:30 | -0.63513 | 0 | N/A | 0 | 0
2021-09-02 14:00 | -0.48448 | 0 | N/A | 0 | 0
2021-09-02 14:30 | -0.40668 | 0 | N/A | 0 | 0
2021-09-02 15:00 | 0.41231 | 0 | N/A | 0 | 0
2021-09-02 15:30 | 0.97386 | 0 | N/A | 0 | 0
2021-09-02 16:00 | 1.3659 | 0 | N/A | 0 | 0
2021-09-02 16:30 | 1.956 | 0 | N/A | 0 | 0
2021-09-02 17:00 | 2.7626 | 0 | N/A | 0 | 0
2021-09-02 17:30 | 3.7602 | 0 | N/A | 0 | 0
2021-09-02 18:00 | 4.778 | 0 | N/A | 0 | 0
2021-09-02 18:30 | 5.5175 | 0 | N/A | 0 | 0
2021-09-02 19:00 | 5.7178 | 0 | N/A | 0 | 0
2021-09-02 19:30 | 5.5213 | 0 | N/A | 0 | 0
2021-09-02 20:00 | 5.1311 | 0 | N/A | 0 | 0
2021-09-02 20:30 | 4.9461 | 0 | N/A | 0 | 0
2021-09-02 21:00 | 4.6589 | 0 | N/A | 0 | 0
2021-09-02 21:30 | 4.8872 | 0 | N/A | 0 | 0
2021-09-02 22:00 | 5.1496 | 0 | N/A | 0 | 0
2021-09-02 22:30 | 4.7594 | 0 | N/A | 0 | 0
2021-09-02 23:00 | 4.6766 | 0 | N/A | 0 | 0
2021-09-02 23:30 | 4.999 | 0 | N/A | 0 | 0
2021-09-03 | 5.3794 | 0 | N/A | 0 | 0
2021-09-03 00:30 | 4.5588 | 0 | N/A | 0 | 0
2021-09-03 01:00 | 3.8039 | 0 | N/A | 0 | 0
2021-09-03 01:30 | 3.7942 | 0 | N/A | 0 | 0
2021-09-03 02:00 | 3.367 | 0 | N/A | 0 | 0
2021-09-03 02:30 | 2.8695 | 0 | N/A | 0 | 0
2021-09-03 03:00 | 2.6551 | 0 | N/A | 0 | 0
2021-09-03 03:30 | 2.4971 | 0 | N/A | 0 | 0
2021-09-03 04:00 | 2.3468 | 0 | N/A | 0 | 0
2021-09-03 04:30 | 2.2981 | 0 | N/A | 0 | 0
2021-09-03 05:00 | 2.3482 | 0 | N/A | 0 | 0
2021-09-03 05:30 | 2.567 | 0 | N/A | 0 | 0
2021-09-03 06:00 | 2.8861 | 0 | N/A | 0 | 0
2021-09-03 06:30 | 3.3715 | 0 | N/A | 0 | 0
2021-09-03 07:00 | 3.6791 | 0 | N/A | 0 | 0
2021-09-03 07:30 | 4.0211 | 0 | N/A | 0 | 0
2021-09-03 08:00 | 4.5235 | 0 | N/A | 0 | 0
2021-09-03 08:30 | 5.0192 | 0 | N/A | 0 | 0
2021-09-03 09:00 | 5.1141 | 0 | N/A | 0 | 0
2021-09-03 09:30 | 4.8919 | 0 | N/A | 0 | 0
2021-09-03 10:00 | 4.2311 | 0 | N/A | 0 | 0
2021-09-03 10:30 | 3.3262 | 0 | N/A | 0 | 0
2021-09-03 11:00 | 4.3848 | 0 | N/A | 0 | 0
2021-09-03 11:30 | 5.1912 | 0 | N/A | 0 | 0
2021-09-03 12:00 | 5.7809 | 0 | N/A | 0 | 0
2021-09-03 12:30 | 5.8487 | 0 | N/A | 0 | 0
2021-09-03 13:00 | 5.2008 | 0 | N/A | 0 | 0
2021-09-03 13:30 | 5.4516 | 0 | N/A | 0 | 0
2021-09-03 14:00 | 5.8003 | 0 | N/A | 0 | 0
2021-09-03 14:30 | 6.0429 | 0 | N/A | 0 | 0
2021-09-03 15:00 | 6.0893 | 0 | N/A | 0 | 0
2021-09-03 15:30 | 6.2308 | 0 | N/A | 0 | 0
2021-09-03 16:00 | 6.3353 | 0 | N/A | 0 | 0
2021-09-03 16:30 | 6.4608 | 0 | N/A | 0 | 0
2021-09-03 17:00 | 6.8114 | 0 | N/A | 0 | 0
2021-09-03 17:30 | 7.2892 | 0 | N/A | 0 | 0
2021-09-03 18:00 | 7.7103 | 0 | N/A | 0 | 0
2021-09-03 18:30 | 7.8341 | 0 | N/A | 0 | 0
2021-09-03 19:00 | 7.7445 | 0 | N/A | 0 | 0
2021-09-03 19:30 | 7.2921 | 0 | N/A | 0 | 0
2021-09-03 20:00 | 6.8666 | 0 | N/A | 0 | 0
2021-09-03 20:30 | 6.5322 | 0 | N/A | 0 | 0
2021-09-03 21:00 | 6.245 | 0 | N/A | 0 | 0
2021-09-03 21:30 | 6.5374 | 0 | N/A | 0 | 0
2021-09-03 22:00 | 6.7918 | 0 | N/A | 0 | 0
2021-09-03 22:30 | 6.4845 | 0 | N/A | 0 | 0
2021-09-03 23:00 | 6.3122 | 0 | N/A | 0 | 0
2021-09-03 23:30 | 6.5218 | 0 | N/A | 0 | 0
2021-09-04 | 6.798 | 0 | N/A | 0 | 0
2021-09-04 00:30 | 6.0308 | 0 | N/A | 0 | 0
2021-09-04 01:00 | 5.1811 | 0 | N/A | 0 | 0
2021-09-04 01:30 | 4.9321 | 0 | N/A | 0 | 0
2021-09-04 02:00 | 4.6093 | 0 | N/A | 0 | 0
2021-09-04 02:30 | 3.9773 | 0 | N/A | 0 | 0
2021-09-04 03:00 | 3.769 | 0 | N/A | 0 | 0
2021-09-04 03:30 | 3.5691 | 0 | N/A | 0 | 0
2021-09-04 04:00 | 3.3789 | 0 | N/A | 0 | 0
2021-09-04 04:30 | 3.3009 | 0 | N/A | 0 | 0
2021-09-04 05:00 | 3.2948 | 0 | N/A | 0 | 0
2021-09-04 05:30 | 3.4071 | 0 | N/A | 0 | 0
2021-09-04 06:00 | 3.6146 | 0 | N/A | 0 | 0
2021-09-04 06:30 | 3.9134 | 0 | N/A | 0 | 0
2021-09-04 07:00 | 4.1158 | 0 | N/A | 0 | 0
2021-09-04 07:30 | 4.0154 | 0 | N/A | 0 | 0
2021-09-04 08:00 | 4.2389 | 0 | N/A | 0 | 0
2021-09-04 08:30 | 4.5387 | 0 | N/A | 0 | 0
2021-09-04 09:00 | 4.5326 | 0 | N/A | 0 | 0
2021-09-04 09:30 | 3.8064 | 0 | N/A | 0 | 0
2021-09-04 10:00 | 4.0065 | 0 | N/A | 0 | 0
2021-09-04 10:30 | 3.992 | 0 | N/A | 0 | 0
2021-09-04 11:00 | 3.5587 | 0 | N/A | 0 | 0
2021-09-04 11:30 | 3.288 | 0 | N/A | 0 | 0
2021-09-04 12:00 | 3.7997 | 0 | N/A | 0 | 0
2021-09-04 12:30 | 3.6173 | 0 | N/A | 0 | 0
2021-09-04 13:00 | 3.6047 | 0 | N/A | 0 | 0
2021-09-04 13:30 | 3.2579 | 0 | N/A | 0 | 0
2021-09-04 14:00 | 3.4836 | 0 | N/A | 0 | 0
2021-09-04 14:30 | 2.8045 | 0 | N/A | 0 | 0
2021-09-04 15:00 | 3.3115 | 0 | N/A | 0 | 0
2021-09-04 15:30 | 3.214 | 0 | N/A | 0 | 0
2021-09-04 16:00 | 3.463 | 0 | N/A | 0 | 0
2021-09-04 16:30 | 4.2219 | 0 | N/A | 0 | 0
2021-09-04 17:00 | 4.7673 | 0 | N/A | 0 | 0
2021-09-04 17:30 | 5.9525 | 0 | N/A | 0 | 0
2021-09-04 18:00 | 7.0553 | 0 | N/A | 0 | 0
2021-09-04 18:30 | 7.7055 | 0 | N/A | 0 | 0
2021-09-04 19:00 | 8.071 | 0 | N/A | 0 | 0
2021-09-04 19:30 | 7.7466 | 0 | N/A | 0 | 0
2021-09-04 20:00 | 7.4458 | 0 | N/A | 0 | 0
2021-09-04 20:30 | 6.9478 | 0 | N/A | 0 | 0
2021-09-04 21:00 | 6.5841 | 0 | N/A | 0 | 0
2021-09-04 21:30 | 6.994 | 0 | N/A | 0 | 0
2021-09-04 22:00 | 7.2841 | 0 | N/A | 0 | 0
2021-09-04 22:30 | 6.8478 | 0 | N/A | 0 | 0
2021-09-04 23:00 | 6.8073 | 0 | N/A | 0 | 0
2021-09-04 23:30 | 6.895 | 0 | N/A | 0 | 0
2021-09-05 | 7.0982 | 0 | N/A | 0 | 0
2021-09-05 00:30 | 6.5284 | 0 | N/A | 0 | 0
2021-09-05 01:00 | 5.7048 | 0 | N/A | 0 | 0
2021-09-05 01:30 | 5.5751 | 0 | N/A | 0 | 0
2021-09-05 02:00 | 5.1229 | 0 | N/A | 0 | 0
2021-09-05 02:30 | 4.4159 | 0 | N/A | 0 | 0
2021-09-05 03:00 | 4.0403 | 0 | N/A | 0 | 0
2021-09-05 03:30 | 3.7723 | 0 | N/A | 0 | 0
2021-09-05 04:00 | 3.6405 | 0 | N/A | 0 | 0
2021-09-05 04:30 | 3.4749 | 0 | N/A | 0 | 0
2021-09-05 05:00 | 3.4116 | 0 | N/A | 0 | 0
2021-09-05 05:30 | 3.6268 | 0 | N/A | 0 | 0
2021-09-05 06:00 | 3.7674 | 0 | N/A | 0 | 0
2021-09-05 06:30 | 4.0315 | 0 | N/A | 0 | 0
2021-09-05 07:00 | 4.2119 | 0 | N/A | 0 | 0
2021-09-05 07:30 | 3.9879 | 0 | N/A | 0 | 0
2021-09-05 08:00 | 3.9622 | 0 | N/A | 0 | 0
2021-09-05 08:30 | 4.1141 | 0 | N/A | 0 | 0
2021-09-05 09:00 | 4.0903 | 0 | N/A | 0 | 0
2021-09-05 09:30 | 3.6518 | 0 | N/A | 0 | 0
2021-09-05 10:00 | 3.7483 | 0 | N/A | 0 | 0
2021-09-05 10:30 | 3.7769 | 0 | N/A | 0 | 0
2021-09-05 11:00 | 3.1117 | 0 | N/A | 0 | 0
2021-09-05 11:30 | 3.401 | 0 | N/A | 0 | 0
2021-09-05 12:00 | 3.0389 | 0 | N/A | 0 | 0
2021-09-05 12:30 | 3.1624 | 0 | N/A | 0 | 0
2021-09-05 13:00 | 2.4805 | 0 | N/A | 0 | 0
2021-09-05 13:30 | 4.0237 | 0 | N/A | 0 | 0
2021-09-05 14:00 | 3.419 | 0 | N/A | 0 | 0
2021-09-05 14:30 | 2.9975 | 0 | N/A | 0 | 0
2021-09-05 15:00 | 4.2103 | 0 | N/A | 0 | 0
2021-09-05 15:30 | 4.5605 | 0 | N/A | 0 | 0
2021-09-05 16:00 | 4.613 | 0 | N/A | 0 | 0
2021-09-05 16:30 | 4.8344 | 0 | N/A | 0 | 0
2021-09-05 17:00 | 5.3997 | 0 | N/A | 0 | 0
2021-09-05 17:30 | 6.5445 | 0 | N/A | 0 | 0
2021-09-05 18:00 | 7.4195 | 0 | N/A | 0 | 0
2021-09-05 18:30 | 8.1005 | 0 | N/A | 0 | 0
2021-09-05 19:00 | 8.1054 | 0 | N/A | 0 | 0
2021-09-05 19:30 | 7.6846 | 0 | N/A | 0 | 0
2021-09-05 20:00 | 7.1717 | 0 | N/A | 0 | 0
2021-09-05 20:30 | 6.8573 | 0 | N/A | 0 | 0
2021-09-05 21:00 | 6.4605 | 0 | N/A | 0 | 0
2021-09-05 21:30 | 6.7018 | 0 | N/A | 0 | 0
2021-09-05 22:00 | 6.9379 | 0 | N/A | 0 | 0
2021-09-05 22:30 | 6.5058 | 0 | N/A | 0 | 0
2021-09-05 23:00 | 6.3716 | 0 | N/A | 0 | 0
2021-09-05 23:30 | 6.4668 | 0 | N/A | 0 | 0
2021-09-06 | 6.7332 | 0 | N/A | 0 | 0
2021-09-06 00:30 | 6.0992 | 0 | N/A | 0 | 0
2021-09-06 01:00 | 5.3086 | 0 | N/A | 0 | 0
2021-09-06 01:30 | 5.2069 | 0 | N/A | 0 | 0
2021-09-06 02:00 | 4.8635 | 0 | N/A | 0 | 0
2021-09-06 02:30 | 4.3185 | 0 | N/A | 0 | 0
2021-09-06 03:00 | 3.9011 | 0 | N/A | 0 | 0
2021-09-06 03:30 | 3.6631 | 0 | N/A | 0 | 0
2021-09-06 04:00 | 3.5212 | 0 | N/A | 0 | 0
2021-09-06 04:30 | 3.4875 | 0 | N/A | 0 | 0
2021-09-06 05:00 | 3.5534 | 0 | N/A | 0 | 0
2021-09-06 05:30 | 3.8668 | 0 | N/A | 0 | 0
2021-09-06 06:00 | 4.4172 | 0 | N/A | 0 | 0
2021-09-06 06:30 | 5.1218 | 0 | N/A | 0 | 0
2021-09-06 07:00 | 5.5934 | 0 | N/A | 0 | 0
2021-09-06 07:30 | 5.6535 | 0 | N/A | 0 | 0
2021-09-06 08:00 | 5.5084 | 0 | N/A | 0 | 0
2021-09-06 08:30 | 5.4222 | 0 | N/A | 0 | 0
2021-09-06 09:00 | 5.0802 | 0 | N/A | 0 | 0
2021-09-06 09:30 | 4.3802 | 0 | N/A | 0 | 0
2021-09-06 10:00 | 3.7167 | 0 | N/A | 0 | 0
2021-09-06 10:30 | 2.6564 | 0 | N/A | 0 | 0
2021-09-06 11:00 | 2.2595 | 0 | N/A | 0 | 0
2021-09-06 11:30 | 1.8144 | 0 | N/A | 0 | 0
2021-09-06 12:00 | 1.4305 | 0 | N/A | 0 | 0
2021-09-06 12:30 | 0.92679 | 0 | N/A | 0 | 0
2021-09-06 13:00 | 0.53767 | 0 | N/A | 0 | 0
2021-09-06 13:30 | 0.68219 | 0 | N/A | 0 | 0
2021-09-06 14:00 | 0.88577 | 0 | N/A | 0 | 0
2021-09-06 14:30 | 1.123 | 0 | N/A | 0 | 0
2021-09-06 15:00 | 1.4293 | 0 | N/A | 0 | 0
2021-09-06 15:30 | 1.5547 | 0 | N/A | 0 | 0
2021-09-06 16:00 | 2.0625 | 0 | N/A | 0 | 0
2021-09-06 16:30 | 2.7683 | 0 | N/A | 0 | 0
2021-09-06 17:00 | 3.7889 | 0 | N/A | 0 | 0
2021-09-06 17:30 | 4.7709 | 0 | N/A | 0 | 0
2021-09-06 18:00 | 6.2031 | 0 | N/A | 0 | 0
2021-09-06 18:30 | 7.1606 | 0 | N/A | 0 | 0
2021-09-06 19:00 | 7.6464 | 0 | N/A | 0 | 0
2021-09-06 19:30 | 7.4732 | 0 | N/A | 0 | 0
2021-09-06 20:00 | 7.2683 | 0 | N/A | 0 | 0
2021-09-06 20:30 | 6.9445 | 0 | N/A | 0 | 0
2021-09-06 21:00 | 6.592 | 0 | N/A | 0 | 0
2021-09-06 21:30 | 6.801 | 0 | N/A | 0 | 0
2021-09-06 22:00 | 6.826 | 0 | N/A | 0 | 0
2021-09-06 22:30 | 6.3388 | 0 | N/A | 0 | 0
2021-09-06 23:00 | 6.1702 | 0 | N/A | 0 | 0
2021-09-06 23:30 | 6.4034 | 0 | N/A | 0 | 0
2021-09-07 | 6.5747 | 0 | N/A | 0 | 0
2021-09-07 00:30 | 5.8193 | 0 | N/A | 0 | 0
2021-09-07 01:00 | 5.0931 | 0 | N/A | 0 | 0
2021-09-07 01:30 | 5.0065 | 0 | N/A | 0 | 0
2021-09-07 02:00 | 4.7484 | 0 | N/A | 0 | 0
2021-09-07 02:30 | 4.1832 | 0 | N/A | 0 | 0
2021-09-07 03:00 | 3.8597 | 0 | N/A | 0 | 0
2021-09-07 03:30 | 3.5407 | 0 | N/A | 0 | 0
2021-09-07 04:00 | 3.3727 | 0 | N/A | 0 | 0
2021-09-07 04:30 | 3.2857 | 0 | N/A | 0 | 0
2021-09-07 05:00 | 3.3947 | 0 | N/A | 0 | 0
2021-09-07 05:30 | 3.6607 | 0 | N/A | 0 | 0
2021-09-07 06:00 | 4.0629 | 0 | N/A | 0 | 0
2021-09-07 06:30 | 4.7394 | 0 | N/A | 0 | 0
2021-09-07 07:00 | 5.4663 | 0 | N/A | 0 | 0
2021-09-07 07:30 | 5.6706 | 0 | N/A | 0 | 0
2021-09-07 08:00 | 6.0308 | 0 | N/A | 0 | 0
2021-09-07 08:30 | 6.1908 | 0 | N/A | 0 | 0
2021-09-07 09:00 | 5.9636 | 0 | N/A | 0 | 0
2021-09-07 09:30 | 4.93 | 0 | N/A | 0 | 0
2021-09-07 10:00 | 4.6733 | 0 | N/A | 0 | 0
2021-09-07 10:30 | 3.9569 | 0 | N/A | 0 | 0
2021-09-07 11:00 | 4.2335 | 0 | N/A | 0 | 0
2021-09-07 11:30 | 4.0801 | 0 | N/A | 0 | 0
2021-09-07 12:00 | 4.5536 | 0 | N/A | 0 | 0
2021-09-07 12:30 | 4.4342 | 0 | N/A | 0 | 0
2021-09-07 13:00 | 4.4853 | 0 | N/A | 0 | 0
2021-09-07 13:30 | 4.6814 | 0 | N/A | 0 | 0
2021-09-07 14:00 | 4.8082 | 0 | N/A | 0 | 0
2021-09-07 14:30 | 4.9417 | 0 | N/A | 0 | 0
2021-09-07 15:00 | 4.9551 | 0 | N/A | 0 | 0
2021-09-07 15:30 | 5.0424 | 0 | N/A | 0 | 0
2021-09-07 16:00 | 5.2422 | 0 | N/A | 0 | 0
2021-09-07 16:30 | 5.4344 | 0 | N/A | 0 | 0
2021-09-07 17:00 | 5.9604 | 0 | N/A | 0 | 0
2021-09-07 17:30 | 6.5938 | 0 | N/A | 0 | 0
2021-09-07 18:00 | 7.355 | 0 | N/A | 0 | 0
2021-09-07 18:30 | 7.7775 | 0 | N/A | 0 | 0
2021-09-07 19:00 | 7.7934 | 0 | N/A | 0 | 0
2021-09-07 19:30 | 7.3713 | 0 | N/A | 0 | 0
2021-09-07 20:00 | 6.9985 | 0 | N/A | 0 | 0
2021-09-07 20:30 | 6.7255 | 0 | N/A | 0 | 0
2021-09-07 21:00 | 6.3483 | 0 | N/A | 0 | 0
2021-09-07 21:30 | 6.5781 | 0 | N/A | 0 | 0
2021-09-07 22:00 | 6.5656 | 0 | N/A | 0 | 0
2021-09-07 22:30 | 6.1354 | 0 | N/A | 0 | 0
2021-09-07 23:00 | 6.0244 | 0 | N/A | 0 | 0
2021-09-07 23:30 | 6.2085 | 0 | N/A | 0 | 0
2021-09-08 | 6.5975 | 0 | N/A | 0 | 0
2021-09-08 00:30 | 5.9186 | 0 | N/A | 0 | 0
2021-09-08 01:00 | 5.1289 | 0 | N/A | 0 | 0
2021-09-08 01:30 | 5.0175 | 0 | N/A | 0 | 0
2021-09-08 02:00 | 4.6892 | 0 | N/A | 0 | 0
2021-09-08 02:30 | 4.1499 | 0 | N/A | 0 | 0
2021-09-08 03:00 | 3.8451 | 0 | N/A | 0 | 0
2021-09-08 03:30 | 3.6451 | 0 | N/A | 0 | 0
2021-09-08 04:00 | 3.5188 | 0 | N/A | 0 | 0
2021-09-08 04:30 | 3.6039 | 0 | N/A | 0 | 0
2021-09-08 05:00 | 3.7772 | 0 | N/A | 0 | 0
2021-09-08 05:30 | 4.075 | 0 | N/A | 0 | 0
2021-09-08 06:00 | 4.565 | 0 | N/A | 0 | 0
2021-09-08 06:30 | 5.384 | 0 | N/A | 0 | 0
2021-09-08 07:00 | 6.0919 | 0 | N/A | 0 | 0
2021-09-08 07:30 | 5.9325 | 0 | N/A | 0 | 0
2021-09-08 08:00 | 6.0146 | 0 | N/A | 0 | 0
2021-09-08 08:30 | 5.6033 | 0 | N/A | 0 | 0
2021-09-08 09:00 | 4.82 | 0 | N/A | 0 | 0
2021-09-08 09:30 | 3.8033 | 0 | N/A | 0 | 0
2021-09-08 10:00 | 2.82 | 0 | N/A | 0 | 0
2021-09-08 10:30 | 1.92 | 0 | N/A | 0 | 0
2021-09-08 11:00 | 1.3667 | 0 | N/A | 0 | 0
2021-09-08 11:30 | 0.85667 | 0 | N/A | 0 | 0
2021-09-08 12:00 | 0.53667 | 0 | N/A | 0 | 0
2021-09-08 12:30 | 0.32335 | 0 | N/A | 0 | 0
2021-09-08 13:00 | 0.14907 | 0 | N/A | 0 | 0
2021-09-08 13:30 | 0.094399 | 0 | N/A | 0 | 0
2021-09-08 14:00 | 0.058214 | 0 | N/A | 0 | 0
2021-09-08 14:30 | 0.23286 | 0 | N/A | 0 | 0
2021-09-08 15:00 | 0.63805 | 0 | N/A | 0 | 0
2021-09-08 15:30 | 1.0577 | 0 | N/A | 0 | 0
2021-09-08 16:00 | 1.4585 | 0 | N/A | 0 | 0
2021-09-08 16:30 | 2.2931 | 0 | N/A | 0 | 0
2021-09-08 17:00 | 3.2026 | 0 | N/A | 0 | 0
2021-09-08 17:30 | 4.3306 | 0 | N/A | 0 | 0
2021-09-08 18:00 | 5.5315 | 0 | N/A | 0 | 0
2021-09-08 18:30 | 6.4776 | 0 | N/A | 0 | 0
2021-09-08 19:00 | 7.0521 | 0 | N/A | 0 | 0
2021-09-08 19:30 | 6.7883 | 0 | N/A | 0 | 0
2021-09-08 20:00 | 6.5292 | 0 | N/A | 0 | 0
2021-09-08 20:30 | 6.3249 | 0 | N/A | 0 | 0
2021-09-08 21:00 | 5.957 | 0 | N/A | 0 | 0
2021-09-08 21:30 | 6.3204 | 0 | N/A | 0 | 0
2021-09-08 22:00 | 6.3732 | 0 | N/A | 0 | 0
2021-09-08 22:30 | 5.889 | 0 | N/A | 0 | 0
2021-09-08 23:00 | 5.7738 | 0 | N/A | 0 | 0
2021-09-08 23:30 | 5.914 | 0 | N/A | 0 | 0
2021-09-09 | 6.192 | 0 | N/A | 0 | 0
2021-09-09 00:30 | 5.5296 | 0 | N/A | 0 | 0
2021-09-09 01:00 | 4.8707 | 0 | N/A | 0 | 0
2021-09-09 01:30 | 4.8392 | 0 | N/A | 0 | 0
2021-09-09 02:00 | 4.3879 | 0 | N/A | 0 | 0
2021-09-09 02:30 | 3.8574 | 0 | N/A | 0 | 0
2021-09-09 03:00 | 3.5453 | 0 | N/A | 0 | 0
2021-09-09 03:30 | 3.191 | 0 | N/A | 0 | 0
2021-09-09 04:00 | 3.1181 | 0 | N/A | 0 | 0
2021-09-09 04:30 | 3.0753 | 0 | N/A | 0 | 0
2021-09-09 05:00 | 3.1975 | 0 | N/A | 0 | 0
2021-09-09 05:30 | 3.5338 | 0 | N/A | 0 | 0
2021-09-09 06:00 | 3.8677 | 0 | N/A | 0 | 0
2021-09-09 06:30 | 4.5694 | 0 | N/A | 0 | 0
2021-09-09 07:00 | 5.0492 | 0 | N/A | 0 | 0
2021-09-09 07:30 | 5.0546 | 0 | N/A | 0 | 0
2021-09-09 08:00 | 5.2994 | 0 | N/A | 0 | 0
2021-09-09 08:30 | 4.9801 | 0 | N/A | 0 | 0
2021-09-09 09:00 | 4.0002 | 0 | N/A | 0 | 0
2021-09-09 09:30 | 3.4271 | 0 | N/A | 0 | 0
2021-09-09 10:00 | 2.4848 | 0 | N/A | 0 | 0
2021-09-09 10:30 | 1.6644 | 0 | N/A | 0 | 0
2021-09-09 11:00 | 0.84744 | 0 | N/A | 0 | 0
2021-09-09 11:30 | 0.56949 | 0 | N/A | 0 | 0
2021-09-09 12:00 | 0.47 | 0 | N/A | 0 | 0
2021-09-09 12:30 | 0.2301 | 0 | N/A | 0 | 0
2021-09-09 13:00 | 0.20677 | 0 | N/A | 0 | 0
2021-09-09 13:30 | -0.02357 | 0 | N/A | 0 | 0
2021-09-09 14:00 | -0.014907 | 0 | N/A | 0 | 0
2021-09-09 14:30 | 0.17493 | 0 | N/A | 0 | 0
2021-09-09 15:00 | 0.47221 | 0 | N/A | 0 | 0
2021-09-09 15:30 | 0.91113 | 0 | N/A | 0 | 0
2021-09-09 16:00 | 0.98478 | 0 | N/A | 0 | 0
2021-09-09 16:30 | 1.6428 | 0 | N/A | 0 | 0
2021-09-09 17:00 | 3.5233 | 0 | N/A | 0 | 0
2021-09-09 17:30 | 4.7152 | 0 | N/A | 0 | 0
2021-09-09 18:00 | 5.1747 | 0 | N/A | 0 | 0
2021-09-09 18:30 | 5.8312 | 0 | N/A | 0 | 0
2021-09-09 19:00 | 6.088 | 0 | N/A | 0 | 0
2021-09-09 19:30 | 5.8346 | 0 | N/A | 0 | 0
2021-09-09 20:00 | 5.4945 | 0 | N/A | 0 | 0
2021-09-09 20:30 | 5.3114 | 0 | N/A | 0 | 0
2021-09-09 21:00 | 5.0966 | 0 | N/A | 0 | 0
2021-09-09 21:30 | 5.4671 | 0 | N/A | 0 | 0
2021-09-09 22:00 | 5.7024 | 0 | N/A | 0 | 0
2021-09-09 22:30 | 5.3361 | 0 | N/A | 0 | 0
2021-09-09 23:00 | 5.2595 | 0 | N/A | 0 | 0
2021-09-09 23:30 | 5.4826 | 0 | N/A | 0 | 0
2021-09-10 | 5.7193 | 0 | N/A | 0 | 0
2021-09-10 00:30 | 4.9371 | 0 | N/A | 0 | 0
2021-09-10 01:00 | 4.3211 | 0 | N/A | 0 | 0
2021-09-10 01:30 | 4.2984 | 0 | N/A | 0 | 0
2021-09-10 02:00 | 3.8939 | 0 | N/A | 0 | 0
2021-09-10 02:30 | 3.4664 | 0 | N/A | 0 | 0
2021-09-10 03:00 | 3.1484 | 0 | N/A | 0 | 0
2021-09-10 03:30 | 2.9697 | 0 | N/A | 0 | 0
2021-09-10 04:00 | 2.8952 | 0 | N/A | 0 | 0
2021-09-10 04:30 | 2.8102 | 0 | N/A | 0 | 0
2021-09-10 05:00 | 2.8741 | 0 | N/A | 0 | 0
2021-09-10 05:30 | 3.1174 | 0 | N/A | 0 | 0
2021-09-10 06:00 | 3.5332 | 0 | N/A | 0 | 0
2021-09-10 06:30 | 4.297 | 0 | N/A | 0 | 0
2021-09-10 07:00 | 4.7865 | 0 | N/A | 0 | 0
2021-09-10 07:30 | 4.913 | 0 | N/A | 0 | 0
2021-09-10 08:00 | 5.621 | 0 | N/A | 0 | 0
2021-09-10 08:30 | 5.825 | 0 | N/A | 0 | 0
2021-09-10 09:00 | 5.4458 | 0 | N/A | 0 | 0
2021-09-10 09:30 | 5.3268 | 0 | N/A | 0 | 0
2021-09-10 10:00 | 4.2267 | 0 | N/A | 0 | 0
2021-09-10 10:30 | 3.5293 | 0 | N/A | 0 | 0
2021-09-10 11:00 | 3.4744 | 0 | N/A | 0 | 0
2021-09-10 11:30 | 3.0719 | 0 | N/A | 0 | 0
2021-09-10 12:00 | 2.9017 | 0 | N/A | 0 | 0
2021-09-10 12:30 | 2.4762 | 0 | N/A | 0 | 0
2021-09-10 13:00 | 2.4881 | 0 | N/A | 0 | 0
2021-09-10 13:30 | 1.4781 | 0 | N/A | 0 | 0
2021-09-10 14:00 | 1.542 | 0 | N/A | 0 | 0
2021-09-10 14:30 | 2.2744 | 0 | N/A | 0 | 0
2021-09-10 15:00 | 1.7307 | 0 | N/A | 0 | 0
2021-09-10 15:30 | 1.9679 | 0 | N/A | 0 | 0
2021-09-10 16:00 | 2.3289 | 0 | N/A | 0 | 0
2021-09-10 16:30 | 2.6485 | 0 | N/A | 0 | 0
2021-09-10 17:00 | 3.6716 | 0 | N/A | 0 | 0
2021-09-10 17:30 | 4.6327 | 0 | N/A | 0 | 0
2021-09-10 18:00 | 5.4613 | 0 | N/A | 0 | 0
2021-09-10 18:30 | 6.2243 | 0 | N/A | 0 | 0
2021-09-10 19:00 | 6.6497 | 0 | N/A | 0 | 0
2021-09-10 19:30 | 6.5464 | 0 | N/A | 0 | 0
2021-09-10 20:00 | 6.3227 | 0 | N/A | 0 | 0
2021-09-10 20:30 | 6.0368 | 0 | N/A | 0 | 0
2021-09-10 21:00 | 5.7747 | 0 | N/A | 0 | 0
2021-09-10 21:30 | 6.0875 | 0 | N/A | 0 | 0
2021-09-10 22:00 | 6.291 | 0 | N/A | 0 | 0
2021-09-10 22:30 | 5.84 | 0 | N/A | 0 | 0
2021-09-10 23:00 | 5.7248 | 0 | N/A | 0 | 0
2021-09-10 23:30 | 6.0911 | 0 | N/A | 0 | 0
2021-09-11 | 6.3237 | 0 | N/A | 0 | 0
2021-09-11 00:30 | 5.4968 | 0 | N/A | 0 | 0
2021-09-11 01:00 | 4.6607 | 0 | N/A | 0 | 0
2021-09-11 01:30 | 4.4883 | 0 | N/A | 0 | 0
2021-09-11 02:00 | 4.0609 | 0 | N/A | 0 | 0
2021-09-11 02:30 | 3.5014 | 0 | N/A | 0 | 0
2021-09-11 03:00 | 3.1535 | 0 | N/A | 0 | 0
2021-09-11 03:30 | 2.8209 | 0 | N/A | 0 | 0
2021-09-11 04:00 | 2.729 | 0 | N/A | 0 | 0
2021-09-11 04:30 | 2.6411 | 0 | N/A | 0 | 0
2021-09-11 05:00 | 2.6636 | 0 | N/A | 0 | 0
2021-09-11 05:30 | 2.806 | 0 | N/A | 0 | 0
2021-09-11 06:00 | 2.9409 | 0 | N/A | 0 | 0
2021-09-11 06:30 | 3.2362 | 0 | N/A | 0 | 0
2021-09-11 07:00 | 3.5986 | 0 | N/A | 0 | 0
2021-09-11 07:30 | 3.3486 | 0 | N/A | 0 | 0
2021-09-11 08:00 | 3.3791 | 0 | N/A | 0 | 0
2021-09-11 08:30 | 3.6843 | 0 | N/A | 0 | 0
2021-09-11 09:00 | 3.9208 | 0 | N/A | 0 | 0
2021-09-11 09:30 | 3.4191 | 0 | N/A | 0 | 0
2021-09-11 10:00 | 2.6173 | 0 | N/A | 0 | 0
2021-09-11 10:30 | 2.3252 | 0 | N/A | 0 | 0
2021-09-11 11:00 | 3.3955 | 0 | N/A | 0 | 0
2021-09-11 11:30 | 4.1837 | 0 | N/A | 0 | 0
2021-09-11 12:00 | 4.2286 | 0 | N/A | 0 | 0
2021-09-11 12:30 | 4.0362 | 0 | N/A | 0 | 0
2021-09-11 13:00 | 3.6559 | 0 | N/A | 0 | 0
2021-09-11 13:30 | 3.2007 | 0 | N/A | 0 | 0
2021-09-11 14:00 | 3.0426 | 0 | N/A | 0 | 0
2021-09-11 14:30 | 3.3666 | 0 | N/A | 0 | 0
2021-09-11 15:00 | 3.857 | 0 | N/A | 0 | 0
2021-09-11 15:30 | 4.3232 | 0 | N/A | 0 | 0
2021-09-11 16:00 | 4.6528 | 0 | N/A | 0 | 0
2021-09-11 16:30 | 4.9099 | 0 | N/A | 0 | 0
2021-09-11 17:00 | 5.5393 | 0 | N/A | 0 | 0
2021-09-11 17:30 | 6.0744 | 0 | N/A | 0 | 0
2021-09-11 18:00 | 6.5543 | 0 | N/A | 0 | 0
2021-09-11 18:30 | 6.9353 | 0 | N/A | 0 | 0
2021-09-11 19:00 | 6.8681 | 0 | N/A | 0 | 0
2021-09-11 19:30 | 6.6141 | 0 | N/A | 0 | 0
2021-09-11 20:00 | 6.2559 | 0 | N/A | 0 | 0
2021-09-11 20:30 | 5.7662 | 0 | N/A | 0 | 0
2021-09-11 21:00 | 5.3955 | 0 | N/A | 0 | 0
2021-09-11 21:30 | 5.7978 | 0 | N/A | 0 | 0
2021-09-11 22:00 | 6.0382 | 0 | N/A | 0 | 0
2021-09-11 22:30 | 5.7642 | 0 | N/A | 0 | 0
2021-09-11 23:00 | 5.6961 | 0 | N/A | 0 | 0
2021-09-11 23:30 | 5.8731 | 0 | N/A | 0 | 0
2021-09-12 | 6.203 | 0 | N/A | 0 | 0
2021-09-12 00:30 | 5.515 | 0 | N/A | 0 | 0
2021-09-12 01:00 | 4.818 | 0 | N/A | 0 | 0
2021-09-12 01:30 | 4.7002 | 0 | N/A | 0 | 0
2021-09-12 02:00 | 4.3494 | 0 | N/A | 0 | 0
2021-09-12 02:30 | 3.7494 | 0 | N/A | 0 | 0
2021-09-12 03:00 | 3.3922 | 0 | N/A | 0 | 0
2021-09-12 03:30 | 3.1749 | 0 | N/A | 0 | 0
2021-09-12 04:00 | 3.0516 | 0 | N/A | 0 | 0
2021-09-12 04:30 | 2.9356 | 0 | N/A | 0 | 0
2021-09-12 05:00 | 2.9055 | 0 | N/A | 0 | 0
2021-09-12 05:30 | 3.096 | 0 | N/A | 0 | 0
2021-09-12 06:00 | 3.3543 | 0 | N/A | 0 | 0
2021-09-12 06:30 | 3.6268 | 0 | N/A | 0 | 0
2021-09-12 07:00 | 3.6995 | 0 | N/A | 0 | 0
2021-09-12 07:30 | 3.3704 | 0 | N/A | 0 | 0
2021-09-12 08:00 | 3.3209 | 0 | N/A | 0 | 0
2021-09-12 08:30 | 3.1232 | 0 | N/A | 0 | 0
2021-09-12 09:00 | 3.7747 | 0 | N/A | 0 | 0
2021-09-12 09:30 | 2.9765 | 0 | N/A | 0 | 0
2021-09-12 10:00 | 2.3199 | 0 | N/A | 0 | 0
2021-09-12 10:30 | 2.3493 | 0 | N/A | 0 | 0
2021-09-12 11:00 | 1.5805 | 0 | N/A | 0 | 0
2021-09-12 11:30 | 1.3571 | 0 | N/A | 0 | 0
2021-09-12 12:00 | 0.78021 | 0 | N/A | 0 | 0
2021-09-12 12:30 | 1.7616 | 0 | N/A | 0 | 0
2021-09-12 13:00 | 1.8871 | 0 | N/A | 0 | 0
2021-09-12 13:30 | 2.2446 | 0 | N/A | 0 | 0
2021-09-12 14:00 | 1.8879 | 0 | N/A | 0 | 0
2021-09-12 14:30 | 1.6943 | 0 | N/A | 0 | 0
2021-09-12 15:00 | 3.4004 | 0 | N/A | 0 | 0
2021-09-12 15:30 | 3.2308 | 0 | N/A | 0 | 0
2021-09-12 16:00 | 3.9039 | 0 | N/A | 0 | 0
2021-09-12 16:30 | 5.3763 | 0 | N/A | 0 | 0
2021-09-12 17:00 | 6.3096 | 0 | N/A | 0 | 0
2021-09-12 17:30 | 6.736 | 0 | N/A | 0 | 0
2021-09-12 18:00 | 7.4088 | 0 | N/A | 0 | 0
2021-09-12 18:30 | 8.0424 | 0 | N/A | 0 | 0
2021-09-12 19:00 | 8.094 | 0 | N/A | 0 | 0
2021-09-12 19:30 | 7.7885 | 0 | N/A | 0 | 0
2021-09-12 20:00 | 7.3262 | 0 | N/A | 0 | 0
2021-09-12 20:30 | 6.8744 | 0 | N/A | 0 | 0
2021-09-12 21:00 | 6.44 | 0 | N/A | 0 | 0
2021-09-12 21:30 | 6.6913 | 0 | N/A | 0 | 0
2021-09-12 22:00 | 6.8828 | 0 | N/A | 0 | 0
2021-09-12 22:30 | 6.3752 | 0 | N/A | 0 | 0
2021-09-12 23:00 | 6.2396 | 0 | N/A | 0 | 0
2021-09-12 23:30 | 6.3664 | 0 | N/A | 0 | 0
2021-09-13 | 6.6961 | 0 | N/A | 0 | 0
2021-09-13 00:30 | 6.0477 | 0 | N/A | 0 | 0
2021-09-13 01:00 | 5.2447 | 0 | N/A | 0 | 0
2021-09-13 01:30 | 5.2612 | 0 | N/A | 0 | 0
2021-09-13 02:00 | 4.8777 | 0 | N/A | 0 | 0
2021-09-13 02:30 | 4.337 | 0 | N/A | 0 | 0
2021-09-13 03:00 | 4.035 | 0 | N/A | 0 | 0
2021-09-13 03:30 | 3.8014 | 0 | N/A | 0 | 0
2021-09-13 04:00 | 3.7102 | 0 | N/A | 0 | 0
2021-09-13 04:30 | 3.6927 | 0 | N/A | 0 | 0
2021-09-13 05:00 | 3.7602 | 0 | N/A | 0 | 0
2021-09-13 05:30 | 4.0933 | 0 | N/A | 0 | 0
2021-09-13 06:00 | 4.6227 | 0 | N/A | 0 | 0
2021-09-13 06:30 | 5.4755 | 0 | N/A | 0 | 0
2021-09-13 07:00 | 6.1948 | 0 | N/A | 0 | 0
2021-09-13 07:30 | 5.9621 | 0 | N/A | 0 | 0
2021-09-13 08:00 | 6.0959 | 0 | N/A | 0 | 0
2021-09-13 08:30 | 5.8801 | 0 | N/A | 0 | 0
2021-09-13 09:00 | 4.837 | 0 | N/A | 0 | 0
2021-09-13 09:30 | 4.0636 | 0 | N/A | 0 | 0
2021-09-13 10:00 | 4.5641 | 0 | N/A | 0 | 0
2021-09-13 10:30 | 4.7109 | 0 | N/A | 0 | 0
2021-09-13 11:00 | 3.9166 | 0 | N/A | 0 | 0
2021-09-13 11:30 | 2.8734 | 0 | N/A | 0 | 0
2021-09-13 12:00 | 3.8734 | 0 | N/A | 0 | 0
2021-09-13 12:30 | 3.1167 | 0 | N/A | 0 | 0
2021-09-13 13:00 | 3.1182 | 0 | N/A | 0 | 0
2021-09-13 13:30 | 2.9706 | 0 | N/A | 0 | 0
2021-09-13 14:00 | 2.3333 | 0 | N/A | 0 | 0
2021-09-13 14:30 | 3.2443 | 0 | N/A | 0 | 0
2021-09-13 15:00 | 2.9732 | 0 | N/A | 0 | 0
2021-09-13 15:30 | 3.6651 | 0 | N/A | 0 | 0
2021-09-13 16:00 | 3.4603 | 0 | N/A | 0 | 0
2021-09-13 16:30 | 4.8506 | 0 | N/A | 0 | 0
2021-09-13 17:00 | 5.4163 | 0 | N/A | 0 | 0
2021-09-13 17:30 | 6.4582 | 0 | N/A | 0 | 0
2021-09-13 18:00 | 7.5338 | 0 | N/A | 0 | 0
2021-09-13 18:30 | 8.1617 | 0 | N/A | 0 | 0
2021-09-13 19:00 | 8.3513 | 0 | N/A | 0 | 0
2021-09-13 19:30 | 8.0456 | 0 | N/A | 0 | 0
2021-09-13 20:00 | 7.6583 | 0 | N/A | 0 | 0
2021-09-13 20:30 | 7.3888 | 0 | N/A | 0 | 0
2021-09-13 21:00 | 6.9096 | 0 | N/A | 0 | 0
2021-09-13 21:30 | 6.9623 | 0 | N/A | 0 | 0
2021-09-13 22:00 | 7.017 | 0 | N/A | 0 | 0
2021-09-13 22:30 | 6.4589 | 0 | N/A | 0 | 0
2021-09-13 23:00 | 6.2324 | 0 | N/A | 0 | 0
2021-09-13 23:30 | 6.4999 | 0 | N/A | 0 | 0
2021-09-14 | 6.7464 | 0 | N/A | 0 | 0
2021-09-14 00:30 | 6.1096 | 0 | N/A | 0 | 0
2021-09-14 01:00 | 5.3301 | 0 | N/A | 0 | 0
2021-09-14 01:30 | 5.0778 | 0 | N/A | 0 | 0
2021-09-14 02:00 | 4.8508 | 0 | N/A | 0 | 0
2021-09-14 02:30 | 4.3189 | 0 | N/A | 0 | 0
2021-09-14 03:00 | 3.8879 | 0 | N/A | 0 | 0
2021-09-14 03:30 | 3.6842 | 0 | N/A | 0 | 0
2021-09-14 04:00 | 3.5652 | 0 | N/A | 0 | 0
2021-09-14 04:30 | 3.6007 | 0 | N/A | 0 | 0
2021-09-14 05:00 | 3.7165 | 0 | N/A | 0 | 0
2021-09-14 05:30 | 4.1124 | 0 | N/A | 0 | 0
2021-09-14 06:00 | 4.6461 | 0 | N/A | 0 | 0
2021-09-14 06:30 | 5.5441 | 0 | N/A | 0 | 0
2021-09-14 07:00 | 6.0054 | 0 | N/A | 0 | 0
2021-09-14 07:30 | 5.6496 | 0 | N/A | 0 | 0
2021-09-14 08:00 | 5.5174 | 0 | N/A | 0 | 0
2021-09-14 08:30 | 5.156 | 0 | N/A | 0 | 0
2021-09-14 09:00 | 4.6175 | 0 | N/A | 0 | 0
2021-09-14 09:30 | 3.6748 | 0 | N/A | 0 | 0
2021-09-14 10:00 | 3.0525 | 0 | N/A | 0 | 0
2021-09-14 10:30 | 2.6968 | 0 | N/A | 0 | 0
2021-09-14 11:00 | 2.5666 | 0 | N/A | 0 | 0
2021-09-14 11:30 | 2.6949 | 0 | N/A | 0 | 0
2021-09-14 12:00 | 2.3175 | 0 | N/A | 0 | 0
2021-09-14 12:30 | 2.8836 | 0 | N/A | 0 | 0
2021-09-14 13:00 | 2.5123 | 0 | N/A | 0 | 0
2021-09-14 13:30 | 2.7424 | 0 | N/A | 0 | 0
2021-09-14 14:00 | 2.5285 | 0 | N/A | 0 | 0
2021-09-14 14:30 | 2.7218 | 0 | N/A | 0 | 0
2021-09-14 15:00 | 3.1914 | 0 | N/A | 0 | 0
2021-09-14 15:30 | 3.9019 | 0 | N/A | 0 | 0
2021-09-14 16:00 | 4.3227 | 0 | N/A | 0 | 0
2021-09-14 16:30 | 4.9481 | 0 | N/A | 0 | 0
2021-09-14 17:00 | 5.5541 | 0 | N/A | 0 | 0
2021-09-14 17:30 | 6.3596 | 0 | N/A | 0 | 0
2021-09-14 18:00 | 7.379 | 0 | N/A | 0 | 0
2021-09-14 18:30 | 7.85 | 0 | N/A | 0 | 0
2021-09-14 19:00 | 7.954 | 0 | N/A | 0 | 0
2021-09-14 19:30 | 7.6928 | 0 | N/A | 0 | 0
2021-09-14 20:00 | 7.3911 | 0 | N/A | 0 | 0
2021-09-14 20:30 | 7.0364 | 0 | N/A | 0 | 0
2021-09-14 21:00 | 6.6435 | 0 | N/A | 0 | 0
2021-09-14 21:30 | 6.8319 | 0 | N/A | 0 | 0
2021-09-14 22:00 | 6.9592 | 0 | N/A | 0 | 0
2021-09-14 22:30 | 6.3943 | 0 | N/A | 0 | 0
2021-09-14 23:00 | 6.3288 | 0 | N/A | 0 | 0
2021-09-14 23:30 | 6.4581 | 0 | N/A | 0 | 0
2021-09-15 | 6.6626 | 0 | N/A | 0 | 0
2021-09-15 00:30 | 5.9773 | 0 | N/A | 0 | 0
2021-09-15 01:00 | 5.2269 | 0 | N/A | 0 | 0
2021-09-15 01:30 | 5.2 | 0 | N/A | 0 | 0
2021-09-15 02:00 | 4.9243 | 0 | N/A | 0 | 0
2021-09-15 02:30 | 4.4512 | 0 | N/A | 0 | 0
2021-09-15 03:00 | 4.0364 | 0 | N/A | 0 | 0
2021-09-15 03:30 | 3.8184 | 0 | N/A | 0 | 0
2021-09-15 04:00 | 3.7146 | 0 | N/A | 0 | 0
2021-09-15 04:30 | 3.6992 | 0 | N/A | 0 | 0
2021-09-15 05:00 | 3.841 | 0 | N/A | 0 | 0
2021-09-15 05:30 | 4.0772 | 0 | N/A | 0 | 0
2021-09-15 06:00 | 4.6225 | 0 | N/A | 0 | 0
2021-09-15 06:30 | 5.5787 | 0 | N/A | 0 | 0
2021-09-15 07:00 | 6.0613 | 0 | N/A | 0 | 0
2021-09-15 07:30 | 5.8423 | 0 | N/A | 0 | 0
2021-09-15 08:00 | 5.8505 | 0 | N/A | 0 | 0
2021-09-15 08:30 | 5.6999 | 0 | N/A | 0 | 0
2021-09-15 09:00 | 5.0312 | 0 | N/A | 0 | 0
2021-09-15 09:30 | 4.6262 | 0 | N/A | 0 | 0
2021-09-15 10:00 | 4.5723 | 0 | N/A | 0 | 0
2021-09-15 10:30 | 4.679 | 0 | N/A | 0 | 0
2021-09-15 11:00 | 4.3717 | 0 | N/A | 0 | 0
2021-09-15 11:30 | 3.8768 | 0 | N/A | 0 | 0
2021-09-15 12:00 | 3.3924 | 0 | N/A | 0 | 0
2021-09-15 12:30 | 3.4201 | 0 | N/A | 0 | 0
2021-09-15 13:00 | 3.0348 | 0 | N/A | 0 | 0
2021-09-15 13:30 | 3.6794 | 0 | N/A | 0 | 0
2021-09-15 14:00 | 3.7557 | 0 | N/A | 0 | 0
2021-09-15 14:30 | 3.3374 | 0 | N/A | 0 | 0
2021-09-15 15:00 | 2.6248 | 0 | N/A | 0 | 0
2021-09-15 15:30 | 2.7195 | 0 | N/A | 0 | 0
2021-09-15 16:00 | 3.2597 | 0 | N/A | 0 | 0
2021-09-15 16:30 | 3.798 | 0 | N/A | 0 | 0
2021-09-15 17:00 | 4.305 | 0 | N/A | 0 | 0
2021-09-15 17:30 | 5.3273 | 0 | N/A | 0 | 0
2021-09-15 18:00 | 6.4048 | 0 | N/A | 0 | 0
2021-09-15 18:30 | 7.3215 | 0 | N/A | 0 | 0
2021-09-15 19:00 | 7.8928 | 0 | N/A | 0 | 0
2021-09-15 19:30 | 7.7728 | 0 | N/A | 0 | 0
2021-09-15 20:00 | 7.5128 | 0 | N/A | 0 | 0
2021-09-15 20:30 | 7.1983 | 0 | N/A | 0 | 0
2021-09-15 21:00 | 6.8472 | 0 | N/A | 0 | 0
2021-09-15 21:30 | 7.1237 | 0 | N/A | 0 | 0
2021-09-15 22:00 | 7.1575 | 0 | N/A | 0 | 0
2021-09-15 22:30 | 6.515 | 0 | N/A | 0 | 0
2021-09-15 23:00 | 6.2887 | 0 | N/A | 0 | 0
2021-09-15 23:30 | 6.4121 | 0 | N/A | 0 | 0
2021-09-16 | 6.725 | 0 | N/A | 0 | 0
2021-09-16 00:30 | 5.9959 | 0 | N/A | 0 | 0
2021-09-16 01:00 | 5.3106 | 0 | N/A | 0 | 0
2021-09-16 01:30 | 5.1003 | 0 | N/A | 0 | 0
2021-09-16 02:00 | 4.8142 | 0 | N/A | 0 | 0
2021-09-16 02:30 | 4.2786 | 0 | N/A | 0 | 0
2021-09-16 03:00 | 3.8883 | 0 | N/A | 0 | 0
2021-09-16 03:30 | 3.7812 | 0 | N/A | 0 | 0
2021-09-16 04:00 | 3.6106 | 0 | N/A | 0 | 0
2021-09-16 04:30 | 3.576 | 0 | N/A | 0 | 0
2021-09-16 05:00 | 3.6567 | 0 | N/A | 0 | 0
2021-09-16 05:30 | 4.0043 | 0 | N/A | 0 | 0
2021-09-16 06:00 | 4.5807 | 0 | N/A | 0 | 0
2021-09-16 06:30 | 5.2518 | 0 | N/A | 0 | 0
2021-09-16 07:00 | 5.5969 | 0 | N/A | 0 | 0
2021-09-16 07:30 | 5.2632 | 0 | N/A | 0 | 0
2021-09-16 08:00 | 5.2382 | 0 | N/A | 0 | 0
2021-09-16 08:30 | 4.8397 | 0 | N/A | 0 | 0
2021-09-16 09:00 | 4.0486 | 0 | N/A | 0 | 0
2021-09-16 09:30 | 2.9713 | 0 | N/A | 0 | 0
2021-09-16 10:00 | 1.9049 | 0 | N/A | 0 | 0
2021-09-16 10:30 | 1.2111 | 0 | N/A | 0 | 0
2021-09-16 11:00 | 1.0687 | 0 | N/A | 0 | 0
2021-09-16 11:30 | 1.8946 | 0 | N/A | 0 | 0
2021-09-16 12:00 | 1.1028 | 0 | N/A | 0 | 0
2021-09-16 12:30 | 1.5749 | 0 | N/A | 0 | 0
2021-09-16 13:00 | 2.1154 | 0 | N/A | 0 | 0
2021-09-16 13:30 | 2.6828 | 0 | N/A | 0 | 0
2021-09-16 14:00 | 2.6184 | 0 | N/A | 0 | 0
2021-09-16 14:30 | 2.5674 | 0 | N/A | 0 | 0
2021-09-16 15:00 | 2.9251 | 0 | N/A | 0 | 0
2021-09-16 15:30 | 3.2756 | 0 | N/A | 0 | 0
2021-09-16 16:00 | 3.2995 | 0 | N/A | 0 | 0
2021-09-16 16:30 | 3.0901 | 0 | N/A | 0 | 0
2021-09-16 17:00 | 3.5113 | 0 | N/A | 0 | 0
2021-09-16 17:30 | 4.4897 | 0 | N/A | 0 | 0
2021-09-16 18:00 | 5.6878 | 0 | N/A | 0 | 0
2021-09-16 18:30 | 6.7358 | 0 | N/A | 0 | 0
2021-09-16 19:00 | 7.2281 | 0 | N/A | 0 | 0
2021-09-16 19:30 | 7.2348 | 0 | N/A | 0 | 0
2021-09-16 20:00 | 6.9334 | 0 | N/A | 0 | 0
2021-09-16 20:30 | 6.7554 | 0 | N/A | 0 | 0
2021-09-16 21:00 | 6.5096 | 0 | N/A | 0 | 0
2021-09-16 21:30 | 6.7612 | 0 | N/A | 0 | 0
2021-09-16 22:00 | 6.8029 | 0 | N/A | 0 | 0
2021-09-16 22:30 | 6.4203 | 0 | N/A | 0 | 0
2021-09-16 23:00 | 6.2651 | 0 | N/A | 0 | 0
2021-09-16 23:30 | 6.249 | 0 | N/A | 0 | 0
2021-09-17 | 6.5943 | 0 | N/A | 0 | 0
2021-09-17 00:30 | 5.9748 | 0 | N/A | 0 | 0
2021-09-17 01:00 | 5.3152 | 0 | N/A | 0 | 0
2021-09-17 01:30 | 5.1294 | 0 | N/A | 0 | 0
2021-09-17 02:00 | 4.7298 | 0 | N/A | 0 | 0
2021-09-17 02:30 | 4.1065 | 0 | N/A | 0 | 0
2021-09-17 03:00 | 3.7439 | 0 | N/A | 0 | 0
2021-09-17 03:30 | 3.4802 | 0 | N/A | 0 | 0
2021-09-17 04:00 | 3.2884 | 0 | N/A | 0 | 0
2021-09-17 04:30 | 3.2664 | 0 | N/A | 0 | 0
2021-09-17 05:00 | 3.3434 | 0 | N/A | 0 | 0
2021-09-17 05:30 | 3.5436 | 0 | N/A | 0 | 0
2021-09-17 06:00 | 3.9727 | 0 | N/A | 0 | 0
2021-09-17 06:30 | 4.6991 | 0 | N/A | 0 | 0
2021-09-17 07:00 | 4.9885 | 0 | N/A | 0 | 0
2021-09-17 07:30 | 4.1791 | 0 | N/A | 0 | 0
2021-09-17 08:00 | 4.3537 | 0 | N/A | 0 | 0
2021-09-17 08:30 | 4.5994 | 0 | N/A | 0 | 0
2021-09-17 09:00 | 3.6057 | 0 | N/A | 0 | 0
2021-09-17 09:30 | 3.1509 | 0 | N/A | 0 | 0
2021-09-17 10:00 | 4.578 | 0 | N/A | 0 | 0
2021-09-17 10:30 | 2.8341 | 0 | N/A | 0 | 0
2021-09-17 11:00 | 1.1313 | 0 | N/A | 0 | 0
2021-09-17 11:30 | 2.3171 | 0 | N/A | 0 | 0
2021-09-17 12:00 | 2.3967 | 0 | N/A | 0 | 0
2021-09-17 12:30 | 1.8718 | 0 | N/A | 0 | 0
2021-09-17 13:00 | 1.8631 | 0 | N/A | 0 | 0
2021-09-17 13:30 | 0.3941 | 0 | N/A | 0 | 0
2021-09-17 14:00 | -0.34294 | 0 | N/A | 0 | 0
2021-09-17 14:30 | -0.5069 | 0 | N/A | 0 | 0
2021-09-17 15:00 | -0.5101 | 0 | N/A | 0 | 0
2021-09-17 15:30 | 1.8243 | 0 | N/A | 0 | 0
2021-09-17 16:00 | 2.2635 | 0 | N/A | 0 | 0
2021-09-17 16:30 | 2.2265 | 0 | N/A | 0 | 0
2021-09-17 17:00 | 3.4683 | 0 | N/A | 0 | 0
2021-09-17 17:30 | 4.4344 | 0 | N/A | 0 | 0
2021-09-17 18:00 | 5.0879 | 0 | N/A | 0 | 0
2021-09-17 18:30 | 6.0154 | 0 | N/A | 0 | 0
2021-09-17 19:00 | 6.4797 | 0 | N/A | 0 | 0
2021-09-17 19:30 | 6.1661 | 0 | N/A | 0 | 0
2021-09-17 20:00 | 5.9446 | 0 | N/A | 0 | 0
2021-09-17 20:30 | 5.6579 | 0 | N/A | 0 | 0
2021-09-17 21:00 | 5.289 | 0 | N/A | 0 | 0
2021-09-17 21:30 | 5.5957 | 0 | N/A | 0 | 0
2021-09-17 22:00 | 2.2674 | 0 | N/A | 0 | 0
2021-09-17 22:30 | 6.6072 | 0 | N/A | 0 | 0
2021-09-17 23:00 | 6.7623 | 0 | N/A | 0 | 0
2021-09-17 23:30 | 5.4811 | 0 | N/A | 0 | 0
2021-09-18 | 5.9579 | 0 | N/A | 0 | 0
2021-09-18 00:30 | 5.2906 | 0 | N/A | 0 | 0
2021-09-18 01:00 | 4.5011 | 0 | N/A | 0 | 0
2021-09-18 01:30 | 4.4311 | 0 | N/A | 0 | 0
2021-09-18 02:00 | 4.1898 | 0 | N/A | 0 | 0
2021-09-18 02:30 | 3.5813 | 0 | N/A | 0 | 0
2021-09-18 03:00 | 3.1735 | 0 | N/A | 0 | 0
2021-09-18 03:30 | 2.9665 | 0 | N/A | 0 | 0
2021-09-18 04:00 | 2.8187 | 0 | N/A | 0 | 0
2021-09-18 04:30 | 2.7952 | 0 | N/A | 0 | 0
2021-09-18 05:00 | 2.7388 | 0 | N/A | 0 | 0
2021-09-18 05:30 | 2.8772 | 0 | N/A | 0 | 0
2021-09-18 06:00 | 2.997 | 0 | N/A | 0 | 0
2021-09-18 06:30 | 3.3566 | 0 | N/A | 0 | 0
2021-09-18 07:00 | 3.4963 | 0 | N/A | 0 | 0
2021-09-18 07:30 | 3.2862 | 0 | N/A | 0 | 0
2021-09-18 08:00 | 3.0132 | 0 | N/A | 0 | 0
2021-09-18 08:30 | 3.3123 | 0 | N/A | 0 | 0
2021-09-18 09:00 | 2.4035 | 0 | N/A | 0 | 0
2021-09-18 09:30 | 2.3888 | 0 | N/A | 0 | 0
2021-09-18 10:00 | 1.9297 | 0 | N/A | 0 | 0
2021-09-18 10:30 | 2.0741 | 0 | N/A | 0 | 0
2021-09-18 11:00 | 2.16 | 0 | N/A | 0 | 0
2021-09-18 11:30 | 2.9697 | 0 | N/A | 0 | 0
2021-09-18 12:00 | 1.5485 | 0 | N/A | 0 | 0
2021-09-18 12:30 | 1.941 | 0 | N/A | 0 | 0
2021-09-18 13:00 | 1.9679 | 0 | N/A | 0 | 0
2021-09-18 13:30 | 0.59876 | 0 | N/A | 0 | 0
2021-09-18 14:00 | 1.4982 | 0 | N/A | 0 | 0
2021-09-18 14:30 | 1.6462 | 0 | N/A | 0 | 0
2021-09-18 15:00 | 1.3763 | 0 | N/A | 0 | 0
2021-09-18 15:30 | 3.5468 | 0 | N/A | 0 | 0
2021-09-18 16:00 | 3.3261 | 0 | N/A | 0 | 0
2021-09-18 16:30 | 3.1725 | 0 | N/A | 0 | 0
2021-09-18 17:00 | 4.8018 | 0 | N/A | 0 | 0
2021-09-18 17:30 | 5.7557 | 0 | N/A | 0 | 0
2021-09-18 18:00 | 6.6769 | 0 | N/A | 0 | 0
2021-09-18 18:30 | 7.2782 | 0 | N/A | 0 | 0
2021-09-18 19:00 | 7.6127 | 0 | N/A | 0 | 0
2021-09-18 19:30 | 7.237 | 0 | N/A | 0 | 0
2021-09-18 20:00 | 6.8715 | 0 | N/A | 0 | 0
2021-09-18 20:30 | 6.5153 | 0 | N/A | 0 | 0
2021-09-18 21:00 | 6.2786 | 0 | N/A | 0 | 0
2021-09-18 21:30 | 6.6105 | 0 | N/A | 0 | 0
2021-09-18 22:00 | 6.7018 | 0 | N/A | 0 | 0
2021-09-18 22:30 | 6.4637 | 0 | N/A | 0 | 0
2021-09-18 23:00 | 6.3475 | 0 | N/A | 0 | 0
2021-09-18 23:30 | 6.5279 | 0 | N/A | 0 | 0
2021-09-19 | 6.8507 | 0 | N/A | 0 | 0
2021-09-19 00:30 | 6.1628 | 0 | N/A | 0 | 0
2021-09-19 01:00 | 5.4147 | 0 | N/A | 0 | 0
2021-09-19 01:30 | 5.2714 | 0 | N/A | 0 | 0
2021-09-19 02:00 | 4.7826 | 0 | N/A | 0 | 0
2021-09-19 02:30 | 4.2708 | 0 | N/A | 0 | 0
2021-09-19 03:00 | 3.9518 | 0 | N/A | 0 | 0
2021-09-19 03:30 | 3.6437 | 0 | N/A | 0 | 0
2021-09-19 04:00 | 3.3957 | 0 | N/A | 0 | 0
2021-09-19 04:30 | 3.2513 | 0 | N/A | 0 | 0
2021-09-19 05:00 | 3.2058 | 0 | N/A | 0 | 0
2021-09-19 05:30 | 3.347 | 0 | N/A | 0 | 0
2021-09-19 06:00 | 3.5326 | 0 | N/A | 0 | 0
2021-09-19 06:30 | 3.7827 | 0 | N/A | 0 | 0
2021-09-19 07:00 | 3.9591 | 0 | N/A | 0 | 0
2021-09-19 07:30 | 3.5343 | 0 | N/A | 0 | 0
2021-09-19 08:00 | 3.2468 | 0 | N/A | 0 | 0
2021-09-19 08:30 | 3.4739 | 0 | N/A | 0 | 0
2021-09-19 09:00 | 3.0041 | 0 | N/A | 0 | 0
2021-09-19 09:30 | 2.5848 | 0 | N/A | 0 | 0
2021-09-19 10:00 | 3.1602 | 0 | N/A | 0 | 0
2021-09-19 10:30 | 2.5819 | 0 | N/A | 0 | 0
2021-09-19 11:00 | 1.8127 | 0 | N/A | 0 | 0
2021-09-19 11:30 | 1.8212 | 0 | N/A | 0 | 0
2021-09-19 12:00 | 3.5657 | 0 | N/A | 0 | 0
2021-09-19 12:30 | 3.8689 | 0 | N/A | 0 | 0
2021-09-19 13:00 | 3.5412 | 0 | N/A | 0 | 0
2021-09-19 13:30 | 3.2376 | 0 | N/A | 0 | 0
2021-09-19 14:00 | 3.5376 | 0 | N/A | 0 | 0
2021-09-19 14:30 | 3.4624 | 0 | N/A | 0 | 0
2021-09-19 15:00 | 4.0994 | 0 | N/A | 0 | 0
2021-09-19 15:30 | 5.1583 | 0 | N/A | 0 | 0
2021-09-19 16:00 | 5.2268 | 0 | N/A | 0 | 0
2021-09-19 16:30 | 5.6148 | 0 | N/A | 0 | 0
2021-09-19 17:00 | 6.0608 | 0 | N/A | 0 | 0
2021-09-19 17:30 | 6.8544 | 0 | N/A | 0 | 0
2021-09-19 18:00 | 7.5343 | 0 | N/A | 0 | 0
2021-09-19 18:30 | 7.5466 | 0 | N/A | 0 | 0
2021-09-19 19:00 | 7.402 | 0 | N/A | 0 | 0
2021-09-19 19:30 | 6.9843 | 0 | N/A | 0 | 0
2021-09-19 20:00 | 6.5161 | 0 | N/A | 0 | 0
2021-09-19 20:30 | 6.1548 | 0 | N/A | 0 | 0
2021-09-19 21:00 | 5.7838 | 0 | N/A | 0 | 0
2021-09-19 21:30 | 6.055 | 0 | N/A | 0 | 0
2021-09-19 22:00 | 6.2395 | 0 | N/A | 0 | 0
2021-09-19 22:30 | 5.8806 | 0 | N/A | 0 | 0
2021-09-19 23:00 | 5.8722 | 0 | N/A | 0 | 0
2021-09-19 23:30 | 5.8 | 0 | N/A | 0 | 0
2021-09-20 | 6.1137 | 0 | N/A | 0 | 0
2021-09-20 00:30 | 5.5772 | 0 | N/A | 0 | 0
2021-09-20 01:00 | 4.9617 | 0 | N/A | 0 | 0
2021-09-20 01:30 | 4.8032 | 0 | N/A | 0 | 0
2021-09-20 02:00 | 4.4918 | 0 | N/A | 0 | 0
2021-09-20 02:30 | 4.0024 | 0 | N/A | 0 | 0
2021-09-20 03:00 | 3.6367 | 0 | N/A | 0 | 0
2021-09-20 03:30 | 3.4296 | 0 | N/A | 0 | 0
2021-09-20 04:00 | 3.2231 | 0 | N/A | 0 | 0
2021-09-20 04:30 | 3.2903 | 0 | N/A | 0 | 0
2021-09-20 05:00 | 3.3234 | 0 | N/A | 0 | 0
2021-09-20 05:30 | 3.613 | 0 | N/A | 0 | 0
2021-09-20 06:00 | 4.0348 | 0 | N/A | 0 | 0
2021-09-20 06:30 | 4.8793 | 0 | N/A | 0 | 0
2021-09-20 07:00 | 5.1342 | 0 | N/A | 0 | 0
2021-09-20 07:30 | 4.9755 | 0 | N/A | 0 | 0
2021-09-20 08:00 | 5.05 | 0 | N/A | 0 | 0
2021-09-20 08:30 | 4.727 | 0 | N/A | 0 | 0
2021-09-20 09:00 | 5.8891 | 0 | N/A | 0 | 0
2021-09-20 09:30 | 5.3536 | 0 | N/A | 0 | 0
2021-09-20 10:00 | 5.5011 | 0 | N/A | 0 | 0
2021-09-20 10:30 | 5.3421 | 0 | N/A | 0 | 0
2021-09-20 11:00 | 4.7784 | 0 | N/A | 0 | 0
2021-09-20 11:30 | 5.2953 | 0 | N/A | 0 | 0
2021-09-20 12:00 | 5.1744 | 0 | N/A | 0 | 0
2021-09-20 12:30 | 7.1152 | 0 | N/A | 0 | 0
2021-09-20 13:00 | 5.1903 | 0 | N/A | 0 | 0
2021-09-20 13:30 | 4.7367 | 0 | N/A | 0 | 0
2021-09-20 14:00 | 6.0668 | 0 | N/A | 0 | 0
2021-09-20 14:30 | 5.7001 | 0 | N/A | 0 | 0
2021-09-20 15:00 | 6.8767 | 0 | N/A | 0 | 0
2021-09-20 15:30 | 6.5601 | 0 | N/A | 0 | 0
2021-09-20 16:00 | 4.8996 | 0 | N/A | 0 | 0
2021-09-20 16:30 | 6.6094 | 0 | N/A | 0 | 0
2021-09-20 17:00 | 6.8117 | 0 | N/A | 0 | 0
2021-09-20 17:30 | 7.8613 | 0 | N/A | 0 | 0
2021-09-20 18:00 | 8.9574 | 0 | N/A | 0 | 0
2021-09-20 18:30 | 9.5 | 0 | N/A | 0 | 0
2021-09-20 19:00 | 9.4733 | 0 | N/A | 0 | 0
2021-09-20 19:30 | 8.9436 | 0 | N/A | 0 | 0
2021-09-20 20:00 | 8.3912 | 0 | N/A | 0 | 0
2021-09-20 20:30 | 8.0254 | 0 | N/A | 0 | 0
2021-09-20 21:00 | 7.5986 | 0 | N/A | 0 | 0
2021-09-20 21:30 | 7.8242 | 0 | N/A | 0 | 0
2021-09-20 22:00 | 7.8272 | 0 | N/A | 0 | 0
2021-09-20 22:30 | 7.109 | 0 | N/A | 0 | 0
2021-09-20 23:00 | 6.9809 | 0 | N/A | 0 | 0
2021-09-20 23:30 | 6.9689 | 0 | N/A | 0 | 0
2021-09-21 | 7.3687 | 0 | N/A | 0 | 0
2021-09-21 00:30 | 6.7962 | 0 | N/A | 0 | 0
2021-09-21 01:00 | 6.0674 | 0 | N/A | 0 | 0
2021-09-21 01:30 | 5.9305 | 0 | N/A | 0 | 0
2021-09-21 02:00 | 5.4834 | 0 | N/A | 0 | 0
2021-09-21 02:30 | 4.9402 | 0 | N/A | 0 | 0
2021-09-21 03:00 | 4.5146 | 0 | N/A | 0 | 0
2021-09-21 03:30 | 4.2928 | 0 | N/A | 0 | 0
2021-09-21 04:00 | 4.091 | 0 | N/A | 0 | 0
2021-09-21 04:30 | 4.0305 | 0 | N/A | 0 | 0
2021-09-21 05:00 | 4.1116 | 0 | N/A | 0 | 0
2021-09-21 05:30 | 4.4368 | 0 | N/A | 0 | 0
2021-09-21 06:00 | 4.8361 | 0 | N/A | 0 | 0
2021-09-21 06:30 | 5.632 | 0 | N/A | 0 | 0
2021-09-21 07:00 | 5.9659 | 0 | N/A | 0 | 0
2021-09-21 07:30 | 6.08 | 0 | N/A | 0 | 0
2021-09-21 08:00 | 6.3141 | 0 | N/A | 0 | 0
2021-09-21 08:30 | 6.4424 | 0 | N/A | 0 | 0
2021-09-21 09:00 | 5.9451 | 0 | N/A | 0 | 0
2021-09-21 09:30 | 5.0961 | 0 | N/A | 0 | 0
2021-09-21 10:00 | 4.1932 | 0 | N/A | 0 | 0
2021-09-21 10:30 | 4.792 | 0 | N/A | 0 | 0
2021-09-21 11:00 | 4.964 | 0 | N/A | 0 | 0
2021-09-21 11:30 | 2.7433 | 0 | N/A | 0 | 0
2021-09-21 12:00 | 3.6945 | 0 | N/A | 0 | 0
2021-09-21 12:30 | 3.9152 | 0 | N/A | 0 | 0
2021-09-21 13:00 | 3.9082 | 0 | N/A | 0 | 0
2021-09-21 13:30 | 4.3136 | 0 | N/A | 0 | 0
2021-09-21 14:00 | 5.3636 | 0 | N/A | 0 | 0
2021-09-21 14:30 | 6.0202 | 0 | N/A | 0 | 0
2021-09-21 15:00 | 6.3904 | 0 | N/A | 0 | 0
2021-09-21 15:30 | 6.5141 | 0 | N/A | 0 | 0
2021-09-21 16:00 | 6.3723 | 0 | N/A | 0 | 0
2021-09-21 16:30 | 6.7834 | 0 | N/A | 0 | 0
2021-09-21 17:00 | 6.9601 | 0 | N/A | 0 | 0
2021-09-21 17:30 | 7.516 | 0 | N/A | 0 | 0
2021-09-21 18:00 | 8.3641 | 0 | N/A | 0 | 0
2021-09-21 18:30 | 8.7779 | 0 | N/A | 0 | 0
2021-09-21 19:00 | 8.6706 | 0 | N/A | 0 | 0
2021-09-21 19:30 | 8.2871 | 0 | N/A | 0 | 0
2021-09-21 20:00 | 7.9279 | 0 | N/A | 0 | 0
2021-09-21 20:30 | 7.4719 | 0 | N/A | 0 | 0
2021-09-21 21:00 | 7.0216 | 0 | N/A | 0 | 0
2021-09-21 21:30 | 7.0521 | 0 | N/A | 0 | 0
2021-09-21 22:00 | 7.0867 | 0 | N/A | 0 | 0
2021-09-21 22:30 | 6.657 | 0 | N/A | 0 | 0
2021-09-21 23:00 | 6.454 | 0 | N/A | 0 | 0
2021-09-21 23:30 | 6.6387 | 0 | N/A | 0 | 0
2021-09-22 | 6.9421 | 0 | N/A | 0 | 0
2021-09-22 00:30 | 6.3315 | 0 | N/A | 0 | 0
2021-09-22 01:00 | 5.4358 | 0 | N/A | 0 | 0
2021-09-22 01:30 | 5.3233 | 0 | N/A | 0 | 0
2021-09-22 02:00 | 4.8991 | 0 | N/A | 0 | 0
2021-09-22 02:30 | 4.3388 | 0 | N/A | 0 | 0
2021-09-22 03:00 | 3.9483 | 0 | N/A | 0 | 0
2021-09-22 03:30 | 3.7699 | 0 | N/A | 0 | 0
2021-09-22 04:00 | 3.5485 | 0 | N/A | 0 | 0
2021-09-22 04:30 | 3.4515 | 0 | N/A | 0 | 0
2021-09-22 05:00 | 3.5381 | 0 | N/A | 0 | 0
2021-09-22 05:30 | 3.7629 | 0 | N/A | 0 | 0
2021-09-22 06:00 | 4.2116 | 0 | N/A | 0 | 0
2021-09-22 06:30 | 4.8178 | 0 | N/A | 0 | 0
2021-09-22 07:00 | 5.0451 | 0 | N/A | 0 | 0
2021-09-22 07:30 | 5.3015 | 0 | N/A | 0 | 0
2021-09-22 08:00 | 5.7273 | 0 | N/A | 0 | 0
2021-09-22 08:30 | 6.034 | 0 | N/A | 0 | 0
2021-09-22 09:00 | 5.8238 | 0 | N/A | 0 | 0
2021-09-22 09:30 | 5.4674 | 0 | N/A | 0 | 0
2021-09-22 10:00 | 5.0474 | 0 | N/A | 0 | 0
2021-09-22 10:30 | 4.8605 | 0 | N/A | 0 | 0
2021-09-22 11:00 | 4.5367 | 0 | N/A | 0 | 0
2021-09-22 11:30 | 4.0235 | 0 | N/A | 0 | 0
2021-09-22 12:00 | 3.4836 | 0 | N/A | 0 | 0
2021-09-22 12:30 | 3.0706 | 0 | N/A | 0 | 0
2021-09-22 13:00 | 3.1282 | 0 | N/A | 0 | 0
2021-09-22 13:30 | 3.408 | 0 | N/A | 0 | 0
2021-09-22 14:00 | 2.563 | 0 | N/A | 0 | 0
2021-09-22 14:30 | 2.3646 | 0 | N/A | 0 | 0
2021-09-22 15:00 | 2.6739 | 0 | N/A | 0 | 0
2021-09-22 15:30 | 2.4869 | 0 | N/A | 0 | 0
2021-09-22 16:00 | 2.5307 | 0 | N/A | 0 | 0
2021-09-22 16:30 | 2.9249 | 0 | N/A | 0 | 0
2021-09-22 17:00 | 3.4069 | 0 | N/A | 0 | 0
2021-09-22 17:30 | 4.4852 | 0 | N/A | 0 | 0
2021-09-22 18:00 | 5.5008 | 0 | N/A | 0 | 0
2021-09-22 18:30 | 6.436 | 0 | N/A | 0 | 0
2021-09-22 19:00 | 6.8327 | 0 | N/A | 0 | 0
2021-09-22 19:30 | 6.749 | 0 | N/A | 0 | 0
2021-09-22 20:00 | 6.4998 | 0 | N/A | 0 | 0
2021-09-22 20:30 | 6.3234 | 0 | N/A | 0 | 0
2021-09-22 21:00 | 6.0704 | 0 | N/A | 0 | 0
2021-09-22 21:30 | 6.4145 | 0 | N/A | 0 | 0
2021-09-22 22:00 | 6.5722 | 0 | N/A | 0 | 0
2021-09-22 22:30 | 6.1964 | 0 | N/A | 0 | 0
2021-09-22 23:00 | 5.9969 | 0 | N/A | 0 | 0
2021-09-22 23:30 | 6.1949 | 0 | N/A | 0 | 0
2021-09-23 | 6.5213 | 0 | N/A | 0 | 0
2021-09-23 00:30 | 5.7979 | 0 | N/A | 0 | 0
2021-09-23 01:00 | 4.9457 | 0 | N/A | 0 | 0
2021-09-23 01:30 | 4.8527 | 0 | N/A | 0 | 0
2021-09-23 02:00 | 4.4899 | 0 | N/A | 0 | 0
2021-09-23 02:30 | 3.9351 | 0 | N/A | 0 | 0
2021-09-23 03:00 | 3.6333 | 0 | N/A | 0 | 0
2021-09-23 03:30 | 3.4619 | 0 | N/A | 0 | 0
2021-09-23 04:00 | 3.3371 | 0 | N/A | 0 | 0
2021-09-23 04:30 | 3.3399 | 0 | N/A | 0 | 0
2021-09-23 05:00 | 3.4162 | 0 | N/A | 0 | 0
2021-09-23 05:30 | 3.6414 | 0 | N/A | 0 | 0
2021-09-23 06:00 | 4.0794 | 0 | N/A | 0 | 0
2021-09-23 06:30 | 4.8211 | 0 | N/A | 0 | 0
2021-09-23 07:00 | 5.1779 | 0 | N/A | 0 | 0
2021-09-23 07:30 | 5.4991 | 0 | N/A | 0 | 0
2021-09-23 08:00 | 5.7806 | 0 | N/A | 0 | 0
2021-09-23 08:30 | 5.9518 | 0 | N/A | 0 | 0
2021-09-23 09:00 | 5.7345 | 0 | N/A | 0 | 0
2021-09-23 09:30 | 5.3073 | 0 | N/A | 0 | 0
2021-09-23 10:00 | 4.4211 | 0 | N/A | 0 | 0
2021-09-23 10:30 | 2.8491 | 0 | N/A | 0 | 0
2021-09-23 11:00 | 2.0667 | 0 | N/A | 0 | 0
2021-09-23 11:30 | 0.74506 | 0 | N/A | 0 | 0
2021-09-23 12:00 | 0.51777 | 0 | N/A | 0 | 0
2021-09-23 12:30 | 0.3265 | 0 | N/A | 0 | 0
2021-09-23 13:00 | -0.24306 | 0 | N/A | 0 | 0
2021-09-23 13:30 | -0.17464 | 0 | N/A | 0 | 0
2021-09-23 14:00 | -0.19576 | 0 | N/A | 0 | 0
2021-09-23 14:30 | 0.21934 | 0 | N/A | 0 | 0
2021-09-23 15:00 | 0.24585 | 0 | N/A | 0 | 0
2021-09-23 15:30 | 0.47853 | 0 | N/A | 0 | 0
2021-09-23 16:00 | 1.0737 | 0 | N/A | 0 | 0
2021-09-23 16:30 | 1.6269 | 0 | N/A | 0 | 0
2021-09-23 17:00 | 2.5628 | 0 | N/A | 0 | 0
2021-09-23 17:30 | 3.6008 | 0 | N/A | 0 | 0
2021-09-23 18:00 | 4.7916 | 0 | N/A | 0 | 0
2021-09-23 18:30 | 5.6362 | 0 | N/A | 0 | 0
2021-09-23 19:00 | 6.3154 | 0 | N/A | 0 | 0
2021-09-23 19:30 | 6.4588 | 0 | N/A | 0 | 0
2021-09-23 20:00 | 6.3315 | 0 | N/A | 0 | 0
2021-09-23 20:30 | 6.1408 | 0 | N/A | 0 | 0
2021-09-23 21:00 | 5.9073 | 0 | N/A | 0 | 0
2021-09-23 21:30 | 6.2348 | 0 | N/A | 0 | 0
2021-09-23 22:00 | 6.3685 | 0 | N/A | 0 | 0
2021-09-23 22:30 | 6.0402 | 0 | N/A | 0 | 0
2021-09-23 23:00 | 5.9082 | 0 | N/A | 0 | 0
2021-09-23 23:30 | 6.0274 | 0 | N/A | 0 | 0
2021-09-24 | 6.3265 | 0 | N/A | 0 | 0
2021-09-24 00:30 | 5.4268 | 0 | N/A | 0 | 0
2021-09-24 01:00 | 4.749 | 0 | N/A | 0 | 0
2021-09-24 01:30 | 4.5992 | 0 | N/A | 0 | 0
2021-09-24 02:00 | 4.2401 | 0 | N/A | 0 | 0
2021-09-24 02:30 | 3.7084 | 0 | N/A | 0 | 0
2021-09-24 03:00 | 3.3311 | 0 | N/A | 0 | 0
2021-09-24 03:30 | 3.2504 | 0 | N/A | 0 | 0
2021-09-24 04:00 | 3.1009 | 0 | N/A | 0 | 0
2021-09-24 04:30 | 3.0862 | 0 | N/A | 0 | 0
2021-09-24 05:00 | 3.0661 | 0 | N/A | 0 | 0
2021-09-24 05:30 | 3.2776 | 0 | N/A | 0 | 0
2021-09-24 06:00 | 3.4408 | 0 | N/A | 0 | 0
2021-09-24 06:30 | 3.8018 | 0 | N/A | 0 | 0
2021-09-24 07:00 | 3.8264 | 0 | N/A | 0 | 0
2021-09-24 07:30 | 3.2466 | 0 | N/A | 0 | 0
2021-09-24 08:00 | 2.9124 | 0 | N/A | 0 | 0
2021-09-24 08:30 | 3.3168 | 0 | N/A | 0 | 0
2021-09-24 09:00 | 3.1458 | 0 | N/A | 0 | 0
2021-09-24 09:30 | 3.7604 | 0 | N/A | 0 | 0
2021-09-24 10:00 | 4.8407 | 0 | N/A | 0 | 0
2021-09-24 10:30 | 4.3762 | 0 | N/A | 0 | 0
2021-09-24 11:00 | 4.899 | 0 | N/A | 0 | 0
2021-09-24 11:30 | 4.3762 | 0 | N/A | 0 | 0
2021-09-24 12:00 | 4.0499 | 0 | N/A | 0 | 0
2021-09-24 12:30 | 1.9688 | 0 | N/A | 0 | 0
2021-09-24 13:00 | 1.2875 | 0 | N/A | 0 | 0
2021-09-24 13:30 | 1.2662 | 0 | N/A | 0 | 0
2021-09-24 14:00 | 1.5515 | 0 | N/A | 0 | 0
2021-09-24 14:30 | 1.6467 | 0 | N/A | 0 | 0
2021-09-24 15:00 | 1.3185 | 0 | N/A | 0 | 0
2021-09-24 15:30 | 1.6309 | 0 | N/A | 0 | 0
2021-09-24 16:00 | 2.1029 | 0 | N/A | 0 | 0
2021-09-24 16:30 | 3.1944 | 0 | N/A | 0 | 0
2021-09-24 17:00 | 4.1303 | 0 | N/A | 0 | 0
2021-09-24 17:30 | 5.246 | 0 | N/A | 0 | 0
2021-09-24 18:00 | 6.5257 | 0 | N/A | 0 | 0
2021-09-24 18:30 | 7.1845 | 0 | N/A | 0 | 0
2021-09-24 19:00 | 7.3565 | 0 | N/A | 0 | 0
2021-09-24 19:30 | 7.2562 | 0 | N/A | 0 | 0
2021-09-24 20:00 | 7.0132 | 0 | N/A | 0 | 0
2021-09-24 20:30 | 6.8204 | 0 | N/A | 0 | 0
2021-09-24 21:00 | 6.5287 | 0 | N/A | 0 | 0
2021-09-24 21:30 | 6.7386 | 0 | N/A | 0 | 0
2021-09-24 22:00 | 6.9273 | 0 | N/A | 0 | 0
2021-09-24 22:30 | 6.5227 | 0 | N/A | 0 | 0
2021-09-24 23:00 | 6.5625 | 0 | N/A | 0 | 0
2021-09-24 23:30 | 6.7402 | 0 | N/A | 0 | 0
2021-09-25 | 6.9158 | 0 | N/A | 0 | 0
2021-09-25 00:30 | 6.1878 | 0 | N/A | 0 | 0
2021-09-25 01:00 | 5.4796 | 0 | N/A | 0 | 0
2021-09-25 01:30 | 5.3943 | 0 | N/A | 0 | 0
2021-09-25 02:00 | 4.8931 | 0 | N/A | 0 | 0
2021-09-25 02:30 | 4.3911 | 0 | N/A | 0 | 0
2021-09-25 03:00 | 4.0122 | 0 | N/A | 0 | 0
2021-09-25 03:30 | 3.7701 | 0 | N/A | 0 | 0
2021-09-25 04:00 | 3.622 | 0 | N/A | 0 | 0
2021-09-25 04:30 | 3.5311 | 0 | N/A | 0 | 0
2021-09-25 05:00 | 3.5146 | 0 | N/A | 0 | 0
2021-09-25 05:30 | 3.6577 | 0 | N/A | 0 | 0
2021-09-25 06:00 | 3.858 | 0 | N/A | 0 | 0
2021-09-25 06:30 | 4.152 | 0 | N/A | 0 | 0
2021-09-25 07:00 | 4.3156 | 0 | N/A | 0 | 0
2021-09-25 07:30 | 4.0271 | 0 | N/A | 0 | 0
2021-09-25 08:00 | 4.1651 | 0 | N/A | 0 | 0
2021-09-25 08:30 | 3.8518 | 0 | N/A | 0 | 0
2021-09-25 09:00 | 3.2767 | 0 | N/A | 0 | 0
2021-09-25 09:30 | 2.7392 | 0 | N/A | 0 | 0
2021-09-25 10:00 | 3.0837 | 0 | N/A | 0 | 0
2021-09-25 10:30 | 2.7884 | 0 | N/A | 0 | 0
2021-09-25 11:00 | 3.2654 | 0 | N/A | 0 | 0
2021-09-25 11:30 | 1.597 | 0 | N/A | 0 | 0
2021-09-25 12:00 | 2.8354 | 0 | N/A | 0 | 0
2021-09-25 12:30 | 2.0581 | 0 | N/A | 0 | 0
2021-09-25 13:00 | 1.8911 | 0 | N/A | 0 | 0
2021-09-25 13:30 | 2.9412 | 0 | N/A | 0 | 0
2021-09-25 14:00 | 1.6678 | 0 | N/A | 0 | 0
2021-09-25 14:30 | 2.0513 | 0 | N/A | 0 | 0
2021-09-25 15:00 | 1.5481 | 0 | N/A | 0 | 0
2021-09-25 15:30 | 2.2242 | 0 | N/A | 0 | 0
2021-09-25 16:00 | 2.2969 | 0 | N/A | 0 | 0
2021-09-25 16:30 | 2.9719 | 0 | N/A | 0 | 0
2021-09-25 17:00 | 4.1838 | 0 | N/A | 0 | 0
2021-09-25 17:30 | 5.1555 | 0 | N/A | 0 | 0
2021-09-25 18:00 | 6.2115 | 0 | N/A | 0 | 0
2021-09-25 18:30 | 7.202 | 0 | N/A | 0 | 0
2021-09-25 19:00 | 7.4324 | 0 | N/A | 0 | 0
2021-09-25 19:30 | 7.3167 | 0 | N/A | 0 | 0
2021-09-25 20:00 | 7.075 | 0 | N/A | 0 | 0
2021-09-25 20:30 | 6.7082 | 0 | N/A | 0 | 0
2021-09-25 21:00 | 6.5945 | 0 | N/A | 0 | 0
2021-09-25 21:30 | 6.9319 | 0 | N/A | 0 | 0
2021-09-25 22:00 | 7.2966 | 0 | N/A | 0 | 0
2021-09-25 22:30 | 7.1368 | 0 | N/A | 0 | 0
2021-09-25 23:00 | 7.0805 | 0 | N/A | 0 | 0
2021-09-25 23:30 | 7.1417 | 0 | N/A | 0 | 0
2021-09-26 | 7.3427 | 0 | N/A | 0 | 0
2021-09-26 00:30 | 6.6686 | 0 | N/A | 0 | 0
2021-09-26 01:00 | 5.859 | 0 | N/A | 0 | 0
2021-09-26 01:30 | 5.6974 | 0 | N/A | 0 | 0
2021-09-26 02:00 | 5.3147 | 0 | N/A | 0 | 0
2021-09-26 02:30 | 4.8027 | 0 | N/A | 0 | 0
2021-09-26 03:00 | 4.4944 | 0 | N/A | 0 | 0
2021-09-26 03:30 | 4.2593 | 0 | N/A | 0 | 0
2021-09-26 04:00 | 4.1123 | 0 | N/A | 0 | 0
2021-09-26 04:30 | 4.035 | 0 | N/A | 0 | 0
2021-09-26 05:00 | 3.9603 | 0 | N/A | 0 | 0
2021-09-26 05:30 | 4.0515 | 0 | N/A | 0 | 0
2021-09-26 06:00 | 4.1897 | 0 | N/A | 0 | 0
2021-09-26 06:30 | 4.6114 | 0 | N/A | 0 | 0
2021-09-26 07:00 | 4.5538 | 0 | N/A | 0 | 0
2021-09-26 07:30 | 4.2786 | 0 | N/A | 0 | 0
2021-09-26 08:00 | 3.8256 | 0 | N/A | 0 | 0
2021-09-26 08:30 | 3.2922 | 0 | N/A | 0 | 0
2021-09-26 09:00 | 2.706 | 0 | N/A | 0 | 0
2021-09-26 09:30 | 2.0121 | 0 | N/A | 0 | 0
2021-09-26 10:00 | 1.3829 | 0 | N/A | 0 | 0
2021-09-26 10:30 | 1.0087 | 0 | N/A | 0 | 0
2021-09-26 11:00 | 0.51229 | 0 | N/A | 0 | 0
2021-09-26 11:30 | -0.54546 | 0 | N/A | 0 | 0
2021-09-26 12:00 | -0.67476 | 0 | N/A | 0 | 0
2021-09-26 12:30 | -0.77029 | 0 | N/A | 0 | 0
2021-09-26 13:00 | -0.95862 | 0 | N/A | 0 | 0
2021-09-26 13:30 | -0.96128 | 0 | N/A | 0 | 0
2021-09-26 14:00 | -0.98035 | 0 | N/A | 0 | 0
2021-09-26 14:30 | -0.84086 | 0 | N/A | 0 | 0
2021-09-26 15:00 | -0.72987 | 0 | N/A | 0 | 0
2021-09-26 15:30 | 0.61757 | 0 | N/A | 0 | 0
2021-09-26 16:00 | 0.98552 | 0 | N/A | 0 | 0
2021-09-26 16:30 | 1.6443 | 0 | N/A | 0 | 0
2021-09-26 17:00 | 2.7502 | 0 | N/A | 0 | 0
2021-09-26 17:30 | 4.1506 | 0 | N/A | 0 | 0
2021-09-26 18:00 | 5.4263 | 0 | N/A | 0 | 0
2021-09-26 18:30 | 6.56 | 0 | N/A | 0 | 0
2021-09-26 19:00 | 7.3698 | 0 | N/A | 0 | 0
2021-09-26 19:30 | 7.3912 | 0 | N/A | 0 | 0
2021-09-26 20:00 | 7.0233 | 0 | N/A | 0 | 0
2021-09-26 20:30 | 6.6992 | 0 | N/A | 0 | 0
2021-09-26 21:00 | 6.4742 | 0 | N/A | 0 | 0
2021-09-26 21:30 | 6.7319 | 0 | N/A | 0 | 0
2021-09-26 22:00 | 6.8125 | 0 | N/A | 0 | 0
2021-09-26 22:30 | 6.3705 | 0 | N/A | 0 | 0
2021-09-26 23:00 | 6.2688 | 0 | N/A | 0 | 0
2021-09-26 23:30 | 6.3172 | 0 | N/A | 0 | 0
2021-09-27 | 6.6855 | 0 | N/A | 0 | 0
2021-09-27 00:30 | 6.0332 | 0 | N/A | 0 | 0
2021-09-27 01:00 | 5.3627 | 0 | N/A | 0 | 0
2021-09-27 01:30 | 5.2447 | 0 | N/A | 0 | 0
2021-09-27 02:00 | 4.9682 | 0 | N/A | 0 | 0
2021-09-27 02:30 | 4.4814 | 0 | N/A | 0 | 0
2021-09-27 03:00 | 4.1438 | 0 | N/A | 0 | 0
2021-09-27 03:30 | 3.9116 | 0 | N/A | 0 | 0
2021-09-27 04:00 | 3.7011 | 0 | N/A | 0 | 0
2021-09-27 04:30 | 3.6752 | 0 | N/A | 0 | 0
2021-09-27 05:00 | 3.6995 | 0 | N/A | 0 | 0
2021-09-27 05:30 | 4.1675 | 0 | N/A | 0 | 0
2021-09-27 06:00 | 4.5538 | 0 | N/A | 0 | 0
2021-09-27 06:30 | 5.3958 | 0 | N/A | 0 | 0
2021-09-27 07:00 | 5.8482 | 0 | N/A | 0 | 0
2021-09-27 07:30 | 5.4035 | 0 | N/A | 0 | 0
2021-09-27 08:00 | 4.9963 | 0 | N/A | 0 | 0
2021-09-27 08:30 | 5.3894 | 0 | N/A | 0 | 0
2021-09-27 09:00 | 4.0704 | 0 | N/A | 0 | 0
2021-09-27 09:30 | 2.8918 | 0 | N/A | 0 | 0
2021-09-27 10:00 | 1.9331 | 0 | N/A | 0 | 0
2021-09-27 10:30 | 1.1202 | 0 | N/A | 0 | 0
2021-09-27 11:00 | 1.2148 | 0 | N/A | 0 | 0
2021-09-27 11:30 | 0.97548 | 0 | N/A | 0 | 0
2021-09-27 12:00 | 0.66416 | 0 | N/A | 0 | 0
2021-09-27 12:30 | -0.24895 | 0 | N/A | 0 | 0
2021-09-27 13:00 | -0.30463 | 0 | N/A | 0 | 0
2021-09-27 13:30 | -0.21082 | 0 | N/A | 0 | 0
2021-09-27 14:00 | -0.36401 | 0 | N/A | 0 | 0
2021-09-27 14:30 | 0.23795 | 0 | N/A | 0 | 0
2021-09-27 15:00 | 0.32014 | 0 | N/A | 0 | 0
2021-09-27 15:30 | 0.65552 | 0 | N/A | 0 | 0
2021-09-27 16:00 | 1.2449 | 0 | N/A | 0 | 0
2021-09-27 16:30 | 1.9158 | 0 | N/A | 0 | 0
2021-09-27 17:00 | 2.9654 | 0 | N/A | 0 | 0
2021-09-27 17:30 | 3.9957 | 0 | N/A | 0 | 0
2021-09-27 18:00 | 5.1089 | 0 | N/A | 0 | 0
2021-09-27 18:30 | 6.02 | 0 | N/A | 0 | 0
2021-09-27 19:00 | 6.6132 | 0 | N/A | 0 | 0
2021-09-27 19:30 | 6.6813 | 0 | N/A | 0 | 0
2021-09-27 20:00 | 6.5524 | 0 | N/A | 0 | 0
2021-09-27 20:30 | 6.3475 | 0 | N/A | 0 | 0
2021-09-27 21:00 | 6.1999 | 0 | N/A | 0 | 0
2021-09-27 21:30 | 6.4522 | 0 | N/A | 0 | 0
2021-09-27 22:00 | 6.5002 | 0 | N/A | 0 | 0
2021-09-27 22:30 | 6.1129 | 0 | N/A | 0 | 0
2021-09-27 23:00 | 5.9269 | 0 | N/A | 0 | 0
2021-09-27 23:30 | 6.038 | 0 | N/A | 0 | 0
2021-09-28 | 6.3454 | 0 | N/A | 0 | 0
2021-09-28 00:30 | 5.6478 | 0 | N/A | 0 | 0
2021-09-28 01:00 | 4.9167 | 0 | N/A | 0 | 0
2021-09-28 01:30 | 4.7963 | 0 | N/A | 0 | 0
2021-09-28 02:00 | 4.4564 | 0 | N/A | 0 | 0
2021-09-28 02:30 | 4.0245 | 0 | N/A | 0 | 0
2021-09-28 03:00 | 3.7181 | 0 | N/A | 0 | 0
2021-09-28 03:30 | 3.5004 | 0 | N/A | 0 | 0
2021-09-28 04:00 | 3.3503 | 0 | N/A | 0 | 0
2021-09-28 04:30 | 3.3649 | 0 | N/A | 0 | 0
2021-09-28 05:00 | 3.4132 | 0 | N/A | 0 | 0
2021-09-28 05:30 | 3.8137 | 0 | N/A | 0 | 0
2021-09-28 06:00 | 4.1709 | 0 | N/A | 0 | 0
2021-09-28 06:30 | 4.8153 | 0 | N/A | 0 | 0
2021-09-28 07:00 | 5.1224 | 0 | N/A | 0 | 0
2021-09-28 07:30 | 4.8778 | 0 | N/A | 0 | 0
2021-09-28 08:00 | 4.5743 | 0 | N/A | 0 | 0
2021-09-28 08:30 | 4.7722 | 0 | N/A | 0 | 0
2021-09-28 09:00 | 5.8954 | 0 | N/A | 0 | 0
2021-09-28 09:30 | 4.7621 | 0 | N/A | 0 | 0
2021-09-28 10:00 | 3.1561 | 0 | N/A | 0 | 0
2021-09-28 10:30 | 3.5189 | 0 | N/A | 0 | 0
2021-09-28 11:00 | 1.8782 | 0 | N/A | 0 | 0
2021-09-28 11:30 | 1.3729 | 0 | N/A | 0 | 0
2021-09-28 12:00 | 1.0961 | 0 | N/A | 0 | 0
2021-09-28 12:30 | 1.1795 | 0 | N/A | 0 | 0
2021-09-28 13:00 | 1.386 | 0 | N/A | 0 | 0
2021-09-28 13:30 | 1.8678 | 0 | N/A | 0 | 0
2021-09-28 14:00 | 1.3275 | 0 | N/A | 0 | 0
2021-09-28 14:30 | 1.5053 | 0 | N/A | 0 | 0
2021-09-28 15:00 | 1.8958 | 0 | N/A | 0 | 0
2021-09-28 15:30 | 2.1892 | 0 | N/A | 0 | 0
2021-09-28 16:00 | 3.3582 | 0 | N/A | 0 | 0
2021-09-28 16:30 | 3.7739 | 0 | N/A | 0 | 0
2021-09-28 17:00 | 3.4291 | 0 | N/A | 0 | 0
2021-09-28 17:30 | 4.0152 | 0 | N/A | 0 | 0
2021-09-28 18:00 | 4.9084 | 0 | N/A | 0 | 0
2021-09-28 18:30 | 5.6156 | 0 | N/A | 0 | 0
2021-09-28 19:00 | 6.0141 | 0 | N/A | 0 | 0
2021-09-28 19:30 | 6.0374 | 0 | N/A | 0 | 0
2021-09-28 20:00 | 5.8417 | 0 | N/A | 0 | 0
2021-09-28 20:30 | 5.551 | 0 | N/A | 0 | 0
2021-09-28 21:00 | 5.2207 | 0 | N/A | 0 | 0
2021-09-28 21:30 | 5.5761 | 0 | N/A | 0 | 0
2021-09-28 22:00 | 5.754 | 0 | N/A | 0 | 0
2021-09-28 22:30 | 5.1756 | 0 | N/A | 0 | 0
2021-09-28 23:00 | 5.0022 | 0 | N/A | 0 | 0
2021-09-28 23:30 | 5.2898 | 0 | N/A | 0 | 0
2021-09-29 | 5.6569 | 0 | N/A | 0 | 0
2021-09-29 00:30 | 5.0128 | 0 | N/A | 0 | 0
2021-09-29 01:00 | 4.2741 | 0 | N/A | 0 | 0
2021-09-29 01:30 | 4.0825 | 0 | N/A | 0 | 0
2021-09-29 02:00 | 3.7544 | 0 | N/A | 0 | 0
2021-09-29 02:30 | 3.3249 | 0 | N/A | 0 | 0
2021-09-29 03:00 | 3.0526 | 0 | N/A | 0 | 0
2021-09-29 03:30 | 2.8872 | 0 | N/A | 0 | 0
2021-09-29 04:00 | 2.7232 | 0 | N/A | 0 | 0
2021-09-29 04:30 | 2.7797 | 0 | N/A | 0 | 0
2021-09-29 05:00 | 2.7482 | 0 | N/A | 0 | 0
2021-09-29 05:30 | 2.9869 | 0 | N/A | 0 | 0
2021-09-29 06:00 | 3.3407 | 0 | N/A | 0 | 0
2021-09-29 06:30 | 3.9164 | 0 | N/A | 0 | 0
2021-09-29 07:00 | 4.1415 | 0 | N/A | 0 | 0
2021-09-29 07:30 | 4.0538 | 0 | N/A | 0 | 0
2021-09-29 08:00 | 3.9886 | 0 | N/A | 0 | 0
2021-09-29 08:30 | 4.2038 | 0 | N/A | 0 | 0
2021-09-29 09:00 | 4.2088 | 0 | N/A | 0 | 0
2021-09-29 09:30 | 3.24 | 0 | N/A | 0 | 0
2021-09-29 10:00 | 3.9855 | 0 | N/A | 0 | 0
2021-09-29 10:30 | 4.211 | 0 | N/A | 0 | 0
2021-09-29 11:00 | 3.6876 | 0 | N/A | 0 | 0
2021-09-29 11:30 | 3.447 | 0 | N/A | 0 | 0
2021-09-29 12:00 | 3.1834 | 0 | N/A | 0 | 0
2021-09-29 12:30 | 3.2353 | 0 | N/A | 0 | 0
2021-09-29 13:00 | 2.2971 | 0 | N/A | 0 | 0
2021-09-29 13:30 | 2.6116 | 0 | N/A | 0 | 0
2021-09-29 14:00 | 3.0006 | 0 | N/A | 0 | 0
2021-09-29 14:30 | 2.1723 | 0 | N/A | 0 | 0
2021-09-29 15:00 | 2.0657 | 0 | N/A | 0 | 0
2021-09-29 15:30 | 3.0819 | 0 | N/A | 0 | 0
2021-09-29 16:00 | 3.846 | 0 | N/A | 0 | 0
2021-09-29 16:30 | 4.4306 | 0 | N/A | 0 | 0
2021-09-29 17:00 | 5.2645 | 0 | N/A | 0 | 0
2021-09-29 17:30 | 5.5865 | 0 | N/A | 0 | 0
2021-09-29 18:00 | 6.2672 | 0 | N/A | 0 | 0
2021-09-29 18:30 | 6.8744 | 0 | N/A | 0 | 0
2021-09-29 19:00 | 7.0736 | 0 | N/A | 0 | 0
2021-09-29 19:30 | 6.7197 | 0 | N/A | 0 | 0
2021-09-29 20:00 | 6.4211 | 0 | N/A | 0 | 0
2021-09-29 20:30 | 6.1421 | 0 | N/A | 0 | 0
2021-09-29 21:00 | 5.855 | 0 | N/A | 0 | 0
2021-09-29 21:30 | 6.0653 | 0 | N/A | 0 | 0
2021-09-29 22:00 | 6.2056 | 0 | N/A | 0 | 0
2021-09-29 22:30 | 5.8456 | 0 | N/A | 0 | 0
2021-09-29 23:00 | 5.7248 | 0 | N/A | 0 | 0
2021-09-29 23:30 | 5.8746 | 0 | N/A | 0 | 0
2021-09-30 | 6.2525 | 0 | N/A | 0 | 0
2021-09-30 00:30 | 5.5005 | 0 | N/A | 0 | 0
2021-09-30 01:00 | 4.6437 | 0 | N/A | 0 | 0
2021-09-30 01:30 | 4.4859 | 0 | N/A | 0 | 0
2021-09-30 02:00 | 4.0348 | 0 | N/A | 0 | 0
2021-09-30 02:30 | 3.5095 | 0 | N/A | 0 | 0
2021-09-30 03:00 | 3.2024 | 0 | N/A | 0 | 0
2021-09-30 03:30 | 3.0896 | 0 | N/A | 0 | 0
2021-09-30 04:00 | 2.8745 | 0 | N/A | 0 | 0
2021-09-30 04:30 | 2.8819 | 0 | N/A | 0 | 0
2021-09-30 05:00 | 2.9421 | 0 | N/A | 0 | 0
2021-09-30 05:30 | 3.1346 | 0 | N/A | 0 | 0
2021-09-30 06:00 | 3.5363 | 0 | N/A | 0 | 0
2021-09-30 06:30 | 4.0958 | 0 | N/A | 0 | 0
2021-09-30 07:00 | 4.3501 | 0 | N/A | 0 | 0
2021-09-30 07:30 | 4.4508 | 0 | N/A | 0 | 0
2021-09-30 08:00 | 4.7164 | 0 | N/A | 0 | 0
2021-09-30 08:30 | 4.9164 | 0 | N/A | 0 | 0
2021-09-30 09:00 | 4.7584 | 0 | N/A | 0 | 0
2021-09-30 09:30 | 4.1904 | 0 | N/A | 0 | 0
2021-09-30 10:00 | 3.7206 | 0 | N/A | 0 | 0
2021-09-30 10:30 | 3.4342 | 0 | N/A | 0 | 0
2021-09-30 11:00 | 3.9834 | 0 | N/A | 0 | 0
2021-09-30 11:30 | 4.3357 | 0 | N/A | 0 | 0
2021-09-30 12:00 | 4.1986 | 0 | N/A | 0 | 0
2021-09-30 12:30 | 4.4434 | 0 | N/A | 0 | 0
2021-09-30 13:00 | 4.5854 | 0 | N/A | 0 | 0
2021-09-30 13:30 | 5.1618 | 0 | N/A | 0 | 0
2021-09-30 14:00 | 4.7154 | 0 | N/A | 0 | 0
2021-09-30 14:30 | 4.7435 | 0 | N/A | 0 | 0
2021-09-30 15:00 | 4.9603 | 0 | N/A | 0 | 0
2021-09-30 15:30 | 5.0531 | 0 | N/A | 0 | 0
2021-09-30 16:00 | 5.0769 | 0 | N/A | 0 | 0
2021-09-30 16:30 | 5.2167 | 0 | N/A | 0 | 0
2021-09-30 17:00 | 5.6848 | 0 | N/A | 0 | 0
2021-09-30 17:30 | 6.0895 | 0 | N/A | 0 | 0
2021-09-30 18:00 | 6.7092 | 0 | N/A | 0 | 0
2021-09-30 18:30 | 7.131 | 0 | N/A | 0 | 0
2021-09-30 19:00 | 7.2649 | 0 | N/A | 0 | 0
2021-09-30 19:30 | 6.9201 | 0 | N/A | 0 | 0
2021-09-30 20:00 | 6.6065 | 0 | N/A | 0 | 0
2021-09-30 20:30 | 6.3792 | 0 | N/A | 0 | 0
2021-09-30 21:00 | 6.0065 | 0 | N/A | 0 | 0
2021-09-30 21:30 | 6.1728 | 0 | N/A | 0 | 0
2021-09-30 22:00 | 6.2325 | 0 | N/A | 0 | 0
2021-09-30 22:30 | 5.8276 | 0 | N/A | 0 | 0
2021-09-30 23:00 | 5.6855 | 0 | N/A | 0 | 0
2021-09-30 23:30 | 6.0476 | 0 | N/A | 0 | 0
2021-10-01 | 6.2963 | 0 | N/A | 0 | 0
2021-10-01 00:30 | 5.5576 | 0 | N/A | 0 | 0
2021-10-01 01:00 | 4.6564 | 0 | N/A | 0 | 0
2021-10-01 01:30 | 4.5509 | 0 | N/A | 0 | 0
2021-10-01 02:00 | 4.1734 | 0 | N/A | 0 | 0
2021-10-01 02:30 | 3.5833 | 0 | N/A | 0 | 0
2021-10-01 03:00 | 3.34 | 0 | N/A | 0 | 0
2021-10-01 03:30 | 3.1923 | 0 | N/A | 0 | 0
2021-10-01 04:00 | 2.9995 | 0 | N/A | 0 | 0
2021-10-01 04:30 | 3.0195 | 0 | N/A | 0 | 0
2021-10-01 05:00 | 3.0142 | 0 | N/A | 0 | 0
2021-10-01 05:30 | 3.2802 | 0 | N/A | 0 | 0
2021-10-01 06:00 | 3.6009 | 0 | N/A | 0 | 0
2021-10-01 06:30 | 4.2037 | 0 | N/A | 0 | 0
2021-10-01 07:00 | 4.4596 | 0 | N/A | 0 | 0
2021-10-01 07:30 | 4.7064 | 0 | N/A | 0 | 0
2021-10-01 08:00 | 5.1935 | 0 | N/A | 0 | 0
2021-10-01 08:30 | 5.4155 | 0 | N/A | 0 | 0
2021-10-01 09:00 | 4.7819 | 0 | N/A | 0 | 0
2021-10-01 09:30 | 4.2828 | 0 | N/A | 0 | 0
2021-10-01 10:00 | 4.2823 | 0 | N/A | 0 | 0
2021-10-01 10:30 | 3.9773 | 0 | N/A | 0 | 0
2021-10-01 11:00 | 3.1938 | 0 | N/A | 0 | 0
2021-10-01 11:30 | 3.575 | 0 | N/A | 0 | 0
2021-10-01 12:00 | 3.8511 | 0 | N/A | 0 | 0
2021-10-01 12:30 | 2.7916 | 0 | N/A | 0 | 0
2021-10-01 13:00 | 2.8127 | 0 | N/A | 0 | 0
2021-10-01 13:30 | 2.8633 | 0 | N/A | 0 | 0
2021-10-01 14:00 | 3.277 | 0 | N/A | 0 | 0
2021-10-01 14:30 | 3.1195 | 0 | N/A | 0 | 0
2021-10-01 15:00 | 2.0457 | 0 | N/A | 0 | 0
2021-10-01 15:30 | 1.6181 | 0 | N/A | 0 | 0
2021-10-01 16:00 | 1.9786 | 0 | N/A | 0 | 0
2021-10-01 16:30 | 2.3773 | 0 | N/A | 0 | 0
2021-10-01 17:00 | 2.6817 | 0 | N/A | 0 | 0
2021-10-01 17:30 | 4.1084 | 0 | N/A | 0 | 0
2021-10-01 18:00 | 5.5179 | 0 | N/A | 0 | 0
2021-10-01 18:30 | 5.9885 | 0 | N/A | 0 | 0
2021-10-01 19:00 | 6.2389 | 0 | N/A | 0 | 0
2021-10-01 19:30 | 6.2736 | 0 | N/A | 0 | 0
2021-10-01 20:00 | 5.9817 | 0 | N/A | 0 | 0
2021-10-01 20:30 | 5.7666 | 0 | N/A | 0 | 0
2021-10-01 21:00 | 5.5367 | 0 | N/A | 0 | 0
2021-10-01 21:30 | 5.8821 | 0 | N/A | 0 | 0
2021-10-01 22:00 | 6.1099 | 0 | N/A | 0 | 0
2021-10-01 22:30 | 5.779 | 0 | N/A | 0 | 0
2021-10-01 23:00 | 5.7002 | 0 | N/A | 0 | 0
2021-10-01 23:30 | 6.1013 | 0 | N/A | 0 | 0
2021-10-02 | 6.3418 | 0 | N/A | 0 | 0
2021-10-02 00:30 | 5.4982 | 0 | N/A | 0 | 0
2021-10-02 01:00 | 4.6269 | 0 | N/A | 0 | 0
2021-10-02 01:30 | 4.5294 | 0 | N/A | 0 | 0
2021-10-02 02:00 | 4.1317 | 0 | N/A | 0 | 0
2021-10-02 02:30 | 3.5324 | 0 | N/A | 0 | 0
2021-10-02 03:00 | 3.2848 | 0 | N/A | 0 | 0
2021-10-02 03:30 | 3.0647 | 0 | N/A | 0 | 0
2021-10-02 04:00 | 2.8968 | 0 | N/A | 0 | 0
2021-10-02 04:30 | 2.871 | 0 | N/A | 0 | 0
2021-10-02 05:00 | 2.8739 | 0 | N/A | 0 | 0
2021-10-02 05:30 | 2.9947 | 0 | N/A | 0 | 0
2021-10-02 06:00 | 3.1279 | 0 | N/A | 0 | 0
2021-10-02 06:30 | 3.3209 | 0 | N/A | 0 | 0
2021-10-02 07:00 | 3.5109 | 0 | N/A | 0 | 0
2021-10-02 07:30 | 3.5392 | 0 | N/A | 0 | 0
2021-10-02 08:00 | 3.5487 | 0 | N/A | 0 | 0
2021-10-02 08:30 | 3.8097 | 0 | N/A | 0 | 0
2021-10-02 09:00 | 4.2047 | 0 | N/A | 0 | 0
2021-10-02 09:30 | 4.4289 | 0 | N/A | 0 | 0
2021-10-02 10:00 | 4.0734 | 0 | N/A | 0 | 0
2021-10-02 10:30 | 3.4205 | 0 | N/A | 0 | 0
2021-10-02 11:00 | 2.6987 | 0 | N/A | 0 | 0
2021-10-02 11:30 | 2.406 | 0 | N/A | 0 | 0
2021-10-02 12:00 | 1.8907 | 0 | N/A | 0 | 0
2021-10-02 12:30 | 2.2541 | 0 | N/A | 0 | 0
2021-10-02 13:00 | 1.6465 | 0 | N/A | 0 | 0
2021-10-02 13:30 | 2.3742 | 0 | N/A | 0 | 0
2021-10-02 14:00 | 2.042 | 0 | N/A | 0 | 0
2021-10-02 14:30 | 2.1484 | 0 | N/A | 0 | 0
2021-10-02 15:00 | 1.3216 | 0 | N/A | 0 | 0
2021-10-02 15:30 | 1.4435 | 0 | N/A | 0 | 0
2021-10-02 16:00 | 1.6017 | 0 | N/A | 0 | 0
2021-10-02 16:30 | 2.2854 | 0 | N/A | 0 | 0
2021-10-02 17:00 | 3.679 | 0 | N/A | 0 | 0
2021-10-02 17:30 | 4.3872 | 0 | N/A | 0 | 0
2021-10-02 18:00 | 5.2224 | 0 | N/A | 0 | 0
2021-10-02 18:30 | 5.7925 | 0 | N/A | 0 | 0
2021-10-02 19:00 | 6.1934 | 0 | N/A | 0 | 0
2021-10-02 19:30 | 6.1922 | 0 | N/A | 0 | 0
2021-10-02 20:00 | 5.8308 | 0 | N/A | 0 | 0
2021-10-02 20:30 | 5.556 | 0 | N/A | 0 | 0
2021-10-02 21:00 | 5.2551 | 0 | N/A | 0 | 0
2021-10-02 21:30 | 5.6052 | 0 | N/A | 0 | 0
2021-10-02 22:00 | 5.8678 | 0 | N/A | 0 | 0
2021-10-02 22:30 | 5.5146 | 0 | N/A | 0 | 0
2021-10-02 23:00 | 5.4317 | 0 | N/A | 0 | 0
2021-10-02 23:30 | 5.676 | 0 | N/A | 0 | 0
2021-10-03 | 6.0364 | 0 | N/A | 0 | 0
2021-10-03 00:30 | 5.2874 | 0 | N/A | 0 | 0
2021-10-03 01:00 | 4.5723 | 0 | N/A | 0 | 0
2021-10-03 01:30 | 4.4328 | 0 | N/A | 0 | 0
2021-10-03 02:00 | 3.9821 | 0 | N/A | 0 | 0
2021-10-03 03:30 | 3.3982 | 0 | N/A | 0 | 0
2021-10-03 04:00 | 3.157 | 0 | N/A | 0 | 0
2021-10-03 04:30 | 2.9616 | 0 | N/A | 0 | 0
2021-10-03 05:00 | 2.8328 | 0 | N/A | 0 | 0
2021-10-03 05:30 | 2.8251 | 0 | N/A | 0 | 0
2021-10-03 06:00 | 2.834 | 0 | N/A | 0 | 0
2021-10-03 06:30 | 3.0738 | 0 | N/A | 0 | 0
2021-10-03 07:00 | 3.1744 | 0 | N/A | 0 | 0
2021-10-03 07:30 | 3.4639 | 0 | N/A | 0 | 0
2021-10-03 08:00 | 3.2688 | 0 | N/A | 0 | 0
2021-10-03 08:30 | 2.843 | 0 | N/A | 0 | 0
2021-10-03 09:00 | 2.3708 | 0 | N/A | 0 | 0
2021-10-03 09:30 | 1.7279 | 0 | N/A | 0 | 0
2021-10-03 10:00 | 1.4872 | 0 | N/A | 0 | 0
2021-10-03 10:30 | 1.2442 | 0 | N/A | 0 | 0
2021-10-03 11:00 | 1.4268 | 0 | N/A | 0 | 0
2021-10-03 11:30 | 1.4341 | 0 | N/A | 0 | 0
2021-10-03 12:00 | 1.6967 | 0 | N/A | 0 | 0
2021-10-03 12:30 | 1.2277 | 0 | N/A | 0 | 0
2021-10-03 13:00 | 2.6259 | 0 | N/A | 0 | 0
2021-10-03 13:30 | 2.681 | 0 | N/A | 0 | 0
2021-10-03 14:00 | 2.861 | 0 | N/A | 0 | 0
2021-10-03 14:30 | 2.8457 | 0 | N/A | 0 | 0
2021-10-03 15:00 | 3.4926 | 0 | N/A | 0 | 0
2021-10-03 15:30 | 4.1302 | 0 | N/A | 0 | 0
2021-10-03 16:00 | 4.5985 | 0 | N/A | 0 | 0
2021-10-03 16:30 | 5.1689 | 0 | N/A | 0 | 0
2021-10-03 17:00 | 5.5942 | 0 | N/A | 0 | 0
2021-10-03 17:30 | 5.8558 | 0 | N/A | 0 | 0
2021-10-03 18:00 | 6.168 | 0 | N/A | 0 | 0
2021-10-03 18:30 | 6.308 | 0 | N/A | 0 | 0
2021-10-03 19:00 | 6.3308 | 0 | N/A | 0 | 0
2021-10-03 19:30 | 6.6205 | 0 | N/A | 0 | 0
2021-10-03 20:00 | 6.4566 | 0 | N/A | 0 | 0
2021-10-03 20:30 | 6.2503 | 0 | N/A | 0 | 0
2021-10-03 21:00 | 6.0158 | 0 | N/A | 0 | 0
2021-10-03 21:30 | 5.6737 | 0 | N/A | 0 | 0
2021-10-03 22:00 | 5.2301 | 0 | N/A | 0 | 0
2021-10-03 22:30 | 5.3544 | 0 | N/A | 0 | 0
2021-10-03 23:00 | 5.3956 | 0 | N/A | 0 | 0
2021-10-03 23:30 | 5.0441 | 0 | N/A | 0 | 0
2021-10-04 | 5.1003 | 0 | N/A | 0 | 0
2021-10-04 00:30 | 5.2609 | 0 | N/A | 0 | 0
2021-10-04 01:00 | 5.7309 | 0 | N/A | 0 | 0
2021-10-04 01:30 | 5.0757 | 0 | N/A | 0 | 0
2021-10-04 02:00 | 4.53 | 0 | N/A | 0 | 0
2021-10-04 02:30 | 4.4082 | 0 | N/A | 0 | 0
2021-10-04 03:00 | 3.9713 | 0 | N/A | 0 | 0
2021-10-04 03:30 | 3.5195 | 0 | N/A | 0 | 0
2021-10-04 04:00 | 3.2976 | 0 | N/A | 0 | 0
2021-10-04 04:30 | 3.2451 | 0 | N/A | 0 | 0
2021-10-04 05:00 | 3.2353 | 0 | N/A | 0 | 0
2021-10-04 05:30 | 3.3709 | 0 | N/A | 0 | 0
2021-10-04 06:00 | 3.7457 | 0 | N/A | 0 | 0
2021-10-04 06:30 | 4.5475 | 0 | N/A | 0 | 0
2021-10-04 07:00 | 5.1306 | 0 | N/A | 0 | 0
2021-10-04 07:30 | 6.2796 | 0 | N/A | 0 | 0
2021-10-04 08:00 | 7.0592 | 0 | N/A | 0 | 0
2021-10-04 08:30 | 6.8533 | 0 | N/A | 0 | 0
2021-10-04 09:00 | 6.2767 | 0 | N/A | 0 | 0
2021-10-04 09:30 | 5.1567 | 0 | N/A | 0 | 0
2021-10-04 10:00 | 4.6309 | 0 | N/A | 0 | 0
2021-10-04 10:30 | 4.1003 | 0 | N/A | 0 | 0
2021-10-04 11:00 | 3.5379 | 0 | N/A | 0 | 0
2021-10-04 11:30 | 3.2559 | 0 | N/A | 0 | 0
2021-10-04 12:00 | 2.2521 | 0 | N/A | 0 | 0
2021-10-04 12:30 | 2.3925 | 0 | N/A | 0 | 0
2021-10-04 13:00 | 4.8583 | 0 | N/A | 0 | 0
2021-10-04 13:30 | 4.6089 | 0 | N/A | 0 | 0
2021-10-04 14:00 | 2.899 | 0 | N/A | 0 | 0
2021-10-04 14:30 | 1.7583 | 0 | N/A | 0 | 0
2021-10-04 15:00 | 2.405 | 0 | N/A | 0 | 0
2021-10-04 15:30 | 3.3209 | 0 | N/A | 0 | 0
2021-10-04 16:00 | 1.6286 | 0 | N/A | 0 | 0
2021-10-04 16:30 | 2.0909 | 0 | N/A | 0 | 0
2021-10-04 17:00 | 3.2015 | 0 | N/A | 0 | 0
2021-10-04 17:30 | 3.7763 | 0 | N/A | 0 | 0
2021-10-04 18:00 | 5.243 | 0 | N/A | 0 | 0
2021-10-04 18:30 | 6.7319 | 0 | N/A | 0 | 0
2021-10-04 19:00 | 7.4738 | 0 | N/A | 0 | 0
2021-10-04 19:30 | 7.6991 | 0 | N/A | 0 | 0
2021-10-04 20:00 | 7.5417 | 0 | N/A | 0 | 0
2021-10-04 20:30 | 7.3513 | 0 | N/A | 0 | 0
2021-10-04 21:00 | 6.9543 | 0 | N/A | 0 | 0
2021-10-04 21:30 | 6.4947 | 0 | N/A | 0 | 0
2021-10-04 22:00 | 5.9483 | 0 | N/A | 0 | 0
2021-10-04 22:30 | 6.0355 | 0 | N/A | 0 | 0
2021-10-04 23:00 | 6.0161 | 0 | N/A | 0 | 0
2021-10-04 23:30 | 5.5916 | 0 | N/A | 0 | 0
2021-10-05 | 5.539 | 0 | N/A | 0 | 0
2021-10-05 00:30 | 5.8497 | 0 | N/A | 0 | 0
2021-10-05 01:00 | 6.2547 | 0 | N/A | 0 | 0
2021-10-05 01:30 | 5.6655 | 0 | N/A | 0 | 0
2021-10-05 02:00 | 5.0224 | 0 | N/A | 0 | 0
2021-10-05 02:30 | 4.995 | 0 | N/A | 0 | 0
2021-10-05 03:00 | 4.5774 | 0 | N/A | 0 | 0
2021-10-05 03:30 | 4.2919 | 0 | N/A | 0 | 0
2021-10-05 04:00 | 3.9416 | 0 | N/A | 0 | 0
2021-10-05 04:30 | 3.7852 | 0 | N/A | 0 | 0
2021-10-05 05:00 | 3.7739 | 0 | N/A | 0 | 0
2021-10-05 05:30 | 3.9923 | 0 | N/A | 0 | 0
2021-10-05 06:00 | 4.3179 | 0 | N/A | 0 | 0
2021-10-05 06:30 | 5.1445 | 0 | N/A | 0 | 0
2021-10-05 07:00 | 5.7673 | 0 | N/A | 0 | 0
2021-10-05 07:30 | 7.0771 | 0 | N/A | 0 | 0
2021-10-05 08:00 | 7.5567 | 0 | N/A | 0 | 0
2021-10-05 08:30 | 7.3871 | 0 | N/A | 0 | 0
2021-10-05 09:00 | 8.48 | 0 | N/A | 0 | 0
2021-10-05 09:30 | 8.1233 | 0 | N/A | 0 | 0
2021-10-05 10:00 | 7.7834 | 0 | N/A | 0 | 0
2021-10-05 10:30 | 7.4904 | 0 | N/A | 0 | 0
2021-10-05 11:00 | 6.41 | 0 | N/A | 0 | 0
2021-10-05 11:30 | 6.1767 | 0 | N/A | 0 | 0
2021-10-05 12:00 | 5.9067 | 0 | N/A | 0 | 0
2021-10-05 12:30 | 4.6828 | 0 | N/A | 0 | 0
2021-10-05 13:00 | 4.153 | 0 | N/A | 0 | 0
2021-10-05 13:30 | 3.4405 | 0 | N/A | 0 | 0
2021-10-05 14:00 | 2.81 | 0 | N/A | 0 | 0
2021-10-05 14:30 | 2.4906 | 0 | N/A | 0 | 0
2021-10-05 15:00 | 2.3146 | 0 | N/A | 0 | 0
2021-10-05 15:30 | 2.1155 | 0 | N/A | 0 | 0
2021-10-05 16:00 | 2.3446 | 0 | N/A | 0 | 0
2021-10-05 16:30 | 2.9953 | 0 | N/A | 0 | 0
2021-10-05 17:00 | 3.0119 | 0 | N/A | 0 | 0
2021-10-05 17:30 | 4.2508 | 0 | N/A | 0 | 0
2021-10-05 18:00 | 4.9117 | 0 | N/A | 0 | 0
2021-10-05 18:30 | 4.7145 | 0 | N/A | 0 | 0
2021-10-05 19:00 | 5.5696 | 0 | N/A | 0 | 0
2021-10-05 19:30 | 6.1062 | 0 | N/A | 0 | 0
2021-10-05 20:00 | 6.3881 | 0 | N/A | 0 | 0
2021-10-05 20:30 | 6.4596 | 0 | N/A | 0 | 0
2021-10-05 21:00 | 6.3162 | 0 | N/A | 0 | 0
2021-10-05 21:30 | 6.0031 | 0 | N/A | 0 | 0
2021-10-05 22:00 | 5.5919 | 0 | N/A | 0 | 0
2021-10-05 22:30 | 5.7582 | 0 | N/A | 0 | 0
2021-10-05 23:00 | 5.6486 | 0 | N/A | 0 | 0
2021-10-05 23:30 | 5.1588 | 0 | N/A | 0 | 0
2021-10-06 | 5.024 | 0 | N/A | 0 | 0
2021-10-06 00:30 | 5.4288 | 0 | N/A | 0 | 0
2021-10-06 01:00 | 5.9033 | 0 | N/A | 0 | 0
2021-10-06 01:30 | 5.2707 | 0 | N/A | 0 | 0
2021-10-06 02:00 | 4.6734 | 0 | N/A | 0 | 0
2021-10-06 02:30 | 4.5682 | 0 | N/A | 0 | 0
2021-10-06 03:00 | 4.3168 | 0 | N/A | 0 | 0
2021-10-06 03:30 | 3.8685 | 0 | N/A | 0 | 0
2021-10-06 04:00 | 3.5869 | 0 | N/A | 0 | 0
2021-10-06 04:30 | 3.5616 | 0 | N/A | 0 | 0
2021-10-06 05:00 | 3.5401 | 0 | N/A | 0 | 0
2021-10-06 05:30 | 3.7979 | 0 | N/A | 0 | 0
2021-10-06 06:00 | 4.108 | 0 | N/A | 0 | 0
2021-10-06 06:30 | 4.9644 | 0 | N/A | 0 | 0
2021-10-06 07:00 | 5.776 | 0 | N/A | 0 | 0
2021-10-06 07:30 | 7.0567 | 0 | N/A | 0 | 0
2021-10-06 08:00 | 7.3619 | 0 | N/A | 0 | 0
2021-10-06 08:30 | 6.3 | 0 | N/A | 0 | 0
2021-10-06 09:00 | 5.2503 | 0 | N/A | 0 | 0
2021-10-06 09:30 | 4.1347 | 0 | N/A | 0 | 0
2021-10-06 10:00 | 3.1206 | 0 | N/A | 0 | 0
2021-10-06 10:30 | 2.0074 | 0 | N/A | 0 | 0
2021-10-06 11:00 | 1.1821 | 0 | N/A | 0 | 0
2021-10-06 11:30 | 0.51683 | 0 | N/A | 0 | 0
2021-10-06 12:00 | 0.11795 | 0 | N/A | 0 | 0
2021-10-06 12:30 | -0.092856 | 0 | N/A | 0 | 0
2021-10-06 13:00 | -0.40828 | 0 | N/A | 0 | 0
2021-10-06 13:30 | -0.29719 | 0 | N/A | 0 | 0
2021-10-06 14:00 | 0.23279 | 0 | N/A | 0 | 0
2021-10-06 14:30 | 0.26352 | 0 | N/A | 0 | 0
2021-10-06 15:00 | 0.79239 | 0 | N/A | 0 | 0
2021-10-06 15:30 | 1.9645 | 0 | N/A | 0 | 0
2021-10-06 16:00 | 2.0511 | 0 | N/A | 0 | 0
2021-10-06 16:30 | 2.1919 | 0 | N/A | 0 | 0
2021-10-06 17:00 | 2.4008 | 0 | N/A | 0 | 0
2021-10-06 17:30 | 4.2339 | 0 | N/A | 0 | 0
2021-10-06 18:00 | 4.9868 | 0 | N/A | 0 | 0
2021-10-06 18:30 | 5.5747 | 0 | N/A | 0 | 0
2021-10-06 19:00 | 5.8997 | 0 | N/A | 0 | 0
2021-10-06 19:30 | 5.9247 | 0 | N/A | 0 | 0
2021-10-06 20:00 | 6.0396 | 0 | N/A | 0 | 0
2021-10-06 20:30 | 5.8749 | 0 | N/A | 0 | 0
2021-10-06 21:00 | 5.6313 | 0 | N/A | 0 | 0
2021-10-06 21:30 | 5.3335 | 0 | N/A | 0 | 0
2021-10-06 22:00 | 4.9641 | 0 | N/A | 0 | 0
2021-10-06 22:30 | 5.0345 | 0 | N/A | 0 | 0
2021-10-06 23:00 | 4.9934 | 0 | N/A | 0 | 0
2021-10-06 23:30 | 4.7332 | 0 | N/A | 0 | 0
2021-10-07 | 4.7065 | 0 | N/A | 0 | 0
2021-10-07 00:30 | 5.0216 | 0 | N/A | 0 | 0
2021-10-07 01:00 | 5.4632 | 0 | N/A | 0 | 0
2021-10-07 01:30 | 4.851 | 0 | N/A | 0 | 0
2021-10-07 02:00 | 4.2397 | 0 | N/A | 0 | 0
2021-10-07 02:30 | 4.2539 | 0 | N/A | 0 | 0
2021-10-07 03:00 | 3.9422 | 0 | N/A | 0 | 0
2021-10-07 03:30 | 3.4963 | 0 | N/A | 0 | 0
2021-10-07 04:00 | 3.2906 | 0 | N/A | 0 | 0
2021-10-07 04:30 | 3.1771 | 0 | N/A | 0 | 0
2021-10-07 05:00 | 3.2013 | 0 | N/A | 0 | 0
2021-10-07 05:30 | 3.4583 | 0 | N/A | 0 | 0
2021-10-07 06:00 | 3.8152 | 0 | N/A | 0 | 0
2021-10-07 06:30 | 4.6588 | 0 | N/A | 0 | 0
2021-10-07 07:00 | 5.3007 | 0 | N/A | 0 | 0
2021-10-07 07:30 | 6.3244 | 0 | N/A | 0 | 0
2021-10-07 08:00 | 6.6774 | 0 | N/A | 0 | 0
2021-10-07 08:30 | 6.0234 | 0 | N/A | 0 | 0
2021-10-07 09:00 | 5.2852 | 0 | N/A | 0 | 0
2021-10-07 09:30 | 5.3051 | 0 | N/A | 0 | 0
2021-10-07 10:00 | 4.2259 | 0 | N/A | 0 | 0
2021-10-07 10:30 | 3.7336 | 0 | N/A | 0 | 0
2021-10-07 11:00 | 3.2874 | 0 | N/A | 0 | 0
2021-10-07 11:30 | 2.9005 | 0 | N/A | 0 | 0
2021-10-07 12:00 | 2.7417 | 0 | N/A | 0 | 0
2021-10-07 12:30 | 2.9064 | 0 | N/A | 0 | 0
2021-10-07 13:00 | 1.7769 | 0 | N/A | 0 | 0
2021-10-07 13:30 | 1.3134 | 0 | N/A | 0 | 0
2021-10-07 14:00 | 1.286 | 0 | N/A | 0 | 0
2021-10-07 14:30 | 2.7738 | 0 | N/A | 0 | 0
2021-10-07 15:00 | 2.2948 | 0 | N/A | 0 | 0
2021-10-07 15:30 | 3.7528 | 0 | N/A | 0 | 0
2021-10-07 16:00 | 4.0749 | 0 | N/A | 0 | 0
2021-10-07 16:30 | 3.0485 | 0 | N/A | 0 | 0
2021-10-07 17:00 | 3.5562 | 0 | N/A | 0 | 0
2021-10-07 17:30 | 4.3699 | 0 | N/A | 0 | 0
2021-10-07 18:00 | 4.8164 | 0 | N/A | 0 | 0
2021-10-07 18:30 | 5.3038 | 0 | N/A | 0 | 0
2021-10-07 19:00 | 5.8947 | 0 | N/A | 0 | 0
2021-10-07 19:30 | 6.3338 | 0 | N/A | 0 | 0
2021-10-07 20:00 | 6.7251 | 0 | N/A | 0 | 0
2021-10-07 20:30 | 6.9151 | 0 | N/A | 0 | 0
2021-10-07 21:00 | 6.6794 | 0 | N/A | 0 | 0
2021-10-07 21:30 | 6.3188 | 0 | N/A | 0 | 0
2021-10-07 22:00 | 6.0478 | 0 | N/A | 0 | 0
2021-10-07 22:30 | 6.0727 | 0 | N/A | 0 | 0
2021-10-07 23:00 | 5.971 | 0 | N/A | 0 | 0
2021-10-07 23:30 | 5.4987 | 0 | N/A | 0 | 0
2021-10-08 | 5.4189 | 0 | N/A | 0 | 0
2021-10-08 00:30 | 5.7941 | 0 | N/A | 0 | 0
2021-10-08 01:00 | 6.1692 | 0 | N/A | 0 | 0
2021-10-08 01:30 | 5.6206 | 0 | N/A | 0 | 0
2021-10-08 02:00 | 4.9222 | 0 | N/A | 0 | 0
2021-10-08 02:30 | 4.8618 | 0 | N/A | 0 | 0
2021-10-08 03:00 | 4.5068 | 0 | N/A | 0 | 0
2021-10-08 03:30 | 4.077 | 0 | N/A | 0 | 0
2021-10-08 04:00 | 3.9121 | 0 | N/A | 0 | 0
2021-10-08 04:30 | 3.7612 | 0 | N/A | 0 | 0
2021-10-08 05:00 | 3.7853 | 0 | N/A | 0 | 0
2021-10-08 05:30 | 4.0205 | 0 | N/A | 0 | 0
2021-10-08 06:00 | 4.4689 | 0 | N/A | 0 | 0
2021-10-08 06:30 | 5.2317 | 0 | N/A | 0 | 0
2021-10-08 07:00 | 6.1063 | 0 | N/A | 0 | 0
2021-10-08 07:30 | 7.2772 | 0 | N/A | 0 | 0
2021-10-08 08:00 | 7.4184 | 0 | N/A | 0 | 0
2021-10-08 08:30 | 6.4136 | 0 | N/A | 0 | 0
2021-10-08 09:00 | 5.5673 | 0 | N/A | 0 | 0
2021-10-08 09:30 | 4.6809 | 0 | N/A | 0 | 0
2021-10-08 10:00 | 3.4486 | 0 | N/A | 0 | 0
2021-10-08 10:30 | 2.3093 | 0 | N/A | 0 | 0
2021-10-08 11:00 | 1.5476 | 0 | N/A | 0 | 0
2021-10-08 11:30 | 1.5211 | 0 | N/A | 0 | 0
2021-10-08 12:00 | 0.66092 | 0 | N/A | 0 | 0
2021-10-08 12:30 | 0.89525 | 0 | N/A | 0 | 0
2021-10-08 13:00 | 0.75902 | 0 | N/A | 0 | 0
2021-10-08 13:30 | -0.25009 | 0 | N/A | 0 | 0
2021-10-08 14:00 | -0.57847 | 0 | N/A | 0 | 0
2021-10-08 14:30 | -0.60668 | 0 | N/A | 0 | 0
2021-10-08 15:00 | -1.0041 | 0 | N/A | 0 | 0
2021-10-08 15:30 | -1.0303 | 0 | N/A | 0 | 0
2021-10-08 16:00 | -0.92348 | 0 | N/A | 0 | 0
2021-10-08 16:30 | -0.6526 | 0 | N/A | 0 | 0
2021-10-08 17:00 | 0.86361 | 0 | N/A | 0 | 0
2021-10-08 17:30 | 1.7844 | 0 | N/A | 0 | 0
2021-10-08 18:00 | 2.9585 | 0 | N/A | 0 | 0
2021-10-08 18:30 | 3.6767 | 0 | N/A | 0 | 0
2021-10-08 19:00 | 4.3604 | 0 | N/A | 0 | 0
2021-10-08 19:30 | 4.9305 | 0 | N/A | 0 | 0
2021-10-08 20:00 | 5.3523 | 0 | N/A | 0 | 0
2021-10-08 20:30 | 5.5681 | 0 | N/A | 0 | 0
2021-10-08 21:00 | 5.649 | 0 | N/A | 0 | 0
2021-10-08 21:30 | 5.4259 | 0 | N/A | 0 | 0
2021-10-08 22:00 | 5.2229 | 0 | N/A | 0 | 0
2021-10-08 22:30 | 5.3441 | 0 | N/A | 0 | 0
2021-10-08 23:00 | 5.4287 | 0 | N/A | 0 | 0
2021-10-08 23:30 | 5.0795 | 0 | N/A | 0 | 0
2021-10-09 | 5.0641 | 0 | N/A | 0 | 0
2021-10-09 00:30 | 5.394 | 0 | N/A | 0 | 0
2021-10-09 01:00 | 5.6767 | 0 | N/A | 0 | 0
2021-10-09 01:30 | 5.0136 | 0 | N/A | 0 | 0
2021-10-09 02:00 | 4.3761 | 0 | N/A | 0 | 0
2021-10-09 02:30 | 4.3508 | 0 | N/A | 0 | 0
2021-10-09 03:00 | 3.9783 | 0 | N/A | 0 | 0
2021-10-09 03:30 | 3.4684 | 0 | N/A | 0 | 0
2021-10-09 04:00 | 3.2478 | 0 | N/A | 0 | 0
2021-10-09 04:30 | 3.1307 | 0 | N/A | 0 | 0
2021-10-09 05:00 | 3.0266 | 0 | N/A | 0 | 0
2021-10-09 05:30 | 3.0759 | 0 | N/A | 0 | 0
2021-10-09 06:00 | 3.2531 | 0 | N/A | 0 | 0
2021-10-09 06:30 | 3.5883 | 0 | N/A | 0 | 0
2021-10-09 07:00 | 3.875 | 0 | N/A | 0 | 0
2021-10-09 07:30 | 4.2972 | 0 | N/A | 0 | 0
2021-10-09 08:00 | 4.5371 | 0 | N/A | 0 | 0
2021-10-09 08:30 | 3.8184 | 0 | N/A | 0 | 0
2021-10-09 09:00 | 3.3115 | 0 | N/A | 0 | 0
2021-10-09 09:30 | 3.263 | 0 | N/A | 0 | 0
2021-10-09 10:00 | 2.9037 | 0 | N/A | 0 | 0
2021-10-09 10:30 | 1.9425 | 0 | N/A | 0 | 0
2021-10-09 11:00 | 1.8142 | 0 | N/A | 0 | 0
2021-10-09 11:30 | 0.91688 | 0 | N/A | 0 | 0
2021-10-09 12:00 | -0.63668 | 0 | N/A | 0 | 0
2021-10-09 12:30 | -0.60019 | 0 | N/A | 0 | 0
2021-10-09 13:00 | 1.5995 | 0 | N/A | 0 | 0
2021-10-09 13:30 | 1.038 | 0 | N/A | 0 | 0
2021-10-09 14:00 | 1.39 | 0 | N/A | 0 | 0
2021-10-09 14:30 | 1.6792 | 0 | N/A | 0 | 0
2021-10-09 15:00 | 1.6177 | 0 | N/A | 0 | 0
2021-10-09 15:30 | 2.3472 | 0 | N/A | 0 | 0
2021-10-09 16:00 | 2.6903 | 0 | N/A | 0 | 0
2021-10-09 16:30 | 2.8201 | 0 | N/A | 0 | 0
2021-10-09 17:00 | 3.0945 | 0 | N/A | 0 | 0
2021-10-09 17:30 | 3.2222 | 0 | N/A | 0 | 0
2021-10-09 18:00 | 3.9326 | 0 | N/A | 0 | 0
2021-10-09 18:30 | 4.6065 | 0 | N/A | 0 | 0
2021-10-09 19:00 | 5.0851 | 0 | N/A | 0 | 0
2021-10-09 19:30 | 5.4433 | 0 | N/A | 0 | 0
2021-10-09 20:00 | 5.581 | 0 | N/A | 0 | 0
2021-10-09 20:30 | 5.5927 | 0 | N/A | 0 | 0
2021-10-09 21:00 | 5.4721 | 0 | N/A | 0 | 0
2021-10-09 21:30 | 5.1832 | 0 | N/A | 0 | 0
2021-10-09 22:00 | 4.8613 | 0 | N/A | 0 | 0
2021-10-09 22:30 | 5.1447 | 0 | N/A | 0 | 0
2021-10-09 23:00 | 5.3045 | 0 | N/A | 0 | 0
2021-10-09 23:30 | 4.9495 | 0 | N/A | 0 | 0
2021-10-10 | 5.0235 | 0 | N/A | 0 | 0
2021-10-10 00:30 | 5.2312 | 0 | N/A | 0 | 0
2021-10-10 01:00 | 5.663 | 0 | N/A | 0 | 0
2021-10-10 01:30 | 4.9912 | 0 | N/A | 0 | 0
2021-10-10 02:00 | 4.4394 | 0 | N/A | 0 | 0
2021-10-10 02:30 | 4.3168 | 0 | N/A | 0 | 0
2021-10-10 03:00 | 4.035 | 0 | N/A | 0 | 0
2021-10-10 03:30 | 3.4776 | 0 | N/A | 0 | 0
2021-10-10 04:00 | 3.1844 | 0 | N/A | 0 | 0
2021-10-10 04:30 | 3.1064 | 0 | N/A | 0 | 0
2021-10-10 05:00 | 2.9638 | 0 | N/A | 0 | 0
2021-10-10 05:30 | 2.9878 | 0 | N/A | 0 | 0
2021-10-10 06:00 | 3.1551 | 0 | N/A | 0 | 0
2021-10-10 06:30 | 3.4124 | 0 | N/A | 0 | 0
2021-10-10 07:00 | 3.7181 | 0 | N/A | 0 | 0
2021-10-10 07:30 | 4.0803 | 0 | N/A | 0 | 0
2021-10-10 08:00 | 4.0431 | 0 | N/A | 0 | 0
2021-10-10 08:30 | 3.6043 | 0 | N/A | 0 | 0
2021-10-10 09:00 | 3.4357 | 0 | N/A | 0 | 0
2021-10-10 09:30 | 2.471 | 0 | N/A | 0 | 0
2021-10-10 10:00 | 2.1941 | 0 | N/A | 0 | 0
2021-10-10 10:30 | 1.9979 | 0 | N/A | 0 | 0
2021-10-10 11:00 | 1.4639 | 0 | N/A | 0 | 0
2021-10-10 11:30 | 1.2929 | 0 | N/A | 0 | 0
2021-10-10 12:00 | 1.0026 | 0 | N/A | 0 | 0
2021-10-10 12:30 | 0.76464 | 0 | N/A | 0 | 0
2021-10-10 13:00 | 0.78003 | 0 | N/A | 0 | 0
2021-10-10 13:30 | 0.67185 | 0 | N/A | 0 | 0
2021-10-10 14:00 | 1.1286 | 0 | N/A | 0 | 0
2021-10-10 14:30 | 0.82564 | 0 | N/A | 0 | 0
2021-10-10 15:00 | 0.89607 | 0 | N/A | 0 | 0
2021-10-10 15:30 | 0.76327 | 0 | N/A | 0 | 0
2021-10-10 16:00 | 1.6444 | 0 | N/A | 0 | 0
2021-10-10 16:30 | 2.4091 | 0 | N/A | 0 | 0
2021-10-10 17:00 | 3.6135 | 0 | N/A | 0 | 0
2021-10-10 17:30 | 4.2864 | 0 | N/A | 0 | 0
2021-10-10 18:00 | 4.8603 | 0 | N/A | 0 | 0
2021-10-10 18:30 | 5.1533 | 0 | N/A | 0 | 0
2021-10-10 19:00 | 5.8551 | 0 | N/A | 0 | 0
2021-10-10 19:30 | 6.4435 | 0 | N/A | 0 | 0
2021-10-10 20:00 | 6.648 | 0 | N/A | 0 | 0
2021-10-10 20:30 | 6.7775 | 0 | N/A | 0 | 0
2021-10-10 21:00 | 6.5787 | 0 | N/A | 0 | 0
2021-10-10 21:30 | 6.2924 | 0 | N/A | 0 | 0
2021-10-10 22:00 | 5.759 | 0 | N/A | 0 | 0
2021-10-10 22:30 | 5.8984 | 0 | N/A | 0 | 0
2021-10-10 23:00 | 5.8305 | 0 | N/A | 0 | 0
2021-10-10 23:30 | 5.4782 | 0 | N/A | 0 | 0
2021-10-11 | 5.5353 | 0 | N/A | 0 | 0
2021-10-11 00:30 | 5.6887 | 0 | N/A | 0 | 0
2021-10-11 01:00 | 6.091 | 0 | N/A | 0 | 0
2021-10-11 01:30 | 5.5382 | 0 | N/A | 0 | 0
2021-10-11 02:00 | 4.9605 | 0 | N/A | 0 | 0
2021-10-11 02:30 | 4.9879 | 0 | N/A | 0 | 0
2021-10-11 03:00 | 4.6919 | 0 | N/A | 0 | 0
2021-10-11 03:30 | 4.2392 | 0 | N/A | 0 | 0
2021-10-11 04:00 | 4.0269 | 0 | N/A | 0 | 0
2021-10-11 04:30 | 3.9648 | 0 | N/A | 0 | 0
2021-10-11 05:00 | 3.8647 | 0 | N/A | 0 | 0
2021-10-11 05:30 | 4.1607 | 0 | N/A | 0 | 0
2021-10-11 06:00 | 4.603 | 0 | N/A | 0 | 0
2021-10-11 06:30 | 5.4777 | 0 | N/A | 0 | 0
2021-10-11 07:00 | 5.9697 | 0 | N/A | 0 | 0
2021-10-11 07:30 | 2.332 | 0 | N/A | 0 | 0
2021-10-11 08:00 | 9.0433 | 0 | N/A | 0 | 0
2021-10-11 08:30 | 8.1401 | 0 | N/A | 0 | 0
2021-10-11 09:00 | 7.1537 | 0 | N/A | 0 | 0
2021-10-11 09:30 | 6.2404 | 0 | N/A | 0 | 0
2021-10-11 10:00 | 6.1369 | 0 | N/A | 0 | 0
2021-10-11 10:30 | 6.0035 | 0 | N/A | 0 | 0
2021-10-11 11:00 | 5.6369 | 0 | N/A | 0 | 0
2021-10-11 11:30 | 5.2555 | 0 | N/A | 0 | 0
2021-10-11 12:00 | 5.2054 | 0 | N/A | 0 | 0
2021-10-11 12:30 | 4.5185 | 0 | N/A | 0 | 0
2021-10-11 13:00 | 3.7011 | 0 | N/A | 0 | 0
2021-10-11 13:30 | 2.2909 | 0 | N/A | 0 | 0
2021-10-11 14:00 | 2.4939 | 0 | N/A | 0 | 0
2021-10-11 14:30 | 2.4225 | 0 | N/A | 0 | 0
2021-10-11 15:00 | 1.5674 | 0 | N/A | 0 | 0
2021-10-11 15:30 | 1.7761 | 0 | N/A | 0 | 0
2021-10-11 16:00 | 2.0798 | 0 | N/A | 0 | 0
2021-10-11 16:30 | 2.2341 | 0 | N/A | 0 | 0
2021-10-11 17:00 | 2.5931 | 0 | N/A | 0 | 0
2021-10-11 17:30 | 3.3977 | 0 | N/A | 0 | 0
2021-10-11 18:00 | 4.4704 | 0 | N/A | 0 | 0
2021-10-11 18:30 | 5.2289 | 0 | N/A | 0 | 0
2021-10-11 19:00 | 6.0071 | 0 | N/A | 0 | 0
2021-10-11 19:30 | 6.3808 | 0 | N/A | 0 | 0
2021-10-11 20:00 | 6.8914 | 0 | N/A | 0 | 0
2021-10-11 20:30 | 7.0359 | 0 | N/A | 0 | 0
2021-10-11 21:00 | 6.8928 | 0 | N/A | 0 | 0
2021-10-11 21:30 | 6.4295 | 0 | N/A | 0 | 0
2021-10-11 22:00 | 5.9845 | 0 | N/A | 0 | 0
2021-10-11 22:30 | 5.9829 | 0 | N/A | 0 | 0
2021-10-11 23:00 | 5.7716 | 0 | N/A | 0 | 0
2021-10-11 23:30 | 5.3919 | 0 | N/A | 0 | 0
2021-10-12 | 5.3765 | 0 | N/A | 0 | 0
2021-10-12 00:30 | 5.7258 | 0 | N/A | 0 | 0
2021-10-12 01:00 | 6.0666 | 0 | N/A | 0 | 0
2021-10-12 01:30 | 5.5259 | 0 | N/A | 0 | 0
2021-10-12 02:00 | 4.9962 | 0 | N/A | 0 | 0
2021-10-12 02:30 | 4.8827 | 0 | N/A | 0 | 0
2021-10-12 03:00 | 4.5565 | 0 | N/A | 0 | 0
2021-10-12 03:30 | 4.1034 | 0 | N/A | 0 | 0
2021-10-12 04:00 | 3.795 | 0 | N/A | 0 | 0
2021-10-12 04:30 | 3.7228 | 0 | N/A | 0 | 0
2021-10-12 05:00 | 3.6118 | 0 | N/A | 0 | 0
2021-10-12 05:30 | 3.9008 | 0 | N/A | 0 | 0
2021-10-12 06:00 | 4.3783 | 0 | N/A | 0 | 0
2021-10-12 06:30 | 5.2897 | 0 | N/A | 0 | 0
2021-10-12 07:00 | 6.2486 | 0 | N/A | 0 | 0
2021-10-12 07:30 | 7.4376 | 0 | N/A | 0 | 0
2021-10-12 08:00 | 7.4416 | 0 | N/A | 0 | 0
2021-10-12 08:30 | 6.2767 | 0 | N/A | 0 | 0
2021-10-12 09:00 | 5.04 | 0 | N/A | 0 | 0
2021-10-12 09:30 | 3.7967 | 0 | N/A | 0 | 0
2021-10-12 10:00 | 2.6885 | 0 | N/A | 0 | 0
2021-10-12 10:30 | 1.5174 | 0 | N/A | 0 | 0
2021-10-12 11:00 | 0.91039 | 0 | N/A | 0 | 0
2021-10-12 11:30 | 0.46506 | 0 | N/A | 0 | 0
2021-10-12 12:00 | 0.39294 | 0 | N/A | 0 | 0
2021-10-12 12:30 | -0.087686 | 0 | N/A | 0 | 0
2021-10-12 13:00 | 0.086474 | 0 | N/A | 0 | 0
2021-10-12 13:30 | -0.24777 | 0 | N/A | 0 | 0
2021-10-12 14:00 | 0.8465 | 0 | N/A | 0 | 0
2021-10-12 14:30 | 1.5725 | 0 | N/A | 0 | 0
2021-10-12 15:00 | 1.5995 | 0 | N/A | 0 | 0
2021-10-12 15:30 | 1.5139 | 0 | N/A | 0 | 0
2021-10-12 16:00 | 1.8668 | 0 | N/A | 0 | 0
2021-10-12 16:30 | 1.9132 | 0 | N/A | 0 | 0
2021-10-12 17:00 | 2.8822 | 0 | N/A | 0 | 0
2021-10-12 17:30 | 3.5244 | 0 | N/A | 0 | 0
2021-10-12 18:00 | 4.2182 | 0 | N/A | 0 | 0
2021-10-12 18:30 | 5.1746 | 0 | N/A | 0 | 0
2021-10-12 19:00 | 5.6729 | 0 | N/A | 0 | 0
2021-10-12 19:30 | 5.7612 | 0 | N/A | 0 | 0
2021-10-12 20:00 | 5.9348 | 0 | N/A | 0 | 0
2021-10-12 20:30 | 6.0661 | 0 | N/A | 0 | 0
2021-10-12 21:00 | 5.8817 | 0 | N/A | 0 | 0
2021-10-12 21:30 | 5.638 | 0 | N/A | 0 | 0
2021-10-12 22:00 | 5.0776 | 0 | N/A | 0 | 0
2021-10-12 22:30 | 5.1044 | 0 | N/A | 0 | 0
2021-10-12 23:00 | 4.9825 | 0 | N/A | 0 | 0
2021-10-12 23:30 | 4.7699 | 0 | N/A | 0 | 0
2021-10-13 | 4.7776 | 0 | N/A | 0 | 0
2021-10-13 00:30 | 5.0706 | 0 | N/A | 0 | 0
2021-10-13 01:00 | 5.361 | 0 | N/A | 0 | 0
2021-10-13 01:30 | 4.839 | 0 | N/A | 0 | 0
2021-10-13 02:00 | 4.2179 | 0 | N/A | 0 | 0
2021-10-13 02:30 | 4.1101 | 0 | N/A | 0 | 0
2021-10-13 03:00 | 3.79 | 0 | N/A | 0 | 0
2021-10-13 03:30 | 3.3276 | 0 | N/A | 0 | 0
2021-10-13 04:00 | 2.985 | 0 | N/A | 0 | 0
2021-10-13 04:30 | 2.9686 | 0 | N/A | 0 | 0
2021-10-13 05:00 | 2.9948 | 0 | N/A | 0 | 0
2021-10-13 05:30 | 3.2011 | 0 | N/A | 0 | 0
2021-10-13 06:00 | 3.6122 | 0 | N/A | 0 | 0
2021-10-13 06:30 | 4.4454 | 0 | N/A | 0 | 0
2021-10-13 07:00 | 5.0558 | 0 | N/A | 0 | 0
2021-10-13 07:30 | 6.308 | 0 | N/A | 0 | 0
2021-10-13 08:00 | 6.3423 | 0 | N/A | 0 | 0
2021-10-13 08:30 | 5.5094 | 0 | N/A | 0 | 0
2021-10-13 09:00 | 5.3034 | 0 | N/A | 0 | 0
2021-10-13 09:30 | 4.4853 | 0 | N/A | 0 | 0
2021-10-13 10:00 | 3.7702 | 0 | N/A | 0 | 0
2021-10-13 10:30 | 3.4351 | 0 | N/A | 0 | 0
2021-10-13 11:00 | 3.3502 | 0 | N/A | 0 | 0
2021-10-13 11:30 | 3.5436 | 0 | N/A | 0 | 0
2021-10-13 12:00 | 3.4877 | 0 | N/A | 0 | 0
2021-10-13 12:30 | 3.7692 | 0 | N/A | 0 | 0
2021-10-13 13:00 | 4.028 | 0 | N/A | 0 | 0
2021-10-13 13:30 | 3.439 | 0 | N/A | 0 | 0
2021-10-13 14:00 | 2.4911 | 0 | N/A | 0 | 0
2021-10-13 14:30 | 2.2887 | 0 | N/A | 0 | 0
2021-10-13 15:00 | 2.2326 | 0 | N/A | 0 | 0
2021-10-13 15:30 | 1.6331 | 0 | N/A | 0 | 0
2021-10-13 16:00 | 1.506 | 0 | N/A | 0 | 0
2021-10-13 16:30 | 1.5327 | 0 | N/A | 0 | 0
2021-10-13 17:00 | 2.2844 | 0 | N/A | 0 | 0
2021-10-13 17:30 | 2.8927 | 0 | N/A | 0 | 0
2021-10-13 18:00 | 4.8381 | 0 | N/A | 0 | 0
2021-10-13 18:30 | 5.8243 | 0 | N/A | 0 | 0
2021-10-13 19:00 | 6.3187 | 0 | N/A | 0 | 0
2021-10-13 19:30 | 6.5563 | 0 | N/A | 0 | 0
2021-10-13 20:00 | 6.5458 | 0 | N/A | 0 | 0
2021-10-13 20:30 | 6.3871 | 0 | N/A | 0 | 0
2021-10-13 21:00 | 6.1393 | 0 | N/A | 0 | 0
2021-10-13 21:30 | 5.8297 | 0 | N/A | 0 | 0
2021-10-13 22:00 | 5.4921 | 0 | N/A | 0 | 0
2021-10-13 22:30 | 5.4542 | 0 | N/A | 0 | 0
2021-10-13 23:00 | 5.4163 | 0 | N/A | 0 | 0
2021-10-13 23:30 | 4.9175 | 0 | N/A | 0 | 0
2021-10-14 | 4.9676 | 0 | N/A | 0 | 0
2021-10-14 00:30 | 5.3142 | 0 | N/A | 0 | 0
2021-10-14 01:00 | 5.7012 | 0 | N/A | 0 | 0
2021-10-14 01:30 | 5.1166 | 0 | N/A | 0 | 0
2021-10-14 02:00 | 4.3689 | 0 | N/A | 0 | 0
2021-10-14 02:30 | 4.2635 | 0 | N/A | 0 | 0
2021-10-14 03:00 | 3.9973 | 0 | N/A | 0 | 0
2021-10-14 03:30 | 3.6106 | 0 | N/A | 0 | 0
2021-10-14 04:00 | 3.3787 | 0 | N/A | 0 | 0
2021-10-14 04:30 | 3.2345 | 0 | N/A | 0 | 0
2021-10-14 05:00 | 3.2433 | 0 | N/A | 0 | 0
2021-10-14 05:30 | 3.4834 | 0 | N/A | 0 | 0
2021-10-14 06:00 | 3.8821 | 0 | N/A | 0 | 0
2021-10-14 06:30 | 4.7158 | 0 | N/A | 0 | 0
2021-10-14 07:00 | 5.4162 | 0 | N/A | 0 | 0
2021-10-14 07:30 | 6.6589 | 0 | N/A | 0 | 0
2021-10-14 08:00 | 7.2652 | 0 | N/A | 0 | 0
2021-10-14 08:30 | 6.67 | 0 | N/A | 0 | 0
2021-10-14 09:00 | 5.8967 | 0 | N/A | 0 | 0
2021-10-14 09:30 | 5.14 | 0 | N/A | 0 | 0
2021-10-14 10:00 | 4.4711 | 0 | N/A | 0 | 0
2021-10-14 10:30 | 4.4208 | 0 | N/A | 0 | 0
2021-10-14 11:00 | 4.4934 | 0 | N/A | 0 | 0
2021-10-14 11:30 | 3.9989 | 0 | N/A | 0 | 0
2021-10-14 12:00 | 3.4292 | 0 | N/A | 0 | 0
2021-10-14 12:30 | 2.3998 | 0 | N/A | 0 | 0
2021-10-14 13:00 | 1.7555 | 0 | N/A | 0 | 0
2021-10-14 13:30 | 1.3408 | 0 | N/A | 0 | 0
2021-10-14 14:00 | 1.666 | 0 | N/A | 0 | 0
2021-10-14 14:30 | 1.7748 | 0 | N/A | 0 | 0
2021-10-14 15:00 | 2.0601 | 0 | N/A | 0 | 0
2021-10-14 15:30 | 1.6323 | 0 | N/A | 0 | 0
2021-10-14 16:00 | 3.3946 | 0 | N/A | 0 | 0
2021-10-14 16:30 | 4.2652 | 0 | N/A | 0 | 0
2021-10-14 17:00 | 4.7291 | 0 | N/A | 0 | 0
2021-10-14 17:30 | 5.2066 | 0 | N/A | 0 | 0
2021-10-14 18:00 | 5.1169 | 0 | N/A | 0 | 0
2021-10-14 18:30 | 5.0218 | 0 | N/A | 0 | 0
2021-10-14 19:00 | 5.4716 | 0 | N/A | 0 | 0
2021-10-14 19:30 | 5.9848 | 0 | N/A | 0 | 0
2021-10-14 20:00 | 6.4106 | 0 | N/A | 0 | 0
2021-10-14 20:30 | 6.5867 | 0 | N/A | 0 | 0
2021-10-14 21:00 | 6.4727 | 0 | N/A | 0 | 0
2021-10-14 21:30 | 6.0672 | 0 | N/A | 0 | 0
2021-10-14 22:00 | 5.5732 | 0 | N/A | 0 | 0
2021-10-14 22:30 | 5.5855 | 0 | N/A | 0 | 0
2021-10-14 23:00 | 5.3717 | 0 | N/A | 0 | 0
2021-10-14 23:30 | 4.9747 | 0 | N/A | 0 | 0
2021-10-15 | 4.9605 | 0 | N/A | 0 | 0
2021-10-15 00:30 | 5.2924 | 0 | N/A | 0 | 0
2021-10-15 01:00 | 5.6955 | 0 | N/A | 0 | 0
2021-10-15 01:30 | 5.1508 | 0 | N/A | 0 | 0
2021-10-15 02:00 | 4.518 | 0 | N/A | 0 | 0
2021-10-15 02:30 | 4.4317 | 0 | N/A | 0 | 0
2021-10-15 03:00 | 4.1539 | 0 | N/A | 0 | 0
2021-10-15 03:30 | 3.769 | 0 | N/A | 0 | 0
2021-10-15 04:00 | 3.4565 | 0 | N/A | 0 | 0
2021-10-15 04:30 | 3.3653 | 0 | N/A | 0 | 0
2021-10-15 05:00 | 3.2954 | 0 | N/A | 0 | 0
2021-10-15 05:30 | 3.5931 | 0 | N/A | 0 | 0
2021-10-15 06:00 | 3.9678 | 0 | N/A | 0 | 0
2021-10-15 06:30 | 4.8844 | 0 | N/A | 0 | 0
2021-10-15 07:00 | 5.749 | 0 | N/A | 0 | 0
2021-10-15 07:30 | 6.7415 | 0 | N/A | 0 | 0
2021-10-15 08:00 | 7.3847 | 0 | N/A | 0 | 0
2021-10-15 08:30 | 6.5679 | 0 | N/A | 0 | 0
2021-10-15 09:00 | 5.5707 | 0 | N/A | 0 | 0
2021-10-15 09:30 | 4.6412 | 0 | N/A | 0 | 0
2021-10-15 10:00 | 4.1079 | 0 | N/A | 0 | 0
2021-10-15 10:30 | 3.3228 | 0 | N/A | 0 | 0
2021-10-15 11:00 | 2.8833 | 0 | N/A | 0 | 0
2021-10-15 11:30 | 2.7688 | 0 | N/A | 0 | 0
2021-10-15 12:00 | 3.455 | 0 | N/A | 0 | 0
2021-10-15 12:30 | 4.6156 | 0 | N/A | 0 | 0
2021-10-15 13:00 | 5.4989 | 0 | N/A | 0 | 0
2021-10-15 13:30 | 5.4535 | 0 | N/A | 0 | 0
2021-10-15 14:00 | 4.809 | 0 | N/A | 0 | 0
2021-10-15 14:30 | 4.8766 | 0 | N/A | 0 | 0
2021-10-15 15:00 | 5.4499 | 0 | N/A | 0 | 0
2021-10-15 15:30 | 5.5903 | 0 | N/A | 0 | 0
2021-10-15 16:00 | 5.7235 | 0 | N/A | 0 | 0
2021-10-15 16:30 | 5.9414 | 0 | N/A | 0 | 0
2021-10-15 17:00 | 6.4484 | 0 | N/A | 0 | 0
2021-10-15 17:30 | 6.8459 | 0 | N/A | 0 | 0
2021-10-15 18:00 | 7.0515 | 0 | N/A | 0 | 0
2021-10-15 18:30 | 7.496 | 0 | N/A | 0 | 0
2021-10-15 19:00 | 7.5946 | 0 | N/A | 0 | 0
2021-10-15 19:30 | 7.7634 | 0 | N/A | 0 | 0
2021-10-15 20:00 | 7.753 | 0 | N/A | 0 | 0
2021-10-15 20:30 | 7.5225 | 0 | N/A | 0 | 0
2021-10-15 21:00 | 7.131 | 0 | N/A | 0 | 0
2021-10-15 21:30 | 6.6876 | 0 | N/A | 0 | 0
2021-10-15 22:00 | 6.35 | 0 | N/A | 0 | 0
2021-10-15 22:30 | 6.4739 | 0 | N/A | 0 | 0
2021-10-15 23:00 | 6.3059 | 0 | N/A | 0 | 0
2021-10-15 23:30 | 5.7225 | 0 | N/A | 0 | 0
2021-10-16 | 5.6531 | 0 | N/A | 0 | 0
2021-10-16 00:30 | 5.9567 | 0 | N/A | 0 | 0
2021-10-16 01:00 | 6.3837 | 0 | N/A | 0 | 0
2021-10-16 01:30 | 5.7908 | 0 | N/A | 0 | 0
2021-10-16 02:00 | 5.0976 | 0 | N/A | 0 | 0
2021-10-16 02:30 | 5.0098 | 0 | N/A | 0 | 0
2021-10-16 03:00 | 4.6275 | 0 | N/A | 0 | 0
2021-10-16 03:30 | 4.1897 | 0 | N/A | 0 | 0
2021-10-16 04:00 | 3.8984 | 0 | N/A | 0 | 0
2021-10-16 04:30 | 3.7222 | 0 | N/A | 0 | 0
2021-10-16 05:00 | 3.5568 | 0 | N/A | 0 | 0
2021-10-16 05:30 | 3.6983 | 0 | N/A | 0 | 0
2021-10-16 06:00 | 3.883 | 0 | N/A | 0 | 0
2021-10-16 06:30 | 4.2805 | 0 | N/A | 0 | 0
2021-10-16 07:00 | 4.6507 | 0 | N/A | 0 | 0
2021-10-16 07:30 | 4.9929 | 0 | N/A | 0 | 0
2021-10-16 08:00 | 5.5076 | 0 | N/A | 0 | 0
2021-10-16 08:30 | 5.519 | 0 | N/A | 0 | 0
2021-10-16 09:00 | 5.616 | 0 | N/A | 0 | 0
2021-10-16 09:30 | 5.781 | 0 | N/A | 0 | 0
2021-10-16 10:00 | 5.2128 | 0 | N/A | 0 | 0
2021-10-16 10:30 | 5.2544 | 0 | N/A | 0 | 0
2021-10-16 11:00 | 4.6098 | 0 | N/A | 0 | 0
2021-10-16 11:30 | 4.294 | 0 | N/A | 0 | 0
2021-10-16 12:00 | 4.2079 | 0 | N/A | 0 | 0
2021-10-16 12:30 | 3.9977 | 0 | N/A | 0 | 0
2021-10-16 13:00 | 4.2538 | 0 | N/A | 0 | 0
2021-10-16 13:30 | 3.6129 | 0 | N/A | 0 | 0
2021-10-16 14:00 | 2.8719 | 0 | N/A | 0 | 0
2021-10-16 14:30 | 2.9505 | 0 | N/A | 0 | 0
2021-10-16 15:00 | 2.8986 | 0 | N/A | 0 | 0
2021-10-16 15:30 | 2.4853 | 0 | N/A | 0 | 0
2021-10-16 16:00 | 3.1156 | 0 | N/A | 0 | 0
2021-10-16 16:30 | 3.4668 | 0 | N/A | 0 | 0
2021-10-16 17:00 | 3.5611 | 0 | N/A | 0 | 0
2021-10-16 17:30 | 4.6849 | 0 | N/A | 0 | 0
2021-10-16 18:00 | 5.2661 | 0 | N/A | 0 | 0
2021-10-16 18:30 | 5.9753 | 0 | N/A | 0 | 0
2021-10-16 19:00 | 6.4636 | 0 | N/A | 0 | 0
2021-10-16 19:30 | 6.6396 | 0 | N/A | 0 | 0
2021-10-16 20:00 | 6.59 | 0 | N/A | 0 | 0
2021-10-16 20:30 | 6.589 | 0 | N/A | 0 | 0
2021-10-16 21:00 | 6.2215 | 0 | N/A | 0 | 0
2021-10-16 21:30 | 5.9463 | 0 | N/A | 0 | 0
2021-10-16 22:00 | 5.7031 | 0 | N/A | 0 | 0
2021-10-16 22:30 | 5.9048 | 0 | N/A | 0 | 0
2021-10-16 23:00 | 5.946 | 0 | N/A | 0 | 0
2021-10-16 23:30 | 5.5113 | 0 | N/A | 0 | 0
2021-10-17 | 5.4123 | 0 | N/A | 0 | 0
2021-10-17 00:30 | 5.621 | 0 | N/A | 0 | 0
2021-10-17 01:00 | 6.0573 | 0 | N/A | 0 | 0
2021-10-17 01:30 | 5.4232 | 0 | N/A | 0 | 0
2021-10-17 02:00 | 4.7446 | 0 | N/A | 0 | 0
2021-10-17 02:30 | 4.6631 | 0 | N/A | 0 | 0
2021-10-17 03:00 | 4.3194 | 0 | N/A | 0 | 0
2021-10-17 03:30 | 3.8475 | 0 | N/A | 0 | 0
2021-10-17 04:00 | 3.5358 | 0 | N/A | 0 | 0
2021-10-17 04:30 | 3.2859 | 0 | N/A | 0 | 0
2021-10-17 05:00 | 3.1591 | 0 | N/A | 0 | 0
2021-10-17 05:30 | 3.2427 | 0 | N/A | 0 | 0
2021-10-17 06:00 | 3.2681 | 0 | N/A | 0 | 0
2021-10-17 06:30 | 3.5429 | 0 | N/A | 0 | 0
2021-10-17 07:00 | 3.7667 | 0 | N/A | 0 | 0
2021-10-17 07:30 | 4.1279 | 0 | N/A | 0 | 0
2021-10-17 08:00 | 4.3098 | 0 | N/A | 0 | 0
2021-10-17 08:30 | 4.2061 | 0 | N/A | 0 | 0
2021-10-17 09:00 | 4.4426 | 0 | N/A | 0 | 0
2021-10-17 09:30 | 4.5801 | 0 | N/A | 0 | 0
2021-10-17 10:00 | 4.3801 | 0 | N/A | 0 | 0
2021-10-17 10:30 | 3.9303 | 0 | N/A | 0 | 0
2021-10-17 11:00 | 3.3843 | 0 | N/A | 0 | 0
2021-10-17 11:30 | 2.818 | 0 | N/A | 0 | 0
2021-10-17 12:00 | 1.9371 | 0 | N/A | 0 | 0
2021-10-17 12:30 | 1.2033 | 0 | N/A | 0 | 0
2021-10-17 13:00 | 1.0886 | 0 | N/A | 0 | 0
2021-10-17 13:30 | 1.7119 | 0 | N/A | 0 | 0
2021-10-17 14:00 | 1.9622 | 0 | N/A | 0 | 0
2021-10-17 14:30 | 0.99537 | 0 | N/A | 0 | 0
2021-10-17 15:00 | 0.76107 | 0 | N/A | 0 | 0
2021-10-17 15:30 | 0.85147 | 0 | N/A | 0 | 0
2021-10-17 16:00 | 1.3708 | 0 | N/A | 0 | 0
2021-10-17 16:30 | 1.6916 | 0 | N/A | 0 | 0
2021-10-17 17:00 | 2.4908 | 0 | N/A | 0 | 0
2021-10-17 17:30 | 3.8752 | 0 | N/A | 0 | 0
2021-10-17 18:00 | 4.631 | 0 | N/A | 0 | 0
2021-10-17 18:30 | 5.3945 | 0 | N/A | 0 | 0
2021-10-17 19:00 | 6.2497 | 0 | N/A | 0 | 0
2021-10-17 19:30 | 6.5358 | 0 | N/A | 0 | 0
2021-10-17 20:00 | 6.6458 | 0 | N/A | 0 | 0
2021-10-17 20:30 | 6.6053 | 0 | N/A | 0 | 0
2021-10-17 21:00 | 6.4035 | 0 | N/A | 0 | 0
2021-10-17 21:30 | 6.0788 | 0 | N/A | 0 | 0
2021-10-17 22:00 | 5.7384 | 0 | N/A | 0 | 0
2021-10-17 22:30 | 5.8975 | 0 | N/A | 0 | 0
2021-10-17 23:00 | 5.9883 | 0 | N/A | 0 | 0
2021-10-17 23:30 | 5.6269 | 0 | N/A | 0 | 0
2021-10-18 | 5.8289 | 0 | N/A | 0 | 0
2021-10-18 00:30 | 6.0037 | 0 | N/A | 0 | 0
2021-10-18 01:00 | 6.4974 | 0 | N/A | 0 | 0
2021-10-18 01:30 | 5.9351 | 0 | N/A | 0 | 0
2021-10-18 02:00 | 5.3758 | 0 | N/A | 0 | 0
2021-10-18 02:30 | 5.3001 | 0 | N/A | 0 | 0
2021-10-18 03:00 | 4.933 | 0 | N/A | 0 | 0
2021-10-18 03:30 | 4.4663 | 0 | N/A | 0 | 0
2021-10-18 04:00 | 4.1671 | 0 | N/A | 0 | 0
2021-10-18 04:30 | 3.9688 | 0 | N/A | 0 | 0
2021-10-18 05:00 | 3.9295 | 0 | N/A | 0 | 0
2021-10-18 05:30 | 4.0627 | 0 | N/A | 0 | 0
2021-10-18 06:00 | 4.4811 | 0 | N/A | 0 | 0
2021-10-18 06:30 | 5.24 | 0 | N/A | 0 | 0
2021-10-18 07:00 | 5.8945 | 0 | N/A | 0 | 0
2021-10-18 07:30 | 6.8927 | 0 | N/A | 0 | 0
2021-10-18 08:00 | 7.5688 | 0 | N/A | 0 | 0
2021-10-18 08:30 | 6.9623 | 0 | N/A | 0 | 0
2021-10-18 09:00 | 7.0018 | 0 | N/A | 0 | 0
2021-10-18 09:30 | 6.7926 | 0 | N/A | 0 | 0
2021-10-18 10:00 | 6.1723 | 0 | N/A | 0 | 0
2021-10-18 10:30 | 4.4206 | 0 | N/A | 0 | 0
2021-10-18 11:00 | 3.6051 | 0 | N/A | 0 | 0
2021-10-18 11:30 | 2.1127 | 0 | N/A | 0 | 0
2021-10-18 12:00 | 1.6775 | 0 | N/A | 0 | 0
2021-10-18 12:30 | 2.048 | 0 | N/A | 0 | 0
2021-10-18 13:00 | 2.2072 | 0 | N/A | 0 | 0
2021-10-18 13:30 | 2.3544 | 0 | N/A | 0 | 0
2021-10-18 14:00 | 2.2076 | 0 | N/A | 0 | 0
2021-10-18 14:30 | 1.506 | 0 | N/A | 0 | 0
2021-10-18 15:00 | 2.1125 | 0 | N/A | 0 | 0
2021-10-18 15:30 | 2.5189 | 0 | N/A | 0 | 0
2021-10-18 16:00 | 3.8455 | 0 | N/A | 0 | 0
2021-10-18 16:30 | 4.423 | 0 | N/A | 0 | 0
2021-10-18 17:00 | 4.6883 | 0 | N/A | 0 | 0
2021-10-18 17:30 | 4.7721 | 0 | N/A | 0 | 0
2021-10-18 18:00 | 5.139 | 0 | N/A | 0 | 0
2021-10-18 18:30 | 6.1047 | 0 | N/A | 0 | 0
2021-10-18 19:00 | 6.2822 | 0 | N/A | 0 | 0
2021-10-18 19:30 | 6.6748 | 0 | N/A | 0 | 0
2021-10-18 20:00 | 6.9806 | 0 | N/A | 0 | 0
2021-10-18 20:30 | 7.0401 | 0 | N/A | 0 | 0
2021-10-18 21:00 | 6.8641 | 0 | N/A | 0 | 0
2021-10-18 21:30 | 6.5172 | 0 | N/A | 0 | 0
2021-10-18 22:00 | 6.1071 | 0 | N/A | 0 | 0
2021-10-18 22:30 | 6.08 | 0 | N/A | 0 | 0
2021-10-18 23:00 | 6.0487 | 0 | N/A | 0 | 0
2021-10-18 23:30 | 5.7309 | 0 | N/A | 0 | 0
2021-10-19 | 5.6686 | 0 | N/A | 0 | 0
2021-10-19 00:30 | 6.084 | 0 | N/A | 0 | 0
2021-10-19 01:00 | 6.5346 | 0 | N/A | 0 | 0
2021-10-19 01:30 | 5.8803 | 0 | N/A | 0 | 0
2021-10-19 02:00 | 5.1678 | 0 | N/A | 0 | 0
2021-10-19 02:30 | 5.0493 | 0 | N/A | 0 | 0
2021-10-19 03:00 | 4.7375 | 0 | N/A | 0 | 0
2021-10-19 03:30 | 4.4036 | 0 | N/A | 0 | 0
2021-10-19 04:00 | 4.1707 | 0 | N/A | 0 | 0
2021-10-19 04:30 | 4.0068 | 0 | N/A | 0 | 0
2021-10-19 05:00 | 4.0225 | 0 | N/A | 0 | 0
2021-10-19 05:30 | 4.1943 | 0 | N/A | 0 | 0
2021-10-19 06:00 | 4.5061 | 0 | N/A | 0 | 0
2021-10-19 06:30 | 5.432 | 0 | N/A | 0 | 0
2021-10-19 07:00 | 6.2357 | 0 | N/A | 0 | 0
2021-10-19 07:30 | 7.2601 | 0 | N/A | 0 | 0
2021-10-19 08:00 | 7.8293 | 0 | N/A | 0 | 0
2021-10-19 08:30 | 7.0639 | 0 | N/A | 0 | 0
2021-10-19 09:00 | 6.0309 | 0 | N/A | 0 | 0
2021-10-19 09:30 | 5.7846 | 0 | N/A | 0 | 0
2021-10-19 10:00 | 5.0671 | 0 | N/A | 0 | 0
2021-10-19 10:30 | 4.7855 | 0 | N/A | 0 | 0
2021-10-19 11:00 | 3.5118 | 0 | N/A | 0 | 0
2021-10-19 11:30 | 3.4453 | 0 | N/A | 0 | 0
2021-10-19 12:00 | 3.2613 | 0 | N/A | 0 | 0
2021-10-19 12:30 | 2.6806 | 0 | N/A | 0 | 0
2021-10-19 13:00 | 2.5198 | 0 | N/A | 0 | 0
2021-10-19 13:30 | 1.9423 | 0 | N/A | 0 | 0
2021-10-19 14:00 | 2.833 | 0 | N/A | 0 | 0
2021-10-19 14:30 | 1.9037 | 0 | N/A | 0 | 0
2021-10-19 15:00 | 3.1273 | 0 | N/A | 0 | 0
2021-10-19 15:30 | 3.5794 | 0 | N/A | 0 | 0
2021-10-19 16:00 | 3.8092 | 0 | N/A | 0 | 0
2021-10-19 16:30 | 3.8547 | 0 | N/A | 0 | 0
2021-10-19 17:00 | 3.2285 | 0 | N/A | 0 | 0
2021-10-19 17:30 | 3.2852 | 0 | N/A | 0 | 0
2021-10-19 18:00 | 4.6488 | 0 | N/A | 0 | 0
2021-10-19 18:30 | 5.6769 | 0 | N/A | 0 | 0
2021-10-19 19:00 | 6.3478 | 0 | N/A | 0 | 0
2021-10-19 19:30 | 6.6116 | 0 | N/A | 0 | 0
2021-10-19 20:00 | 6.9693 | 0 | N/A | 0 | 0
2021-10-19 20:30 | 7.121 | 0 | N/A | 0 | 0
2021-10-19 21:00 | 6.9494 | 0 | N/A | 0 | 0
2021-10-19 21:30 | 6.4758 | 0 | N/A | 0 | 0
2021-10-19 22:00 | 6.056 | 0 | N/A | 0 | 0
2021-10-19 22:30 | 6.0265 | 0 | N/A | 0 | 0
2021-10-19 23:00 | 5.8646 | 0 | N/A | 0 | 0
2021-10-19 23:30 | 5.5063 | 0 | N/A | 0 | 0
2021-10-20 | 5.5497 | 0 | N/A | 0 | 0
2021-10-20 00:30 | 5.8521 | 0 | N/A | 0 | 0
2021-10-20 01:00 | 6.2341 | 0 | N/A | 0 | 0
2021-10-20 01:30 | 5.6977 | 0 | N/A | 0 | 0
2021-10-20 02:00 | 5.0506 | 0 | N/A | 0 | 0
2021-10-20 02:30 | 4.9455 | 0 | N/A | 0 | 0
2021-10-20 03:00 | 4.6026 | 0 | N/A | 0 | 0
2021-10-20 03:30 | 4.1741 | 0 | N/A | 0 | 0
2021-10-20 04:00 | 3.957 | 0 | N/A | 0 | 0
2021-10-20 04:30 | 3.8646 | 0 | N/A | 0 | 0
2021-10-20 05:00 | 3.8123 | 0 | N/A | 0 | 0
2021-10-20 05:30 | 4.0602 | 0 | N/A | 0 | 0
2021-10-20 06:00 | 4.4323 | 0 | N/A | 0 | 0
2021-10-20 06:30 | 5.2027 | 0 | N/A | 0 | 0
2021-10-20 07:00 | 5.9704 | 0 | N/A | 0 | 0
2021-10-20 07:30 | 6.8833 | 0 | N/A | 0 | 0
2021-10-20 08:00 | 6.8817 | 0 | N/A | 0 | 0
2021-10-20 08:30 | 5.4432 | 0 | N/A | 0 | 0
2021-10-20 09:00 | 4.3457 | 0 | N/A | 0 | 0
2021-10-20 09:30 | 3.1981 | 0 | N/A | 0 | 0
2021-10-20 10:00 | 2.1422 | 0 | N/A | 0 | 0
2021-10-20 10:30 | 1.3497 | 0 | N/A | 0 | 0
2021-10-20 11:00 | 0.71309 | 0 | N/A | 0 | 0
2021-10-20 11:30 | 0.40421 | 0 | N/A | 0 | 0
2021-10-20 12:00 | -0.23704 | 0 | N/A | 0 | 0
2021-10-20 12:30 | -0.28382 | 0 | N/A | 0 | 0
2021-10-20 13:00 | -0.37074 | 0 | N/A | 0 | 0
2021-10-20 13:30 | -0.54712 | 0 | N/A | 0 | 0
2021-10-20 14:00 | -0.67267 | 0 | N/A | 0 | 0
2021-10-20 14:30 | 0.27588 | 0 | N/A | 0 | 0
2021-10-20 15:00 | -0.4151 | 0 | N/A | 0 | 0
2021-10-20 15:30 | -0.31471 | 0 | N/A | 0 | 0
2021-10-20 16:00 | 0.36056 | 0 | N/A | 0 | 0
2021-10-20 16:30 | 0.70036 | 0 | N/A | 0 | 0
2021-10-20 17:00 | 1.5494 | 0 | N/A | 0 | 0
2021-10-20 17:30 | 2.535 | 0 | N/A | 0 | 0
2021-10-20 18:00 | 3.6158 | 0 | N/A | 0 | 0
2021-10-20 18:30 | 4.4749 | 0 | N/A | 0 | 0
2021-10-20 19:00 | 5.0038 | 0 | N/A | 0 | 0
2021-10-20 19:30 | 5.1578 | 0 | N/A | 0 | 0
2021-10-20 20:00 | 5.4252 | 0 | N/A | 0 | 0
2021-10-20 20:30 | 5.44 | 0 | N/A | 0 | 0
2021-10-20 21:00 | 5.4197 | 0 | N/A | 0 | 0
2021-10-20 21:30 | 5.1149 | 0 | N/A | 0 | 0
2021-10-20 22:00 | 4.7839 | 0 | N/A | 0 | 0
2021-10-20 22:30 | 5.0043 | 0 | N/A | 0 | 0
2021-10-20 23:00 | 5.0467 | 0 | N/A | 0 | 0
2021-10-20 23:30 | 4.7987 | 0 | N/A | 0 | 0
2021-10-21 | 4.8959 | 0 | N/A | 0 | 0
2021-10-21 00:30 | 5.2763 | 0 | N/A | 0 | 0
2021-10-21 01:00 | 5.5503 | 0 | N/A | 0 | 0
2021-10-21 01:30 | 4.8442 | 0 | N/A | 0 | 0
2021-10-21 02:00 | 4.2428 | 0 | N/A | 0 | 0
2021-10-21 02:30 | 4.1354 | 0 | N/A | 0 | 0
2021-10-21 03:00 | 3.8443 | 0 | N/A | 0 | 0
2021-10-21 03:30 | 3.4616 | 0 | N/A | 0 | 0
2021-10-21 04:00 | 3.3584 | 0 | N/A | 0 | 0
2021-10-21 04:30 | 3.264 | 0 | N/A | 0 | 0
2021-10-21 05:00 | 3.2837 | 0 | N/A | 0 | 0
2021-10-21 05:30 | 3.3563 | 0 | N/A | 0 | 0
2021-10-21 06:00 | 3.5957 | 0 | N/A | 0 | 0
2021-10-21 06:30 | 4.1796 | 0 | N/A | 0 | 0
2021-10-21 07:00 | 4.7344 | 0 | N/A | 0 | 0
2021-10-21 07:30 | 5.699 | 0 | N/A | 0 | 0
2021-10-21 08:00 | 5.8179 | 0 | N/A | 0 | 0
2021-10-21 08:30 | 5.4711 | 0 | N/A | 0 | 0
2021-10-21 09:00 | 5.2256 | 0 | N/A | 0 | 0
2021-10-21 09:30 | 4.4025 | 0 | N/A | 0 | 0
2021-10-21 10:00 | 3.5199 | 0 | N/A | 0 | 0
2021-10-21 10:30 | 2.6253 | 0 | N/A | 0 | 0
2021-10-21 11:00 | 2.288 | 0 | N/A | 0 | 0
2021-10-21 11:30 | 1.958 | 0 | N/A | 0 | 0
2021-10-21 12:00 | 1.3394 | 0 | N/A | 0 | 0
2021-10-21 12:30 | 0.74685 | 0 | N/A | 0 | 0
2021-10-21 13:00 | -0.39011 | 0 | N/A | 0 | 0
2021-10-21 13:30 | -0.6357 | 0 | N/A | 0 | 0
2021-10-21 14:00 | -0.46934 | 0 | N/A | 0 | 0
2021-10-21 14:30 | 0.31988 | 0 | N/A | 0 | 0
2021-10-21 15:00 | 0.91601 | 0 | N/A | 0 | 0
2021-10-21 15:30 | 0.37602 | 0 | N/A | 0 | 0
2021-10-21 16:00 | 0.636 | 0 | N/A | 0 | 0
2021-10-21 16:30 | 1.7918 | 0 | N/A | 0 | 0
2021-10-21 17:00 | 2.3205 | 0 | N/A | 0 | 0
2021-10-21 17:30 | 3.0086 | 0 | N/A | 0 | 0
2021-10-21 18:00 | 3.77 | 0 | N/A | 0 | 0
2021-10-21 18:30 | 4.2985 | 0 | N/A | 0 | 0
2021-10-21 19:00 | 4.726 | 0 | N/A | 0 | 0
2021-10-21 19:30 | 5.0082 | 0 | N/A | 0 | 0
2021-10-21 20:00 | 4.6701 | 0 | N/A | 0 | 0
2021-10-21 20:30 | 5.022 | 0 | N/A | 0 | 0
2021-10-21 21:00 | 4.784 | 0 | N/A | 0 | 0
2021-10-21 21:30 | 4.7006 | 0 | N/A | 0 | 0
2021-10-21 22:00 | 4.6488 | 0 | N/A | 0 | 0
2021-10-21 22:30 | 4.2092 | 0 | N/A | 0 | 0
2021-10-21 23:00 | 4.3056 | 0 | N/A | 0 | 0
2021-10-21 23:30 | 3.9928 | 0 | N/A | 0 | 0
2021-10-22 | 4.0202 | 0 | N/A | 0 | 0
2021-10-22 00:30 | 4.4964 | 0 | N/A | 0 | 0
2021-10-22 01:00 | 4.8255 | 0 | N/A | 0 | 0
2021-10-22 01:30 | 4.1483 | 0 | N/A | 0 | 0
2021-10-22 02:00 | 3.4626 | 0 | N/A | 0 | 0
2021-10-22 02:30 | 3.4291 | 0 | N/A | 0 | 0
2021-10-22 03:00 | 3.0876 | 0 | N/A | 0 | 0
2021-10-22 03:30 | 2.6857 | 0 | N/A | 0 | 0
2021-10-22 04:00 | 2.5677 | 0 | N/A | 0 | 0
2021-10-22 04:30 | 2.5631 | 0 | N/A | 0 | 0
2021-10-22 05:00 | 2.5858 | 0 | N/A | 0 | 0
2021-10-22 05:30 | 2.7063 | 0 | N/A | 0 | 0
2021-10-22 06:00 | 3.0313 | 0 | N/A | 0 | 0
2021-10-22 06:30 | 3.5802 | 0 | N/A | 0 | 0
2021-10-22 07:00 | 4.1618 | 0 | N/A | 0 | 0
2021-10-22 07:30 | 4.656 | 0 | N/A | 0 | 0
2021-10-22 08:00 | 4.6966 | 0 | N/A | 0 | 0
2021-10-22 08:30 | 3.561 | 0 | N/A | 0 | 0
2021-10-22 09:00 | 2.6536 | 0 | N/A | 0 | 0
2021-10-22 09:30 | 2.4351 | 0 | N/A | 0 | 0
2021-10-22 10:00 | 1.7317 | 0 | N/A | 0 | 0
2021-10-22 10:30 | 0.57628 | 0 | N/A | 0 | 0
2021-10-22 11:00 | 0.58139 | 0 | N/A | 0 | 0
2021-10-22 11:30 | 1.473 | 0 | N/A | 0 | 0
2021-10-22 12:00 | 1.4419 | 0 | N/A | 0 | 0
2021-10-22 12:30 | 1.6457 | 0 | N/A | 0 | 0
2021-10-22 13:00 | 0.58207 | 0 | N/A | 0 | 0
2021-10-22 13:30 | 0.33134 | 0 | N/A | 0 | 0
2021-10-22 14:00 | 1.1563 | 0 | N/A | 0 | 0
2021-10-22 14:30 | 1.5691 | 0 | N/A | 0 | 0
2021-10-22 15:00 | 2.7754 | 0 | N/A | 0 | 0
2021-10-22 15:30 | 3.1588 | 0 | N/A | 0 | 0
2021-10-22 16:00 | 1.742 | 0 | N/A | 0 | 0
2021-10-22 16:30 | 1.9064 | 0 | N/A | 0 | 0
2021-10-22 17:00 | 2.4547 | 0 | N/A | 0 | 0
2021-10-22 17:30 | 3.5105 | 0 | N/A | 0 | 0
2021-10-22 18:00 | 3.8976 | 0 | N/A | 0 | 0
2021-10-22 18:30 | 4.1013 | 0 | N/A | 0 | 0
2021-10-22 19:00 | 4.3267 | 0 | N/A | 0 | 0
2021-10-22 19:30 | 4.5771 | 0 | N/A | 0 | 0
2021-10-22 20:00 | 4.8103 | 0 | N/A | 0 | 0
2021-10-22 20:30 | 4.7783 | 0 | N/A | 0 | 0
2021-10-22 21:00 | 4.6063 | 0 | N/A | 0 | 0
2021-10-22 21:30 | 4.3303 | 0 | N/A | 0 | 0
2021-10-22 22:00 | 4.0765 | 0 | N/A | 0 | 0
2021-10-22 22:30 | 4.3842 | 0 | N/A | 0 | 0
2021-10-22 23:00 | 4.5355 | 0 | N/A | 0 | 0
2021-10-22 23:30 | 4.2432 | 0 | N/A | 0 | 0
2021-10-23 | 4.4059 | 0 | N/A | 0 | 0
2021-10-23 00:30 | 4.7905 | 0 | N/A | 0 | 0
2021-10-23 01:00 | 5.0825 | 0 | N/A | 0 | 0
2021-10-23 01:30 | 4.3181 | 0 | N/A | 0 | 0
2021-10-23 02:00 | 3.554 | 0 | N/A | 0 | 0
2021-10-23 02:30 | 3.4823 | 0 | N/A | 0 | 0
2021-10-23 03:00 | 3.1163 | 0 | N/A | 0 | 0
2021-10-23 03:30 | 2.8167 | 0 | N/A | 0 | 0
2021-10-23 04:00 | 2.5782 | 0 | N/A | 0 | 0
2021-10-23 04:30 | 2.5255 | 0 | N/A | 0 | 0
2021-10-23 05:00 | 2.5138 | 0 | N/A | 0 | 0
2021-10-23 05:30 | 2.5722 | 0 | N/A | 0 | 0
2021-10-23 06:00 | 2.6721 | 0 | N/A | 0 | 0
2021-10-23 06:30 | 2.8836 | 0 | N/A | 0 | 0
2021-10-23 07:00 | 3.2045 | 0 | N/A | 0 | 0
2021-10-23 07:30 | 3.3183 | 0 | N/A | 0 | 0
2021-10-23 08:00 | 3.3136 | 0 | N/A | 0 | 0
2021-10-23 08:30 | 3.3963 | 0 | N/A | 0 | 0
2021-10-23 09:00 | 3.6826 | 0 | N/A | 0 | 0
2021-10-23 09:30 | 4.0609 | 0 | N/A | 0 | 0
2021-10-23 10:00 | 3.7132 | 0 | N/A | 0 | 0
2021-10-23 10:30 | 3.5432 | 0 | N/A | 0 | 0
2021-10-23 11:00 | 3.4562 | 0 | N/A | 0 | 0
2021-10-23 11:30 | 2.8563 | 0 | N/A | 0 | 0
2021-10-23 12:00 | 2.3828 | 0 | N/A | 0 | 0
2021-10-23 12:30 | 1.8178 | 0 | N/A | 0 | 0
2021-10-23 13:00 | 2.9995 | 0 | N/A | 0 | 0
2021-10-23 13:30 | 2.5914 | 0 | N/A | 0 | 0
2021-10-23 14:00 | 1.5998 | 0 | N/A | 0 | 0
2021-10-23 14:30 | 2.6868 | 0 | N/A | 0 | 0
2021-10-23 15:00 | 2.527 | 0 | N/A | 0 | 0
2021-10-23 15:30 | 1.4151 | 0 | N/A | 0 | 0
2021-10-23 16:00 | 2.1761 | 0 | N/A | 0 | 0
2021-10-23 16:30 | 3.7909 | 0 | N/A | 0 | 0
2021-10-23 17:00 | 4.4273 | 0 | N/A | 0 | 0
2021-10-23 17:30 | 4.3391 | 0 | N/A | 0 | 0
2021-10-23 18:00 | 4.9326 | 0 | N/A | 0 | 0
2021-10-23 18:30 | 5.3476 | 0 | N/A | 0 | 0
2021-10-23 19:00 | 6.1087 | 0 | N/A | 0 | 0
2021-10-23 19:30 | 6.3176 | 0 | N/A | 0 | 0
2021-10-23 20:00 | 6.2473 | 0 | N/A | 0 | 0
2021-10-23 20:30 | 6.1669 | 0 | N/A | 0 | 0
2021-10-23 21:00 | 6.0786 | 0 | N/A | 0 | 0
2021-10-23 21:30 | 5.8072 | 0 | N/A | 0 | 0
2021-10-23 22:00 | 5.4161 | 0 | N/A | 0 | 0
2021-10-23 22:30 | 5.5555 | 0 | N/A | 0 | 0
2021-10-23 23:00 | 5.5715 | 0 | N/A | 0 | 0
2021-10-23 23:30 | 5.2744 | 0 | N/A | 0 | 0
2021-10-24 | 5.3362 | 0 | N/A | 0 | 0
2021-10-24 00:30 | 5.5709 | 0 | N/A | 0 | 0
2021-10-24 01:00 | 5.8883 | 0 | N/A | 0 | 0
2021-10-24 01:30 | 5.2176 | 0 | N/A | 0 | 0
2021-10-24 02:00 | 4.5552 | 0 | N/A | 0 | 0
2021-10-24 02:30 | 4.3036 | 0 | N/A | 0 | 0
2021-10-24 03:00 | 3.9383 | 0 | N/A | 0 | 0
2021-10-24 03:30 | 3.5728 | 0 | N/A | 0 | 0
2021-10-24 04:00 | 3.2794 | 0 | N/A | 0 | 0
2021-10-24 04:30 | 3.1258 | 0 | N/A | 0 | 0
2021-10-24 05:00 | 3.0245 | 0 | N/A | 0 | 0
2021-10-24 05:30 | 3.0919 | 0 | N/A | 0 | 0
2021-10-24 06:00 | 3.155 | 0 | N/A | 0 | 0
2021-10-24 06:30 | 3.4553 | 0 | N/A | 0 | 0
2021-10-24 07:00 | 3.5156 | 0 | N/A | 0 | 0
2021-10-24 07:30 | 3.5273 | 0 | N/A | 0 | 0
2021-10-24 08:00 | 3.7006 | 0 | N/A | 0 | 0
2021-10-24 08:30 | 3.391 | 0 | N/A | 0 | 0
2021-10-24 09:00 | 3.957 | 0 | N/A | 0 | 0
2021-10-24 09:30 | 3.566 | 0 | N/A | 0 | 0
2021-10-24 10:00 | 3.3809 | 0 | N/A | 0 | 0
2021-10-24 10:30 | 3.385 | 0 | N/A | 0 | 0
2021-10-24 11:00 | 2.9919 | 0 | N/A | 0 | 0
2021-10-24 11:30 | 3.1249 | 0 | N/A | 0 | 0
2021-10-24 12:00 | 2.0682 | 0 | N/A | 0 | 0
2021-10-24 12:30 | 1.8605 | 0 | N/A | 0 | 0
2021-10-24 13:00 | 1.6515 | 0 | N/A | 0 | 0
2021-10-24 13:30 | 1.8669 | 0 | N/A | 0 | 0
2021-10-24 14:00 | 1.2526 | 0 | N/A | 0 | 0
2021-10-24 14:30 | 1.3813 | 0 | N/A | 0 | 0
2021-10-24 15:00 | 2.1512 | 0 | N/A | 0 | 0
2021-10-24 15:30 | 1.6166 | 0 | N/A | 0 | 0
2021-10-24 16:00 | 2.1508 | 0 | N/A | 0 | 0
2021-10-24 16:30 | 2.071 | 0 | N/A | 0 | 0
2021-10-24 17:00 | 3.7432 | 0 | N/A | 0 | 0
2021-10-24 17:30 | 4.2147 | 0 | N/A | 0 | 0
2021-10-24 18:00 | 4.986 | 0 | N/A | 0 | 0
2021-10-24 18:30 | 5.8125 | 0 | N/A | 0 | 0
2021-10-24 19:00 | 5.6903 | 0 | N/A | 0 | 0
2021-10-24 19:30 | 6.1696 | 0 | N/A | 0 | 0
2021-10-24 20:00 | 6.5136 | 0 | N/A | 0 | 0
2021-10-24 20:30 | 6.5188 | 0 | N/A | 0 | 0
2021-10-24 21:00 | 6.4724 | 0 | N/A | 0 | 0
2021-10-24 21:30 | 6.1254 | 0 | N/A | 0 | 0
2021-10-24 22:00 | 5.5729 | 0 | N/A | 0 | 0
2021-10-24 22:30 | 5.6592 | 0 | N/A | 0 | 0
2021-10-24 23:00 | 5.6536 | 0 | N/A | 0 | 0
2021-10-24 23:30 | 5.357 | 0 | N/A | 0 | 0
2021-10-25 | 5.3688 | 0 | N/A | 0 | 0
2021-10-25 00:30 | 5.549 | 0 | N/A | 0 | 0
2021-10-25 01:00 | 5.8931 | 0 | N/A | 0 | 0
2021-10-25 01:30 | 5.3709 | 0 | N/A | 0 | 0
2021-10-25 02:00 | 4.7205 | 0 | N/A | 0 | 0
2021-10-25 02:30 | 4.6518 | 0 | N/A | 0 | 0
2021-10-25 03:00 | 4.3061 | 0 | N/A | 0 | 0
2021-10-25 03:30 | 3.8388 | 0 | N/A | 0 | 0
2021-10-25 04:00 | 3.5313 | 0 | N/A | 0 | 0
2021-10-25 04:30 | 3.43 | 0 | N/A | 0 | 0
2021-10-25 05:00 | 3.3259 | 0 | N/A | 0 | 0
2021-10-25 05:30 | 3.5479 | 0 | N/A | 0 | 0
2021-10-25 06:00 | 3.8699 | 0 | N/A | 0 | 0
2021-10-25 06:30 | 4.7262 | 0 | N/A | 0 | 0
2021-10-25 07:00 | 5.4862 | 0 | N/A | 0 | 0
2021-10-25 07:30 | 6.5238 | 0 | N/A | 0 | 0
2021-10-25 08:00 | 6.8831 | 0 | N/A | 0 | 0
2021-10-25 08:30 | 5.844 | 0 | N/A | 0 | 0
2021-10-25 09:00 | 5.1771 | 0 | N/A | 0 | 0
2021-10-25 09:30 | 5.047 | 0 | N/A | 0 | 0
2021-10-25 10:00 | 4.873 | 0 | N/A | 0 | 0
2021-10-25 10:30 | 5.146 | 0 | N/A | 0 | 0
2021-10-25 11:00 | 4.8504 | 0 | N/A | 0 | 0
2021-10-25 11:30 | 4.1336 | 0 | N/A | 0 | 0
2021-10-25 12:00 | 4.1355 | 0 | N/A | 0 | 0
2021-10-25 12:30 | 4.1131 | 0 | N/A | 0 | 0
2021-10-25 13:00 | 3.4332 | 0 | N/A | 0 | 0
2021-10-25 13:30 | 3.042 | 0 | N/A | 0 | 0
2021-10-25 14:00 | 3.3128 | 0 | N/A | 0 | 0
2021-10-25 14:30 | 3.0807 | 0 | N/A | 0 | 0
2021-10-25 15:00 | 2.5085 | 0 | N/A | 0 | 0
2021-10-25 15:30 | 2.7647 | 0 | N/A | 0 | 0
2021-10-25 16:00 | 2.6149 | 0 | N/A | 0 | 0
2021-10-25 16:30 | 2.4333 | 0 | N/A | 0 | 0
2021-10-25 17:00 | 2.7553 | 0 | N/A | 0 | 0
2021-10-25 17:30 | 3.9522 | 0 | N/A | 0 | 0
2021-10-25 18:00 | 5.0559 | 0 | N/A | 0 | 0
2021-10-25 18:30 | 5.7672 | 0 | N/A | 0 | 0
2021-10-25 19:00 | 6.0666 | 0 | N/A | 0 | 0
2021-10-25 19:30 | 6.4612 | 0 | N/A | 0 | 0
2021-10-25 20:00 | 6.6628 | 0 | N/A | 0 | 0
2021-10-25 20:30 | 6.6425 | 0 | N/A | 0 | 0
2021-10-25 21:00 | 6.4184 | 0 | N/A | 0 | 0
2021-10-25 21:30 | 6.0491 | 0 | N/A | 0 | 0
2021-10-25 22:00 | 5.5155 | 0 | N/A | 0 | 0
2021-10-25 22:30 | 5.4087 | 0 | N/A | 0 | 0
2021-10-25 23:00 | 5.3869 | 0 | N/A | 0 | 0
2021-10-25 23:30 | 5.0485 | 0 | N/A | 0 | 0
2021-10-26 | 5.0622 | 0 | N/A | 0 | 0
2021-10-26 00:30 | 5.3358 | 0 | N/A | 0 | 0
2021-10-26 01:00 | 5.7131 | 0 | N/A | 0 | 0
2021-10-26 01:30 | 5.1182 | 0 | N/A | 0 | 0
2021-10-26 02:00 | 4.4565 | 0 | N/A | 0 | 0
2021-10-26 02:30 | 4.3945 | 0 | N/A | 0 | 0
2021-10-26 03:00 | 4.1368 | 0 | N/A | 0 | 0
2021-10-26 03:30 | 3.7225 | 0 | N/A | 0 | 0
2021-10-26 04:00 | 3.4069 | 0 | N/A | 0 | 0
2021-10-26 04:30 | 3.2922 | 0 | N/A | 0 | 0
2021-10-26 05:00 | 3.2658 | 0 | N/A | 0 | 0
2021-10-26 05:30 | 3.5539 | 0 | N/A | 0 | 0
2021-10-26 06:00 | 4.0181 | 0 | N/A | 0 | 0
2021-10-26 06:30 | 4.9594 | 0 | N/A | 0 | 0
2021-10-26 07:00 | 5.6724 | 0 | N/A | 0 | 0
2021-10-26 07:30 | 6.4855 | 0 | N/A | 0 | 0
2021-10-26 08:00 | 6.6168 | 0 | N/A | 0 | 0
2021-10-26 08:30 | 5.2231 | 0 | N/A | 0 | 0
2021-10-26 09:00 | 4.0253 | 0 | N/A | 0 | 0
2021-10-26 09:30 | 2.9699 | 0 | N/A | 0 | 0
2021-10-26 10:00 | 1.9112 | 0 | N/A | 0 | 0
2021-10-26 10:30 | 1.0259 | 0 | N/A | 0 | 0
2021-10-26 11:00 | 0.5745 | 0 | N/A | 0 | 0
2021-10-26 11:30 | 0.13744 | 0 | N/A | 0 | 0
2021-10-26 12:00 | -0.28288 | 0 | N/A | 0 | 0
2021-10-26 12:30 | -0.65293 | 0 | N/A | 0 | 0
2021-10-26 13:00 | -0.95836 | 0 | N/A | 0 | 0
2021-10-26 13:30 | -0.91735 | 0 | N/A | 0 | 0
2021-10-26 14:00 | -0.78726 | 0 | N/A | 0 | 0
2021-10-26 14:30 | -1.0094 | 0 | N/A | 0 | 0
2021-10-26 15:00 | -0.77049 | 0 | N/A | 0 | 0
2021-10-26 15:30 | -0.55733 | 0 | N/A | 0 | 0
2021-10-26 16:00 | -0.68337 | 0 | N/A | 0 | 0
2021-10-26 16:30 | -0.50703 | 0 | N/A | 0 | 0
2021-10-26 17:00 | 0.79286 | 0 | N/A | 0 | 0
2021-10-26 17:30 | 1.7818 | 0 | N/A | 0 | 0
2021-10-26 18:00 | 2.7384 | 0 | N/A | 0 | 0
2021-10-26 18:30 | 3.6955 | 0 | N/A | 0 | 0
2021-10-26 19:00 | 3.8824 | 0 | N/A | 0 | 0
2021-10-26 19:30 | 4.4233 | 0 | N/A | 0 | 0
2021-10-26 20:00 | 4.7272 | 0 | N/A | 0 | 0
2021-10-26 20:30 | 4.9006 | 0 | N/A | 0 | 0
2021-10-26 21:00 | 5.0038 | 0 | N/A | 0 | 0
2021-10-26 21:30 | 4.739 | 0 | N/A | 0 | 0
2021-10-26 22:00 | 4.459 | 0 | N/A | 0 | 0
2021-10-26 22:30 | 4.5904 | 0 | N/A | 0 | 0
2021-10-26 23:00 | 4.6486 | 0 | N/A | 0 | 0
2021-10-26 23:30 | 4.2971 | 0 | N/A | 0 | 0
2021-10-27 | 4.3766 | 0 | N/A | 0 | 0
2021-10-27 00:30 | 4.7297 | 0 | N/A | 0 | 0
2021-10-27 01:00 | 5.1796 | 0 | N/A | 0 | 0
2021-10-27 01:30 | 4.519 | 0 | N/A | 0 | 0
2021-10-27 02:00 | 3.8617 | 0 | N/A | 0 | 0
2021-10-27 02:30 | 3.8009 | 0 | N/A | 0 | 0
2021-10-27 03:00 | 3.5121 | 0 | N/A | 0 | 0
2021-10-27 03:30 | 3.1549 | 0 | N/A | 0 | 0
2021-10-27 04:00 | 2.9904 | 0 | N/A | 0 | 0
2021-10-27 04:30 | 2.8495 | 0 | N/A | 0 | 0
2021-10-27 05:00 | 2.8569 | 0 | N/A | 0 | 0
2021-10-27 05:30 | 3.1779 | 0 | N/A | 0 | 0
2021-10-27 06:00 | 3.4697 | 0 | N/A | 0 | 0
2021-10-27 06:30 | 4.479 | 0 | N/A | 0 | 0
2021-10-27 07:00 | 5.4191 | 0 | N/A | 0 | 0
2021-10-27 07:30 | 6.08 | 0 | N/A | 0 | 0
2021-10-27 08:00 | 5.771 | 0 | N/A | 0 | 0
2021-10-27 08:30 | 4.3419 | 0 | N/A | 0 | 0
2021-10-27 09:00 | 3.2417 | 0 | N/A | 0 | 0
2021-10-27 09:30 | 2.1397 | 0 | N/A | 0 | 0
2021-10-27 10:00 | 1.0819 | 0 | N/A | 0 | 0
2021-10-27 10:30 | 0.38737 | 0 | N/A | 0 | 0
2021-10-27 11:00 | -0.15264 | 0 | N/A | 0 | 0
2021-10-27 11:30 | -0.44327 | 0 | N/A | 0 | 0
2021-10-27 12:00 | -0.7574 | 0 | N/A | 0 | 0
2021-10-27 12:30 | -0.78058 | 0 | N/A | 0 | 0
2021-10-27 13:00 | -0.51148 | 0 | N/A | 0 | 0
2021-10-27 13:30 | -1.6179 | 0 | N/A | 0 | 0
2021-10-27 14:00 | -1.5826 | 0 | N/A | 0 | 0
2021-10-27 14:30 | -0.70907 | 0 | N/A | 0 | 0
2021-10-27 15:00 | -0.53159 | 0 | N/A | 0 | 0
2021-10-27 15:30 | -0.71126 | 0 | N/A | 0 | 0
2021-10-27 16:00 | -0.37814 | 0 | N/A | 0 | 0
2021-10-27 16:30 | 1.1625 | 0 | N/A | 0 | 0
2021-10-27 17:00 | 1.6788 | 0 | N/A | 0 | 0
2021-10-27 17:30 | 2.6967 | 0 | N/A | 0 | 0
2021-10-27 18:00 | 3.1923 | 0 | N/A | 0 | 0
2021-10-27 18:30 | 3.7138 | 0 | N/A | 0 | 0
2021-10-27 19:00 | 4.3201 | 0 | N/A | 0 | 0
2021-10-27 19:30 | 4.4134 | 0 | N/A | 0 | 0
2021-10-27 20:00 | 4.5202 | 0 | N/A | 0 | 0
2021-10-27 20:30 | 4.5711 | 0 | N/A | 0 | 0
2021-10-27 21:00 | 4.4289 | 0 | N/A | 0 | 0
2021-10-27 21:30 | 4.176 | 0 | N/A | 0 | 0
2021-10-27 22:00 | 3.8285 | 0 | N/A | 0 | 0
2021-10-27 22:30 | 4.0118 | 0 | N/A | 0 | 0
2021-10-27 23:00 | 4.0945 | 0 | N/A | 0 | 0
2021-10-27 23:30 | 3.71 | 0 | N/A | 0 | 0
2021-10-28 | 3.8905 | 0 | N/A | 0 | 0
2021-10-28 00:30 | 4.2294 | 0 | N/A | 0 | 0
2021-10-28 01:00 | 4.5558 | 0 | N/A | 0 | 0
2021-10-28 01:30 | 3.8385 | 0 | N/A | 0 | 0
2021-10-28 02:00 | 3.2299 | 0 | N/A | 0 | 0
2021-10-28 02:30 | 3.23 | 0 | N/A | 0 | 0
2021-10-28 03:00 | 2.9513 | 0 | N/A | 0 | 0
2021-10-28 03:30 | 2.5929 | 0 | N/A | 0 | 0
2021-10-28 04:00 | 2.3792 | 0 | N/A | 0 | 0
2021-10-28 04:30 | 2.3632 | 0 | N/A | 0 | 0
2021-10-28 05:00 | 2.3247 | 0 | N/A | 0 | 0
2021-10-28 05:30 | 2.4478 | 0 | N/A | 0 | 0
2021-10-28 06:00 | 2.8574 | 0 | N/A | 0 | 0
2021-10-28 06:30 | 3.5872 | 0 | N/A | 0 | 0
2021-10-28 07:00 | 4.2723 | 0 | N/A | 0 | 0
2021-10-28 07:30 | 4.938 | 0 | N/A | 0 | 0
2021-10-28 08:00 | 5.2127 | 0 | N/A | 0 | 0
2021-10-28 08:30 | 4.7168 | 0 | N/A | 0 | 0
2021-10-28 09:00 | 4.224 | 0 | N/A | 0 | 0
2021-10-28 09:30 | 3.317 | 0 | N/A | 0 | 0
2021-10-28 10:00 | 2.2452 | 0 | N/A | 0 | 0
2021-10-28 10:30 | 0.69636 | 0 | N/A | 0 | 0
2021-10-28 11:00 | 0.94913 | 0 | N/A | 0 | 0
2021-10-28 11:30 | -0.098489 | 0 | N/A | 0 | 0
2021-10-28 12:00 | -0.6929 | 0 | N/A | 0 | 0
2021-10-28 12:30 | -0.93291 | 0 | N/A | 0 | 0
2021-10-28 13:00 | -1.0934 | 0 | N/A | 0 | 0
2021-10-28 13:30 | -1.0967 | 0 | N/A | 0 | 0
2021-10-28 14:00 | -0.88667 | 0 | N/A | 0 | 0
2021-10-28 14:30 | -0.63032 | 0 | N/A | 0 | 0
2021-10-28 15:00 | 0.88131 | 0 | N/A | 0 | 0
2021-10-28 15:30 | 0.4618 | 0 | N/A | 0 | 0
2021-10-28 16:00 | 3.2367 | 0 | N/A | 0 | 0
2021-10-28 16:30 | 4.3313 | 0 | N/A | 0 | 0
2021-10-28 17:00 | 4.6116 | 0 | N/A | 0 | 0
2021-10-28 17:30 | 4.0724 | 0 | N/A | 0 | 0
2021-10-28 18:00 | 3.6244 | 0 | N/A | 0 | 0
2021-10-28 18:30 | 3.9954 | 0 | N/A | 0 | 0
2021-10-28 19:00 | 4.6723 | 0 | N/A | 0 | 0
2021-10-28 19:30 | 4.781 | 0 | N/A | 0 | 0
2021-10-28 20:00 | 4.8652 | 0 | N/A | 0 | 0
2021-10-28 20:30 | 4.7992 | 0 | N/A | 0 | 0
2021-10-28 21:00 | 4.6438 | 0 | N/A | 0 | 0
2021-10-28 21:30 | 4.3443 | 0 | N/A | 0 | 0
2021-10-28 22:00 | 3.9246 | 0 | N/A | 0 | 0
2021-10-28 22:30 | 4.1629 | 0 | N/A | 0 | 0
2021-10-28 23:00 | 4.2693 | 0 | N/A | 0 | 0
2021-10-28 23:30 | 3.9643 | 0 | N/A | 0 | 0
2021-10-29 | 4.004 | 0 | N/A | 0 | 0
2021-10-29 00:30 | 4.4304 | 0 | N/A | 0 | 0
2021-10-29 01:00 | 4.6579 | 0 | N/A | 0 | 0
2021-10-29 01:30 | 3.9261 | 0 | N/A | 0 | 0
2021-10-29 02:00 | 3.3667 | 0 | N/A | 0 | 0
2021-10-29 02:30 | 3.2946 | 0 | N/A | 0 | 0
2021-10-29 03:00 | 2.9348 | 0 | N/A | 0 | 0
2021-10-29 03:30 | 2.6341 | 0 | N/A | 0 | 0
2021-10-29 04:00 | 2.4459 | 0 | N/A | 0 | 0
2021-10-29 04:30 | 2.4748 | 0 | N/A | 0 | 0
2021-10-29 05:00 | 2.5579 | 0 | N/A | 0 | 0
2021-10-29 05:30 | 1.1081 | 0 | N/A | 0 | 0
2021-10-29 06:00 | 0 | 0 | N/A | 0 | 0
2021-10-29 06:30 | 2.7083 | 0 | N/A | 0 | 0
2021-10-29 07:00 | 4.3578 | 0 | N/A | 0 | 0
2021-10-29 07:30 | 5.4118 | 0 | N/A | 0 | 0
2021-10-29 08:00 | 6.5739 | 0 | N/A | 0 | 0
2021-10-29 08:30 | 5.9148 | 0 | N/A | 0 | 0
2021-10-29 09:00 | 4.5037 | 0 | N/A | 0 | 0
2021-10-29 09:30 | 4.385 | 0 | N/A | 0 | 0
2021-10-29 10:00 | 3.7902 | 0 | N/A | 0 | 0
2021-10-29 10:30 | 3.105 | 0 | N/A | 0 | 0
2021-10-29 11:00 | 2.5557 | 0 | N/A | 0 | 0
2021-10-29 11:30 | 2.3856 | 0 | N/A | 0 | 0
2021-10-29 12:00 | 1.1064 | 0 | N/A | 0 | 0
2021-10-29 12:30 | 0.80456 | 0 | N/A | 0 | 0
2021-10-29 13:00 | 1.1338 | 0 | N/A | 0 | 0
2021-10-29 13:30 | 1.1078 | 0 | N/A | 0 | 0
2021-10-29 14:00 | 1.4833 | 0 | N/A | 0 | 0
2021-10-29 14:30 | 1.6291 | 0 | N/A | 0 | 0
2021-10-29 15:00 | 1.3301 | 0 | N/A | 0 | 0
2021-10-29 15:30 | 0.60023 | 0 | N/A | 0 | 0
2021-10-29 16:00 | 0.79001 | 0 | N/A | 0 | 0
2021-10-29 16:30 | 1.7524 | 0 | N/A | 0 | 0
2021-10-29 17:00 | 2.348 | 0 | N/A | 0 | 0
2021-10-29 17:30 | 2.3978 | 0 | N/A | 0 | 0
2021-10-29 18:00 | 3.6394 | 0 | N/A | 0 | 0
2021-10-29 18:30 | 3.7471 | 0 | N/A | 0 | 0
2021-10-29 19:00 | 4.6262 | 0 | N/A | 0 | 0
2021-10-29 19:30 | 5.773 | 0 | N/A | 0 | 0
2021-10-29 20:00 | 5.8901 | 0 | N/A | 0 | 0
2021-10-29 20:30 | 6.2651 | 0 | N/A | 0 | 0
2021-10-29 21:00 | 6.3799 | 0 | N/A | 0 | 0
2021-10-29 21:30 | 6.0528 | 0 | N/A | 0 | 0
2021-10-29 22:00 | 5.721 | 0 | N/A | 0 | 0
2021-10-29 22:30 | 5.8309 | 0 | N/A | 0 | 0
2021-10-29 23:00 | 5.7862 | 0 | N/A | 0 | 0
2021-10-29 23:30 | 5.2551 | 0 | N/A | 0 | 0
2021-10-30 | 5.2269 | 0 | N/A | 0 | 0
2021-10-30 00:30 | 5.5972 | 0 | N/A | 0 | 0
2021-10-30 01:00 | 5.8728 | 0 | N/A | 0 | 0
2021-10-30 01:30 | 5.1827 | 0 | N/A | 0 | 0
2021-10-30 02:00 | 4.5231 | 0 | N/A | 0 | 0
2021-10-30 02:30 | 4.4025 | 0 | N/A | 0 | 0
2021-10-30 03:00 | 4.1239 | 0 | N/A | 0 | 0
2021-10-30 03:30 | 3.7358 | 0 | N/A | 0 | 0
2021-10-30 04:00 | 3.4554 | 0 | N/A | 0 | 0
2021-10-30 04:30 | 3.4385 | 0 | N/A | 0 | 0
2021-10-30 05:00 | 3.3732 | 0 | N/A | 0 | 0
2021-10-30 05:30 | 3.491 | 0 | N/A | 0 | 0
2021-10-30 06:00 | 3.6799 | 0 | N/A | 0 | 0
2021-10-30 06:30 | 4.0674 | 0 | N/A | 0 | 0
2021-10-30 07:00 | 4.3504 | 0 | N/A | 0 | 0
2021-10-30 07:30 | 4.6924 | 0 | N/A | 0 | 0
2021-10-30 08:00 | 4.5473 | 0 | N/A | 0 | 0
2021-10-30 08:30 | 3.7265 | 0 | N/A | 0 | 0
2021-10-30 09:00 | 3.1582 | 0 | N/A | 0 | 0
2021-10-30 09:30 | 2.3753 | 0 | N/A | 0 | 0
2021-10-30 10:00 | 2.0792 | 0 | N/A | 0 | 0
2021-10-30 10:30 | 2.0032 | 0 | N/A | 0 | 0
2021-10-30 11:00 | 1.7606 | 0 | N/A | 0 | 0
2021-10-30 11:30 | 2.4976 | 0 | N/A | 0 | 0
2021-10-30 12:00 | 1.7373 | 0 | N/A | 0 | 0
2021-10-30 12:30 | 1.4476 | 0 | N/A | 0 | 0
2021-10-30 13:00 | 1.3317 | 0 | N/A | 0 | 0
2021-10-30 13:30 | 2.765 | 0 | N/A | 0 | 0
2021-10-30 14:00 | 2.1208 | 0 | N/A | 0 | 0
2021-10-30 14:30 | 0.94662 | 0 | N/A | 0 | 0
2021-10-30 15:00 | 1.7941 | 0 | N/A | 0 | 0
2021-10-30 15:30 | 2.2573 | 0 | N/A | 0 | 0
2021-10-30 16:00 | 2.095 | 0 | N/A | 0 | 0
2021-10-30 16:30 | 1.3992 | 0 | N/A | 0 | 0
2021-10-30 17:00 | 3.3035 | 0 | N/A | 0 | 0
2021-10-30 17:30 | 3.9551 | 0 | N/A | 0 | 0
2021-10-30 18:00 | 4.1543 | 0 | N/A | 0 | 0
2021-10-30 18:30 | 4.5583 | 0 | N/A | 0 | 0
2021-10-30 19:00 | 4.8979 | 0 | N/A | 0 | 0
2021-10-30 19:30 | 5.1133 | 0 | N/A | 0 | 0
2021-10-30 20:00 | 5.5103 | 0 | N/A | 0 | 0
2021-10-30 20:30 | 5.6937 | 0 | N/A | 0 | 0
2021-10-30 21:00 | 5.8486 | 0 | N/A | 0 | 0
2021-10-30 21:30 | 5.5391 | 0 | N/A | 0 | 0
2021-10-30 22:00 | 5.4104 | 0 | N/A | 0 | 0
2021-10-30 22:30 | 5.6198 | 0 | N/A | 0 | 0
2021-10-30 23:00 | 5.7016 | 0 | N/A | 0 | 0
2021-10-30 23:30 | 5.4136 | 0 | N/A | 0 | 0
2021-10-31 | 5.3869 | 0 | N/A | 0 | 0
2021-10-31 00:30 | 5.6398 | 0 | N/A | 0 | 0
2021-10-31 01:00 | 6.0138 | 0 | N/A | 0 | 0
2021-10-31 01:30 | 5.3578 | 0 | N/A | 0 | 0
2021-10-31 02:00 | 4.7362 | 0 | N/A | 0 | 0
2021-10-31 02:30 | 4.6926 | 0 | N/A | 0 | 0
2021-10-31 03:00 | 4.4067 | 0 | N/A | 0 | 0
2021-10-31 03:30 | 3.9124 | 0 | N/A | 0 | 0
2021-10-31 04:00 | 3.5963 | 0 | N/A | 0 | 0
2021-10-31 04:30 | 3.4582 | 0 | N/A | 0 | 0
2021-10-31 05:00 | 3.3543 | 0 | N/A | 0 | 0
2021-10-31 05:30 | 3.4131 | 0 | N/A | 0 | 0
2021-10-31 06:00 | 3.5769 | 0 | N/A | 0 | 0
2021-10-31 06:30 | 3.7877 | 0 | N/A | 0 | 0
2021-10-31 07:00 | 3.9632 | 0 | N/A | 0 | 0
2021-10-31 07:30 | 4.2153 | 0 | N/A | 0 | 0
2021-10-31 08:00 | 4.1452 | 0 | N/A | 0 | 0
2021-10-31 08:30 | 3.5101 | 0 | N/A | 0 | 0
2021-10-31 09:00 | 3.0115 | 0 | N/A | 0 | 0
2021-10-31 09:30 | 2.2518 | 0 | N/A | 0 | 0
2021-10-31 10:00 | 1.4527 | 0 | N/A | 0 | 0
2021-10-31 10:30 | 0.70775 | 0 | N/A | 0 | 0
2021-10-31 11:00 | -0.56702 | 0 | N/A | 0 | 0
2021-10-31 11:30 | -0.70007 | 0 | N/A | 0 | 0
2021-10-31 12:00 | -0.96418 | 0 | N/A | 0 | 0
2021-10-31 12:30 | -1.2926 | 0 | N/A | 0 | 0
2021-10-31 13:00 | -1.4496 | 0 | N/A | 0 | 0
2021-10-31 13:30 | -1.6685 | 0 | N/A | 0 | 0
2021-10-31 14:00 | -1.7175 | 0 | N/A | 0 | 0
2021-10-31 14:30 | -1.4417 | 0 | N/A | 0 | 0
2021-10-31 15:00 | -1.1553 | 0 | N/A | 0 | 0
2021-10-31 15:30 | -0.95857 | 0 | N/A | 0 | 0
2021-10-31 16:00 | -0.95482 | 0 | N/A | 0 | 0
2021-10-31 16:30 | 0.65364 | 0 | N/A | 0 | 0
2021-10-31 17:00 | 0.76632 | 0 | N/A | 0 | 0
2021-10-31 17:30 | 1.21 | 0 | N/A | 0 | 0
2021-10-31 18:00 | 2.0639 | 0 | N/A | 0 | 0
2021-10-31 18:30 | 2.9839 | 0 | N/A | 0 | 0
2021-10-31 19:00 | 3.7021 | 0 | N/A | 0 | 0
2021-10-31 19:30 | 4.1217 | 0 | N/A | 0 | 0
2021-10-31 20:00 | 4.4373 | 0 | N/A | 0 | 0
2021-10-31 20:30 | 4.6229 | 0 | N/A | 0 | 0
2021-10-31 21:00 | 4.7691 | 0 | N/A | 0 | 0
2021-10-31 21:30 | 4.5983 | 0 | N/A | 0 | 0
2021-10-31 22:00 | 4.3831 | 0 | N/A | 0 | 0
2021-10-31 22:30 | 4.5826 | 0 | N/A | 0 | 0
2021-10-31 23:00 | 4.6925 | 0 | N/A | 0 | 0
2021-10-31 23:30 | 4.4788 | 0 | N/A | 0 | 0
2021-11-01 | 4.5559 | 0 | N/A | 0 | 0
2021-11-01 00:30 | 4.7676 | 0 | N/A | 0 | 0
2021-11-01 01:00 | 5.1191 | 0 | N/A | 0 | 0
2021-11-01 01:30 | 4.514 | 0 | N/A | 0 | 0
2021-11-01 02:00 | 3.9591 | 0 | N/A | 0 | 0
2021-11-01 02:30 | 3.9964 | 0 | N/A | 0 | 0
2021-11-01 03:00 | 3.6726 | 0 | N/A | 0 | 0
2021-11-01 03:30 | 3.2396 | 0 | N/A | 0 | 0
2021-11-01 04:00 | 2.9501 | 0 | N/A | 0 | 0
2021-11-01 04:30 | 2.9557 | 0 | N/A | 0 | 0
2021-11-01 05:00 | 2.9 | 0 | N/A | 0 | 0
2021-11-01 05:30 | 2.9811 | 0 | N/A | 0 | 0
2021-11-01 06:00 | 3.2409 | 0 | N/A | 0 | 0
2021-11-01 06:30 | 3.8316 | 0 | N/A | 0 | 0
2021-11-01 07:00 | 4.4493 | 0 | N/A | 0 | 0
2021-11-01 07:30 | 4.7912 | 0 | N/A | 0 | 0
2021-11-01 08:00 | 4.5628 | 0 | N/A | 0 | 0
2021-11-01 08:30 | 3.3669 | 0 | N/A | 0 | 0
2021-11-01 09:00 | 2.3585 | 0 | N/A | 0 | 0
2021-11-01 09:30 | 1.4268 | 0 | N/A | 0 | 0
2021-11-01 10:00 | 0.70384 | 0 | N/A | 0 | 0
2021-11-01 10:30 | 0.64402 | 0 | N/A | 0 | 0
2021-11-01 11:00 | -0.58951 | 0 | N/A | 0 | 0
2021-11-01 11:30 | -0.85115 | 0 | N/A | 0 | 0
2021-11-01 12:00 | -1.0576 | 0 | N/A | 0 | 0
2021-11-01 12:30 | -1.1675 | 0 | N/A | 0 | 0
2021-11-01 13:00 | -1.2401 | 0 | N/A | 0 | 0
2021-11-01 13:30 | -1.3167 | 0 | N/A | 0 | 0
2021-11-01 14:00 | -1.2273 | 0 | N/A | 0 | 0
2021-11-01 14:30 | -1.5854 | 0 | N/A | 0 | 0
2021-11-01 15:00 | -1.3124 | 0 | N/A | 0 | 0
2021-11-01 15:30 | -1.2281 | 0 | N/A | 0 | 0
2021-11-01 16:00 | -0.79694 | 0 | N/A | 0 | 0
2021-11-01 16:30 | -0.59168 | 0 | N/A | 0 | 0
2021-11-01 17:00 | 0.60722 | 0 | N/A | 0 | 0
2021-11-01 17:30 | 1.2476 | 0 | N/A | 0 | 0
2021-11-01 18:00 | 2.1915 | 0 | N/A | 0 | 0
2021-11-01 18:30 | 2.9507 | 0 | N/A | 0 | 0
2021-11-01 19:00 | 3.4742 | 0 | N/A | 0 | 0
2021-11-01 19:30 | 3.9565 | 0 | N/A | 0 | 0
2021-11-01 20:00 | 4.2161 | 0 | N/A | 0 | 0
2021-11-01 20:30 | 4.2797 | 0 | N/A | 0 | 0
2021-11-01 21:00 | 4.2739 | 0 | N/A | 0 | 0
2021-11-01 21:30 | 4.0929 | 0 | N/A | 0 | 0
2021-11-01 22:00 | 3.8076 | 0 | N/A | 0 | 0
2021-11-01 22:30 | 3.9771 | 0 | N/A | 0 | 0
2021-11-01 23:00 | 4.17 | 0 | N/A | 0 | 0
2021-11-01 23:30 | 3.9109 | 0 | N/A | 0 | 0
2021-11-02 | 4.0657 | 0 | N/A | 0 | 0
2021-11-02 00:30 | 4.4188 | 0 | N/A | 0 | 0
2021-11-02 01:00 | 4.6868 | 0 | N/A | 0 | 0
2021-11-02 01:30 | 4.0158 | 0 | N/A | 0 | 0
2021-11-02 02:00 | 3.4095 | 0 | N/A | 0 | 0
2021-11-02 02:30 | 3.3185 | 0 | N/A | 0 | 0
2021-11-02 03:00 | 3.0569 | 0 | N/A | 0 | 0
2021-11-02 03:30 | 2.7259 | 0 | N/A | 0 | 0
2021-11-02 04:00 | 2.5419 | 0 | N/A | 0 | 0
2021-11-02 04:30 | 2.4092 | 0 | N/A | 0 | 0
2021-11-02 05:00 | 2.3978 | 0 | N/A | 0 | 0
2021-11-02 05:30 | 2.402 | 0 | N/A | 0 | 0
2021-11-02 06:00 | 2.5089 | 0 | N/A | 0 | 0
2021-11-02 06:30 | 2.8043 | 0 | N/A | 0 | 0
2021-11-02 07:00 | 3.0251 | 0 | N/A | 0 | 0
2021-11-02 07:30 | 3.2393 | 0 | N/A | 0 | 0
2021-11-02 08:00 | 3.0569 | 0 | N/A | 0 | 0
2021-11-02 08:30 | 2.1908 | 0 | N/A | 0 | 0
2021-11-02 09:00 | 1.5558 | 0 | N/A | 0 | 0
2021-11-02 09:30 | 0.91848 | 0 | N/A | 0 | 0
2021-11-02 10:00 | 0.60059 | 0 | N/A | 0 | 0
2021-11-02 10:30 | -0.74825 | 0 | N/A | 0 | 0
2021-11-02 11:00 | -1.0574 | 0 | N/A | 0 | 0
2021-11-02 11:30 | -1.4016 | 0 | N/A | 0 | 0
2021-11-02 12:00 | -1.5595 | 0 | N/A | 0 | 0
2021-11-02 12:30 | -1.6925 | 0 | N/A | 0 | 0
2021-11-02 13:00 | -1.8336 | 0 | N/A | 0 | 0
2021-11-02 13:30 | -2.0209 | 0 | N/A | 0 | 0
2021-11-02 14:00 | -2.0874 | 0 | N/A | 0 | 0
2021-11-02 14:30 | -1.81 | 0 | N/A | 0 | 0
2021-11-02 15:00 | -1.3631 | 0 | N/A | 0 | 0
2021-11-02 15:30 | -0.78712 | 0 | N/A | 0 | 0
2021-11-02 16:00 | -0.4831 | 0 | N/A | 0 | 0
2021-11-02 16:30 | -0.58694 | 0 | N/A | 0 | 0
2021-11-02 17:00 | 1.0102 | 0 | N/A | 0 | 0
2021-11-02 17:30 | 1.8407 | 0 | N/A | 0 | 0
2021-11-02 18:00 | 2.9048 | 0 | N/A | 0 | 0
2021-11-02 18:30 | 3.8896 | 0 | N/A | 0 | 0
2021-11-02 19:00 | 4.1177 | 0 | N/A | 0 | 0
2021-11-02 19:30 | 4.343 | 0 | N/A | 0 | 0
2021-11-02 20:00 | 4.475 | 0 | N/A | 0 | 0
2021-11-02 20:30 | 4.4757 | 0 | N/A | 0 | 0
2021-11-02 21:00 | 4.3371 | 0 | N/A | 0 | 0
2021-11-02 21:30 | 4.0643 | 0 | N/A | 0 | 0
2021-11-02 22:00 | 3.765 | 0 | N/A | 0 | 0
2021-11-02 22:30 | 4.025 | 0 | N/A | 0 | 0
2021-11-02 23:00 | 4.0998 | 0 | N/A | 0 | 0
2021-11-02 23:30 | 3.8943 | 0 | N/A | 0 | 0
2021-11-03 | 3.9513 | 0 | N/A | 0 | 0
2021-11-03 00:30 | 4.4003 | 0 | N/A | 0 | 0
2021-11-03 01:00 | 4.7063 | 0 | N/A | 0 | 0
2021-11-03 01:30 | 4.0583 | 0 | N/A | 0 | 0
2021-11-03 02:00 | 3.4513 | 0 | N/A | 0 | 0
2021-11-03 02:30 | 3.2878 | 0 | N/A | 0 | 0
2021-11-03 03:00 | 3.0517 | 0 | N/A | 0 | 0
2021-11-03 03:30 | 2.5808 | 0 | N/A | 0 | 0
2021-11-03 04:00 | 2.4519 | 0 | N/A | 0 | 0
2021-11-03 04:30 | 2.3167 | 0 | N/A | 0 | 0
2021-11-03 05:00 | 2.3429 | 0 | N/A | 0 | 0
2021-11-03 05:30 | 2.4352 | 0 | N/A | 0 | 0
2021-11-03 06:00 | 2.6007 | 0 | N/A | 0 | 0
2021-11-03 06:30 | 3.0605 | 0 | N/A | 0 | 0
2021-11-03 07:00 | 3.4851 | 0 | N/A | 0 | 0
2021-11-03 07:30 | 3.9217 | 0 | N/A | 0 | 0
2021-11-03 08:00 | 3.9369 | 0 | N/A | 0 | 0
2021-11-03 08:30 | 3.1718 | 0 | N/A | 0 | 0
2021-11-03 09:00 | 2.6951 | 0 | N/A | 0 | 0
2021-11-03 09:30 | 2.8579 | 0 | N/A | 0 | 0
2021-11-03 10:00 | 2.9219 | 0 | N/A | 0 | 0
2021-11-03 10:30 | 3.3174 | 0 | N/A | 0 | 0
2021-11-03 11:00 | 3.5775 | 0 | N/A | 0 | 0
2021-11-03 11:30 | 3.6525 | 0 | N/A | 0 | 0
2021-11-03 12:00 | 3.9318 | 0 | N/A | 0 | 0
2021-11-03 12:30 | 4.3211 | 0 | N/A | 0 | 0
2021-11-03 13:00 | 3.9795 | 0 | N/A | 0 | 0
2021-11-03 13:30 | 3.4576 | 0 | N/A | 0 | 0
2021-11-03 14:00 | 3.8939 | 0 | N/A | 0 | 0
2021-11-03 14:30 | 3.9252 | 0 | N/A | 0 | 0
2021-11-03 15:00 | 4.2944 | 0 | N/A | 0 | 0
2021-11-03 15:30 | 4.5811 | 0 | N/A | 0 | 0
2021-11-03 16:00 | 4.5614 | 0 | N/A | 0 | 0
2021-11-03 16:30 | 4.7546 | 0 | N/A | 0 | 0
2021-11-03 17:00 | 4.8772 | 0 | N/A | 0 | 0
2021-11-03 17:30 | 5.3328 | 0 | N/A | 0 | 0
2021-11-03 18:00 | 5.5618 | 0 | N/A | 0 | 0
2021-11-03 18:30 | 5.4121 | 0 | N/A | 0 | 0
2021-11-03 19:00 | 5.6905 | 0 | N/A | 0 | 0
2021-11-03 19:30 | 5.7338 | 0 | N/A | 0 | 0
2021-11-03 20:00 | 5.5535 | 0 | N/A | 0 | 0
2021-11-03 20:30 | 5.4836 | 0 | N/A | 0 | 0
2021-11-03 21:00 | 5.3251 | 0 | N/A | 0 | 0
2021-11-03 21:30 | 4.9589 | 0 | N/A | 0 | 0
2021-11-03 22:00 | 4.5774 | 0 | N/A | 0 | 0
2021-11-03 22:30 | 4.8018 | 0 | N/A | 0 | 0
2021-11-03 23:00 | 4.8839 | 0 | N/A | 0 | 0
2021-11-03 23:30 | 4.5434 | 0 | N/A | 0 | 0
2021-11-04 | 4.6382 | 0 | N/A | 0 | 0
2021-11-04 00:30 | 5.0222 | 0 | N/A | 0 | 0
2021-11-04 01:00 | 5.4442 | 0 | N/A | 0 | 0
2021-11-04 01:30 | 4.678 | 0 | N/A | 0 | 0
2021-11-04 02:00 | 3.8809 | 0 | N/A | 0 | 0
2021-11-04 02:30 | 3.7813 | 0 | N/A | 0 | 0
2021-11-04 03:00 | 3.4791 | 0 | N/A | 0 | 0
2021-11-04 03:30 | 3.1879 | 0 | N/A | 0 | 0
2021-11-04 04:00 | 2.9199 | 0 | N/A | 0 | 0
2021-11-04 04:30 | 2.8285 | 0 | N/A | 0 | 0
2021-11-04 05:00 | 2.8556 | 0 | N/A | 0 | 0
2021-11-04 05:30 | 3.0809 | 0 | N/A | 0 | 0
2021-11-04 06:00 | 3.3511 | 0 | N/A | 0 | 0
2021-11-04 06:30 | 4.0244 | 0 | N/A | 0 | 0
2021-11-04 07:00 | 4.6889 | 0 | N/A | 0 | 0
2021-11-04 07:30 | 5.7193 | 0 | N/A | 0 | 0
2021-11-04 08:00 | 5.9886 | 0 | N/A | 0 | 0
2021-11-04 08:30 | 4.753 | 0 | N/A | 0 | 0
2021-11-04 09:00 | 3.9341 | 0 | N/A | 0 | 0
2021-11-04 09:30 | 2.8756 | 0 | N/A | 0 | 0
2021-11-04 10:00 | 2.1718 | 0 | N/A | 0 | 0
2021-11-04 10:30 | 1.3777 | 0 | N/A | 0 | 0
2021-11-04 11:00 | 0.51025 | 0 | N/A | 0 | 0
2021-11-04 11:30 | -0.35876 | 0 | N/A | 0 | 0
2021-11-04 12:00 | -0.70033 | 0 | N/A | 0 | 0
2021-11-04 12:30 | -0.65055 | 0 | N/A | 0 | 0
2021-11-04 13:00 | -1.0735 | 0 | N/A | 0 | 0
2021-11-04 13:30 | -1.1796 | 0 | N/A | 0 | 0
2021-11-04 14:00 | -1.4067 | 0 | N/A | 0 | 0
2021-11-04 14:30 | -1.3723 | 0 | N/A | 0 | 0
2021-11-04 15:00 | -1.1727 | 0 | N/A | 0 | 0
2021-11-04 15:30 | -1.1545 | 0 | N/A | 0 | 0
2021-11-04 16:00 | -1.2523 | 0 | N/A | 0 | 0
2021-11-04 16:30 | -0.90232 | 0 | N/A | 0 | 0
2021-11-04 17:00 | -0.64399 | 0 | N/A | 0 | 0
2021-11-04 17:30 | 1.1355 | 0 | N/A | 0 | 0
2021-11-04 18:00 | 2.2152 | 0 | N/A | 0 | 0
2021-11-04 18:30 | 3.2978 | 0 | N/A | 0 | 0
2021-11-04 19:00 | 4.0786 | 0 | N/A | 0 | 0
2021-11-04 19:30 | 4.3754 | 0 | N/A | 0 | 0
2021-11-04 20:00 | 4.8104 | 0 | N/A | 0 | 0
2021-11-04 20:30 | 5.0481 | 0 | N/A | 0 | 0
2021-11-04 21:00 | 5.114 | 0 | N/A | 0 | 0
2021-11-04 21:30 | 4.9015 | 0 | N/A | 0 | 0
2021-11-04 22:00 | 4.6002 | 0 | N/A | 0 | 0
2021-11-04 22:30 | 4.8227 | 0 | N/A | 0 | 0
2021-11-04 23:00 | 4.8685 | 0 | N/A | 0 | 0
2021-11-04 23:30 | 4.5062 | 0 | N/A | 0 | 0
2021-11-05 | 4.5911 | 0 | N/A | 0 | 0
2021-11-05 00:30 | 4.959 | 0 | N/A | 0 | 0
2021-11-05 01:00 | 5.0962 | 0 | N/A | 0 | 0
2021-11-05 01:30 | 4.3394 | 0 | N/A | 0 | 0
2021-11-05 02:00 | 3.6822 | 0 | N/A | 0 | 0
2021-11-05 02:30 | 3.6117 | 0 | N/A | 0 | 0
2021-11-05 03:00 | 3.3494 | 0 | N/A | 0 | 0
2021-11-05 03:30 | 3.0288 | 0 | N/A | 0 | 0
2021-11-05 04:00 | 2.7013 | 0 | N/A | 0 | 0
2021-11-05 04:30 | 2.6397 | 0 | N/A | 0 | 0
2021-11-05 05:00 | 2.6179 | 0 | N/A | 0 | 0
2021-11-05 05:30 | 2.7706 | 0 | N/A | 0 | 0
2021-11-05 06:00 | 3.1033 | 0 | N/A | 0 | 0
2021-11-05 06:30 | 3.9804 | 0 | N/A | 0 | 0
2021-11-05 07:00 | 4.5754 | 0 | N/A | 0 | 0
2021-11-05 07:30 | 5.1251 | 0 | N/A | 0 | 0
2021-11-05 08:00 | 5.1784 | 0 | N/A | 0 | 0
2021-11-05 08:30 | 4.3084 | 0 | N/A | 0 | 0
2021-11-05 09:00 | 3.8091 | 0 | N/A | 0 | 0
2021-11-05 09:30 | 3.1105 | 0 | N/A | 0 | 0
2021-11-05 10:00 | 1.7915 | 0 | N/A | 0 | 0
2021-11-05 10:30 | 0.43278 | 0 | N/A | 0 | 0
2021-11-05 11:00 | -0.29067 | 0 | N/A | 0 | 0
2021-11-05 11:30 | -0.65056 | 0 | N/A | 0 | 0
2021-11-05 12:00 | -0.94658 | 0 | N/A | 0 | 0
2021-11-05 12:30 | -1.0528 | 0 | N/A | 0 | 0
2021-11-05 13:00 | -1.2787 | 0 | N/A | 0 | 0
2021-11-05 13:30 | -0.36644 | 0 | N/A | 0 | 0
2021-11-05 14:00 | -0.21932 | 0 | N/A | 0 | 0
2021-11-05 14:30 | 0.2145 | 0 | N/A | 0 | 0
2021-11-05 15:00 | 0.28168 | 0 | N/A | 0 | 0
2021-11-05 15:30 | 0.28771 | 0 | N/A | 0 | 0
2021-11-05 16:00 | 0.7812 | 0 | N/A | 0 | 0
2021-11-05 16:30 | 0.75608 | 0 | N/A | 0 | 0
2021-11-05 17:00 | 2.0753 | 0 | N/A | 0 | 0
2021-11-05 17:30 | 2.2144 | 0 | N/A | 0 | 0
2021-11-05 18:00 | 2.3685 | 0 | N/A | 0 | 0
2021-11-05 18:30 | 2.9084 | 0 | N/A | 0 | 0
2021-11-05 19:00 | 3.4979 | 0 | N/A | 0 | 0
2021-11-05 19:30 | 3.9434 | 0 | N/A | 0 | 0
2021-11-05 20:00 | 4.1851 | 0 | N/A | 0 | 0
2021-11-05 20:30 | 4.2114 | 0 | N/A | 0 | 0
2021-11-05 21:00 | 4.2377 | 0 | N/A | 0 | 0
2021-11-05 21:30 | 4.0255 | 0 | N/A | 0 | 0
2021-11-05 22:00 | 3.75 | 0 | N/A | 0 | 0
2021-11-05 22:30 | 4.0436 | 0 | N/A | 0 | 0
2021-11-05 23:00 | 4.198 | 0 | N/A | 0 | 0
2021-11-05 23:30 | 3.9409 | 0 | N/A | 0 | 0
2021-11-06 | 4.0114 | 0 | N/A | 0 | 0
2021-11-06 00:30 | 4.3989 | 0 | N/A | 0 | 0
2021-11-06 01:00 | 4.5872 | 0 | N/A | 0 | 0
2021-11-06 01:30 | 3.8364 | 0 | N/A | 0 | 0
2021-11-06 02:00 | 3.2101 | 0 | N/A | 0 | 0
2021-11-06 02:30 | 3.1166 | 0 | N/A | 0 | 0
2021-11-06 03:00 | 2.8598 | 0 | N/A | 0 | 0
2021-11-06 03:30 | 2.5935 | 0 | N/A | 0 | 0
2021-11-06 04:00 | 2.398 | 0 | N/A | 0 | 0
2021-11-06 04:30 | 2.2748 | 0 | N/A | 0 | 0
2021-11-06 05:00 | 2.3018 | 0 | N/A | 0 | 0
2021-11-06 05:30 | 2.3033 | 0 | N/A | 0 | 0
2021-11-06 06:00 | 2.3929 | 0 | N/A | 0 | 0
2021-11-06 06:30 | 2.5605 | 0 | N/A | 0 | 0
2021-11-06 07:00 | 2.66 | 0 | N/A | 0 | 0
2021-11-06 07:30 | 2.8773 | 0 | N/A | 0 | 0
2021-11-06 08:00 | 2.8394 | 0 | N/A | 0 | 0
2021-11-06 08:30 | 2.4167 | 0 | N/A | 0 | 0
2021-11-06 09:00 | 2.2463 | 0 | N/A | 0 | 0
2021-11-06 09:30 | 1.452 | 0 | N/A | 0 | 0
2021-11-06 10:00 | 0.97867 | 0 | N/A | 0 | 0
2021-11-06 10:30 | 1.0114 | 0 | N/A | 0 | 0
2021-11-06 11:00 | 1.0404 | 0 | N/A | 0 | 0
2021-11-06 11:30 | 0.7642 | 0 | N/A | 0 | 0
2021-11-06 12:00 | 0.51175 | 0 | N/A | 0 | 0
2021-11-06 12:30 | 2.0189 | 0 | N/A | 0 | 0
2021-11-06 13:00 | 2.4206 | 0 | N/A | 0 | 0
2021-11-06 13:30 | 1.9862 | 0 | N/A | 0 | 0
2021-11-06 14:00 | 2.4469 | 0 | N/A | 0 | 0
2021-11-06 14:30 | 3.0188 | 0 | N/A | 0 | 0
2021-11-06 15:00 | 2.4245 | 0 | N/A | 0 | 0
2021-11-06 15:30 | 1.7908 | 0 | N/A | 0 | 0
2021-11-06 16:00 | 1.4312 | 0 | N/A | 0 | 0
2021-11-06 16:30 | 3.0029 | 0 | N/A | 0 | 0
2021-11-06 17:00 | 1.8688 | 0 | N/A | 0 | 0
2021-11-06 17:30 | 1.7845 | 0 | N/A | 0 | 0
2021-11-06 18:00 | 2.1653 | 0 | N/A | 0 | 0
2021-11-06 18:30 | 3.1804 | 0 | N/A | 0 | 0
2021-11-06 19:00 | 4.0591 | 0 | N/A | 0 | 0
2021-11-06 19:30 | 4.0886 | 0 | N/A | 0 | 0
2021-11-06 20:00 | 4.0222 | 0 | N/A | 0 | 0
2021-11-06 20:30 | 4.0041 | 0 | N/A | 0 | 0
2021-11-06 21:00 | 4.1028 | 0 | N/A | 0 | 0
2021-11-06 21:30 | 3.9627 | 0 | N/A | 0 | 0
2021-11-06 22:00 | 3.7909 | 0 | N/A | 0 | 0
2021-11-06 22:30 | 4.1137 | 0 | N/A | 0 | 0
2021-11-06 23:00 | 4.3156 | 0 | N/A | 0 | 0
2021-11-06 23:30 | 4.1267 | 0 | N/A | 0 | 0
2021-11-07 | 4.2302 | 0 | N/A | 0 | 0
2021-11-07 00:30 | 4.5192 | 0 | N/A | 0 | 0
2021-11-07 01:00 | 4.8525 | 0 | N/A | 0 | 0
2021-11-07 01:30 | 4.1188 | 0 | N/A | 0 | 0
2021-11-07 02:00 | 3.4387 | 0 | N/A | 0 | 0
2021-11-07 02:30 | 3.2817 | 0 | N/A | 0 | 0
2021-11-07 03:00 | 3.0149 | 0 | N/A | 0 | 0
2021-11-07 03:30 | 2.7021 | 0 | N/A | 0 | 0
2021-11-07 04:00 | 2.4406 | 0 | N/A | 0 | 0
2021-11-07 04:30 | 2.3257 | 0 | N/A | 0 | 0
2021-11-07 05:00 | 2.2707 | 0 | N/A | 0 | 0
2021-11-07 05:30 | 2.2634 | 0 | N/A | 0 | 0
2021-11-07 06:00 | 2.3389 | 0 | N/A | 0 | 0
2021-11-07 06:30 | 2.5819 | 0 | N/A | 0 | 0
2021-11-07 07:00 | 2.7058 | 0 | N/A | 0 | 0
2021-11-07 07:30 | 2.8312 | 0 | N/A | 0 | 0
2021-11-07 08:00 | 2.9863 | 0 | N/A | 0 | 0
2021-11-07 08:30 | 3.173 | 0 | N/A | 0 | 0
2021-11-07 09:00 | 3.2945 | 0 | N/A | 0 | 0
2021-11-07 09:30 | 3.5251 | 0 | N/A | 0 | 0
2021-11-07 10:00 | 3.5354 | 0 | N/A | 0 | 0
2021-11-07 10:30 | 3.3769 | 0 | N/A | 0 | 0
2021-11-07 11:00 | 3.2548 | 0 | N/A | 0 | 0
2021-11-07 11:30 | 3.0204 | 0 | N/A | 0 | 0
2021-11-07 12:00 | 2.9179 | 0 | N/A | 0 | 0
2021-11-07 12:30 | 2.9833 | 0 | N/A | 0 | 0
2021-11-07 13:00 | 3.0343 | 0 | N/A | 0 | 0
2021-11-07 13:30 | 2.9647 | 0 | N/A | 0 | 0
2021-11-07 14:00 | 2.571 | 0 | N/A | 0 | 0
2021-11-07 14:30 | 2.4529 | 0 | N/A | 0 | 0
2021-11-07 15:00 | 2.5963 | 0 | N/A | 0 | 0
2021-11-07 15:30 | 3.033 | 0 | N/A | 0 | 0
2021-11-07 16:00 | 3.1992 | 0 | N/A | 0 | 0
2021-11-07 16:30 | 3.6068 | 0 | N/A | 0 | 0
2021-11-07 17:00 | 4.0591 | 0 | N/A | 0 | 0
2021-11-07 17:30 | 4.7029 | 0 | N/A | 0 | 0
2021-11-07 18:00 | 5.0055 | 0 | N/A | 0 | 0
2021-11-07 18:30 | 5.1052 | 0 | N/A | 0 | 0
2021-11-07 19:00 | 5.5998 | 0 | N/A | 0 | 0
2021-11-07 19:30 | 5.6895 | 0 | N/A | 0 | 0
2021-11-07 20:00 | 5.6668 | 0 | N/A | 0 | 0
2021-11-07 20:30 | 5.5909 | 0 | N/A | 0 | 0
2021-11-07 21:00 | 5.5932 | 0 | N/A | 0 | 0
2021-11-07 21:30 | 5.3454 | 0 | N/A | 0 | 0
2021-11-07 22:00 | 4.9895 | 0 | N/A | 0 | 0
2021-11-07 22:30 | 5.1469 | 0 | N/A | 0 | 0
2021-11-07 23:00 | 5.1728 | 0 | N/A | 0 | 0
2021-11-07 23:30 | 4.8639 | 0 | N/A | 0 | 0
2021-11-08 | 4.8804 | 0 | N/A | 0 | 0
2021-11-08 00:30 | 5.1481 | 0 | N/A | 0 | 0
2021-11-08 01:00 | 5.5222 | 0 | N/A | 0 | 0
2021-11-08 01:30 | 4.9224 | 0 | N/A | 0 | 0
2021-11-08 02:00 | 4.2667 | 0 | N/A | 0 | 0
2021-11-08 02:30 | 4.2069 | 0 | N/A | 0 | 0
2021-11-08 03:00 | 3.7676 | 0 | N/A | 0 | 0
2021-11-08 03:30 | 3.2762 | 0 | N/A | 0 | 0
2021-11-08 04:00 | 3.0934 | 0 | N/A | 0 | 0
2021-11-08 04:30 | 3.0162 | 0 | N/A | 0 | 0
2021-11-08 05:00 | 3.0283 | 0 | N/A | 0 | 0
2021-11-08 05:30 | 3.254 | 0 | N/A | 0 | 0
2021-11-08 06:00 | 3.6845 | 0 | N/A | 0 | 0
2021-11-08 06:30 | 4.416 | 0 | N/A | 0 | 0
2021-11-08 07:00 | 5.2015 | 0 | N/A | 0 | 0
2021-11-08 07:30 | 5.779 | 0 | N/A | 0 | 0
2021-11-08 08:00 | 5.6906 | 0 | N/A | 0 | 0
2021-11-08 08:30 | 4.71 | 0 | N/A | 0 | 0
2021-11-08 09:00 | 4.1324 | 0 | N/A | 0 | 0
2021-11-08 09:30 | 3.9362 | 0 | N/A | 0 | 0
2021-11-08 10:00 | 3.0908 | 0 | N/A | 0 | 0
2021-11-08 10:30 | 2.0169 | 0 | N/A | 0 | 0
2021-11-08 11:00 | 2.0236 | 0 | N/A | 0 | 0
2021-11-08 11:30 | 1.8923 | 0 | N/A | 0 | 0
2021-11-08 12:00 | 1.7275 | 0 | N/A | 0 | 0
2021-11-08 12:30 | 1.4588 | 0 | N/A | 0 | 0
2021-11-08 13:00 | 1.2138 | 0 | N/A | 0 | 0
2021-11-08 13:30 | 1.3036 | 0 | N/A | 0 | 0
2021-11-08 14:00 | 1.1683 | 0 | N/A | 0 | 0
2021-11-08 14:30 | 1.3151 | 0 | N/A | 0 | 0
2021-11-08 15:00 | 1.7644 | 0 | N/A | 0 | 0
2021-11-08 15:30 | 1.8921 | 0 | N/A | 0 | 0
2021-11-08 16:00 | 1.5865 | 0 | N/A | 0 | 0
2021-11-08 16:30 | 1.5744 | 0 | N/A | 0 | 0
2021-11-08 17:00 | 2.1307 | 0 | N/A | 0 | 0
2021-11-08 17:30 | 3.1251 | 0 | N/A | 0 | 0
2021-11-08 18:00 | 3.8975 | 0 | N/A | 0 | 0
2021-11-08 18:30 | 4.1902 | 0 | N/A | 0 | 0
2021-11-08 19:00 | 4.3972 | 0 | N/A | 0 | 0
2021-11-08 19:30 | 5.1471 | 0 | N/A | 0 | 0
2021-11-08 20:00 | 5.3469 | 0 | N/A | 0 | 0
2021-11-08 20:30 | 5.5906 | 0 | N/A | 0 | 0
2021-11-08 21:00 | 5.7031 | 0 | N/A | 0 | 0
2021-11-08 21:30 | 5.5409 | 0 | N/A | 0 | 0
2021-11-08 22:00 | 5.1492 | 0 | N/A | 0 | 0
2021-11-08 22:30 | 5.2131 | 0 | N/A | 0 | 0
2021-11-08 23:00 | 5.2219 | 0 | N/A | 0 | 0
2021-11-08 23:30 | 4.8288 | 0 | N/A | 0 | 0
2021-11-09 | 4.8869 | 0 | N/A | 0 | 0
2021-11-09 00:30 | 5.2188 | 0 | N/A | 0 | 0
2021-11-09 01:00 | 5.5068 | 0 | N/A | 0 | 0
2021-11-09 01:30 | 4.8303 | 0 | N/A | 0 | 0
2021-11-09 02:00 | 4.2867 | 0 | N/A | 0 | 0
2021-11-09 02:30 | 4.1352 | 0 | N/A | 0 | 0
2021-11-09 03:00 | 3.7761 | 0 | N/A | 0 | 0
2021-11-09 03:30 | 3.3763 | 0 | N/A | 0 | 0
2021-11-09 04:00 | 3.1614 | 0 | N/A | 0 | 0
2021-11-09 04:30 | 3.1649 | 0 | N/A | 0 | 0
2021-11-09 05:00 | 3.219 | 0 | N/A | 0 | 0
2021-11-09 05:30 | 3.5038 | 0 | N/A | 0 | 0
2021-11-09 06:00 | 3.8819 | 0 | N/A | 0 | 0
2021-11-09 06:30 | 4.6839 | 0 | N/A | 0 | 0
2021-11-09 07:00 | 5.4763 | 0 | N/A | 0 | 0
2021-11-09 07:30 | 6.5438 | 0 | N/A | 0 | 0
2021-11-09 08:00 | 6.1386 | 0 | N/A | 0 | 0
2021-11-09 08:30 | 4.5031 | 0 | N/A | 0 | 0
2021-11-09 09:00 | 3.2775 | 0 | N/A | 0 | 0
2021-11-09 09:30 | 2.2027 | 0 | N/A | 0 | 0
2021-11-09 10:00 | 1.4574 | 0 | N/A | 0 | 0
2021-11-09 10:30 | 0.86846 | 0 | N/A | 0 | 0
2021-11-09 11:00 | 0.2754 | 0 | N/A | 0 | 0
2021-11-09 11:30 | 0.17263 | 0 | N/A | 0 | 0
2021-11-09 12:00 | -0.16865 | 0 | N/A | 0 | 0
2021-11-09 12:30 | -0.326 | 0 | N/A | 0 | 0
2021-11-09 13:00 | 0.68431 | 0 | N/A | 0 | 0
2021-11-09 13:30 | 0.8183 | 0 | N/A | 0 | 0
2021-11-09 14:00 | 1.0673 | 0 | N/A | 0 | 0
2021-11-09 14:30 | 0.34913 | 0 | N/A | 0 | 0
2021-11-09 15:00 | 0.71262 | 0 | N/A | 0 | 0
2021-11-09 15:30 | 1.0463 | 0 | N/A | 0 | 0
2021-11-09 16:00 | 1.2498 | 0 | N/A | 0 | 0
2021-11-09 16:30 | 1.3973 | 0 | N/A | 0 | 0
2021-11-09 17:00 | 2.0838 | 0 | N/A | 0 | 0
2021-11-09 17:30 | 2.7949 | 0 | N/A | 0 | 0
2021-11-09 18:00 | 3.297 | 0 | N/A | 0 | 0
2021-11-09 18:30 | 4.1811 | 0 | N/A | 0 | 0
2021-11-09 19:00 | 4.571 | 0 | N/A | 0 | 0
2021-11-09 19:30 | 4.8328 | 0 | N/A | 0 | 0
2021-11-09 20:00 | 5.0257 | 0 | N/A | 0 | 0
2021-11-09 20:30 | 5.0396 | 0 | N/A | 0 | 0
2021-11-09 21:00 | 5.1161 | 0 | N/A | 0 | 0
2021-11-09 21:30 | 4.8615 | 0 | N/A | 0 | 0
2021-11-09 22:00 | 4.5113 | 0 | N/A | 0 | 0
2021-11-09 22:30 | 4.6872 | 0 | N/A | 0 | 0
2021-11-09 23:00 | 4.7199 | 0 | N/A | 0 | 0
2021-11-09 23:30 | 4.2764 | 0 | N/A | 0 | 0
2021-11-10 | 4.371 | 0 | N/A | 0 | 0
2021-11-10 00:30 | 4.7759 | 0 | N/A | 0 | 0
2021-11-10 01:00 | 5.1448 | 0 | N/A | 0 | 0
2021-11-10 01:30 | 4.4555 | 0 | N/A | 0 | 0
2021-11-10 02:00 | 3.819 | 0 | N/A | 0 | 0
2021-11-10 02:30 | 3.7579 | 0 | N/A | 0 | 0
2021-11-10 03:00 | 3.4523 | 0 | N/A | 0 | 0
2021-11-10 03:30 | 3.0322 | 0 | N/A | 0 | 0
2021-11-10 04:00 | 2.8709 | 0 | N/A | 0 | 0
2021-11-10 04:30 | 2.7736 | 0 | N/A | 0 | 0
2021-11-10 05:00 | 2.8486 | 0 | N/A | 0 | 0
2021-11-10 05:30 | 3.0681 | 0 | N/A | 0 | 0
2021-11-10 06:00 | 3.3083 | 0 | N/A | 0 | 0
2021-11-10 06:30 | 4.099 | 0 | N/A | 0 | 0
2021-11-10 07:00 | 5.1129 | 0 | N/A | 0 | 0
2021-11-10 07:30 | 6.3712 | 0 | N/A | 0 | 0
2021-11-10 08:00 | 6.8047 | 0 | N/A | 0 | 0
2021-11-10 08:30 | 6.1283 | 0 | N/A | 0 | 0
2021-11-10 09:00 | 5.644 | 0 | N/A | 0 | 0
2021-11-10 09:30 | 5.318 | 0 | N/A | 0 | 0
2021-11-10 10:00 | 4.8983 | 0 | N/A | 0 | 0
2021-11-10 10:30 | 4.2932 | 0 | N/A | 0 | 0
2021-11-10 11:00 | 4.1325 | 0 | N/A | 0 | 0
2021-11-10 11:30 | 4.0822 | 0 | N/A | 0 | 0
2021-11-10 12:00 | 3.1453 | 0 | N/A | 0 | 0
2021-11-10 12:30 | 3.1941 | 0 | N/A | 0 | 0
2021-11-10 13:00 | 2.2049 | 0 | N/A | 0 | 0
2021-11-10 13:30 | 1.1038 | 0 | N/A | 0 | 0
2021-11-10 14:00 | 0.75955 | 0 | N/A | 0 | 0
2021-11-10 14:30 | 0.75749 | 0 | N/A | 0 | 0
2021-11-10 15:00 | 0.93498 | 0 | N/A | 0 | 0
2021-11-10 15:30 | 0.47527 | 0 | N/A | 0 | 0
2021-11-10 16:00 | 1.2181 | 0 | N/A | 0 | 0
2021-11-10 16:30 | 1.3626 | 0 | N/A | 0 | 0
2021-11-10 17:00 | 1.8217 | 0 | N/A | 0 | 0
2021-11-10 17:30 | 2.9719 | 0 | N/A | 0 | 0
2021-11-10 18:00 | 3.721 | 0 | N/A | 0 | 0
2021-11-10 18:30 | 4.2298 | 0 | N/A | 0 | 0
2021-11-10 19:00 | 4.9282 | 0 | N/A | 0 | 0
2021-11-10 19:30 | 5.165 | 0 | N/A | 0 | 0
2021-11-10 20:00 | 5.6497 | 0 | N/A | 0 | 0
2021-11-10 20:30 | 6.0306 | 0 | N/A | 0 | 0
2021-11-10 21:00 | 6.2061 | 0 | N/A | 0 | 0
2021-11-10 21:30 | 5.9667 | 0 | N/A | 0 | 0
2021-11-10 22:00 | 5.5448 | 0 | N/A | 0 | 0
2021-11-10 22:30 | 5.5612 | 0 | N/A | 0 | 0
2021-11-10 23:00 | 5.5631 | 0 | N/A | 0 | 0
2021-11-10 23:30 | 5.069 | 0 | N/A | 0 | 0
2021-11-11 | 4.9888 | 0 | N/A | 0 | 0
2021-11-11 00:30 | 5.377 | 0 | N/A | 0 | 0
2021-11-11 01:00 | 5.7283 | 0 | N/A | 0 | 0
2021-11-11 01:30 | 4.9852 | 0 | N/A | 0 | 0
2021-11-11 02:00 | 4.3745 | 0 | N/A | 0 | 0
2021-11-11 02:30 | 4.3203 | 0 | N/A | 0 | 0
2021-11-11 03:00 | 3.9307 | 0 | N/A | 0 | 0
2021-11-11 03:30 | 3.5719 | 0 | N/A | 0 | 0
2021-11-11 04:00 | 3.3576 | 0 | N/A | 0 | 0
2021-11-11 04:30 | 3.3046 | 0 | N/A | 0 | 0
2021-11-11 05:00 | 3.3891 | 0 | N/A | 0 | 0
2021-11-11 05:30 | 3.5966 | 0 | N/A | 0 | 0
2021-11-11 06:00 | 4.0591 | 0 | N/A | 0 | 0
2021-11-11 06:30 | 4.9079 | 0 | N/A | 0 | 0
2021-11-11 07:00 | 5.7646 | 0 | N/A | 0 | 0
2021-11-11 07:30 | 6.2814 | 0 | N/A | 0 | 0
2021-11-11 08:00 | 5.9502 | 0 | N/A | 0 | 0
2021-11-11 08:30 | 4.495 | 0 | N/A | 0 | 0
2021-11-11 09:00 | 4.3498 | 0 | N/A | 0 | 0
2021-11-11 09:30 | 3.64 | 0 | N/A | 0 | 0
2021-11-11 10:00 | 3.2335 | 0 | N/A | 0 | 0
2021-11-11 10:30 | 3.5103 | 0 | N/A | 0 | 0
2021-11-11 11:00 | 3.3239 | 0 | N/A | 0 | 0
2021-11-11 11:30 | 2.3888 | 0 | N/A | 0 | 0
2021-11-11 12:00 | 1.6276 | 0 | N/A | 0 | 0
2021-11-11 12:30 | 1.7739 | 0 | N/A | 0 | 0
2021-11-11 13:00 | 1.4815 | 0 | N/A | 0 | 0
2021-11-11 13:30 | 1.2048 | 0 | N/A | 0 | 0
2021-11-11 14:00 | 0.81851 | 0 | N/A | 0 | 0
2021-11-11 14:30 | 0.92784 | 0 | N/A | 0 | 0
2021-11-11 15:00 | 0.92551 | 0 | N/A | 0 | 0
2021-11-11 15:30 | 1.2362 | 0 | N/A | 0 | 0
2021-11-11 16:00 | 1.637 | 0 | N/A | 0 | 0
2021-11-11 16:30 | 1.9759 | 0 | N/A | 0 | 0
2021-11-11 17:00 | 2.0286 | 0 | N/A | 0 | 0
2021-11-11 17:30 | 3.0099 | 0 | N/A | 0 | 0
2021-11-11 18:00 | 4.118 | 0 | N/A | 0 | 0
2021-11-11 18:30 | 5.1547 | 0 | N/A | 0 | 0
2021-11-11 19:00 | 5.4669 | 0 | N/A | 0 | 0
2021-11-11 19:30 | 6.0257 | 0 | N/A | 0 | 0
2021-11-11 20:00 | 6.2663 | 0 | N/A | 0 | 0
2021-11-11 20:30 | 6.477 | 0 | N/A | 0 | 0
2021-11-11 21:00 | 6.3945 | 0 | N/A | 0 | 0
2021-11-11 21:30 | 6.1208 | 0 | N/A | 0 | 0
2021-11-11 22:00 | 5.6094 | 0 | N/A | 0 | 0
2021-11-11 22:30 | 5.5305 | 0 | N/A | 0 | 0
2021-11-11 23:00 | 5.3726 | 0 | N/A | 0 | 0
2021-11-11 23:30 | 4.9024 | 0 | N/A | 0 | 0
2021-11-12 | 4.8936 | 0 | N/A | 0 | 0
2021-11-13 00:30 | 5.8705 | 0 | N/A | 0 | 0
2021-11-13 01:00 | 6.2181 | 0 | N/A | 0 | 0
2021-11-13 01:30 | 5.4511 | 0 | N/A | 0 | 0
2021-11-13 02:00 | 4.7952 | 0 | N/A | 0 | 0
2021-11-13 02:30 | 4.6539 | 0 | N/A | 0 | 0
2021-11-13 03:00 | 4.3279 | 0 | N/A | 0 | 0
2021-11-13 03:30 | 3.9186 | 0 | N/A | 0 | 0
2021-11-13 04:00 | 3.6726 | 0 | N/A | 0 | 0
2021-11-13 04:30 | 3.5357 | 0 | N/A | 0 | 0
2021-11-13 05:00 | 3.4281 | 0 | N/A | 0 | 0
2021-11-13 05:30 | 3.5656 | 0 | N/A | 0 | 0
2021-11-13 06:00 | 3.7068 | 0 | N/A | 0 | 0
2021-11-13 06:30 | 3.9888 | 0 | N/A | 0 | 0
2021-11-13 07:00 | 4.1589 | 0 | N/A | 0 | 0
2021-11-13 07:30 | 4.8494 | 0 | N/A | 0 | 0
2021-11-13 08:00 | 5.1239 | 0 | N/A | 0 | 0
2021-11-13 08:30 | 5.1302 | 0 | N/A | 0 | 0
2021-11-13 09:00 | 5.1753 | 0 | N/A | 0 | 0
2021-11-13 09:30 | 5.4216 | 0 | N/A | 0 | 0
2021-11-13 10:00 | 4.9227 | 0 | N/A | 0 | 0
2021-11-13 10:30 | 3.8683 | 0 | N/A | 0 | 0
2021-11-13 11:00 | 3.7112 | 0 | N/A | 0 | 0
2021-11-13 11:30 | 3.7202 | 0 | N/A | 0 | 0
2021-11-13 12:00 | 3.267 | 0 | N/A | 0 | 0
2021-11-13 12:30 | 3.0376 | 0 | N/A | 0 | 0
2021-11-13 13:00 | 2.2423 | 0 | N/A | 0 | 0
2021-11-13 13:30 | 1.6118 | 0 | N/A | 0 | 0
2021-11-13 14:00 | 1.9954 | 0 | N/A | 0 | 0
2021-11-13 14:30 | 1.6331 | 0 | N/A | 0 | 0
2021-11-13 15:00 | 2.0871 | 0 | N/A | 0 | 0
2021-11-13 15:30 | 1.5948 | 0 | N/A | 0 | 0
2021-11-13 16:00 | 2.637 | 0 | N/A | 0 | 0
2021-11-13 16:30 | 1.8149 | 0 | N/A | 0 | 0
2021-11-13 17:00 | 2.3053 | 0 | N/A | 0 | 0
2021-11-13 17:30 | 3.0319 | 0 | N/A | 0 | 0
2021-11-13 18:00 | 4.3652 | 0 | N/A | 0 | 0
2021-11-13 18:30 | 4.674 | 0 | N/A | 0 | 0
2021-11-13 19:00 | 5.1914 | 0 | N/A | 0 | 0
2021-11-13 19:30 | 5.4762 | 0 | N/A | 0 | 0
2021-11-13 20:00 | 5.6564 | 0 | N/A | 0 | 0
2021-11-13 20:30 | 5.8507 | 0 | N/A | 0 | 0
2021-11-13 21:00 | 5.9623 | 0 | N/A | 0 | 0
2021-11-13 21:30 | 5.8014 | 0 | N/A | 0 | 0
2021-11-13 22:00 | 5.5745 | 0 | N/A | 0 | 0
2021-11-13 22:30 | 5.6823 | 0 | N/A | 0 | 0
2021-11-13 23:00 | 5.8507 | 0 | N/A | 0 | 0
2021-11-13 23:30 | 5.5137 | 0 | N/A | 0 | 0
2021-11-14 | 5.524 | 0 | N/A | 0 | 0
2021-11-14 00:30 | 5.7969 | 0 | N/A | 0 | 0
2021-11-14 01:00 | 6.1963 | 0 | N/A | 0 | 0
2021-11-14 01:30 | 5.4296 | 0 | N/A | 0 | 0
2021-11-14 02:00 | 4.7592 | 0 | N/A | 0 | 0
2021-11-14 02:30 | 4.7408 | 0 | N/A | 0 | 0
2021-11-14 03:00 | 4.3097 | 0 | N/A | 0 | 0
2021-11-14 03:30 | 3.8325 | 0 | N/A | 0 | 0
2021-11-14 04:00 | 3.6347 | 0 | N/A | 0 | 0
2021-11-14 04:30 | 4.0283 | 0 | N/A | 0 | 0
2021-11-14 05:00 | 3.7599 | 0 | N/A | 0 | 0
2021-11-14 05:30 | 3.3006 | 0 | N/A | 0 | 0
2021-11-14 06:00 | 3.3894 | 0 | N/A | 0 | 0
2021-11-14 06:30 | 3.6931 | 0 | N/A | 0 | 0
2021-11-14 07:00 | 3.7595 | 0 | N/A | 0 | 0
2021-11-14 07:30 | 3.9428 | 0 | N/A | 0 | 0
2021-11-14 08:00 | 3.62 | 0 | N/A | 0 | 0
2021-11-14 08:30 | 3.9319 | 0 | N/A | 0 | 0
2021-11-14 09:00 | 4.2273 | 0 | N/A | 0 | 0
2021-11-14 09:30 | 4.7641 | 0 | N/A | 0 | 0
2021-11-14 10:00 | 5.1586 | 0 | N/A | 0 | 0
2021-11-14 10:30 | 3.6379 | 0 | N/A | 0 | 0
2021-11-14 11:00 | 4.3574 | 0 | N/A | 0 | 0
2021-11-14 11:30 | 3.3222 | 0 | N/A | 0 | 0
2021-11-14 12:00 | 3.0908 | 0 | N/A | 0 | 0
2021-11-14 12:30 | 3.3738 | 0 | N/A | 0 | 0
2021-11-14 13:00 | 2.4269 | 0 | N/A | 0 | 0
2021-11-14 13:30 | 4.5315 | 0 | N/A | 0 | 0
2021-11-14 14:00 | 2.1972 | 0 | N/A | 0 | 0
2021-11-14 14:30 | 1.597 | 0 | N/A | 0 | 0
2021-11-14 15:00 | 2.7375 | 0 | N/A | 0 | 0
2021-11-14 15:30 | 2.0479 | 0 | N/A | 0 | 0
2021-11-14 16:00 | 3.8684 | 0 | N/A | 0 | 0
2021-11-14 16:30 | 2.4318 | 0 | N/A | 0 | 0
2021-11-14 17:00 | 3.7188 | 0 | N/A | 0 | 0
2021-11-14 17:30 | 3.7774 | 0 | N/A | 0 | 0
2021-11-14 18:00 | 4.9883 | 0 | N/A | 0 | 0
2021-11-14 18:30 | 5.9431 | 0 | N/A | 0 | 0
2021-11-14 19:00 | 6.4157 | 0 | N/A | 0 | 0
2021-11-14 19:30 | 6.5344 | 0 | N/A | 0 | 0
2021-11-14 20:00 | 6.7991 | 0 | N/A | 0 | 0
2021-11-14 20:30 | 6.9381 | 0 | N/A | 0 | 0
2021-11-14 21:00 | 6.8454 | 0 | N/A | 0 | 0
2021-11-14 21:30 | 6.5131 | 0 | N/A | 0 | 0
2021-11-14 22:00 | 6.0127 | 0 | N/A | 0 | 0
2021-11-14 22:30 | 5.9377 | 0 | N/A | 0 | 0
2021-11-14 23:00 | 5.8367 | 0 | N/A | 0 | 0
2021-11-14 23:30 | 5.4975 | 0 | N/A | 0 | 0
2021-11-15 | 5.6102 | 0 | N/A | 0 | 0
2021-11-15 00:30 | 5.9119 | 0 | N/A | 0 | 0
2021-11-15 01:00 | 6.3287 | 0 | N/A | 0 | 0
2021-11-15 01:30 | 5.5909 | 0 | N/A | 0 | 0
2021-11-15 02:00 | 4.8018 | 0 | N/A | 0 | 0
2021-11-15 02:30 | 4.7388 | 0 | N/A | 0 | 0
2021-11-15 03:00 | 4.4905 | 0 | N/A | 0 | 0
2021-11-15 03:30 | 3.9866 | 0 | N/A | 0 | 0
2021-11-15 04:00 | 3.6543 | 0 | N/A | 0 | 0
2021-11-15 04:30 | 3.5655 | 0 | N/A | 0 | 0
2021-11-15 05:00 | 3.5299 | 0 | N/A | 0 | 0
2021-11-15 05:30 | 3.8364 | 0 | N/A | 0 | 0
2021-11-15 06:00 | 4.1897 | 0 | N/A | 0 | 0
2021-11-15 06:30 | 5.2029 | 0 | N/A | 0 | 0
2021-11-15 07:00 | 6.3266 | 0 | N/A | 0 | 0
2021-11-15 07:30 | 7.4229 | 0 | N/A | 0 | 0
2021-11-15 08:00 | 7.7345 | 0 | N/A | 0 | 0
2021-11-15 08:30 | 7.4 | 0 | N/A | 0 | 0
2021-11-15 09:00 | 6.53 | 0 | N/A | 0 | 0
2021-11-15 09:30 | 4.8967 | 0 | N/A | 0 | 0
2021-11-15 10:00 | 5.78 | 0 | N/A | 0 | 0
2021-11-15 10:30 | 5.4705 | 0 | N/A | 0 | 0
2021-11-15 11:00 | 4.4233 | 0 | N/A | 0 | 0
2021-11-15 11:30 | 3.5734 | 0 | N/A | 0 | 0
2021-11-15 12:00 | 3.6632 | 0 | N/A | 0 | 0
2021-11-15 12:30 | 4.8126 | 0 | N/A | 0 | 0
2021-11-15 13:00 | 3.7258 | 0 | N/A | 0 | 0
2021-11-15 13:30 | 2.649 | 0 | N/A | 0 | 0
2021-11-15 14:00 | 2.6979 | 0 | N/A | 0 | 0
2021-11-15 14:30 | 2.204 | 0 | N/A | 0 | 0
2021-11-15 15:00 | 1.6808 | 0 | N/A | 0 | 0
2021-11-15 15:30 | 2.9955 | 0 | N/A | 0 | 0
2021-11-15 16:00 | 2.6253 | 0 | N/A | 0 | 0
2021-11-15 16:30 | 3.0482 | 0 | N/A | 0 | 0
2021-11-15 17:00 | 3 | 0 | N/A | 0 | 0
2021-11-15 17:30 | 4.2954 | 0 | N/A | 0 | 0
2021-11-15 18:00 | 5.7603 | 0 | N/A | 0 | 0
2021-11-15 18:30 | 6.303 | 0 | N/A | 0 | 0
2021-11-15 19:00 | 6.6763 | 0 | N/A | 0 | 0
2021-11-15 19:30 | 6.9646 | 0 | N/A | 0 | 0
2021-11-15 20:00 | 6.9808 | 0 | N/A | 0 | 0
2021-11-15 20:30 | 7.247 | 0 | N/A | 0 | 0
2021-11-15 21:00 | 7.233 | 0 | N/A | 0 | 0
2021-11-15 21:30 | 6.736 | 0 | N/A | 0 | 0
2021-11-15 22:00 | 6.3211 | 0 | N/A | 0 | 0
2021-11-15 22:30 | 6.1955 | 0 | N/A | 0 | 0
2021-11-15 23:00 | 6.0833 | 0 | N/A | 0 | 0
2021-11-15 23:30 | 5.6498 | 0 | N/A | 0 | 0
2021-11-16 | 5.6269 | 0 | N/A | 0 | 0
2021-11-16 00:30 | 5.8195 | 0 | N/A | 0 | 0
2021-11-16 01:00 | 6.224 | 0 | N/A | 0 | 0
2021-11-16 01:30 | 5.6367 | 0 | N/A | 0 | 0
2021-11-16 02:00 | 5.0645 | 0 | N/A | 0 | 0
2021-11-16 02:30 | 4.9193 | 0 | N/A | 0 | 0
2021-11-16 03:00 | 4.5628 | 0 | N/A | 0 | 0
2021-11-16 03:30 | 4.1264 | 0 | N/A | 0 | 0
2021-11-16 04:00 | 3.8687 | 0 | N/A | 0 | 0
2021-11-16 04:30 | 3.8219 | 0 | N/A | 0 | 0
2021-11-16 05:00 | 3.7619 | 0 | N/A | 0 | 0
2021-11-16 05:30 | 4.0941 | 0 | N/A | 0 | 0
2021-11-16 06:00 | 4.4414 | 0 | N/A | 0 | 0
2021-11-16 06:30 | 5.3627 | 0 | N/A | 0 | 0
2021-11-16 07:00 | 6.3101 | 0 | N/A | 0 | 0
2021-11-16 07:30 | 7.1369 | 0 | N/A | 0 | 0
2021-11-16 08:00 | 7.1345 | 0 | N/A | 0 | 0
2021-11-16 08:30 | 6.3974 | 0 | N/A | 0 | 0
2021-11-16 09:00 | 5.7083 | 0 | N/A | 0 | 0
2021-11-16 09:30 | 5.2484 | 0 | N/A | 0 | 0
2021-11-16 10:00 | 4.4743 | 0 | N/A | 0 | 0
2021-11-16 10:30 | 4.3143 | 0 | N/A | 0 | 0
2021-11-16 11:00 | 4.3451 | 0 | N/A | 0 | 0
2021-11-16 11:30 | 3.8973 | 0 | N/A | 0 | 0
2021-11-16 12:00 | 3.8287 | 0 | N/A | 0 | 0
2021-11-16 12:30 | 3.4055 | 0 | N/A | 0 | 0
2021-11-16 13:00 | 3.8894 | 0 | N/A | 0 | 0
2021-11-16 13:30 | 3.2145 | 0 | N/A | 0 | 0
2021-11-16 14:00 | 3.392 | 0 | N/A | 0 | 0
2021-11-16 14:30 | 3.9725 | 0 | N/A | 0 | 0
2021-11-16 15:00 | 4.2711 | 0 | N/A | 0 | 0
2021-11-16 15:30 | 3.7991 | 0 | N/A | 0 | 0
2021-11-16 16:00 | 4.0197 | 0 | N/A | 0 | 0
2021-11-16 16:30 | 3.7793 | 0 | N/A | 0 | 0
2021-11-16 17:00 | 4.0381 | 0 | N/A | 0 | 0
2021-11-16 17:30 | 4.6253 | 0 | N/A | 0 | 0
2021-11-16 18:00 | 5.8752 | 0 | N/A | 0 | 0
2021-11-16 18:30 | 6.5921 | 0 | N/A | 0 | 0
2021-11-16 19:00 | 6.9475 | 0 | N/A | 0 | 0
2021-11-16 19:30 | 6.9378 | 0 | N/A | 0 | 0
2021-11-16 20:00 | 6.905 | 0 | N/A | 0 | 0
2021-11-16 20:30 | 6.7799 | 0 | N/A | 0 | 0
2021-11-16 21:00 | 6.6913 | 0 | N/A | 0 | 0
2021-11-16 21:30 | 6.3173 | 0 | N/A | 0 | 0
2021-11-16 22:00 | 5.8544 | 0 | N/A | 0 | 0
2021-11-16 22:30 | 5.7186 | 0 | N/A | 0 | 0
2021-11-16 23:00 | 5.6312 | 0 | N/A | 0 | 0
2021-11-16 23:30 | 5.1819 | 0 | N/A | 0 | 0
2021-11-17 | 5.0796 | 0 | N/A | 0 | 0
2021-11-17 00:30 | 5.3748 | 0 | N/A | 0 | 0
2021-11-17 01:00 | 5.8623 | 0 | N/A | 0 | 0
2021-11-17 01:30 | 5.2391 | 0 | N/A | 0 | 0
2021-11-17 02:00 | 4.5273 | 0 | N/A | 0 | 0
2021-11-17 02:30 | 4.4883 | 0 | N/A | 0 | 0
2021-11-17 03:00 | 4.2617 | 0 | N/A | 0 | 0
2021-11-17 03:30 | 3.7999 | 0 | N/A | 0 | 0
2021-11-17 04:00 | 3.5753 | 0 | N/A | 0 | 0
2021-11-17 04:30 | 3.5479 | 0 | N/A | 0 | 0
2021-11-17 05:00 | 3.5963 | 0 | N/A | 0 | 0
2021-11-17 05:30 | 3.913 | 0 | N/A | 0 | 0
2021-11-17 06:00 | 4.3224 | 0 | N/A | 0 | 0
2021-11-17 06:30 | 5.3273 | 0 | N/A | 0 | 0
2021-11-17 07:00 | 6.4106 | 0 | N/A | 0 | 0
2021-11-17 07:30 | 6.8964 | 0 | N/A | 0 | 0
2021-11-17 08:00 | 6.5099 | 0 | N/A | 0 | 0
2021-11-17 08:30 | 5.0482 | 0 | N/A | 0 | 0
2021-11-17 09:00 | 4.2744 | 0 | N/A | 0 | 0
2021-11-17 09:30 | 3.8837 | 0 | N/A | 0 | 0
2021-11-17 10:00 | 3.2774 | 0 | N/A | 0 | 0
2021-11-17 10:30 | 2.8769 | 0 | N/A | 0 | 0
2021-11-17 11:00 | 1.8962 | 0 | N/A | 0 | 0
2021-11-17 11:30 | 1.0638 | 0 | N/A | 0 | 0
2021-11-17 12:00 | 0.092616 | 0 | N/A | 0 | 0
2021-11-17 12:30 | 0.30472 | 0 | N/A | 0 | 0
2021-11-17 13:00 | -0.54496 | 0 | N/A | 0 | 0
2021-11-17 13:30 | -0.64654 | 0 | N/A | 0 | 0
2021-11-17 14:00 | -0.65728 | 0 | N/A | 0 | 0
2021-11-17 14:30 | -0.56828 | 0 | N/A | 0 | 0
2021-11-17 15:00 | -0.19669 | 0 | N/A | 0 | 0
2021-11-17 15:30 | -0.21378 | 0 | N/A | 0 | 0
2021-11-17 16:00 | -0.37222 | 0 | N/A | 0 | 0
2021-11-17 16:30 | 0.59001 | 0 | N/A | 0 | 0
2021-11-17 17:00 | 1.7103 | 0 | N/A | 0 | 0
2021-11-17 17:30 | 1.7622 | 0 | N/A | 0 | 0
2021-11-17 18:00 | 2.1505 | 0 | N/A | 0 | 0
2021-11-17 18:30 | 3.3781 | 0 | N/A | 0 | 0
2021-11-17 19:00 | 3.7175 | 0 | N/A | 0 | 0
2021-11-17 19:30 | 4.1708 | 0 | N/A | 0 | 0
2021-11-17 20:00 | 4.5139 | 0 | N/A | 0 | 0
2021-11-17 20:30 | 4.7491 | 0 | N/A | 0 | 0
2021-11-17 21:00 | 5.0114 | 0 | N/A | 0 | 0
2021-11-17 21:30 | 4.8573 | 0 | N/A | 0 | 0
2021-11-17 22:00 | 4.5663 | 0 | N/A | 0 | 0
2021-11-17 22:30 | 4.7408 | 0 | N/A | 0 | 0
2021-11-17 23:00 | 4.8106 | 0 | N/A | 0 | 0
2021-11-17 23:30 | 4.5558 | 0 | N/A | 0 | 0
2021-11-18 | 4.5009 | 0 | N/A | 0 | 0
2021-11-18 00:30 | 4.7945 | 0 | N/A | 0 | 0
2021-11-18 01:00 | 5.1522 | 0 | N/A | 0 | 0
2021-11-18 01:30 | 4.4959 | 0 | N/A | 0 | 0
2021-11-18 02:00 | 3.9 | 0 | N/A | 0 | 0
2021-11-18 02:30 | 3.7772 | 0 | N/A | 0 | 0
2021-11-18 03:00 | 3.5833 | 0 | N/A | 0 | 0
2021-11-18 03:30 | 3.2414 | 0 | N/A | 0 | 0
2021-11-18 04:00 | 2.9992 | 0 | N/A | 0 | 0
2021-11-18 04:30 | 2.916 | 0 | N/A | 0 | 0
2021-11-18 05:00 | 2.9147 | 0 | N/A | 0 | 0
2021-11-18 05:30 | 3.1402 | 0 | N/A | 0 | 0
2021-11-18 06:00 | 3.4761 | 0 | N/A | 0 | 0
2021-11-18 06:30 | 4.2335 | 0 | N/A | 0 | 0
2021-11-18 07:00 | 4.9069 | 0 | N/A | 0 | 0
2021-11-18 07:30 | 5.6615 | 0 | N/A | 0 | 0
2021-11-18 08:00 | 5.3467 | 0 | N/A | 0 | 0
2021-11-18 08:30 | 4.6594 | 0 | N/A | 0 | 0
2021-11-18 09:00 | 4.0286 | 0 | N/A | 0 | 0
2021-11-18 09:30 | 3.3374 | 0 | N/A | 0 | 0
2021-11-18 10:00 | 4.4233 | 0 | N/A | 0 | 0
2021-11-18 10:30 | 4.2656 | 0 | N/A | 0 | 0
2021-11-18 11:00 | 3.8022 | 0 | N/A | 0 | 0
2021-11-18 11:30 | 1.3021 | 0 | N/A | 0 | 0
2021-11-18 12:00 | 3.3327 | 0 | N/A | 0 | 0
2021-11-18 12:30 | 2.2842 | 0 | N/A | 0 | 0
2021-11-18 13:00 | 1.0128 | 0 | N/A | 0 | 0
2021-11-18 13:30 | 0.43748 | 0 | N/A | 0 | 0
2021-11-18 14:00 | -0.32938 | 0 | N/A | 0 | 0
2021-11-18 14:30 | -1.0409 | 0 | N/A | 0 | 0
2021-11-18 15:00 | -1.1871 | 0 | N/A | 0 | 0
2021-11-18 15:30 | -1.1918 | 0 | N/A | 0 | 0
2021-11-18 16:00 | -0.99426 | 0 | N/A | 0 | 0
2021-11-18 16:30 | -0.87818 | 0 | N/A | 0 | 0
2021-11-18 17:00 | 0.59876 | 0 | N/A | 0 | 0
2021-11-18 17:30 | 2.8071 | 0 | N/A | 0 | 0
2021-11-18 18:00 | 3.6502 | 0 | N/A | 0 | 0
2021-11-18 18:30 | 4.3838 | 0 | N/A | 0 | 0
2021-11-18 19:00 | 4.5222 | 0 | N/A | 0 | 0
2021-11-18 19:30 | 4.4872 | 0 | N/A | 0 | 0
2021-11-18 20:00 | 4.4713 | 0 | N/A | 0 | 0
2021-11-18 20:30 | 4.4335 | 0 | N/A | 0 | 0
2021-11-18 21:00 | 4.5248 | 0 | N/A | 0 | 0
2021-11-18 21:30 | 4.3738 | 0 | N/A | 0 | 0
2021-11-18 22:00 | 4.32 | 0 | N/A | 0 | 0
2021-11-18 22:30 | 4.331 | 0 | N/A | 0 | 0
2021-11-18 23:00 | 4.4042 | 0 | N/A | 0 | 0
2021-11-18 23:30 | 4.209 | 0 | N/A | 0 | 0
2021-11-19 | 4.2586 | 0 | N/A | 0 | 0
2021-11-19 00:30 | 4.6363 | 0 | N/A | 0 | 0
2021-11-19 01:00 | 5.0871 | 0 | N/A | 0 | 0
2021-11-19 01:30 | 4.3097 | 0 | N/A | 0 | 0
2021-11-19 02:00 | 3.5531 | 0 | N/A | 0 | 0
2021-11-19 02:30 | 3.5431 | 0 | N/A | 0 | 0
2021-11-19 03:00 | 3.3145 | 0 | N/A | 0 | 0
2021-11-19 03:30 | 3.0093 | 0 | N/A | 0 | 0
2021-11-19 04:00 | 2.7672 | 0 | N/A | 0 | 0
2021-11-19 04:30 | 2.6949 | 0 | N/A | 0 | 0
2021-11-19 05:00 | 2.6813 | 0 | N/A | 0 | 0
2021-11-19 05:30 | 2.8159 | 0 | N/A | 0 | 0
2021-11-19 06:00 | 3.1349 | 0 | N/A | 0 | 0
2021-11-19 06:30 | 4.1767 | 0 | N/A | 0 | 0
2021-11-19 07:00 | 4.6028 | 0 | N/A | 0 | 0
2021-11-19 07:30 | 5.0666 | 0 | N/A | 0 | 0
2021-11-19 08:00 | 4.7136 | 0 | N/A | 0 | 0
2021-11-19 08:30 | 3.7727 | 0 | N/A | 0 | 0
2021-11-19 09:00 | 3.2235 | 0 | N/A | 0 | 0
2021-11-19 09:30 | 3.0171 | 0 | N/A | 0 | 0
2021-11-19 10:00 | 2.5979 | 0 | N/A | 0 | 0
2021-11-19 10:30 | 2.0005 | 0 | N/A | 0 | 0
2021-11-19 11:00 | 2.0697 | 0 | N/A | 0 | 0
2021-11-19 11:30 | 1.8965 | 0 | N/A | 0 | 0
2021-11-19 12:00 | 1.7585 | 0 | N/A | 0 | 0
2021-11-19 12:30 | 1.5378 | 0 | N/A | 0 | 0
2021-11-19 13:00 | 1.7756 | 0 | N/A | 0 | 0
2021-11-19 13:30 | 1.3104 | 0 | N/A | 0 | 0
2021-11-19 14:00 | 0.54203 | 0 | N/A | 0 | 0
2021-11-19 14:30 | 1.4439 | 0 | N/A | 0 | 0
2021-11-19 15:00 | 1.7522 | 0 | N/A | 0 | 0
2021-11-19 15:30 | 1.9359 | 0 | N/A | 0 | 0
2021-11-19 16:00 | 1.6321 | 0 | N/A | 0 | 0
2021-11-19 16:30 | 1.8489 | 0 | N/A | 0 | 0
2021-11-19 17:00 | 1.9414 | 0 | N/A | 0 | 0
2021-11-19 17:30 | 3.094 | 0 | N/A | 0 | 0
2021-11-19 18:00 | 3.7034 | 0 | N/A | 0 | 0
2021-11-19 18:30 | 4.3672 | 0 | N/A | 0 | 0
2021-11-19 19:00 | 4.7846 | 0 | N/A | 0 | 0
2021-11-19 19:30 | 4.9008 | 0 | N/A | 0 | 0
2021-11-19 20:00 | 5.0131 | 0 | N/A | 0 | 0
2021-11-19 20:30 | 5.153 | 0 | N/A | 0 | 0
2021-11-19 21:00 | 5.2842 | 0 | N/A | 0 | 0
2021-11-19 21:30 | 5.0679 | 0 | N/A | 0 | 0
2021-11-19 22:00 | 4.7413 | 0 | N/A | 0 | 0
2021-11-19 22:30 | 5.0527 | 0 | N/A | 0 | 0
2021-11-19 23:00 | 5.0896 | 0 | N/A | 0 | 0
2021-11-19 23:30 | 4.8257 | 0 | N/A | 0 | 0
2021-11-20 | 4.8529 | 0 | N/A | 0 | 0
2021-11-20 00:30 | 5.1842 | 0 | N/A | 0 | 0
2021-11-20 01:00 | 5.4378 | 0 | N/A | 0 | 0
2021-11-20 01:30 | 4.7264 | 0 | N/A | 0 | 0
2021-11-20 02:00 | 4.0261 | 0 | N/A | 0 | 0
2021-11-20 02:30 | 3.9358 | 0 | N/A | 0 | 0
2021-11-20 03:00 | 3.6149 | 0 | N/A | 0 | 0
2021-11-20 03:30 | 3.2087 | 0 | N/A | 0 | 0
2021-11-20 04:00 | 2.9951 | 0 | N/A | 0 | 0
2021-11-20 04:30 | 2.9043 | 0 | N/A | 0 | 0
2021-11-20 05:00 | 2.82 | 0 | N/A | 0 | 0
2021-11-20 05:30 | 2.9676 | 0 | N/A | 0 | 0
2021-11-20 06:00 | 3.0618 | 0 | N/A | 0 | 0
2021-11-20 06:30 | 3.2942 | 0 | N/A | 0 | 0
2021-11-20 07:00 | 3.4492 | 0 | N/A | 0 | 0
2021-11-20 07:30 | 3.6785 | 0 | N/A | 0 | 0
2021-11-20 08:00 | 3.2367 | 0 | N/A | 0 | 0
2021-11-20 08:30 | 2.8291 | 0 | N/A | 0 | 0
2021-11-20 09:00 | 2.6465 | 0 | N/A | 0 | 0
2021-11-20 09:30 | 2.1014 | 0 | N/A | 0 | 0
2021-11-20 10:00 | 1.6513 | 0 | N/A | 0 | 0
2021-11-20 10:30 | 1.0252 | 0 | N/A | 0 | 0
2021-11-20 11:00 | 0.62514 | 0 | N/A | 0 | 0
2021-11-20 11:30 | 0.60729 | 0 | N/A | 0 | 0
2021-11-20 12:00 | -0.67394 | 0 | N/A | 0 | 0
2021-11-20 12:30 | -0.87453 | 0 | N/A | 0 | 0
2021-11-20 13:00 | -1.2096 | 0 | N/A | 0 | 0
2021-11-20 13:30 | -1.1903 | 0 | N/A | 0 | 0
2021-11-20 14:00 | -1.097 | 0 | N/A | 0 | 0
2021-11-20 14:30 | -0.87133 | 0 | N/A | 0 | 0
2021-11-20 15:00 | -1.0693 | 0 | N/A | 0 | 0
2021-11-20 15:30 | -0.85151 | 0 | N/A | 0 | 0
2021-11-20 16:00 | -0.8544 | 0 | N/A | 0 | 0
2021-11-20 16:30 | -0.76641 | 0 | N/A | 0 | 0
2021-11-20 17:00 | 1.2876 | 0 | N/A | 0 | 0
2021-11-20 17:30 | 1.5845 | 0 | N/A | 0 | 0
2021-11-20 18:00 | 2.5443 | 0 | N/A | 0 | 0
2021-11-20 18:30 | 3.6995 | 0 | N/A | 0 | 0
2021-11-20 19:00 | 4.1023 | 0 | N/A | 0 | 0
2021-11-20 19:30 | 4.6095 | 0 | N/A | 0 | 0
2021-11-20 20:00 | 4.8433 | 0 | N/A | 0 | 0
2021-11-20 20:30 | 4.9447 | 0 | N/A | 0 | 0
2021-11-20 21:00 | 4.9896 | 0 | N/A | 0 | 0
2021-11-20 21:30 | 4.8535 | 0 | N/A | 0 | 0
2021-11-20 22:00 | 4.6166 | 0 | N/A | 0 | 0
2021-11-20 22:30 | 4.8771 | 0 | N/A | 0 | 0
2021-11-20 23:00 | 5.0154 | 0 | N/A | 0 | 0
2021-11-20 23:30 | 4.7815 | 0 | N/A | 0 | 0
2021-11-21 | 4.8219 | 0 | N/A | 0 | 0
2021-11-21 00:30 | 5.0321 | 0 | N/A | 0 | 0
2021-11-21 01:00 | 5.4161 | 0 | N/A | 0 | 0
2021-11-21 01:30 | 4.7826 | 0 | N/A | 0 | 0
2021-11-21 02:00 | 4.2 | 0 | N/A | 0 | 0
2021-11-21 02:30 | 4.1272 | 0 | N/A | 0 | 0
2021-11-21 03:00 | 3.8743 | 0 | N/A | 0 | 0
2021-11-21 03:30 | 3.4239 | 0 | N/A | 0 | 0
2021-11-21 04:00 | 3.1805 | 0 | N/A | 0 | 0
2021-11-21 04:30 | 3.0332 | 0 | N/A | 0 | 0
2021-11-21 05:00 | 2.9823 | 0 | N/A | 0 | 0
2021-11-21 05:30 | 3.0263 | 0 | N/A | 0 | 0
2021-11-21 06:00 | 3.08 | 0 | N/A | 0 | 0
2021-11-21 06:30 | 3.2371 | 0 | N/A | 0 | 0
2021-11-21 07:00 | 3.2869 | 0 | N/A | 0 | 0
2021-11-21 07:30 | 3.4594 | 0 | N/A | 0 | 0
2021-11-21 08:00 | 3.396 | 0 | N/A | 0 | 0
2021-11-21 08:30 | 2.7987 | 0 | N/A | 0 | 0
2021-11-21 09:00 | 3.1586 | 0 | N/A | 0 | 0
2021-11-21 09:30 | 3.2128 | 0 | N/A | 0 | 0
2021-11-21 10:00 | 2.7067 | 0 | N/A | 0 | 0
2021-11-21 10:30 | 2.0983 | 0 | N/A | 0 | 0
2021-11-21 11:00 | 1.3368 | 0 | N/A | 0 | 0
2021-11-21 11:30 | 1.11 | 0 | N/A | 0 | 0
2021-11-21 12:00 | -0.5747 | 0 | N/A | 0 | 0
2021-11-21 12:30 | -0.77208 | 0 | N/A | 0 | 0
2021-11-21 13:00 | -0.90676 | 0 | N/A | 0 | 0
2021-11-21 13:30 | -1.1523 | 0 | N/A | 0 | 0
2021-11-21 14:00 | -1.3312 | 0 | N/A | 0 | 0
2021-11-21 14:30 | -1.4652 | 0 | N/A | 0 | 0
2021-11-21 15:00 | -1.5399 | 0 | N/A | 0 | 0
2021-11-21 15:30 | -1.4753 | 0 | N/A | 0 | 0
2021-11-21 16:00 | -1.1791 | 0 | N/A | 0 | 0
2021-11-21 16:30 | -0.836 | 0 | N/A | 0 | 0
2021-11-21 17:00 | 0.76328 | 0 | N/A | 0 | 0
2021-11-21 17:30 | 1.3487 | 0 | N/A | 0 | 0
2021-11-21 18:00 | 2.3695 | 0 | N/A | 0 | 0
2021-11-21 18:30 | 3.2451 | 0 | N/A | 0 | 0
2021-11-21 19:00 | 3.993 | 0 | N/A | 0 | 0
2021-11-21 19:30 | 4.3785 | 0 | N/A | 0 | 0
2021-11-21 20:00 | 4.7144 | 0 | N/A | 0 | 0
2021-11-21 20:30 | 4.9414 | 0 | N/A | 0 | 0
2021-11-21 21:00 | 5.1601 | 0 | N/A | 0 | 0
2021-11-21 21:30 | 5.0394 | 0 | N/A | 0 | 0
2021-11-21 22:00 | 4.7768 | 0 | N/A | 0 | 0
2021-11-21 22:30 | 4.9232 | 0 | N/A | 0 | 0
2021-11-21 23:00 | 4.9183 | 0 | N/A | 0 | 0
2021-11-21 23:30 | 4.5815 | 0 | N/A | 0 | 0
2021-11-22 | 4.6646 | 0 | N/A | 0 | 0
2021-11-22 00:30 | 4.8931 | 0 | N/A | 0 | 0
2021-11-22 01:00 | 5.2625 | 0 | N/A | 0 | 0
2021-11-22 01:30 | 4.6117 | 0 | N/A | 0 | 0
2021-11-22 02:00 | 3.9455 | 0 | N/A | 0 | 0
2021-11-22 02:30 | 3.817 | 0 | N/A | 0 | 0
2021-11-22 03:00 | 3.5536 | 0 | N/A | 0 | 0
2021-11-22 03:30 | 3.166 | 0 | N/A | 0 | 0
2021-11-22 04:00 | 2.8451 | 0 | N/A | 0 | 0
2021-11-22 04:30 | 2.7628 | 0 | N/A | 0 | 0
2021-11-22 05:00 | 2.7161 | 0 | N/A | 0 | 0
2021-11-22 05:30 | 2.9569 | 0 | N/A | 0 | 0
2021-11-22 06:00 | 3.3468 | 0 | N/A | 0 | 0
2021-11-22 06:30 | 4.1247 | 0 | N/A | 0 | 0
2021-11-22 07:00 | 4.9871 | 0 | N/A | 0 | 0
2021-11-22 07:30 | 5.4838 | 0 | N/A | 0 | 0
2021-11-22 08:00 | 5.1354 | 0 | N/A | 0 | 0
2021-11-22 08:30 | 3.7639 | 0 | N/A | 0 | 0
2021-11-22 09:00 | 2.7593 | 0 | N/A | 0 | 0
2021-11-22 09:30 | 1.69 | 0 | N/A | 0 | 0
2021-11-22 10:00 | 0.82949 | 0 | N/A | 0 | 0
2021-11-22 10:30 | 0.35685 | 0 | N/A | 0 | 0
2021-11-22 11:00 | -0.12579 | 0 | N/A | 0 | 0
2021-11-22 11:30 | -0.51352 | 0 | N/A | 0 | 0
2021-11-22 12:00 | -0.4801 | 0 | N/A | 0 | 0
2021-11-22 12:30 | -0.62405 | 0 | N/A | 0 | 0
2021-11-22 13:00 | -0.55487 | 0 | N/A | 0 | 0
2021-11-22 13:30 | -0.534 | 0 | N/A | 0 | 0
2021-11-22 14:00 | -0.56691 | 0 | N/A | 0 | 0
2021-11-22 14:30 | -0.43881 | 0 | N/A | 0 | 0
2021-11-22 15:00 | -0.15836 | 0 | N/A | 0 | 0
2021-11-22 15:30 | -0.29031 | 0 | N/A | 0 | 0
2021-11-22 16:00 | -0.23343 | 0 | N/A | 0 | 0
2021-11-22 16:30 | 1.2836 | 0 | N/A | 0 | 0
2021-11-22 17:00 | 1.3153 | 0 | N/A | 0 | 0
2021-11-22 17:30 | 2.3686 | 0 | N/A | 0 | 0
2021-11-22 18:00 | 3.2049 | 0 | N/A | 0 | 0
2021-11-22 18:30 | 3.57 | 0 | N/A | 0 | 0
2021-11-22 19:00 | 3.4866 | 0 | N/A | 0 | 0
2021-11-22 19:30 | 3.8707 | 0 | N/A | 0 | 0
2021-11-22 20:00 | 4.2284 | 0 | N/A | 0 | 0
2021-11-22 20:30 | 4.378 | 0 | N/A | 0 | 0
2021-11-22 21:00 | 4.4528 | 0 | N/A | 0 | 0
2021-11-22 21:30 | 4.243 | 0 | N/A | 0 | 0
2021-11-22 22:00 | 3.9324 | 0 | N/A | 0 | 0
2021-11-22 22:30 | 4.1443 | 0 | N/A | 0 | 0
2021-11-22 23:00 | 4.2833 | 0 | N/A | 0 | 0
2021-11-22 23:30 | 4.055 | 0 | N/A | 0 | 0
2021-11-23 | 3.9881 | 0 | N/A | 0 | 0
2021-11-23 00:30 | 4.3221 | 0 | N/A | 0 | 0
2021-11-23 01:00 | 4.6656 | 0 | N/A | 0 | 0
2021-11-23 01:30 | 3.9623 | 0 | N/A | 0 | 0
2021-11-23 02:00 | 3.3725 | 0 | N/A | 0 | 0
2021-11-23 02:30 | 3.2898 | 0 | N/A | 0 | 0
2021-11-23 03:00 | 3.0082 | 0 | N/A | 0 | 0
2021-11-23 03:30 | 2.687 | 0 | N/A | 0 | 0
2021-11-23 04:00 | 2.4704 | 0 | N/A | 0 | 0
2021-11-23 04:30 | 2.4405 | 0 | N/A | 0 | 0
2021-11-23 05:00 | 2.4588 | 0 | N/A | 0 | 0
2021-11-23 05:30 | 2.5854 | 0 | N/A | 0 | 0
2021-11-23 06:00 | 2.8649 | 0 | N/A | 0 | 0
2021-11-23 06:30 | 3.5515 | 0 | N/A | 0 | 0
2021-11-23 07:00 | 4.0315 | 0 | N/A | 0 | 0
2021-11-23 07:30 | 4.2988 | 0 | N/A | 0 | 0
2021-11-23 08:00 | 4.2264 | 0 | N/A | 0 | 0
2021-11-23 08:30 | 3.6111 | 0 | N/A | 0 | 0
2021-11-23 09:00 | 3.2696 | 0 | N/A | 0 | 0
2021-11-23 09:30 | 2.3726 | 0 | N/A | 0 | 0
2021-11-23 10:00 | 1.8249 | 0 | N/A | 0 | 0
2021-11-23 10:30 | 2.4101 | 0 | N/A | 0 | 0
2021-11-23 11:00 | 1.3686 | 0 | N/A | 0 | 0
2021-11-23 11:30 | 1.8076 | 0 | N/A | 0 | 0
2021-11-23 12:00 | 1.7004 | 0 | N/A | 0 | 0
2021-11-23 12:30 | 1.5896 | 0 | N/A | 0 | 0
2021-11-23 13:00 | 0.97505 | 0 | N/A | 0 | 0
2021-11-23 13:30 | 0.50983 | 0 | N/A | 0 | 0
2021-11-23 14:00 | 0.54054 | 0 | N/A | 0 | 0
2021-11-23 14:30 | 0.35617 | 0 | N/A | 0 | 0
2021-11-23 15:00 | 0.54734 | 0 | N/A | 0 | 0
2021-11-23 15:30 | 1.0068 | 0 | N/A | 0 | 0
2021-11-23 16:00 | 0.97348 | 0 | N/A | 0 | 0
2021-11-23 16:30 | 1.6725 | 0 | N/A | 0 | 0
2021-11-23 17:00 | 1.8975 | 0 | N/A | 0 | 0
2021-11-23 17:30 | 2.5419 | 0 | N/A | 0 | 0
2021-11-23 18:00 | 3.8535 | 0 | N/A | 0 | 0
2021-11-23 18:30 | 4.2487 | 0 | N/A | 0 | 0
2021-11-23 19:00 | 4.2134 | 0 | N/A | 0 | 0
2021-11-23 19:30 | 4.1585 | 0 | N/A | 0 | 0
2021-11-23 20:00 | 4.3443 | 0 | N/A | 0 | 0
2021-11-23 20:30 | 4.3314 | 0 | N/A | 0 | 0
2021-11-23 21:00 | 4.3481 | 0 | N/A | 0 | 0
2021-11-23 21:30 | 4.1184 | 0 | N/A | 0 | 0
2021-11-23 22:00 | 3.8854 | 0 | N/A | 0 | 0
2021-11-23 22:30 | 4.1513 | 0 | N/A | 0 | 0
2021-11-23 23:00 | 4.2972 | 0 | N/A | 0 | 0
2021-11-23 23:30 | 4.0512 | 0 | N/A | 0 | 0
2021-11-24 | 4.048 | 0 | N/A | 0 | 0
2021-11-24 00:30 | 4.5048 | 0 | N/A | 0 | 0
2021-11-24 01:00 | 4.7393 | 0 | N/A | 0 | 0
2021-11-24 01:30 | 3.8676 | 0 | N/A | 0 | 0
2021-11-24 02:00 | 3.3009 | 0 | N/A | 0 | 0
2021-11-24 02:30 | 3.2608 | 0 | N/A | 0 | 0
2021-11-24 03:00 | 2.9219 | 0 | N/A | 0 | 0
2021-11-24 03:30 | 2.5745 | 0 | N/A | 0 | 0
2021-11-24 04:00 | 2.4181 | 0 | N/A | 0 | 0
2021-11-24 04:30 | 2.3689 | 0 | N/A | 0 | 0
2021-11-24 05:00 | 2.4392 | 0 | N/A | 0 | 0
2021-11-24 05:30 | 2.5473 | 0 | N/A | 0 | 0
2021-11-24 06:00 | 2.7347 | 0 | N/A | 0 | 0
2021-11-24 06:30 | 3.4214 | 0 | N/A | 0 | 0
2021-11-24 07:00 | 4.1278 | 0 | N/A | 0 | 0
2021-11-24 07:30 | 4.384 | 0 | N/A | 0 | 0
2021-11-24 08:00 | 4.3619 | 0 | N/A | 0 | 0
2021-11-24 08:30 | 3.0845 | 0 | N/A | 0 | 0
2021-11-24 09:00 | 2.5618 | 0 | N/A | 0 | 0
2021-11-24 09:30 | 2.2384 | 0 | N/A | 0 | 0
2021-11-24 10:00 | 1.2981 | 0 | N/A | 0 | 0
2021-11-24 10:30 | 0.36845 | 0 | N/A | 0 | 0
2021-11-24 11:00 | 0.59982 | 0 | N/A | 0 | 0
2021-11-24 11:30 | 0.18601 | 0 | N/A | 0 | 0
2021-11-24 12:00 | -0.51243 | 0 | N/A | 0 | 0
2021-11-24 12:30 | -0.13271 | 0 | N/A | 0 | 0
2021-11-24 13:00 | -0.52462 | 0 | N/A | 0 | 0
2021-11-24 13:30 | -0.33335 | 0 | N/A | 0 | 0
2021-11-24 14:00 | 0.2275 | 0 | N/A | 0 | 0
2021-11-24 14:30 | 0.83733 | 0 | N/A | 0 | 0
2021-11-24 15:00 | 1.1954 | 0 | N/A | 0 | 0
2021-11-24 15:30 | 2.056 | 0 | N/A | 0 | 0
2021-11-24 16:00 | 1.5905 | 0 | N/A | 0 | 0
2021-11-24 16:30 | 2.0173 | 0 | N/A | 0 | 0
2021-11-24 17:00 | 2.2057 | 0 | N/A | 0 | 0
2021-11-24 17:30 | 2.3104 | 0 | N/A | 0 | 0
2021-11-24 18:00 | 2.9225 | 0 | N/A | 0 | 0
2021-11-24 18:30 | 3.8608 | 0 | N/A | 0 | 0
2021-11-24 19:00 | 4.7142 | 0 | N/A | 0 | 0
2021-11-24 19:30 | 4.6868 | 0 | N/A | 0 | 0
2021-11-24 20:00 | 4.5936 | 0 | N/A | 0 | 0
2021-11-24 20:30 | 4.4656 | 0 | N/A | 0 | 0
2021-11-24 21:00 | 4.4218 | 0 | N/A | 0 | 0
2021-11-24 21:30 | 4.2892 | 0 | N/A | 0 | 0
2021-11-24 22:00 | 4.0428 | 0 | N/A | 0 | 0
2021-11-24 22:30 | 4.2337 | 0 | N/A | 0 | 0
2021-11-24 23:00 | 4.2558 | 0 | N/A | 0 | 0
2021-11-24 23:30 | 4.0018 | 0 | N/A | 0 | 0
2021-11-25 | 4.0313 | 0 | N/A | 0 | 0
2021-11-25 00:30 | 4.4198 | 0 | N/A | 0 | 0
2021-11-25 01:00 | 4.5706 | 0 | N/A | 0 | 0
2021-11-25 01:30 | 3.7828 | 0 | N/A | 0 | 0
2021-11-25 02:00 | 3.1529 | 0 | N/A | 0 | 0
2021-11-25 02:30 | 3.0917 | 0 | N/A | 0 | 0
2021-11-25 03:00 | 2.7974 | 0 | N/A | 0 | 0
2021-11-25 03:30 | 2.5045 | 0 | N/A | 0 | 0
2021-11-25 04:00 | 2.3602 | 0 | N/A | 0 | 0
2021-11-25 04:30 | 2.3451 | 0 | N/A | 0 | 0
2021-11-25 05:00 | 2.4352 | 0 | N/A | 0 | 0
2021-11-25 05:30 | 2.5297 | 0 | N/A | 0 | 0
2021-11-25 06:00 | 2.771 | 0 | N/A | 0 | 0
2021-11-25 06:30 | 3.4286 | 0 | N/A | 0 | 0
2021-11-25 07:00 | 4.1384 | 0 | N/A | 0 | 0
2021-11-25 07:30 | 4.8815 | 0 | N/A | 0 | 0
2021-11-25 08:00 | 4.9205 | 0 | N/A | 0 | 0
2021-11-25 08:30 | 4.2973 | 0 | N/A | 0 | 0
2021-11-25 09:00 | 4.146 | 0 | N/A | 0 | 0
2021-11-25 09:30 | 4.3895 | 0 | N/A | 0 | 0
2021-11-25 10:00 | 4.3171 | 0 | N/A | 0 | 0
2021-11-25 10:30 | 4.3228 | 0 | N/A | 0 | 0
2021-11-25 11:00 | 4.3574 | 0 | N/A | 0 | 0
2021-11-25 11:30 | 4.2319 | 0 | N/A | 0 | 0
2021-11-25 12:00 | 4.4486 | 0 | N/A | 0 | 0
2021-11-25 12:30 | 4.6282 | 0 | N/A | 0 | 0
2021-11-25 13:00 | 4.6826 | 0 | N/A | 0 | 0
2021-11-25 13:30 | 4.6956 | 0 | N/A | 0 | 0
2021-11-25 14:00 | 4.3987 | 0 | N/A | 0 | 0
2021-11-25 14:30 | 4.0856 | 0 | N/A | 0 | 0
2021-11-25 15:00 | 4.4173 | 0 | N/A | 0 | 0
2021-11-25 15:30 | 4.4393 | 0 | N/A | 0 | 0
2021-11-25 16:00 | 4.3087 | 0 | N/A | 0 | 0
2021-11-25 16:30 | 4.1913 | 0 | N/A | 0 | 0
2021-11-25 17:00 | 3.7067 | 0 | N/A | 0 | 0
2021-11-25 17:30 | 3.0013 | 0 | N/A | 0 | 0
2021-11-25 18:00 | 4.1407 | 0 | N/A | 0 | 0
2021-11-25 18:30 | 4.5029 | 0 | N/A | 0 | 0
2021-11-25 19:00 | 4.6448 | 0 | N/A | 0 | 0
2021-11-25 19:30 | 4.8262 | 0 | N/A | 0 | 0
2021-11-25 20:00 | 5.0874 | 0 | N/A | 0 | 0
2021-11-25 20:30 | 5.4742 | 0 | N/A | 0 | 0
2021-11-25 21:00 | 5.6122 | 0 | N/A | 0 | 0
2021-11-25 21:30 | 5.3989 | 0 | N/A | 0 | 0
2021-11-25 22:00 | 4.9563 | 0 | N/A | 0 | 0
2021-11-25 22:30 | 5.0653 | 0 | N/A | 0 | 0
2021-11-25 23:00 | 5.067 | 0 | N/A | 0 | 0
2021-11-25 23:30 | 4.6869 | 0 | N/A | 0 | 0
2021-11-26 | 4.716 | 0 | N/A | 0 | 0
2021-11-26 00:30 | 5.0127 | 0 | N/A | 0 | 0
2021-11-26 01:00 | 5.4198 | 0 | N/A | 0 | 0
2021-11-26 01:30 | 4.6653 | 0 | N/A | 0 | 0
2021-11-26 02:00 | 3.9622 | 0 | N/A | 0 | 0
2021-11-26 02:30 | 3.8544 | 0 | N/A | 0 | 0
2021-11-26 03:00 | 3.5 | 0 | N/A | 0 | 0
2021-11-26 03:30 | 3.1929 | 0 | N/A | 0 | 0
2021-11-26 04:00 | 2.947 | 0 | N/A | 0 | 0
2021-11-26 04:30 | 2.9266 | 0 | N/A | 0 | 0
2021-11-26 05:00 | 2.9795 | 0 | N/A | 0 | 0
2021-11-26 05:30 | 3.251 | 0 | N/A | 0 | 0
2021-11-26 06:00 | 3.4942 | 0 | N/A | 0 | 0
2021-11-26 06:30 | 4.4 | 0 | N/A | 0 | 0
2021-11-26 07:00 | 5.4758 | 0 | N/A | 0 | 0
2021-11-26 07:30 | 6.3208 | 0 | N/A | 0 | 0
2021-11-26 08:00 | 6.3747 | 0 | N/A | 0 | 0
2021-11-26 08:30 | 5.8529 | 0 | N/A | 0 | 0
2021-11-26 09:00 | 5.6524 | 0 | N/A | 0 | 0
2021-11-26 09:30 | 5.2228 | 0 | N/A | 0 | 0
2021-11-26 10:00 | 4.8833 | 0 | N/A | 0 | 0
2021-11-26 10:30 | 4.7732 | 0 | N/A | 0 | 0
2021-11-26 11:00 | 4.5189 | 0 | N/A | 0 | 0
2021-11-26 11:30 | 4.4937 | 0 | N/A | 0 | 0
2021-11-26 12:00 | 3.8958 | 0 | N/A | 0 | 0
2021-11-26 12:30 | 3.7286 | 0 | N/A | 0 | 0
2021-11-26 13:00 | 2.9364 | 0 | N/A | 0 | 0
2021-11-26 13:30 | 2.2587 | 0 | N/A | 0 | 0
2021-11-26 14:00 | 1.6187 | 0 | N/A | 0 | 0
2021-11-26 14:30 | 2.3564 | 0 | N/A | 0 | 0
2021-11-26 15:00 | 2.6585 | 0 | N/A | 0 | 0
2021-11-26 15:30 | 1.4881 | 0 | N/A | 0 | 0
2021-11-26 16:00 | 1.7121 | 0 | N/A | 0 | 0
2021-11-26 16:30 | 1.9698 | 0 | N/A | 0 | 0
2021-11-26 17:00 | 2.122 | 0 | N/A | 0 | 0
2021-11-26 17:30 | 2.4149 | 0 | N/A | 0 | 0
2021-11-26 18:00 | 3.7187 | 0 | N/A | 0 | 0
2021-11-26 18:30 | 4.6116 | 0 | N/A | 0 | 0
2021-11-26 19:00 | 4.9109 | 0 | N/A | 0 | 0
2021-11-26 19:30 | 5.1064 | 0 | N/A | 0 | 0
2021-11-26 20:00 | 5.3388 | 0 | N/A | 0 | 0
2021-11-26 20:30 | 5.5023 | 0 | N/A | 0 | 0
2021-11-26 21:00 | 5.5183 | 0 | N/A | 0 | 0
2021-11-26 21:30 | 5.2907 | 0 | N/A | 0 | 0
2021-11-26 22:00 | 4.9731 | 0 | N/A | 0 | 0
2021-11-26 22:30 | 5.1584 | 0 | N/A | 0 | 0
2021-11-26 23:00 | 5.3167 | 0 | N/A | 0 | 0
2021-11-26 23:30 | 5.028 | 0 | N/A | 0 | 0
2021-11-27 | 5.0186 | 0 | N/A | 0 | 0
2021-11-27 00:30 | 5.3485 | 0 | N/A | 0 | 0
2021-11-27 01:00 | 5.5699 | 0 | N/A | 0 | 0
2021-11-27 01:30 | 4.8884 | 0 | N/A | 0 | 0
2021-11-27 02:00 | 4.1862 | 0 | N/A | 0 | 0
2021-11-27 02:30 | 4.0358 | 0 | N/A | 0 | 0
2021-11-27 03:00 | 3.728 | 0 | N/A | 0 | 0
2021-11-27 03:30 | 3.3205 | 0 | N/A | 0 | 0
2021-11-27 04:00 | 3.1082 | 0 | N/A | 0 | 0
2021-11-27 04:30 | 3.0493 | 0 | N/A | 0 | 0
2021-11-27 05:00 | 2.9699 | 0 | N/A | 0 | 0
2021-11-27 05:30 | 3.1607 | 0 | N/A | 0 | 0
2021-11-27 06:00 | 3.3068 | 0 | N/A | 0 | 0
2021-11-27 06:30 | 3.5807 | 0 | N/A | 0 | 0
2021-11-27 07:00 | 3.6338 | 0 | N/A | 0 | 0
2021-11-27 07:30 | 3.8205 | 0 | N/A | 0 | 0
2021-11-27 08:00 | 3.7155 | 0 | N/A | 0 | 0
2021-11-27 08:30 | 3.0341 | 0 | N/A | 0 | 0
2021-11-27 09:00 | 2.7547 | 0 | N/A | 0 | 0
2021-11-27 09:30 | 2.5214 | 0 | N/A | 0 | 0
2021-11-27 10:00 | 2.318 | 0 | N/A | 0 | 0
2021-11-27 10:30 | 1.5298 | 0 | N/A | 0 | 0
2021-11-27 11:00 | 1.2577 | 0 | N/A | 0 | 0
2021-11-27 11:30 | 0.70206 | 0 | N/A | 0 | 0
2021-11-27 12:00 | -0.61718 | 0 | N/A | 0 | 0
2021-11-27 12:30 | -0.60832 | 0 | N/A | 0 | 0
2021-11-27 13:00 | -0.76369 | 0 | N/A | 0 | 0
2021-11-27 13:30 | -0.89706 | 0 | N/A | 0 | 0
2021-11-27 14:00 | -1.43 | 0 | N/A | 0 | 0
2021-11-27 14:30 | -1.746 | 0 | N/A | 0 | 0
2021-11-27 15:00 | -1.8115 | 0 | N/A | 0 | 0
2021-11-27 15:30 | -1.5959 | 0 | N/A | 0 | 0
2021-11-27 16:00 | -1.0306 | 0 | N/A | 0 | 0
2021-11-27 16:30 | -0.82492 | 0 | N/A | 0 | 0
2021-11-27 17:00 | 1.3248 | 0 | N/A | 0 | 0
2021-11-27 17:30 | 2.2926 | 0 | N/A | 0 | 0
2021-11-27 18:00 | 3.1159 | 0 | N/A | 0 | 0
2021-11-27 18:30 | 3.4148 | 0 | N/A | 0 | 0
2021-11-27 19:00 | 3.9883 | 0 | N/A | 0 | 0
2021-11-27 19:30 | 4.29 | 0 | N/A | 0 | 0
2021-11-27 20:00 | 4.3241 | 0 | N/A | 0 | 0
2021-11-27 20:30 | 4.4167 | 0 | N/A | 0 | 0
2021-11-27 21:00 | 4.5595 | 0 | N/A | 0 | 0
2021-11-27 21:30 | 4.5977 | 0 | N/A | 0 | 0
2021-11-27 22:00 | 4.4048 | 0 | N/A | 0 | 0
2021-11-27 22:30 | 4.6983 | 0 | N/A | 0 | 0
2021-11-27 23:00 | 4.8732 | 0 | N/A | 0 | 0
2021-11-27 23:30 | 4.6107 | 0 | N/A | 0 | 0
2021-11-28 | 4.6383 | 0 | N/A | 0 | 0
2021-11-28 00:30 | 4.9951 | 0 | N/A | 0 | 0
2021-11-28 01:00 | 5.2298 | 0 | N/A | 0 | 0
2021-11-28 01:30 | 4.488 | 0 | N/A | 0 | 0
2021-11-28 02:00 | 3.8802 | 0 | N/A | 0 | 0
2021-11-28 02:30 | 3.848 | 0 | N/A | 0 | 0
2021-11-28 03:00 | 3.4562 | 0 | N/A | 0 | 0
2021-11-28 03:30 | 2.9773 | 0 | N/A | 0 | 0
2021-11-28 04:00 | 2.7693 | 0 | N/A | 0 | 0
2021-11-28 04:30 | 2.7361 | 0 | N/A | 0 | 0
2021-11-28 05:00 | 2.6525 | 0 | N/A | 0 | 0
2021-11-28 05:30 | 2.712 | 0 | N/A | 0 | 0
2021-11-28 06:00 | 2.7741 | 0 | N/A | 0 | 0
2021-11-28 06:30 | 2.9693 | 0 | N/A | 0 | 0
2021-11-28 07:00 | 2.9124 | 0 | N/A | 0 | 0
2021-11-28 07:30 | 2.9514 | 0 | N/A | 0 | 0
2021-11-28 08:00 | 2.67 | 0 | N/A | 0 | 0
2021-11-28 08:30 | 2.002 | 0 | N/A | 0 | 0
2021-11-28 09:00 | 1.4968 | 0 | N/A | 0 | 0
2021-11-28 09:30 | 0.97713 | 0 | N/A | 0 | 0
2021-11-28 10:00 | 0.63814 | 0 | N/A | 0 | 0
2021-11-28 10:30 | -0.71005 | 0 | N/A | 0 | 0
2021-11-28 11:00 | -1.027 | 0 | N/A | 0 | 0
2021-11-28 11:30 | -1.3924 | 0 | N/A | 0 | 0
2021-11-28 12:00 | -1.5939 | 0 | N/A | 0 | 0
2021-11-28 12:30 | -1.8062 | 0 | N/A | 0 | 0
2021-11-28 13:00 | -1.9615 | 0 | N/A | 0 | 0
2021-11-28 13:30 | -2.0999 | 0 | N/A | 0 | 0
2021-11-28 14:00 | -2.2525 | 0 | N/A | 0 | 0
2021-11-28 14:30 | -2.2691 | 0 | N/A | 0 | 0
2021-11-28 15:00 | -2.1652 | 0 | N/A | 0 | 0
2021-11-28 15:30 | -2.0511 | 0 | N/A | 0 | 0
2021-11-28 16:00 | -1.7572 | 0 | N/A | 0 | 0
2021-11-28 16:30 | -1.2643 | 0 | N/A | 0 | 0
2021-11-28 17:00 | -0.7663 | 0 | N/A | 0 | 0
2021-11-28 17:30 | 0.943 | 0 | N/A | 0 | 0
2021-11-28 18:00 | 1.7307 | 0 | N/A | 0 | 0
2021-11-28 18:30 | 2.5805 | 0 | N/A | 0 | 0
2021-11-28 19:00 | 3.3195 | 0 | N/A | 0 | 0
2021-11-28 19:30 | 3.735 | 0 | N/A | 0 | 0
2021-11-28 20:00 | 3.9606 | 0 | N/A | 0 | 0
2021-11-28 20:30 | 4.1118 | 0 | N/A | 0 | 0
2021-11-28 21:00 | 4.2654 | 0 | N/A | 0 | 0
2021-11-28 21:30 | 4.1522 | 0 | N/A | 0 | 0
2021-11-28 22:00 | 3.9202 | 0 | N/A | 0 | 0
2021-11-28 22:30 | 4.1223 | 0 | N/A | 0 | 0
2021-11-28 23:00 | 4.2566 | 0 | N/A | 0 | 0
2021-11-28 23:30 | 3.9884 | 0 | N/A | 0 | 0
2021-11-29 | 4.0731 | 0 | N/A | 0 | 0
2021-11-29 00:30 | 4.2775 | 0 | N/A | 0 | 0
2021-11-29 01:00 | 4.7266 | 0 | N/A | 0 | 0
2021-11-29 01:30 | 4.1194 | 0 | N/A | 0 | 0
2021-11-29 02:00 | 3.5151 | 0 | N/A | 0 | 0
2021-11-29 02:30 | 3.4747 | 0 | N/A | 0 | 0
2021-11-29 03:00 | 3.1784 | 0 | N/A | 0 | 0
2021-11-29 03:30 | 2.7496 | 0 | N/A | 0 | 0
2021-11-29 04:00 | 2.4925 | 0 | N/A | 0 | 0
2021-11-29 04:30 | 2.5372 | 0 | N/A | 0 | 0
2021-11-29 05:00 | 2.4999 | 0 | N/A | 0 | 0
2021-11-29 05:30 | 2.6519 | 0 | N/A | 0 | 0
2021-11-29 06:00 | 3.0353 | 0 | N/A | 0 | 0
2021-11-29 06:30 | 3.722 | 0 | N/A | 0 | 0
2021-11-29 07:00 | 4.4093 | 0 | N/A | 0 | 0
2021-11-29 07:30 | 4.9477 | 0 | N/A | 0 | 0
2021-11-29 08:00 | 4.636 | 0 | N/A | 0 | 0
2021-11-29 08:30 | 3.395 | 0 | N/A | 0 | 0
2021-11-29 09:00 | 2.5468 | 0 | N/A | 0 | 0
2021-11-29 09:30 | 1.6133 | 0 | N/A | 0 | 0
2021-11-29 10:00 | 0.83091 | 0 | N/A | 0 | 0
2021-11-29 10:30 | 0.099107 | 0 | N/A | 0 | 0
2021-11-29 11:00 | -0.66098 | 0 | N/A | 0 | 0
2021-11-29 11:30 | -0.6703 | 0 | N/A | 0 | 0
2021-11-29 12:00 | -0.76667 | 0 | N/A | 0 | 0
2021-11-29 12:30 | -0.8 | 0 | N/A | 0 | 0
2021-11-29 13:00 | -0.72 | 0 | N/A | 0 | 0
2021-11-29 13:30 | -1.06 | 0 | N/A | 0 | 0
2021-11-29 14:00 | -1.0846 | 0 | N/A | 0 | 0
2021-11-29 14:30 | -0.79359 | 0 | N/A | 0 | 0
2021-11-29 15:00 | -0.52971 | 0 | N/A | 0 | 0
2021-11-29 15:30 | -0.31045 | 0 | N/A | 0 | 0
2021-11-29 16:00 | 0.19633 | 0 | N/A | 0 | 0
2021-11-29 16:30 | 0.36603 | 0 | N/A | 0 | 0
2021-11-29 17:00 | 0.71558 | 0 | N/A | 0 | 0
2021-11-29 17:30 | 1.7366 | 0 | N/A | 0 | 0
2021-11-29 18:00 | 2.7549 | 0 | N/A | 0 | 0
2021-11-29 18:30 | 3.4507 | 0 | N/A | 0 | 0
2021-11-29 19:00 | 4.0027 | 0 | N/A | 0 | 0
2021-11-29 19:30 | 4.3148 | 0 | N/A | 0 | 0
2021-11-29 20:00 | 4.501 | 0 | N/A | 0 | 0
2021-11-29 20:30 | 4.3966 | 0 | N/A | 0 | 0
2021-11-29 21:00 | 4.339 | 0 | N/A | 0 | 0
2021-11-29 21:30 | 4.1423 | 0 | N/A | 0 | 0
2021-11-29 22:00 | 3.8256 | 0 | N/A | 0 | 0
2021-11-29 22:30 | 4.0298 | 0 | N/A | 0 | 0
2021-11-29 23:00 | 4.1577 | 0 | N/A | 0 | 0
2021-11-29 23:30 | 3.908 | 0 | N/A | 0 | 0
2021-11-30 | 3.9493 | 0 | N/A | 0 | 0
2021-12-01 00:30 | 4.3663 | 0 | N/A | 0 | 0
2021-12-01 01:00 | 4.5741 | 0 | N/A | 0 | 0
2021-12-01 01:30 | 3.7779 | 0 | N/A | 0 | 0
2021-12-01 02:00 | 3.124 | 0 | N/A | 0 | 0
2021-12-01 02:30 | 3.0488 | 0 | N/A | 0 | 0
2021-12-01 03:00 | 2.7849 | 0 | N/A | 0 | 0
2021-12-01 03:30 | 2.476 | 0 | N/A | 0 | 0
2021-12-01 04:00 | 2.3775 | 0 | N/A | 0 | 0
2021-12-01 04:30 | 2.3181 | 0 | N/A | 0 | 0
2021-12-01 05:00 | 2.3468 | 0 | N/A | 0 | 0
2021-12-01 05:30 | 2.5707 | 0 | N/A | 0 | 0
2021-12-01 06:00 | 2.7488 | 0 | N/A | 0 | 0
2021-12-01 06:30 | 3.2212 | 0 | N/A | 0 | 0
2021-12-01 07:00 | 3.497 | 0 | N/A | 0 | 0
2021-12-01 07:30 | 4.3013 | 0 | N/A | 0 | 0
2021-12-01 08:00 | 4.1351 | 0 | N/A | 0 | 0
2021-12-01 08:30 | 3.2975 | 0 | N/A | 0 | 0
2021-12-01 09:00 | 2.6835 | 0 | N/A | 0 | 0
2021-12-01 09:30 | 2.0414 | 0 | N/A | 0 | 0
2021-12-01 10:00 | 1.4112 | 0 | N/A | 0 | 0
2021-12-01 10:30 | 1.8455 | 0 | N/A | 0 | 0
2021-12-01 11:00 | 1.467 | 0 | N/A | 0 | 0
2021-12-01 11:30 | 1.2675 | 0 | N/A | 0 | 0
2021-12-01 12:00 | 1.7334 | 0 | N/A | 0 | 0
2021-12-01 12:30 | 2.0601 | 0 | N/A | 0 | 0
2021-12-01 13:00 | 2.1534 | 0 | N/A | 0 | 0
2021-12-01 13:30 | 1.755 | 0 | N/A | 0 | 0
2021-12-01 14:00 | 1.3024 | 0 | N/A | 0 | 0
2021-12-01 14:30 | 1.2754 | 0 | N/A | 0 | 0
2021-12-01 15:00 | 2.113 | 0 | N/A | 0 | 0
2021-12-01 15:30 | 1.9624 | 0 | N/A | 0 | 0
2021-12-01 16:00 | 2.8876 | 0 | N/A | 0 | 0
2021-12-01 16:30 | 2.3156 | 0 | N/A | 0 | 0
2021-12-01 17:00 | 3.3177 | 0 | N/A | 0 | 0
2021-12-01 17:30 | 4.6702 | 0 | N/A | 0 | 0
2021-12-01 18:00 | 5.6033 | 0 | N/A | 0 | 0
2021-12-01 18:30 | 5.2201 | 0 | N/A | 0 | 0
2021-12-01 19:00 | 5.8309 | 0 | N/A | 0 | 0
2021-12-01 19:30 | 5.478 | 0 | N/A | 0 | 0
2021-12-01 20:00 | 4.8631 | 0 | N/A | 0 | 0
2021-12-01 20:30 | 5.04 | 0 | N/A | 0 | 0
2021-12-01 21:00 | 5.0396 | 0 | N/A | 0 | 0
2021-12-01 21:30 | 4.8501 | 0 | N/A | 0 | 0
2021-12-01 22:00 | 4.3748 | 0 | N/A | 0 | 0
2021-12-01 22:30 | 4.5488 | 0 | N/A | 0 | 0
2021-12-01 23:00 | 4.4928 | 0 | N/A | 0 | 0
2021-12-01 23:30 | 4.1484 | 0 | N/A | 0 | 0
2021-12-02 | 4.1335 | 0 | N/A | 0 | 0
2021-12-02 00:30 | 4.4343 | 0 | N/A | 0 | 0
2021-12-02 01:00 | 4.6574 | 0 | N/A | 0 | 0
2021-12-02 01:30 | 3.7729 | 0 | N/A | 0 | 0
2021-12-02 02:00 | 3.1424 | 0 | N/A | 0 | 0
2021-12-02 02:30 | 3.0842 | 0 | N/A | 0 | 0
2021-12-02 03:00 | 2.7322 | 0 | N/A | 0 | 0
2021-12-02 03:30 | 2.5098 | 0 | N/A | 0 | 0
2021-12-02 04:00 | 2.3993 | 0 | N/A | 0 | 0
2021-12-02 04:30 | 2.333 | 0 | N/A | 0 | 0
2021-12-02 05:00 | 2.3367 | 0 | N/A | 0 | 0
2021-12-02 05:30 | 2.5242 | 0 | N/A | 0 | 0
2021-12-02 06:00 | 2.7829 | 0 | N/A | 0 | 0
2021-12-02 06:30 | 3.1378 | 0 | N/A | 0 | 0
2021-12-02 07:00 | 3.8273 | 0 | N/A | 0 | 0
2021-12-02 07:30 | 4.3569 | 0 | N/A | 0 | 0
2021-12-02 08:00 | 4.0994 | 0 | N/A | 0 | 0
2021-12-02 08:30 | 3.3364 | 0 | N/A | 0 | 0
2021-12-02 09:00 | 2.4873 | 0 | N/A | 0 | 0
2021-12-02 09:30 | 1.8317 | 0 | N/A | 0 | 0
2021-12-02 10:00 | 1.5576 | 0 | N/A | 0 | 0
2021-12-02 10:30 | 1.4576 | 0 | N/A | 0 | 0
2021-12-02 11:00 | 0.98672 | 0 | N/A | 0 | 0
2021-12-02 11:30 | 0.95 | 0 | N/A | 0 | 0
2021-12-02 12:00 | 0.52941 | 0 | N/A | 0 | 0
2021-12-02 12:30 | 0.38651 | 0 | N/A | 0 | 0
2021-12-02 13:00 | 1.0697 | 0 | N/A | 0 | 0
2021-12-02 13:30 | 1.9333 | 0 | N/A | 0 | 0
2021-12-02 14:00 | 1.629 | 0 | N/A | 0 | 0
2021-12-02 14:30 | 1.9388 | 0 | N/A | 0 | 0
2021-12-02 15:00 | 1.9397 | 0 | N/A | 0 | 0
2021-12-02 15:30 | 1.5101 | 0 | N/A | 0 | 0
2021-12-02 16:00 | 3.4869 | 0 | N/A | 0 | 0
2021-12-02 16:30 | 2.5967 | 0 | N/A | 0 | 0
2021-12-02 17:00 | 2.4134 | 0 | N/A | 0 | 0
2021-12-02 17:30 | 1.8133 | 0 | N/A | 0 | 0
2021-12-02 18:00 | 2.9146 | 0 | N/A | 0 | 0
2021-12-02 18:30 | 4.2748 | 0 | N/A | 0 | 0
2021-12-02 19:00 | 4.8195 | 0 | N/A | 0 | 0
2021-12-02 19:30 | 4.5842 | 0 | N/A | 0 | 0
2021-12-02 20:00 | 4.3569 | 0 | N/A | 0 | 0
2021-12-02 20:30 | 4.0992 | 0 | N/A | 0 | 0
2021-12-02 21:00 | 4.0212 | 0 | N/A | 0 | 0
2021-12-02 21:30 | 3.8154 | 0 | N/A | 0 | 0
2021-12-02 22:00 | 3.5199 | 0 | N/A | 0 | 0
2021-12-02 22:30 | 3.7888 | 0 | N/A | 0 | 0
2021-12-02 23:00 | 3.8227 | 0 | N/A | 0 | 0
2021-12-02 23:30 | 3.4901 | 0 | N/A | 0 | 0
2021-12-03 | 3.5208 | 0 | N/A | 0 | 0
2021-12-03 00:30 | 3.9716 | 0 | N/A | 0 | 0
2021-12-03 01:00 | 4.2649 | 0 | N/A | 0 | 0
2021-12-03 01:30 | 3.4012 | 0 | N/A | 0 | 0
2021-12-03 02:00 | 2.8237 | 0 | N/A | 0 | 0
2021-12-03 02:30 | 2.7357 | 0 | N/A | 0 | 0
2021-12-03 03:00 | 2.5233 | 0 | N/A | 0 | 0
2021-12-03 03:30 | 2.2614 | 0 | N/A | 0 | 0
2021-12-03 04:00 | 2.133 | 0 | N/A | 0 | 0
2021-12-03 04:30 | 2.1826 | 0 | N/A | 0 | 0
2021-12-03 05:00 | 2.186 | 0 | N/A | 0 | 0
2021-12-03 05:30 | 2.3946 | 0 | N/A | 0 | 0
2021-12-03 06:00 | 2.5846 | 0 | N/A | 0 | 0
2021-12-03 06:30 | 3.4109 | 0 | N/A | 0 | 0
2021-12-03 07:00 | 3.8541 | 0 | N/A | 0 | 0
2021-12-03 07:30 | 4.1025 | 0 | N/A | 0 | 0
2021-12-03 08:00 | 3.857 | 0 | N/A | 0 | 0
2021-12-03 08:30 | 2.7956 | 0 | N/A | 0 | 0
2021-12-03 09:00 | 1.9266 | 0 | N/A | 0 | 0
2021-12-03 09:30 | 1.0554 | 0 | N/A | 0 | 0
2021-12-03 10:00 | 0.5894 | 0 | N/A | 0 | 0
2021-12-03 10:30 | -0.34359 | 0 | N/A | 0 | 0
2021-12-03 11:00 | 0.61569 | 0 | N/A | 0 | 0
2021-12-03 11:30 | 0.7385 | 0 | N/A | 0 | 0
2021-12-03 12:00 | -0.23646 | 0 | N/A | 0 | 0
2021-12-03 12:30 | -0.41667 | 0 | N/A | 0 | 0
2021-12-03 13:00 | -0.77489 | 0 | N/A | 0 | 0
2021-12-03 13:30 | -1.0156 | 0 | N/A | 0 | 0
2021-12-03 14:00 | -1.3324 | 0 | N/A | 0 | 0
2021-12-03 14:30 | -1.3049 | 0 | N/A | 0 | 0
2021-12-03 15:00 | -1.2859 | 0 | N/A | 0 | 0
2021-12-03 15:30 | -1.626 | 0 | N/A | 0 | 0
2021-12-03 16:00 | -1.5684 | 0 | N/A | 0 | 0
2021-12-03 16:30 | -1.0517 | 0 | N/A | 0 | 0
2021-12-03 17:00 | -0.48029 | 0 | N/A | 0 | 0
2021-12-03 17:30 | 0.75499 | 0 | N/A | 0 | 0
2021-12-03 18:00 | 1.5197 | 0 | N/A | 0 | 0
2021-12-03 18:30 | 2.3551 | 0 | N/A | 0 | 0
2021-12-03 19:00 | 2.6194 | 0 | N/A | 0 | 0
2021-12-03 19:30 | 3.1643 | 0 | N/A | 0 | 0
2021-12-03 20:00 | 3.6153 | 0 | N/A | 0 | 0
2021-12-03 20:30 | 3.9096 | 0 | N/A | 0 | 0
2021-12-03 21:00 | 4.1008 | 0 | N/A | 0 | 0
2021-12-03 21:30 | 4.1257 | 0 | N/A | 0 | 0
2021-12-03 22:00 | 3.9496 | 0 | N/A | 0 | 0
2021-12-03 22:30 | 4.352 | 0 | N/A | 0 | 0
2021-12-03 23:00 | 4.51 | 0 | N/A | 0 | 0
2021-12-03 23:30 | 4.3067 | 0 | N/A | 0 | 0
2021-12-04 | 4.2237 | 0 | N/A | 0 | 0
2021-12-04 00:30 | 4.6283 | 0 | N/A | 0 | 0
2021-12-04 01:00 | 4.8952 | 0 | N/A | 0 | 0
2021-12-04 01:30 | 4.0103 | 0 | N/A | 0 | 0
2021-12-04 02:00 | 3.3252 | 0 | N/A | 0 | 0
2021-12-04 02:30 | 3.2899 | 0 | N/A | 0 | 0
2021-12-04 03:00 | 3.0073 | 0 | N/A | 0 | 0
2021-12-04 03:30 | 2.7159 | 0 | N/A | 0 | 0
2021-12-04 04:00 | 2.4956 | 0 | N/A | 0 | 0
2021-12-04 04:30 | 2.4329 | 0 | N/A | 0 | 0
2021-12-04 05:00 | 2.4018 | 0 | N/A | 0 | 0
2021-12-04 05:30 | 2.4269 | 0 | N/A | 0 | 0
2021-12-04 06:00 | 2.4779 | 0 | N/A | 0 | 0
2021-12-04 06:30 | 2.7056 | 0 | N/A | 0 | 0
2021-12-04 07:00 | 2.796 | 0 | N/A | 0 | 0
2021-12-04 07:30 | 2.9674 | 0 | N/A | 0 | 0
2021-12-04 08:00 | 3.006 | 0 | N/A | 0 | 0
2021-12-04 08:30 | 2.4231 | 0 | N/A | 0 | 0
2021-12-04 09:00 | 2.1094 | 0 | N/A | 0 | 0
2021-12-04 09:30 | 2.2713 | 0 | N/A | 0 | 0
2021-12-04 10:00 | 2.1635 | 0 | N/A | 0 | 0
2021-12-04 10:30 | 1.3518 | 0 | N/A | 0 | 0
2021-12-04 11:00 | 1.7747 | 0 | N/A | 0 | 0
2021-12-04 11:30 | 1.4603 | 0 | N/A | 0 | 0
2021-12-04 12:00 | 1.4826 | 0 | N/A | 0 | 0
2021-12-04 12:30 | 0.82043 | 0 | N/A | 0 | 0
2021-12-04 13:00 | 1.2409 | 0 | N/A | 0 | 0
2021-12-04 13:30 | 0.73961 | 0 | N/A | 0 | 0
2021-12-04 14:00 | 0.76847 | 0 | N/A | 0 | 0
2021-12-04 14:30 | 0.84675 | 0 | N/A | 0 | 0
2021-12-04 15:00 | 0.79349 | 0 | N/A | 0 | 0
2021-12-04 15:30 | 0.88275 | 0 | N/A | 0 | 0
2021-12-04 16:00 | 1.2422 | 0 | N/A | 0 | 0
2021-12-04 16:30 | 1.0427 | 0 | N/A | 0 | 0
2021-12-04 17:00 | 1.4342 | 0 | N/A | 0 | 0
2021-12-04 17:30 | 2.0192 | 0 | N/A | 0 | 0
2021-12-04 18:00 | 1.9543 | 0 | N/A | 0 | 0
2021-12-04 18:30 | 2.6959 | 0 | N/A | 0 | 0
2021-12-04 19:00 | 3.5831 | 0 | N/A | 0 | 0
2021-12-04 19:30 | 3.7449 | 0 | N/A | 0 | 0
2021-12-04 20:00 | 3.8966 | 0 | N/A | 0 | 0
2021-12-04 20:30 | 4.1451 | 0 | N/A | 0 | 0
2021-12-04 21:00 | 4.2254 | 0 | N/A | 0 | 0
2021-12-04 21:30 | 4.2016 | 0 | N/A | 0 | 0
2021-12-04 22:00 | 4.0147 | 0 | N/A | 0 | 0
2021-12-04 22:30 | 4.4447 | 0 | N/A | 0 | 0
2021-12-04 23:00 | 4.6061 | 0 | N/A | 0 | 0
2021-12-04 23:30 | 4.3531 | 0 | N/A | 0 | 0
2021-12-05 | 4.4355 | 0 | N/A | 0 | 0
2021-12-05 00:30 | 4.7702 | 0 | N/A | 0 | 0
2021-12-05 01:00 | 5.047 | 0 | N/A | 0 | 0
2021-12-05 01:30 | 4.3166 | 0 | N/A | 0 | 0
2021-12-05 02:00 | 3.5976 | 0 | N/A | 0 | 0
2021-12-05 02:30 | 3.5381 | 0 | N/A | 0 | 0
2021-12-05 03:00 | 3.2628 | 0 | N/A | 0 | 0
2021-12-05 03:30 | 2.8556 | 0 | N/A | 0 | 0
2021-12-05 04:00 | 2.6533 | 0 | N/A | 0 | 0
2021-12-05 04:30 | 2.5525 | 0 | N/A | 0 | 0
2021-12-05 05:00 | 2.5478 | 0 | N/A | 0 | 0
2021-12-05 05:30 | 2.6268 | 0 | N/A | 0 | 0
2021-12-05 06:00 | 2.7237 | 0 | N/A | 0 | 0
2021-12-05 06:30 | 2.9418 | 0 | N/A | 0 | 0
2021-12-05 07:00 | 2.8662 | 0 | N/A | 0 | 0
2021-12-05 07:30 | 2.8521 | 0 | N/A | 0 | 0
2021-12-05 08:00 | 2.5672 | 0 | N/A | 0 | 0
2021-12-05 08:30 | 2.3283 | 0 | N/A | 0 | 0
2021-12-05 09:00 | 1.7395 | 0 | N/A | 0 | 0
2021-12-05 09:30 | 1.2092 | 0 | N/A | 0 | 0
2021-12-05 10:00 | 0.96984 | 0 | N/A | 0 | 0
2021-12-05 10:30 | -0.70872 | 0 | N/A | 0 | 0
2021-12-05 11:00 | -1.1062 | 0 | N/A | 0 | 0
2021-12-05 11:30 | -1.3946 | 0 | N/A | 0 | 0
2021-12-05 12:00 | -1.6616 | 0 | N/A | 0 | 0
2021-12-05 12:30 | -1.8863 | 0 | N/A | 0 | 0
2021-12-05 13:00 | -1.9773 | 0 | N/A | 0 | 0
2021-12-05 13:30 | -2.0763 | 0 | N/A | 0 | 0
2021-12-05 14:00 | -2.1286 | 0 | N/A | 0 | 0
2021-12-05 14:30 | -2.1202 | 0 | N/A | 0 | 0
2021-12-05 15:00 | -2.0579 | 0 | N/A | 0 | 0
2021-12-05 15:30 | -1.9129 | 0 | N/A | 0 | 0
2021-12-05 16:00 | -1.5903 | 0 | N/A | 0 | 0
2021-12-05 16:30 | -1.1198 | 0 | N/A | 0 | 0
2021-12-05 17:00 | -0.65869 | 0 | N/A | 0 | 0
2021-12-05 17:30 | 0.74533 | 0 | N/A | 0 | 0
2021-12-05 18:00 | 1.5746 | 0 | N/A | 0 | 0
2021-12-05 18:30 | 2.4087 | 0 | N/A | 0 | 0
2021-12-05 19:00 | 3.0952 | 0 | N/A | 0 | 0
2021-12-05 19:30 | 3.6698 | 0 | N/A | 0 | 0
2021-12-05 20:00 | 3.9465 | 0 | N/A | 0 | 0
2021-12-05 20:30 | 4.0738 | 0 | N/A | 0 | 0
2021-12-05 21:00 | 4.1692 | 0 | N/A | 0 | 0
2021-12-05 21:30 | 4.2095 | 0 | N/A | 0 | 0
2021-12-05 22:00 | 4.0505 | 0 | N/A | 0 | 0
2021-12-05 22:30 | 4.1918 | 0 | N/A | 0 | 0
2021-12-05 23:00 | 4.3631 | 0 | N/A | 0 | 0
2021-12-05 23:30 | 4.0974 | 0 | N/A | 0 | 0
2021-12-06 | 4.1524 | 0 | N/A | 0 | 0
2021-12-08 00:30 | 4.8724 | 0 | N/A | 0 | 0
2021-12-08 01:00 | 5.2385 | 0 | N/A | 0 | 0
2021-12-08 01:30 | 4.4525 | 0 | N/A | 0 | 0
2021-12-08 02:00 | 3.6736 | 0 | N/A | 0 | 0
2021-12-08 02:30 | 3.5788 | 0 | N/A | 0 | 0
2021-12-08 03:00 | 3.4049 | 0 | N/A | 0 | 0
2021-12-08 03:30 | 3.0152 | 0 | N/A | 0 | 0
2021-12-08 04:00 | 2.7983 | 0 | N/A | 0 | 0
2021-12-08 04:30 | 2.7421 | 0 | N/A | 0 | 0
2021-12-08 05:00 | 2.7474 | 0 | N/A | 0 | 0
2021-12-08 05:30 | 3.0389 | 0 | N/A | 0 | 0
2021-12-08 06:00 | 3.3868 | 0 | N/A | 0 | 0
2021-12-08 06:30 | 3.9644 | 0 | N/A | 0 | 0
2021-12-08 07:00 | 4.7 | 0 | N/A | 0 | 0
2021-12-08 07:30 | 5.0817 | 0 | N/A | 0 | 0
2021-12-08 08:00 | 4.9055 | 0 | N/A | 0 | 0
2021-12-08 08:30 | 3.7847 | 0 | N/A | 0 | 0
2021-12-08 09:00 | 2.9806 | 0 | N/A | 0 | 0
2021-12-08 09:30 | 2.875 | 0 | N/A | 0 | 0
2021-12-08 10:00 | 2.0996 | 0 | N/A | 0 | 0
2021-12-08 10:30 | 2.0965 | 0 | N/A | 0 | 0
2021-12-08 11:00 | 2.2015 | 0 | N/A | 0 | 0
2021-12-08 11:30 | 2.3587 | 0 | N/A | 0 | 0
2021-12-08 12:00 | 1.6867 | 0 | N/A | 0 | 0
2021-12-08 12:30 | 1.1062 | 0 | N/A | 0 | 0
2021-12-08 13:00 | 1.5217 | 0 | N/A | 0 | 0
2021-12-08 13:30 | 2.2113 | 0 | N/A | 0 | 0
2021-12-08 14:00 | 1.3788 | 0 | N/A | 0 | 0
2021-12-08 14:30 | 2.9472 | 0 | N/A | 0 | 0
2021-12-08 15:00 | 3.1307 | 0 | N/A | 0 | 0
2021-12-08 15:30 | 3.3494 | 0 | N/A | 0 | 0
2021-12-08 16:00 | 3.1581 | 0 | N/A | 0 | 0
2021-12-08 16:30 | 3.4829 | 0 | N/A | 0 | 0
2021-12-08 17:00 | 3.1137 | 0 | N/A | 0 | 0
2021-12-08 17:30 | 3.3647 | 0 | N/A | 0 | 0
2021-12-08 18:00 | 4.4994 | 0 | N/A | 0 | 0
2021-12-08 18:30 | 5.7197 | 0 | N/A | 0 | 0
2021-12-08 19:00 | 6.1143 | 0 | N/A | 0 | 0
2021-12-08 19:30 | 6.159 | 0 | N/A | 0 | 0
2021-12-08 20:00 | 5.9747 | 0 | N/A | 0 | 0
2021-12-08 20:30 | 6.0101 | 0 | N/A | 0 | 0
2021-12-08 21:00 | 6.1985 | 0 | N/A | 0 | 0
2021-12-08 21:30 | 6.0057 | 0 | N/A | 0 | 0
2021-12-08 22:00 | 5.5441 | 0 | N/A | 0 | 0
2021-12-08 22:30 | 5.5946 | 0 | N/A | 0 | 0
2021-12-08 23:00 | 5.3918 | 0 | N/A | 0 | 0
2021-12-08 23:30 | 4.9253 | 0 | N/A | 0 | 0
2021-12-09 | 5.0207 | 0 | N/A | 0 | 0
2021-12-09 00:30 | 5.2116 | 0 | N/A | 0 | 0
2021-12-09 01:00 | 5.5273 | 0 | N/A | 0 | 0
2021-12-09 01:30 | 4.7421 | 0 | N/A | 0 | 0
2021-12-09 02:00 | 3.9994 | 0 | N/A | 0 | 0
2021-12-09 02:30 | 3.9399 | 0 | N/A | 0 | 0
2021-12-09 03:00 | 3.7451 | 0 | N/A | 0 | 0
2021-12-09 03:30 | 3.2689 | 0 | N/A | 0 | 0
2021-12-09 04:00 | 3.1119 | 0 | N/A | 0 | 0
2021-12-09 04:30 | 2.9674 | 0 | N/A | 0 | 0
2021-12-09 05:00 | 2.9786 | 0 | N/A | 0 | 0
2021-12-09 05:30 | 3.3143 | 0 | N/A | 0 | 0
2021-12-09 06:00 | 3.7431 | 0 | N/A | 0 | 0
2021-12-09 06:30 | 4.4817 | 0 | N/A | 0 | 0
2021-12-09 07:00 | 5.5755 | 0 | N/A | 0 | 0
2021-12-09 07:30 | 6.6844 | 0 | N/A | 0 | 0
2021-12-09 08:00 | 7.3392 | 0 | N/A | 0 | 0
2021-12-09 08:30 | 6.5251 | 0 | N/A | 0 | 0
2021-12-09 09:00 | 5.9389 | 0 | N/A | 0 | 0
2021-12-09 09:30 | 5.7598 | 0 | N/A | 0 | 0
2021-12-09 10:00 | 4.6029 | 0 | N/A | 0 | 0
2021-12-09 10:30 | 4.0896 | 0 | N/A | 0 | 0
2021-12-09 11:00 | 3.7265 | 0 | N/A | 0 | 0
2021-12-09 11:30 | 4.9584 | 0 | N/A | 0 | 0
2021-12-09 12:00 | 4.6835 | 0 | N/A | 0 | 0
2021-12-09 12:30 | 3.529 | 0 | N/A | 0 | 0
2021-12-09 13:00 | 2.7286 | 0 | N/A | 0 | 0
2021-12-09 13:30 | 2.5894 | 0 | N/A | 0 | 0
2021-12-09 14:00 | 3.0119 | 0 | N/A | 0 | 0
2021-12-09 14:30 | 2.395 | 0 | N/A | 0 | 0
2021-12-09 15:00 | 2.4572 | 0 | N/A | 0 | 0
2021-12-09 15:30 | 2.9275 | 0 | N/A | 0 | 0
2021-12-09 16:00 | 2.9019 | 0 | N/A | 0 | 0
2021-12-09 16:30 | 3.3897 | 0 | N/A | 0 | 0
2021-12-09 17:00 | 3.6117 | 0 | N/A | 0 | 0
2021-12-09 17:30 | 3.9272 | 0 | N/A | 0 | 0
2021-12-09 18:00 | 4.9927 | 0 | N/A | 0 | 0
2021-12-09 18:30 | 5.2209 | 0 | N/A | 0 | 0
2021-12-09 19:00 | 5.2906 | 0 | N/A | 0 | 0
2021-12-09 19:30 | 5.4888 | 0 | N/A | 0 | 0
2021-12-09 20:00 | 5.3438 | 0 | N/A | 0 | 0
2021-12-09 20:30 | 5.6102 | 0 | N/A | 0 | 0
2021-12-09 21:00 | 5.833 | 0 | N/A | 0 | 0
2021-12-09 21:30 | 5.7742 | 0 | N/A | 0 | 0
2021-12-09 22:00 | 5.4499 | 0 | N/A | 0 | 0
2021-12-09 22:30 | 5.4467 | 0 | N/A | 0 | 0
2021-12-09 23:00 | 5.3549 | 0 | N/A | 0 | 0
2021-12-09 23:30 | 4.8948 | 0 | N/A | 0 | 0
2021-12-10 | 4.9149 | 0 | N/A | 0 | 0
2021-12-11 00:30 | 5.1078 | 0 | N/A | 0 | 0
2021-12-11 01:00 | 5.3792 | 0 | N/A | 0 | 0
2021-12-11 01:30 | 4.6097 | 0 | N/A | 0 | 0
2021-12-11 02:00 | 3.7734 | 0 | N/A | 0 | 0
2021-12-11 02:30 | 3.7202 | 0 | N/A | 0 | 0
2021-12-11 03:00 | 3.4479 | 0 | N/A | 0 | 0
2021-12-11 03:30 | 3.1008 | 0 | N/A | 0 | 0
2021-12-11 04:00 | 2.8367 | 0 | N/A | 0 | 0
2021-12-11 04:30 | 2.7361 | 0 | N/A | 0 | 0
2021-12-11 05:00 | 2.7056 | 0 | N/A | 0 | 0
2021-12-11 05:30 | 2.8544 | 0 | N/A | 0 | 0
2021-12-11 06:00 | 2.9645 | 0 | N/A | 0 | 0
2021-12-11 06:30 | 3.1907 | 0 | N/A | 0 | 0
2021-12-11 07:00 | 3.2423 | 0 | N/A | 0 | 0
2021-12-11 07:30 | 3.2666 | 0 | N/A | 0 | 0
2021-12-11 08:00 | 3.4026 | 0 | N/A | 0 | 0
2021-12-11 08:30 | 3.1127 | 0 | N/A | 0 | 0
2021-12-11 09:00 | 2.6943 | 0 | N/A | 0 | 0
2021-12-11 09:30 | 2.3802 | 0 | N/A | 0 | 0
2021-12-12 00:30 | 4.6578 | 0 | N/A | 0 | 0
2021-12-12 01:00 | 5.0257 | 0 | N/A | 0 | 0
2021-12-12 01:30 | 4.2519 | 0 | N/A | 0 | 0
2021-12-12 02:00 | 3.5995 | 0 | N/A | 0 | 0
2021-12-12 02:30 | 3.4291 | 0 | N/A | 0 | 0
2021-12-12 03:00 | 3.1023 | 0 | N/A | 0 | 0
2021-12-12 03:30 | 2.7028 | 0 | N/A | 0 | 0
2021-12-12 04:00 | 2.4554 | 0 | N/A | 0 | 0
2021-12-12 04:30 | 2.403 | 0 | N/A | 0 | 0
2021-12-12 05:00 | 2.2937 | 0 | N/A | 0 | 0
2021-12-12 05:30 | 2.3573 | 0 | N/A | 0 | 0
2021-12-12 06:00 | 2.4314 | 0 | N/A | 0 | 0
2021-12-12 06:30 | 2.6247 | 0 | N/A | 0 | 0
2021-12-12 07:00 | 2.6195 | 0 | N/A | 0 | 0
2021-12-12 07:30 | 2.6312 | 0 | N/A | 0 | 0
2021-12-12 08:00 | 2.4209 | 0 | N/A | 0 | 0
2021-12-12 08:30 | 1.8892 | 0 | N/A | 0 | 0
2021-12-12 09:00 | 1.3687 | 0 | N/A | 0 | 0
2021-12-12 09:30 | 0.89134 | 0 | N/A | 0 | 0
2021-12-12 10:00 | -0.57009 | 0 | N/A | 0 | 0
2021-12-12 10:30 | -0.70239 | 0 | N/A | 0 | 0
2021-12-12 11:00 | -1.0439 | 0 | N/A | 0 | 0
2021-12-12 11:30 | -1.2892 | 0 | N/A | 0 | 0
2021-12-12 12:00 | -1.4651 | 0 | N/A | 0 | 0
2021-12-12 12:30 | -1.5428 | 0 | N/A | 0 | 0
2021-12-12 13:00 | -1.6106 | 0 | N/A | 0 | 0
2021-12-12 13:30 | -1.6848 | 0 | N/A | 0 | 0
2021-12-12 14:00 | -1.7514 | 0 | N/A | 0 | 0
2021-12-12 14:30 | -1.7291 | 0 | N/A | 0 | 0
2021-12-12 15:00 | -1.5832 | 0 | N/A | 0 | 0
2021-12-12 15:30 | -1.3121 | 0 | N/A | 0 | 0
2021-12-12 16:00 | -0.95094 | 0 | N/A | 0 | 0
2021-12-12 16:30 | -0.52116 | 0 | N/A | 0 | 0
2021-12-12 17:00 | 0.47202 | 0 | N/A | 0 | 0
2021-12-12 17:30 | 1.2649 | 0 | N/A | 0 | 0
2021-12-12 18:00 | 2.3398 | 0 | N/A | 0 | 0
2021-12-12 18:30 | 3.2912 | 0 | N/A | 0 | 0
2021-12-12 19:00 | 4.0254 | 0 | N/A | 0 | 0
2021-12-12 19:30 | 4.3942 | 0 | N/A | 0 | 0
2021-12-12 20:00 | 4.5595 | 0 | N/A | 0 | 0
2021-12-12 20:30 | 4.5729 | 0 | N/A | 0 | 0
2021-12-12 21:00 | 4.5815 | 0 | N/A | 0 | 0
2021-12-12 21:30 | 4.5131 | 0 | N/A | 0 | 0
2021-12-12 22:00 | 4.1556 | 0 | N/A | 0 | 0
2021-12-12 22:30 | 4.1773 | 0 | N/A | 0 | 0
2021-12-12 23:00 | 4.0831 | 0 | N/A | 0 | 0
2021-12-12 23:30 | 3.771 | 0 | N/A | 0 | 0
2021-12-13 | 3.9152 | 0 | N/A | 0 | 0
2021-12-13 00:30 | 4.2527 | 0 | N/A | 0 | 0
2021-12-13 01:00 | 4.5696 | 0 | N/A | 0 | 0
2021-12-13 01:30 | 3.8307 | 0 | N/A | 0 | 0
2021-12-13 02:00 | 3.1766 | 0 | N/A | 0 | 0
2021-12-13 02:30 | 3.0811 | 0 | N/A | 0 | 0
2021-12-13 03:00 | 2.7529 | 0 | N/A | 0 | 0
2021-12-13 03:30 | 2.4263 | 0 | N/A | 0 | 0
2021-12-13 04:00 | 2.2019 | 0 | N/A | 0 | 0
2021-12-13 04:30 | 2.2733 | 0 | N/A | 0 | 0
2021-12-13 05:00 | 2.254 | 0 | N/A | 0 | 0
2021-12-13 05:30 | 2.4117 | 0 | N/A | 0 | 0
2021-12-13 06:00 | 2.5887 | 0 | N/A | 0 | 0
2021-12-13 06:30 | 3.0004 | 0 | N/A | 0 | 0
2021-12-13 07:00 | 3.765 | 0 | N/A | 0 | 0
2021-12-13 07:30 | 3.739 | 0 | N/A | 0 | 0
2021-12-13 08:00 | 3.7765 | 0 | N/A | 0 | 0
2021-12-13 08:30 | 2.982 | 0 | N/A | 0 | 0
2021-12-13 09:00 | 2.6871 | 0 | N/A | 0 | 0
2021-12-13 09:30 | 2.3845 | 0 | N/A | 0 | 0
2021-12-13 10:00 | 1.9997 | 0 | N/A | 0 | 0
2021-12-13 10:30 | 2.08 | 0 | N/A | 0 | 0
2021-12-13 11:00 | 3.1519 | 0 | N/A | 0 | 0
2021-12-13 11:30 | 2.5324 | 0 | N/A | 0 | 0
2021-12-13 12:00 | 2.8242 | 0 | N/A | 0 | 0
2021-12-13 12:30 | 2.0714 | 0 | N/A | 0 | 0
2021-12-13 13:00 | 1.3267 | 0 | N/A | 0 | 0
2021-12-13 13:30 | 2.33 | 0 | N/A | 0 | 0
2021-12-13 14:00 | 1.78 | 0 | N/A | 0 | 0
2021-12-13 14:30 | 1.8602 | 0 | N/A | 0 | 0
2021-12-13 15:00 | 3.8401 | 0 | N/A | 0 | 0
2021-12-13 15:30 | 3.9367 | 0 | N/A | 0 | 0
2021-12-13 16:00 | 3.4605 | 0 | N/A | 0 | 0
2021-12-13 16:30 | 3.6043 | 0 | N/A | 0 | 0
2021-12-13 17:00 | 2.7033 | 0 | N/A | 0 | 0
2021-12-13 17:30 | 3.6234 | 0 | N/A | 0 | 0
2021-12-13 18:00 | 3.6191 | 0 | N/A | 0 | 0
2021-12-13 18:30 | 4.6053 | 0 | N/A | 0 | 0
2021-12-13 19:00 | 4.5377 | 0 | N/A | 0 | 0
2021-12-13 19:30 | 4.4728 | 0 | N/A | 0 | 0
2021-12-13 20:00 | 4.3364 | 0 | N/A | 0 | 0
2021-12-13 20:30 | 4.3023 | 0 | N/A | 0 | 0
2021-12-13 21:00 | 4.276 | 0 | N/A | 0 | 0
2021-12-13 21:30 | 4.1369 | 0 | N/A | 0 | 0
2021-12-13 22:00 | 3.8802 | 0 | N/A | 0 | 0
2021-12-13 22:30 | 4.1224 | 0 | N/A | 0 | 0
2021-12-13 23:00 | 4.2041 | 0 | N/A | 0 | 0
2021-12-13 23:30 | 3.8389 | 0 | N/A | 0 | 0
2021-12-14 | 3.8686 | 0 | N/A | 0 | 0
2021-12-15 00:30 | 4.3214 | 0 | N/A | 0 | 0
2021-12-15 01:00 | 4.4695 | 0 | N/A | 0 | 0
2021-12-15 01:30 | 3.691 | 0 | N/A | 0 | 0
2021-12-15 02:00 | 3.0126 | 0 | N/A | 0 | 0
2021-12-15 02:30 | 2.9051 | 0 | N/A | 0 | 0
2021-12-15 03:00 | 2.6548 | 0 | N/A | 0 | 0
2021-12-15 03:30 | 2.4136 | 0 | N/A | 0 | 0
2021-12-15 04:00 | 2.3315 | 0 | N/A | 0 | 0
2021-12-15 04:30 | 2.2885 | 0 | N/A | 0 | 0
2021-12-15 05:00 | 2.3211 | 0 | N/A | 0 | 0
2021-12-15 05:30 | 2.5093 | 0 | N/A | 0 | 0
2021-12-15 06:00 | 2.7149 | 0 | N/A | 0 | 0
2021-12-15 06:30 | 3.0405 | 0 | N/A | 0 | 0
2021-12-15 07:00 | 3.4703 | 0 | N/A | 0 | 0
2021-12-15 07:30 | 4.0872 | 0 | N/A | 0 | 0
2021-12-15 08:00 | 4.6929 | 0 | N/A | 0 | 0
2021-12-15 08:30 | 4.7137 | 0 | N/A | 0 | 0
2021-12-15 09:00 | 4.6264 | 0 | N/A | 0 | 0
2021-12-15 09:30 | 4.4092 | 0 | N/A | 0 | 0
2021-12-15 10:00 | 4.1862 | 0 | N/A | 0 | 0
2021-12-15 10:30 | 4.0885 | 0 | N/A | 0 | 0
2021-12-15 11:00 | 3.9542 | 0 | N/A | 0 | 0
2021-12-15 11:30 | 4.0359 | 0 | N/A | 0 | 0
2021-12-15 12:00 | 4.2704 | 0 | N/A | 0 | 0
2021-12-15 12:30 | 4.0994 | 0 | N/A | 0 | 0
2021-12-15 13:00 | 4.3666 | 0 | N/A | 0 | 0
2021-12-15 13:30 | 4.0783 | 0 | N/A | 0 | 0
2021-12-15 14:00 | 3.6898 | 0 | N/A | 0 | 0
2021-12-15 14:30 | 2.9033 | 0 | N/A | 0 | 0
2021-12-15 15:00 | 2.6041 | 0 | N/A | 0 | 0
2021-12-15 15:30 | 1.1954 | 0 | N/A | 0 | 0
2021-12-15 16:00 | 0.31202 | 0 | N/A | 0 | 0
2021-12-15 16:30 | 0.3406 | 0 | N/A | 0 | 0
2021-12-15 17:00 | -0.47143 | 0 | N/A | 0 | 0
2021-12-15 17:30 | 1.0839 | 0 | N/A | 0 | 0
2021-12-15 18:00 | 1.942 | 0 | N/A | 0 | 0
2021-12-15 18:30 | 2.3552 | 0 | N/A | 0 | 0
2021-12-15 19:00 | 2.7798 | 0 | N/A | 0 | 0
2021-12-15 19:30 | 3.2451 | 0 | N/A | 0 | 0
2021-12-15 20:00 | 3.7057 | 0 | N/A | 0 | 0
2021-12-15 20:30 | 3.9711 | 0 | N/A | 0 | 0
2021-12-15 21:00 | 4.1554 | 0 | N/A | 0 | 0
2021-12-15 21:30 | 4.2009 | 0 | N/A | 0 | 0
2021-12-15 22:00 | 4.1112 | 0 | N/A | 0 | 0
2021-12-15 22:30 | 4.3896 | 0 | N/A | 0 | 0
2021-12-15 23:00 | 4.5349 | 0 | N/A | 0 | 0
2021-12-15 23:30 | 4.2674 | 0 | N/A | 0 | 0
2021-12-16 | 4.2591 | 0 | N/A | 0 | 0
2021-12-16 00:30 | 4.5461 | 0 | N/A | 0 | 0
2021-12-16 01:00 | 4.957 | 0 | N/A | 0 | 0
2021-12-16 01:30 | 4.1815 | 0 | N/A | 0 | 0
2021-12-16 02:00 | 3.4737 | 0 | N/A | 0 | 0
2021-12-16 02:30 | 3.3331 | 0 | N/A | 0 | 0
2021-12-16 03:00 | 3.0512 | 0 | N/A | 0 | 0
2021-12-16 03:30 | 2.7898 | 0 | N/A | 0 | 0
2021-12-16 04:00 | 2.6398 | 0 | N/A | 0 | 0
2021-12-16 04:30 | 2.5663 | 0 | N/A | 0 | 0
2021-12-16 05:00 | 2.5899 | 0 | N/A | 0 | 0
2021-12-16 05:30 | 2.8032 | 0 | N/A | 0 | 0
2021-12-16 06:00 | 3.0317 | 0 | N/A | 0 | 0
2021-12-16 06:30 | 3.4528 | 0 | N/A | 0 | 0
2021-12-16 07:00 | 4.0016 | 0 | N/A | 0 | 0
2021-12-16 07:30 | 4.7199 | 0 | N/A | 0 | 0
2021-12-16 08:00 | 4.8895 | 0 | N/A | 0 | 0
2021-12-16 08:30 | 3.996 | 0 | N/A | 0 | 0
2021-12-16 09:00 | 3.3754 | 0 | N/A | 0 | 0
2021-12-16 09:30 | 2.5125 | 0 | N/A | 0 | 0
2021-12-16 10:00 | 2.2162 | 0 | N/A | 0 | 0
2021-12-16 10:30 | 1.1859 | 0 | N/A | 0 | 0
2021-12-16 11:00 | 0.85052 | 0 | N/A | 0 | 0
2021-12-16 11:30 | 0.47668 | 0 | N/A | 0 | 0
2021-12-16 12:00 | 0.22718 | 0 | N/A | 0 | 0
2021-12-16 12:30 | -0.17104 | 0 | N/A | 0 | 0
2021-12-16 13:00 | -0.89822 | 0 | N/A | 0 | 0
2021-12-16 13:30 | -1.3254 | 0 | N/A | 0 | 0
2021-12-16 14:00 | -1.4324 | 0 | N/A | 0 | 0
2021-12-16 14:30 | -1.332 | 0 | N/A | 0 | 0
2021-12-16 15:00 | -1.2761 | 0 | N/A | 0 | 0
2021-12-16 15:30 | -1.2004 | 0 | N/A | 0 | 0
2021-12-16 16:00 | -1.0597 | 0 | N/A | 0 | 0
2021-12-16 16:30 | -1.0153 | 0 | N/A | 0 | 0
2021-12-16 17:00 | -0.62472 | 0 | N/A | 0 | 0
2021-12-16 17:30 | 0.5993 | 0 | N/A | 0 | 0
2021-12-16 18:00 | 1.4208 | 0 | N/A | 0 | 0
2021-12-16 18:30 | 2.3285 | 0 | N/A | 0 | 0
2021-12-16 19:00 | 3.031 | 0 | N/A | 0 | 0
2021-12-16 19:30 | 3.4667 | 0 | N/A | 0 | 0
2021-12-16 20:00 | 3.7936 | 0 | N/A | 0 | 0
2021-12-16 20:30 | 3.8875 | 0 | N/A | 0 | 0
2021-12-16 21:00 | 4.0379 | 0 | N/A | 0 | 0
2021-12-16 21:30 | 4.1264 | 0 | N/A | 0 | 0
2021-12-16 22:00 | 3.9623 | 0 | N/A | 0 | 0
2021-12-16 22:30 | 4.2367 | 0 | N/A | 0 | 0
2021-12-16 23:00 | 4.348 | 0 | N/A | 0 | 0
2021-12-16 23:30 | 4.0812 | 0 | N/A | 0 | 0
2021-12-17 | 4.0835 | 0 | N/A | 0 | 0
2021-12-17 00:30 | 4.3632 | 0 | N/A | 0 | 0
2021-12-17 01:00 | 4.6898 | 0 | N/A | 0 | 0
2021-12-17 01:30 | 3.867 | 0 | N/A | 0 | 0
2021-12-17 02:00 | 3.2224 | 0 | N/A | 0 | 0
2021-12-17 02:30 | 3.1004 | 0 | N/A | 0 | 0
2021-12-17 03:00 | 2.7706 | 0 | N/A | 0 | 0
2021-12-17 03:30 | 2.4943 | 0 | N/A | 0 | 0
2021-12-17 04:00 | 2.402 | 0 | N/A | 0 | 0
2021-12-17 04:30 | 2.3766 | 0 | N/A | 0 | 0
2021-12-17 05:00 | 2.3898 | 0 | N/A | 0 | 0
2021-12-17 05:30 | 2.5724 | 0 | N/A | 0 | 0
2021-12-17 06:00 | 2.8031 | 0 | N/A | 0 | 0
2021-12-17 06:30 | 3.3237 | 0 | N/A | 0 | 0
2021-12-17 07:00 | 3.8143 | 0 | N/A | 0 | 0
2021-12-17 07:30 | 3.8924 | 0 | N/A | 0 | 0
2021-12-17 08:00 | 3.7154 | 0 | N/A | 0 | 0
2021-12-17 08:30 | 2.7912 | 0 | N/A | 0 | 0
2021-12-17 09:00 | 2.0723 | 0 | N/A | 0 | 0
2021-12-17 09:30 | 1.2889 | 0 | N/A | 0 | 0
2021-12-17 10:00 | 0.52515 | 0 | N/A | 0 | 0
2021-12-17 10:30 | -0.2201 | 0 | N/A | 0 | 0
2021-12-17 11:00 | -0.31603 | 0 | N/A | 0 | 0
2021-12-17 11:30 | -0.4172 | 0 | N/A | 0 | 0
2021-12-17 12:00 | -0.63688 | 0 | N/A | 0 | 0
2021-12-17 12:30 | -0.73012 | 0 | N/A | 0 | 0
2021-12-17 13:00 | -0.22136 | 0 | N/A | 0 | 0
2021-12-17 13:30 | -0.55957 | 0 | N/A | 0 | 0
2021-12-17 14:00 | -0.95001 | 0 | N/A | 0 | 0
2021-12-17 14:30 | -0.25179 | 0 | N/A | 0 | 0
2021-12-17 15:00 | 0.043461 | 0 | N/A | 0 | 0
2021-12-17 15:30 | 0.81062 | 0 | N/A | 0 | 0
2021-12-17 16:00 | 0.50205 | 0 | N/A | 0 | 0
2021-12-17 16:30 | 1.4969 | 0 | N/A | 0 | 0
2021-12-17 17:00 | 1.9456 | 0 | N/A | 0 | 0
2021-12-17 17:30 | 2.9433 | 0 | N/A | 0 | 0
2021-12-17 18:00 | 3.618 | 0 | N/A | 0 | 0
2021-12-17 18:30 | 3.9463 | 0 | N/A | 0 | 0
2021-12-17 19:00 | 4.0707 | 0 | N/A | 0 | 0
2021-12-17 19:30 | 4.2248 | 0 | N/A | 0 | 0
2021-12-17 20:00 | 4.2032 | 0 | N/A | 0 | 0
2021-12-17 20:30 | 4.2004 | 0 | N/A | 0 | 0
2021-12-17 21:00 | 4.1928 | 0 | N/A | 0 | 0
2021-12-17 21:30 | 4.1048 | 0 | N/A | 0 | 0
2021-12-17 22:00 | 3.8943 | 0 | N/A | 0 | 0
2021-12-17 22:30 | 4.1113 | 0 | N/A | 0 | 0
2021-12-17 23:00 | 4.1669 | 0 | N/A | 0 | 0
2021-12-17 23:30 | 4.0662 | 0 | N/A | 0 | 0
2021-12-18 | 4.0603 | 0 | N/A | 0 | 0
2021-12-18 00:30 | 4.3961 | 0 | N/A | 0 | 0
2021-12-18 01:00 | 4.4525 | 0 | N/A | 0 | 0
2021-12-18 01:30 | 3.6329 | 0 | N/A | 0 | 0
2021-12-18 02:00 | 3.0092 | 0 | N/A | 0 | 0
2021-12-18 02:30 | 2.9657 | 0 | N/A | 0 | 0
2021-12-18 03:00 | 2.7223 | 0 | N/A | 0 | 0
2021-12-18 03:30 | 2.4515 | 0 | N/A | 0 | 0
2021-12-18 04:00 | 2.299 | 0 | N/A | 0 | 0
2021-12-18 04:30 | 2.2322 | 0 | N/A | 0 | 0
2021-12-18 05:00 | 2.2406 | 0 | N/A | 0 | 0
2021-12-18 05:30 | 2.2541 | 0 | N/A | 0 | 0
2021-12-18 06:00 | 2.3425 | 0 | N/A | 0 | 0
2021-12-18 06:30 | 2.4744 | 0 | N/A | 0 | 0
2021-12-18 07:00 | 2.5228 | 0 | N/A | 0 | 0
2021-12-18 07:30 | 2.6115 | 0 | N/A | 0 | 0
2021-12-18 08:00 | 2.7454 | 0 | N/A | 0 | 0
2021-12-18 08:30 | 2.0016 | 0 | N/A | 0 | 0
2021-12-18 09:00 | 1.679 | 0 | N/A | 0 | 0
2021-12-18 09:30 | 1.4113 | 0 | N/A | 0 | 0
2021-12-18 10:00 | 0.76322 | 0 | N/A | 0 | 0
2021-12-18 10:30 | 0.39419 | 0 | N/A | 0 | 0
2021-12-18 11:00 | 0.35391 | 0 | N/A | 0 | 0
2021-12-18 11:30 | -0.11319 | 0 | N/A | 0 | 0
2021-12-18 12:00 | -0.086474 | 0 | N/A | 0 | 0
2021-12-18 12:30 | 0.22784 | 0 | N/A | 0 | 0
2021-12-18 13:00 | -0.11081 | 0 | N/A | 0 | 0
2021-12-18 13:30 | -0.16987 | 0 | N/A | 0 | 0
2021-12-18 14:00 | -0.19003 | 0 | N/A | 0 | 0
2021-12-18 14:30 | -0.15667 | 0 | N/A | 0 | 0
2021-12-18 15:00 | -0.055176 | 0 | N/A | 0 | 0
2021-12-18 15:30 | 0.20366 | 0 | N/A | 0 | 0
2021-12-18 16:00 | 0.57805 | 0 | N/A | 0 | 0
2021-12-18 16:30 | 1.1218 | 0 | N/A | 0 | 0
2021-12-18 17:00 | 1.6617 | 0 | N/A | 0 | 0
2021-12-18 17:30 | 2.4579 | 0 | N/A | 0 | 0
2021-12-18 18:00 | 3.3014 | 0 | N/A | 0 | 0
2021-12-18 18:30 | 4.0289 | 0 | N/A | 0 | 0
2021-12-18 19:00 | 4.5944 | 0 | N/A | 0 | 0
2021-12-18 19:30 | 4.8549 | 0 | N/A | 0 | 0
2021-12-18 20:00 | 4.9497 | 0 | N/A | 0 | 0
2021-12-18 20:30 | 4.8068 | 0 | N/A | 0 | 0
2021-12-18 21:00 | 4.6551 | 0 | N/A | 0 | 0
2021-12-18 21:30 | 4.25 | 0 | N/A | 0 | 0
2021-12-18 22:00 | 3.9283 | 0 | N/A | 0 | 0
2021-12-18 22:30 | 4.1117 | 0 | N/A | 0 | 0
2021-12-18 23:00 | 4.0897 | 0 | N/A | 0 | 0
2021-12-18 23:30 | 3.8148 | 0 | N/A | 0 | 0
2021-12-19 | 3.8477 | 0 | N/A | 0 | 0
2021-12-19 00:30 | 4.2852 | 0 | N/A | 0 | 0
2021-12-19 01:00 | 4.5079 | 0 | N/A | 0 | 0
2021-12-19 01:30 | 3.5645 | 0 | N/A | 0 | 0
2021-12-19 02:00 | 2.8841 | 0 | N/A | 0 | 0
2021-12-19 02:30 | 2.8527 | 0 | N/A | 0 | 0
2021-12-19 03:00 | 2.6394 | 0 | N/A | 0 | 0
2021-12-19 03:30 | 2.266 | 0 | N/A | 0 | 0
2021-12-19 04:00 | 2.1116 | 0 | N/A | 0 | 0
2021-12-19 04:30 | 2.0169 | 0 | N/A | 0 | 0
2021-12-19 05:00 | 2.0866 | 0 | N/A | 0 | 0
2021-12-19 05:30 | 2.1561 | 0 | N/A | 0 | 0
2021-12-19 06:00 | 2.2161 | 0 | N/A | 0 | 0
2021-12-19 06:30 | 2.3359 | 0 | N/A | 0 | 0
2021-12-19 07:00 | 2.3848 | 0 | N/A | 0 | 0
2021-12-19 07:30 | 2.4545 | 0 | N/A | 0 | 0
2021-12-19 08:00 | 2.4832 | 0 | N/A | 0 | 0
2021-12-19 08:30 | 2.9505 | 0 | N/A | 0 | 0
2021-12-19 09:00 | 3.0137 | 0 | N/A | 0 | 0
2021-12-19 09:30 | 3.6565 | 0 | N/A | 0 | 0
2021-12-19 10:00 | 3.5671 | 0 | N/A | 0 | 0
2021-12-19 10:30 | 3.8175 | 0 | N/A | 0 | 0
2021-12-19 11:00 | 3.7666 | 0 | N/A | 0 | 0
2021-12-19 11:30 | 4.0675 | 0 | N/A | 0 | 0
2021-12-19 12:00 | 4.2356 | 0 | N/A | 0 | 0
2021-12-19 12:30 | 3.6661 | 0 | N/A | 0 | 0
2021-12-19 13:00 | 2.2218 | 0 | N/A | 0 | 0
2021-12-19 13:30 | 2.0694 | 0 | N/A | 0 | 0
2021-12-19 14:00 | 3.4141 | 0 | N/A | 0 | 0
2021-12-19 14:30 | 2.5713 | 0 | N/A | 0 | 0
2021-12-19 15:00 | 1.8176 | 0 | N/A | 0 | 0
2021-12-19 15:30 | 0.80422 | 0 | N/A | 0 | 0
2021-12-19 16:00 | -0.73334 | 0 | N/A | 0 | 0
2021-12-19 16:30 | -0.75955 | 0 | N/A | 0 | 0
2021-12-19 17:00 | 0.62187 | 0 | N/A | 0 | 0
2021-12-19 17:30 | 1.9171 | 0 | N/A | 0 | 0
2021-12-19 18:00 | 2.417 | 0 | N/A | 0 | 0
2021-12-19 18:30 | 2.7581 | 0 | N/A | 0 | 0
2021-12-19 19:00 | 3.2638 | 0 | N/A | 0 | 0
2021-12-19 19:30 | 3.6658 | 0 | N/A | 0 | 0
2021-12-19 20:00 | 4.0829 | 0 | N/A | 0 | 0
2021-12-19 20:30 | 4.4346 | 0 | N/A | 0 | 0
2021-12-19 21:00 | 4.5347 | 0 | N/A | 0 | 0
2021-12-19 21:30 | 4.6517 | 0 | N/A | 0 | 0
2021-12-19 22:00 | 4.457 | 0 | N/A | 0 | 0
2021-12-19 22:30 | 4.7163 | 0 | N/A | 0 | 0
2021-12-19 23:00 | 4.7321 | 0 | N/A | 0 | 0
2021-12-19 23:30 | 4.4188 | 0 | N/A | 0 | 0
2021-12-20 | 4.5014 | 0 | N/A | 0 | 0
2021-12-21 00:30 | 4.4481 | 0 | N/A | 0 | 0
2021-12-21 01:00 | 4.714 | 0 | N/A | 0 | 0
2021-12-21 01:30 | 3.8888 | 0 | N/A | 0 | 0
2021-12-21 02:00 | 3.2837 | 0 | N/A | 0 | 0
2021-12-21 02:30 | 3.2392 | 0 | N/A | 0 | 0
2021-12-21 03:00 | 2.8529 | 0 | N/A | 0 | 0
2021-12-21 03:30 | 2.4642 | 0 | N/A | 0 | 0
2021-12-21 04:00 | 2.3376 | 0 | N/A | 0 | 0
2021-12-21 04:30 | 2.3294 | 0 | N/A | 0 | 0
2021-12-21 05:00 | 2.3278 | 0 | N/A | 0 | 0
2021-12-21 05:30 | 2.4328 | 0 | N/A | 0 | 0
2021-12-21 06:00 | 2.6145 | 0 | N/A | 0 | 0
2021-12-21 06:30 | 2.8691 | 0 | N/A | 0 | 0
2021-12-21 07:00 | 3.0644 | 0 | N/A | 0 | 0
2021-12-21 07:30 | 3.3752 | 0 | N/A | 0 | 0
2021-12-21 08:00 | 3.3473 | 0 | N/A | 0 | 0
2021-12-21 08:30 | 2.5874 | 0 | N/A | 0 | 0
2021-12-21 09:00 | 1.8819 | 0 | N/A | 0 | 0
2021-12-21 09:30 | 1.1563 | 0 | N/A | 0 | 0
2021-12-21 10:00 | 0.418 | 0 | N/A | 0 | 0
2021-12-21 10:30 | -0.30878 | 0 | N/A | 0 | 0
2021-12-21 11:00 | -0.63568 | 0 | N/A | 0 | 0
2021-12-21 11:30 | -0.89867 | 0 | N/A | 0 | 0
2021-12-21 12:00 | -1.1035 | 0 | N/A | 0 | 0
2021-12-21 12:30 | -1.17 | 0 | N/A | 0 | 0
2021-12-21 13:00 | -1.2967 | 0 | N/A | 0 | 0
2021-12-21 13:30 | -1.2533 | 0 | N/A | 0 | 0
2021-12-21 14:00 | -1.3267 | 0 | N/A | 0 | 0
2021-12-21 14:30 | -1.1502 | 0 | N/A | 0 | 0
2021-12-21 15:00 | -1.0667 | 0 | N/A | 0 | 0
2021-12-21 15:30 | -0.89333 | 0 | N/A | 0 | 0
2021-12-21 16:00 | -0.66189 | 0 | N/A | 0 | 0
2021-12-21 16:30 | -0.37263 | 0 | N/A | 0 | 0
2021-12-21 17:00 | 0.2832 | 0 | N/A | 0 | 0
2021-12-21 17:30 | 1.1561 | 0 | N/A | 0 | 0
2021-12-21 18:00 | 3.6094 | 0 | N/A | 0 | 0
2021-12-21 18:30 | 4.6323 | 0 | N/A | 0 | 0
2021-12-21 19:00 | 5.3468 | 0 | N/A | 0 | 0
2021-12-21 19:30 | 5.7391 | 0 | N/A | 0 | 0
2021-12-21 20:00 | 5.8711 | 0 | N/A | 0 | 0
2021-12-21 20:30 | 5.9272 | 0 | N/A | 0 | 0
2021-12-21 21:00 | 5.8972 | 0 | N/A | 0 | 0
2021-12-21 21:30 | 5.7168 | 0 | N/A | 0 | 0
2021-12-21 22:00 | 5.4247 | 0 | N/A | 0 | 0
2021-12-21 22:30 | 5.6587 | 0 | N/A | 0 | 0
2021-12-21 23:00 | 5.6729 | 0 | N/A | 0 | 0
2021-12-21 23:30 | 4.152 | 0 | N/A | 0 | 0
2021-12-22 | 4.0031 | 0 | N/A | 0 | 0
2021-12-22 00:30 | 4.4048 | 0 | N/A | 0 | 0
2021-12-22 01:00 | 4.5888 | 0 | N/A | 0 | 0
2021-12-22 01:30 | 3.6987 | 0 | N/A | 0 | 0
2021-12-22 02:00 | 3.0655 | 0 | N/A | 0 | 0
2021-12-22 02:30 | 3.0786 | 0 | N/A | 0 | 0
2021-12-22 03:00 | 2.7857 | 0 | N/A | 0 | 0
2021-12-22 03:30 | 2.4704 | 0 | N/A | 0 | 0
2021-12-22 04:00 | 2.3151 | 0 | N/A | 0 | 0
2021-12-22 04:30 | 2.3225 | 0 | N/A | 0 | 0
2021-12-22 05:00 | 2.3911 | 0 | N/A | 0 | 0
2021-12-22 05:30 | 2.4243 | 0 | N/A | 0 | 0
2021-12-22 06:00 | 2.5977 | 0 | N/A | 0 | 0
2021-12-22 06:30 | 3.0286 | 0 | N/A | 0 | 0
2021-12-22 07:00 | 3.2459 | 0 | N/A | 0 | 0
2021-12-22 07:30 | 3.5071 | 0 | N/A | 0 | 0
2021-12-22 08:00 | 3.4663 | 0 | N/A | 0 | 0
2021-12-22 08:30 | 3.0617 | 0 | N/A | 0 | 0
2021-12-22 09:00 | 3.4008 | 0 | N/A | 0 | 0
2021-12-22 09:30 | 3.329 | 0 | N/A | 0 | 0
2021-12-22 10:00 | 2.8502 | 0 | N/A | 0 | 0
2021-12-22 10:30 | 2.288 | 0 | N/A | 0 | 0
2021-12-22 11:00 | 2.1794 | 0 | N/A | 0 | 0
2021-12-22 11:30 | 1.2366 | 0 | N/A | 0 | 0
2021-12-22 12:00 | -0.28057 | 0 | N/A | 0 | 0
2021-12-22 12:30 | -0.57482 | 0 | N/A | 0 | 0
2021-12-22 13:00 | -1.3602 | 0 | N/A | 0 | 0
2021-12-22 13:30 | -1.7543 | 0 | N/A | 0 | 0
2021-12-22 14:00 | -1.7833 | 0 | N/A | 0 | 0
2021-12-22 14:30 | -1.6789 | 0 | N/A | 0 | 0
2021-12-22 15:00 | -1.5941 | 0 | N/A | 0 | 0
2021-12-22 15:30 | -1.6004 | 0 | N/A | 0 | 0
2021-12-22 16:00 | -1.4725 | 0 | N/A | 0 | 0
2021-12-22 16:30 | -1.2283 | 0 | N/A | 0 | 0
2021-12-22 17:00 | -0.662 | 0 | N/A | 0 | 0
2021-12-22 17:30 | 0.56824 | 0 | N/A | 0 | 0
2021-12-22 18:00 | 1.4158 | 0 | N/A | 0 | 0
2021-12-22 18:30 | 2.2748 | 0 | N/A | 0 | 0
2021-12-22 19:00 | 2.9762 | 0 | N/A | 0 | 0
2021-12-22 19:30 | 3.444 | 0 | N/A | 0 | 0
2021-12-22 20:00 | 3.6214 | 0 | N/A | 0 | 0
2021-12-22 20:30 | 3.8787 | 0 | N/A | 0 | 0
2021-12-22 21:00 | 4.04 | 0 | N/A | 0 | 0
2021-12-22 21:30 | 4.0526 | 0 | N/A | 0 | 0
2021-12-22 22:00 | 3.8776 | 0 | N/A | 0 | 0
2021-12-22 22:30 | 4.2276 | 0 | N/A | 0 | 0
2021-12-22 23:00 | 4.368 | 0 | N/A | 0 | 0
2021-12-22 23:30 | 4.1333 | 0 | N/A | 0 | 0
2021-12-23 | 4.0885 | 0 | N/A | 0 | 0
2021-12-25 00:30 | 4.5115 | 0 | N/A | 0 | 0
2021-12-25 01:00 | 4.6592 | 0 | N/A | 0 | 0
2021-12-25 01:30 | 3.8354 | 0 | N/A | 0 | 0
2021-12-25 02:00 | 3.1172 | 0 | N/A | 0 | 0
2021-12-25 02:30 | 3.0495 | 0 | N/A | 0 | 0
2021-12-25 03:00 | 2.7835 | 0 | N/A | 0 | 0
2021-12-25 03:30 | 2.413 | 0 | N/A | 0 | 0
2021-12-25 04:00 | 2.2752 | 0 | N/A | 0 | 0
2021-12-25 04:30 | 2.2257 | 0 | N/A | 0 | 0
2021-12-25 05:00 | 2.1386 | 0 | N/A | 0 | 0
2021-12-25 05:30 | 2.1572 | 0 | N/A | 0 | 0
2021-12-25 06:00 | 2.253 | 0 | N/A | 0 | 0
2021-12-25 06:30 | 2.3315 | 0 | N/A | 0 | 0
2021-12-25 07:00 | 2.3793 | 0 | N/A | 0 | 0
2021-12-25 07:30 | 2.5546 | 0 | N/A | 0 | 0
2021-12-25 08:00 | 2.6091 | 0 | N/A | 0 | 0
2021-12-25 08:30 | 2.2172 | 0 | N/A | 0 | 0
2021-12-25 09:00 | 1.8753 | 0 | N/A | 0 | 0
2021-12-25 09:30 | 1.5476 | 0 | N/A | 0 | 0
2021-12-25 10:00 | 0.93669 | 0 | N/A | 0 | 0
2021-12-25 10:30 | 0.66334 | 0 | N/A | 0 | 0
2021-12-25 12:00 | -1.0427 | 0 | N/A | 0 | 0
2021-12-25 12:30 | -1.261 | 0 | N/A | 0 | 0
2021-12-25 13:00 | -1.579 | 0 | N/A | 0 | 0
2021-12-25 13:30 | -2.1115 | 0 | N/A | 0 | 0
2021-12-25 14:00 | -2.5456 | 0 | N/A | 0 | 0
2021-12-25 14:30 | -2.5407 | 0 | N/A | 0 | 0
2021-12-25 15:00 | -2.4576 | 0 | N/A | 0 | 0
2021-12-25 15:30 | -2.2808 | 0 | N/A | 0 | 0
2021-12-25 16:00 | -1.9925 | 0 | N/A | 0 | 0
2021-12-25 16:30 | -1.5331 | 0 | N/A | 0 | 0
2021-12-25 17:00 | -1.0331 | 0 | N/A | 0 | 0
2021-12-25 17:30 | 0.56444 | 0 | N/A | 0 | 0
2021-12-25 18:00 | 1.4459 | 0 | N/A | 0 | 0
2021-12-25 18:30 | 2.0755 | 0 | N/A | 0 | 0
2021-12-25 19:00 | 2.6321 | 0 | N/A | 0 | 0
2021-12-25 19:30 | 2.9538 | 0 | N/A | 0 | 0
2021-12-25 20:00 | 3.1465 | 0 | N/A | 0 | 0
2021-12-25 20:30 | 3.2499 | 0 | N/A | 0 | 0
2021-12-25 21:00 | 3.3046 | 0 | N/A | 0 | 0
2021-12-25 21:30 | 3.3806 | 0 | N/A | 0 | 0
2021-12-25 22:00 | 3.324 | 0 | N/A | 0 | 0
2021-12-25 22:30 | 3.8211 | 0 | N/A | 0 | 0
2021-12-25 23:00 | 3.9699 | 0 | N/A | 0 | 0
2021-12-25 23:30 | 3.7142 | 0 | N/A | 0 | 0
2021-12-26 | 3.8402 | 0 | N/A | 0 | 0
2021-12-26 00:30 | 4.3179 | 0 | N/A | 0 | 0
2021-12-26 01:00 | 4.5477 | 0 | N/A | 0 | 0
2021-12-26 01:30 | 3.8175 | 0 | N/A | 0 | 0
2021-12-26 02:00 | 3.23 | 0 | N/A | 0 | 0
2021-12-26 02:30 | 3.1544 | 0 | N/A | 0 | 0
2021-12-26 03:00 | 2.8883 | 0 | N/A | 0 | 0
2021-12-26 03:30 | 2.5076 | 0 | N/A | 0 | 0
2021-12-26 04:00 | 2.249 | 0 | N/A | 0 | 0
2021-12-26 04:30 | 2.223 | 0 | N/A | 0 | 0
2021-12-26 05:00 | 2.1372 | 0 | N/A | 0 | 0
2021-12-26 05:30 | 2.1644 | 0 | N/A | 0 | 0
2021-12-26 06:00 | 2.2793 | 0 | N/A | 0 | 0
2021-12-26 06:30 | 2.3992 | 0 | N/A | 0 | 0
2021-12-26 07:00 | 2.4014 | 0 | N/A | 0 | 0
2021-12-26 07:30 | 2.4925 | 0 | N/A | 0 | 0
2021-12-26 08:00 | 2.5335 | 0 | N/A | 0 | 0
2021-12-26 08:30 | 2.4182 | 0 | N/A | 0 | 0
2021-12-26 09:00 | 2.415 | 0 | N/A | 0 | 0
2021-12-26 09:30 | 2.3116 | 0 | N/A | 0 | 0
2021-12-26 10:00 | 1.8844 | 0 | N/A | 0 | 0
2021-12-26 10:30 | 1.8867 | 0 | N/A | 0 | 0
2021-12-26 11:00 | 1.3376 | 0 | N/A | 0 | 0
2021-12-26 11:30 | 1.3494 | 0 | N/A | 0 | 0
2021-12-26 12:00 | 0.82963 | 0 | N/A | 0 | 0
2021-12-26 12:30 | 0.78617 | 0 | N/A | 0 | 0
2021-12-26 13:00 | 0.73854 | 0 | N/A | 0 | 0
2021-12-26 13:30 | 0.71371 | 0 | N/A | 0 | 0
2021-12-26 14:00 | -0.69346 | 0 | N/A | 0 | 0
2021-12-26 14:30 | -0.71704 | 0 | N/A | 0 | 0
2021-12-26 15:00 | -0.71126 | 0 | N/A | 0 | 0
2021-12-26 15:30 | -0.74065 | 0 | N/A | 0 | 0
2021-12-26 16:00 | -1.0073 | 0 | N/A | 0 | 0
2021-12-26 16:30 | -1.1487 | 0 | N/A | 0 | 0
2021-12-26 17:00 | -1.1455 | 0 | N/A | 0 | 0
2021-12-26 17:30 | -0.81751 | 0 | N/A | 0 | 0
2021-12-26 18:00 | 0.91585 | 0 | N/A | 0 | 0
2021-12-26 18:30 | 1.6651 | 0 | N/A | 0 | 0
2021-12-26 19:00 | 2.4562 | 0 | N/A | 0 | 0
2021-12-26 19:30 | 3.066 | 0 | N/A | 0 | 0
2021-12-26 20:00 | 3.3409 | 0 | N/A | 0 | 0
2021-12-26 20:30 | 3.6628 | 0 | N/A | 0 | 0
2021-12-26 21:00 | 4.1205 | 0 | N/A | 0 | 0
2021-12-26 21:30 | 4.1213 | 0 | N/A | 0 | 0
2021-12-26 22:00 | 3.9301 | 0 | N/A | 0 | 0
2021-12-26 22:30 | 4.2837 | 0 | N/A | 0 | 0
2021-12-26 23:00 | 4.3983 | 0 | N/A | 0 | 0
2021-12-26 23:30 | 4.1377 | 0 | N/A | 0 | 0
2021-12-27 | 4.3227 | 0 | N/A | 0 | 0
2021-12-27 00:30 | 4.6155 | 0 | N/A | 0 | 0
2021-12-27 01:00 | 4.837 | 0 | N/A | 0 | 0
2021-12-27 01:30 | 4.0302 | 0 | N/A | 0 | 0
2021-12-27 02:00 | 3.4134 | 0 | N/A | 0 | 0
2021-12-27 02:30 | 3.3732 | 0 | N/A | 0 | 0
2021-12-27 03:00 | 3.0232 | 0 | N/A | 0 | 0
2021-12-27 03:30 | 2.6633 | 0 | N/A | 0 | 0
2021-12-27 04:00 | 2.4702 | 0 | N/A | 0 | 0
2021-12-27 04:30 | 2.3884 | 0 | N/A | 0 | 0
2021-12-27 05:00 | 2.3222 | 0 | N/A | 0 | 0
2021-12-27 05:30 | 2.4136 | 0 | N/A | 0 | 0
2021-12-27 06:00 | 2.4821 | 0 | N/A | 0 | 0
2021-12-27 06:30 | 2.6225 | 0 | N/A | 0 | 0
2021-12-27 07:00 | 2.6982 | 0 | N/A | 0 | 0
2021-12-27 07:30 | 2.6854 | 0 | N/A | 0 | 0
2021-12-27 08:00 | 2.652 | 0 | N/A | 0 | 0
2021-12-27 08:30 | 2.2034 | 0 | N/A | 0 | 0
2021-12-27 09:00 | 1.8262 | 0 | N/A | 0 | 0
2021-12-27 09:30 | 1.1725 | 0 | N/A | 0 | 0
2021-12-27 10:00 | -0.8331 | 0 | N/A | 0 | 0
2021-12-27 10:30 | -0.9738 | 0 | N/A | 0 | 0
2021-12-27 11:00 | -1.3864 | 0 | N/A | 0 | 0
2021-12-27 11:30 | -1.7378 | 0 | N/A | 0 | 0
2021-12-27 12:00 | -1.764 | 0 | N/A | 0 | 0
2021-12-27 12:30 | -1.5885 | 0 | N/A | 0 | 0
2021-12-27 13:00 | -1.4285 | 0 | N/A | 0 | 0
2021-12-27 13:30 | -1.4388 | 0 | N/A | 0 | 0
2021-12-27 14:00 | -1.2658 | 0 | N/A | 0 | 0
2021-12-27 14:30 | -1.122 | 0 | N/A | 0 | 0
2021-12-27 15:00 | -1.1424 | 0 | N/A | 0 | 0
2021-12-27 15:30 | -1.3789 | 0 | N/A | 0 | 0
2021-12-27 16:00 | -1.1497 | 0 | N/A | 0 | 0
2021-12-27 16:30 | -0.74192 | 0 | N/A | 0 | 0
2021-12-27 17:00 | 0.82828 | 0 | N/A | 0 | 0
2021-12-27 17:30 | 1.2972 | 0 | N/A | 0 | 0
2021-12-27 18:00 | 2.1863 | 0 | N/A | 0 | 0
2021-12-27 18:30 | 2.8422 | 0 | N/A | 0 | 0
2021-12-27 19:00 | 3.2135 | 0 | N/A | 0 | 0
2021-12-27 19:30 | 3.6914 | 0 | N/A | 0 | 0
2021-12-27 20:00 | 3.9131 | 0 | N/A | 0 | 0
2021-12-27 20:30 | 4.0456 | 0 | N/A | 0 | 0
2021-12-27 21:00 | 4.1522 | 0 | N/A | 0 | 0
2021-12-27 21:30 | 4.0883 | 0 | N/A | 0 | 0
2021-12-27 22:00 | 3.8658 | 0 | N/A | 0 | 0
2021-12-27 22:30 | 4.0694 | 0 | N/A | 0 | 0
2021-12-27 23:00 | 4.1837 | 0 | N/A | 0 | 0
2021-12-27 23:30 | 3.953 | 0 | N/A | 0 | 0
2021-12-28 | 4.1304 | 0 | N/A | 0 | 0
2021-12-28 00:30 | 4.448 | 0 | N/A | 0 | 0
2021-12-28 01:00 | 4.6691 | 0 | N/A | 0 | 0
2021-12-28 01:30 | 3.8675 | 0 | N/A | 0 | 0
2021-12-28 02:00 | 3.2867 | 0 | N/A | 0 | 0
2021-12-28 02:30 | 2.7657 | 0 | N/A | 0 | 0
2021-12-28 03:00 | 2.082 | 0 | N/A | 0 | 0
2021-12-28 03:30 | 2.606 | 0 | N/A | 0 | 0
2021-12-28 04:00 | 2.3809 | 0 | N/A | 0 | 0
2021-12-28 04:30 | 2.3091 | 0 | N/A | 0 | 0
2021-12-28 05:00 | 2.2696 | 0 | N/A | 0 | 0
2021-12-28 05:30 | 2.4062 | 0 | N/A | 0 | 0
2021-12-28 06:00 | 2.4777 | 0 | N/A | 0 | 0
2021-12-28 06:30 | 2.6119 | 0 | N/A | 0 | 0
2021-12-28 07:00 | 2.5276 | 0 | N/A | 0 | 0
2021-12-28 07:30 | 2.5597 | 0 | N/A | 0 | 0
2021-12-28 08:00 | 2.2631 | 0 | N/A | 0 | 0
2021-12-28 08:30 | 1.7399 | 0 | N/A | 0 | 0
2021-12-28 09:00 | 1.3026 | 0 | N/A | 0 | 0
2021-12-28 09:30 | 0.88288 | 0 | N/A | 0 | 0
2021-12-28 10:00 | -0.75769 | 0 | N/A | 0 | 0
2021-12-28 10:30 | -1.032 | 0 | N/A | 0 | 0
2021-12-28 11:00 | -1.3998 | 0 | N/A | 0 | 0
2021-12-28 11:30 | -1.5996 | 0 | N/A | 0 | 0
2021-12-28 12:00 | -1.8295 | 0 | N/A | 0 | 0
2021-12-28 12:30 | -2.0259 | 0 | N/A | 0 | 0
2021-12-28 13:00 | -2.1621 | 0 | N/A | 0 | 0
2021-12-28 13:30 | -2.2713 | 0 | N/A | 0 | 0
2021-12-28 14:00 | -2.3845 | 0 | N/A | 0 | 0
2021-12-28 14:30 | -2.3486 | 0 | N/A | 0 | 0
2021-12-28 15:00 | -2.2798 | 0 | N/A | 0 | 0
2021-12-28 15:30 | -2.009 | 0 | N/A | 0 | 0
2021-12-28 16:00 | -1.8998 | 0 | N/A | 0 | 0
2021-12-28 16:30 | -1.63 | 0 | N/A | 0 | 0
2021-12-28 17:00 | -0.99435 | 0 | N/A | 0 | 0
2021-12-28 17:30 | -0.60535 | 0 | N/A | 0 | 0
2021-12-28 18:00 | 1.4271 | 0 | N/A | 0 | 0
2021-12-28 18:30 | 2.4729 | 0 | N/A | 0 | 0
2021-12-28 19:00 | 2.6785 | 0 | N/A | 0 | 0
2021-12-28 19:30 | 2.8547 | 0 | N/A | 0 | 0
2021-12-28 20:00 | 3.3448 | 0 | N/A | 0 | 0
2021-12-28 20:30 | 3.5744 | 0 | N/A | 0 | 0
2021-12-28 21:00 | 3.7375 | 0 | N/A | 0 | 0
2021-12-28 21:30 | 3.6995 | 0 | N/A | 0 | 0
2021-12-28 22:00 | 3.6479 | 0 | N/A | 0 | 0
2021-12-28 22:30 | 3.9485 | 0 | N/A | 0 | 0
2021-12-28 23:00 | 4.1393 | 0 | N/A | 0 | 0
2021-12-28 23:30 | 3.781 | 0 | N/A | 0 | 0
2021-12-29 | 3.8851 | 0 | N/A | 0 | 0
2021-12-29 00:30 | 4.4373 | 0 | N/A | 0 | 0
2021-12-29 01:00 | 4.6344 | 0 | N/A | 0 | 0
2021-12-29 01:30 | 3.8415 | 0 | N/A | 0 | 0
2021-12-29 02:00 | 3.2329 | 0 | N/A | 0 | 0
2021-12-29 02:30 | 3.2004 | 0 | N/A | 0 | 0
2021-12-29 03:00 | 2.8585 | 0 | N/A | 0 | 0
2021-12-29 03:30 | 2.5091 | 0 | N/A | 0 | 0
2021-12-29 04:00 | 2.336 | 0 | N/A | 0 | 0
2021-12-29 04:30 | 2.2864 | 0 | N/A | 0 | 0
2021-12-29 05:00 | 2.3324 | 0 | N/A | 0 | 0
2021-12-29 05:30 | 2.4284 | 0 | N/A | 0 | 0
2021-12-29 06:00 | 2.4419 | 0 | N/A | 0 | 0
2021-12-29 06:30 | 2.5911 | 0 | N/A | 0 | 0
2021-12-29 07:00 | 2.5987 | 0 | N/A | 0 | 0
2021-12-29 07:30 | 2.7076 | 0 | N/A | 0 | 0
2021-12-29 08:00 | 2.3935 | 0 | N/A | 0 | 0
2021-12-29 08:30 | 1.7152 | 0 | N/A | 0 | 0
2021-12-29 09:00 | 1.2304 | 0 | N/A | 0 | 0
2021-12-29 09:30 | 0.80101 | 0 | N/A | 0 | 0
2021-12-29 10:00 | -0.68307 | 0 | N/A | 0 | 0
2021-12-29 10:30 | -0.85637 | 0 | N/A | 0 | 0
2021-12-29 11:00 | -1.2536 | 0 | N/A | 0 | 0
2021-12-29 11:30 | -1.4197 | 0 | N/A | 0 | 0
2021-12-29 12:00 | -1.5091 | 0 | N/A | 0 | 0
2021-12-29 12:30 | -1.5814 | 0 | N/A | 0 | 0
2021-12-29 13:00 | -1.6972 | 0 | N/A | 0 | 0
2021-12-29 13:30 | -1.7791 | 0 | N/A | 0 | 0
2021-12-29 14:00 | -1.7427 | 0 | N/A | 0 | 0
2021-12-29 14:30 | -1.643 | 0 | N/A | 0 | 0
2021-12-29 15:00 | -1.427 | 0 | N/A | 0 | 0
2021-12-29 15:30 | -1.1586 | 0 | N/A | 0 | 0
2021-12-29 16:00 | -0.72444 | 0 | N/A | 0 | 0
2021-12-29 16:30 | -0.30596 | 0 | N/A | 0 | 0
2021-12-29 17:00 | 0.67602 | 0 | N/A | 0 | 0
2021-12-29 17:30 | 1.5863 | 0 | N/A | 0 | 0
2021-12-29 18:00 | 2.5466 | 0 | N/A | 0 | 0
2021-12-29 18:30 | 3.4562 | 0 | N/A | 0 | 0
2021-12-29 19:00 | 4.1656 | 0 | N/A | 0 | 0
2021-12-29 19:30 | 4.4366 | 0 | N/A | 0 | 0
2021-12-29 20:00 | 4.5029 | 0 | N/A | 0 | 0
2021-12-29 20:30 | 4.4831 | 0 | N/A | 0 | 0
2021-12-29 21:00 | 4.361 | 0 | N/A | 0 | 0
2021-12-29 21:30 | 4.1266 | 0 | N/A | 0 | 0
2021-12-29 22:00 | 3.8726 | 0 | N/A | 0 | 0
2021-12-29 22:30 | 4.1577 | 0 | N/A | 0 | 0
2021-12-29 23:00 | 4.1226 | 0 | N/A | 0 | 0
2021-12-29 23:30 | 3.7733 | 0 | N/A | 0 | 0
2021-12-30 | 3.8279 | 0 | N/A | 0 | 0
2021-12-30 00:30 | 4.2679 | 0 | N/A | 0 | 0
2021-12-30 01:00 | 4.4388 | 0 | N/A | 0 | 0
2021-12-30 01:30 | 3.5802 | 0 | N/A | 0 | 0
2021-12-30 02:00 | 2.9891 | 0 | N/A | 0 | 0
2021-12-30 02:30 | 2.9155 | 0 | N/A | 0 | 0
2021-12-30 03:00 | 2.6636 | 0 | N/A | 0 | 0
2021-12-30 03:30 | 2.3659 | 0 | N/A | 0 | 0
2021-12-30 04:00 | 2.2767 | 0 | N/A | 0 | 0
2021-12-30 04:30 | 2.2554 | 0 | N/A | 0 | 0
2021-12-30 05:00 | 2.3166 | 0 | N/A | 0 | 0
2021-12-30 05:30 | 2.3719 | 0 | N/A | 0 | 0
2021-12-30 06:00 | 2.3826 | 0 | N/A | 0 | 0
2021-12-30 06:30 | 2.5255 | 0 | N/A | 0 | 0
2021-12-30 07:00 | 2.4497 | 0 | N/A | 0 | 0
2021-12-30 07:30 | 2.5456 | 0 | N/A | 0 | 0
2021-12-30 08:00 | 2.2704 | 0 | N/A | 0 | 0
2021-12-30 08:30 | 1.7636 | 0 | N/A | 0 | 0
2021-12-30 09:00 | 1.3023 | 0 | N/A | 0 | 0
2021-12-30 09:30 | 0.85297 | 0 | N/A | 0 | 0
2021-12-30 10:00 | 0.59083 | 0 | N/A | 0 | 0
2021-12-30 10:30 | 0.55766 | 0 | N/A | 0 | 0
2021-12-30 11:00 | -0.51 | 0 | N/A | 0 | 0
2021-12-30 11:30 | -0.57771 | 0 | N/A | 0 | 0
2021-12-30 12:00 | -0.54561 | 0 | N/A | 0 | 0
2021-12-30 12:30 | -0.40832 | 0 | N/A | 0 | 0
2021-12-30 13:00 | -0.37477 | 0 | N/A | 0 | 0
2021-12-30 13:30 | -0.3205 | 0 | N/A | 0 | 0
2021-12-30 14:00 | -0.23795 | 0 | N/A | 0 | 0
2021-12-30 14:30 | 0.1443 | 0 | N/A | 0 | 0
2021-12-30 15:00 | 0.14472 | 0 | N/A | 0 | 0
2021-12-30 15:30 | 0.45618 | 0 | N/A | 0 | 0
2021-12-30 16:00 | 1.04 | 0 | N/A | 0 | 0
2021-12-30 16:30 | 1.78 | 0 | N/A | 0 | 0
2021-12-30 17:00 | 2.718 | 0 | N/A | 0 | 0
2021-12-30 17:30 | 3.7638 | 0 | N/A | 0 | 0
2021-12-30 18:00 | 5.1834 | 0 | N/A | 0 | 0
2021-12-30 18:30 | 5.5239 | 0 | N/A | 0 | 0
2021-12-30 19:00 | 6.191 | 0 | N/A | 0 | 0
2021-12-30 19:30 | 6.0357 | 0 | N/A | 0 | 0
2021-12-30 20:00 | 6.267 | 0 | N/A | 0 | 0
2021-12-30 20:30 | 6.1319 | 0 | N/A | 0 | 0
2021-12-30 21:00 | 5.7676 | 0 | N/A | 0 | 0
2021-12-30 21:30 | 5.2607 | 0 | N/A | 0 | 0
2021-12-30 22:00 | 4.6509 | 0 | N/A | 0 | 0
2021-12-30 22:30 | 4.7398 | 0 | N/A | 0 | 0
2021-12-30 23:00 | 4.6394 | 0 | N/A | 0 | 0
2021-12-30 23:30 | 4.1588 | 0 | N/A | 0 | 0
2021-12-31 | 4.1684 | 0 | N/A | 0 | 0
2021-12-31 00:30 | 4.5671 | 0 | N/A | 0 | 0
2021-12-31 01:00 | 4.4908 | 0 | N/A | 0 | 0
2021-12-31 01:30 | 3.6018 | 0 | N/A | 0 | 0
2021-12-31 02:00 | 2.9422 | 0 | N/A | 0 | 0
2021-12-31 02:30 | 2.9305 | 0 | N/A | 0 | 0
2021-12-31 03:00 | 2.6648 | 0 | N/A | 0 | 0
2021-12-31 03:30 | 2.4616 | 0 | N/A | 0 | 0
2021-12-31 04:00 | 2.2883 | 0 | N/A | 0 | 0
2021-12-31 04:30 | 2.3107 | 0 | N/A | 0 | 0
2021-12-31 05:00 | 2.2585 | 0 | N/A | 0 | 0
2021-12-31 05:30 | 2.3399 | 0 | N/A | 0 | 0
2021-12-31 06:00 | 2.3692 | 0 | N/A | 0 | 0
2021-12-31 06:30 | 2.5071 | 0 | N/A | 0 | 0
2021-12-31 07:00 | 2.5174 | 0 | N/A | 0 | 0
2021-12-31 07:30 | 2.5449 | 0 | N/A | 0 | 0
2021-12-31 08:00 | 2.3331 | 0 | N/A | 0 | 0
2021-12-31 08:30 | 1.8575 | 0 | N/A | 0 | 0
2021-12-31 09:00 | 1.4361 | 0 | N/A | 0 | 0
2021-12-31 09:30 | 1.0807 | 0 | N/A | 0 | 0
2021-12-31 10:00 | 0.71467 | 0 | N/A | 0 | 0
2021-12-31 10:30 | 0.44284 | 0 | N/A | 0 | 0
2021-12-31 11:00 | 0.25309 | 0 | N/A | 0 | 0
2021-12-31 11:30 | 0.23537 | 0 | N/A | 0 | 0
2021-12-31 12:00 | 0.23002 | 0 | N/A | 0 | 0
2021-12-31 12:30 | 0.48671 | 0 | N/A | 0 | 0
2021-12-31 13:00 | 0.68541 | 0 | N/A | 0 | 0
2021-12-31 13:30 | 0.95425 | 0 | N/A | 0 | 0
2021-12-31 14:00 | 1.1856 | 0 | N/A | 0 | 0
2021-12-31 14:30 | 1.581 | 0 | N/A | 0 | 0
2021-12-31 15:00 | 1.9881 | 0 | N/A | 0 | 0
2021-12-31 15:30 | 2.594 | 0 | N/A | 0 | 0
2021-12-31 16:00 | 3.1507 | 0 | N/A | 0 | 0
2021-12-31 16:30 | 3.804 | 0 | N/A | 0 | 0
2021-12-31 17:00 | 4.7567 | 0 | N/A | 0 | 0
2021-12-31 17:30 | 5.4767 | 0 | N/A | 0 | 0
2021-12-31 18:00 | 5.8669 | 0 | N/A | 0 | 0
2021-12-31 18:30 | 6.8106 | 0 | N/A | 0 | 0
2021-12-31 19:00 | 7.327 | 0 | N/A | 0 | 0
2021-12-31 19:30 | 7.2703 | 0 | N/A | 0 | 0
2021-12-31 20:00 | 7.2034 | 0 | N/A | 0 | 0
2021-12-31 20:30 | 6.81 | 0 | N/A | 0 | 0
2021-12-31 21:00 | 6.3635 | 0 | N/A | 0 | 0
2021-12-31 21:30 | 5.6951 | 0 | N/A | 0 | 0
2021-12-31 22:00 | 5.1142 | 0 | N/A | 0 | 0
2021-12-31 22:30 | 5.1059 | 0 | N/A | 0 | 0
2021-12-31 23:00 | 4.9404 | 0 | N/A | 0 | 0
2021-12-31 23:30 | 4.5256 | 0 | N/A | 0 | 0
2022-01-01 | 4.4361 | 0 | N/A | 0 | 0
2022-01-01 00:30 | 4.8758 | 0 | N/A | 0 | 0
2022-01-01 01:00 | 4.7647 | 0 | N/A | 0 | 0
2022-01-01 01:30 | 3.7394 | 0 | N/A | 0 | 0
2022-01-01 02:00 | 3.1425 | 0 | N/A | 0 | 0
2022-01-01 02:30 | 3.0763 | 0 | N/A | 0 | 0
2022-01-01 03:00 | 2.8196 | 0 | N/A | 0 | 0
2022-01-01 03:30 | 2.5298 | 0 | N/A | 0 | 0
2022-01-01 04:00 | 2.3877 | 0 | N/A | 0 | 0
2022-01-01 04:30 | 2.3677 | 0 | N/A | 0 | 0
2022-01-01 05:00 | 2.3014 | 0 | N/A | 0 | 0
2022-01-01 05:30 | 2.2985 | 0 | N/A | 0 | 0
2022-01-01 06:00 | 2.3769 | 0 | N/A | 0 | 0
2022-01-01 06:30 | 2.3992 | 0 | N/A | 0 | 0
2022-01-01 07:00 | 2.3431 | 0 | N/A | 0 | 0
2022-01-01 07:30 | 2.3338 | 0 | N/A | 0 | 0
2022-01-01 08:00 | 2.0923 | 0 | N/A | 0 | 0
2022-01-01 08:30 | 1.8048 | 0 | N/A | 0 | 0
2022-01-01 09:00 | 1.469 | 0 | N/A | 0 | 0
2022-01-01 09:30 | 1.2577 | 0 | N/A | 0 | 0
2022-01-01 10:00 | 1.1309 | 0 | N/A | 0 | 0
2022-01-01 10:30 | 0.95641 | 0 | N/A | 0 | 0
2022-01-01 11:00 | 1.1927 | 0 | N/A | 0 | 0
2022-01-01 11:30 | 2.5067 | 0 | N/A | 0 | 0
2022-01-01 12:00 | 2.0385 | 0 | N/A | 0 | 0
2022-01-01 12:30 | 2.5544 | 0 | N/A | 0 | 0
2022-01-01 13:00 | 2.4143 | 0 | N/A | 0 | 0
2022-01-01 13:30 | 2.1077 | 0 | N/A | 0 | 0
2022-01-01 14:00 | 2.8927 | 0 | N/A | 0 | 0
2022-01-01 14:30 | 2.9099 | 0 | N/A | 0 | 0
2022-01-01 15:00 | 3.1886 | 0 | N/A | 0 | 0
2022-01-01 15:30 | 4.9082 | 0 | N/A | 0 | 0
2022-01-01 16:00 | 4.3447 | 0 | N/A | 0 | 0
2022-01-01 16:30 | 4.3668 | 0 | N/A | 0 | 0
2022-01-01 17:00 | 5.7029 | 0 | N/A | 0 | 0
2022-01-01 17:30 | 5.8012 | 0 | N/A | 0 | 0
2022-01-01 18:00 | 5.7808 | 0 | N/A | 0 | 0
2022-01-01 18:30 | 5.771 | 0 | N/A | 0 | 0
2022-01-01 19:00 | 5.8583 | 0 | N/A | 0 | 0
2022-01-01 19:30 | 5.6115 | 0 | N/A | 0 | 0
2022-01-01 20:00 | 5.4577 | 0 | N/A | 0 | 0
2022-01-01 20:30 | 5.2258 | 0 | N/A | 0 | 0
2022-01-01 21:00 | 4.9925 | 0 | N/A | 0 | 0
2022-01-01 21:30 | 4.7934 | 0 | N/A | 0 | 0
2022-01-01 22:00 | 4.3819 | 0 | N/A | 0 | 0
2022-01-01 22:30 | 4.4157 | 0 | N/A | 0 | 0
2022-01-01 23:00 | 4.3177 | 0 | N/A | 0 | 0
2022-01-01 23:30 | 3.9403 | 0 | N/A | 0 | 0
2022-01-02 | 3.9787 | 0 | N/A | 0 | 0
2022-01-02 00:30 | 4.4289 | 0 | N/A | 0 | 0
2022-01-02 01:00 | 4.4607 | 0 | N/A | 0 | 0
2022-01-02 01:30 | 3.4396 | 0 | N/A | 0 | 0
2022-01-02 02:00 | 2.832 | 0 | N/A | 0 | 0
2022-01-02 02:30 | 2.8467 | 0 | N/A | 0 | 0
2022-01-02 03:00 | 2.5932 | 0 | N/A | 0 | 0
2022-01-02 03:30 | 2.4218 | 0 | N/A | 0 | 0
2022-01-02 04:00 | 2.3561 | 0 | N/A | 0 | 0
2022-01-02 04:30 | 2.3243 | 0 | N/A | 0 | 0
2022-01-02 05:00 | 2.2355 | 0 | N/A | 0 | 0
2022-01-02 05:30 | 2.2832 | 0 | N/A | 0 | 0
2022-01-02 06:00 | 2.3218 | 0 | N/A | 0 | 0
2022-01-02 06:30 | 2.3955 | 0 | N/A | 0 | 0
2022-01-02 07:00 | 2.458 | 0 | N/A | 0 | 0
2022-01-02 07:30 | 2.6239 | 0 | N/A | 0 | 0
2022-01-02 08:00 | 2.6451 | 0 | N/A | 0 | 0
2022-01-02 08:30 | 2.0954 | 0 | N/A | 0 | 0
2022-01-02 09:00 | 1.609 | 0 | N/A | 0 | 0
2022-01-02 09:30 | 0.93393 | 0 | N/A | 0 | 0
2022-01-02 10:00 | 0.68735 | 0 | N/A | 0 | 0
2022-01-02 10:30 | 0.52873 | 0 | N/A | 0 | 0
2022-01-02 11:00 | 0.41955 | 0 | N/A | 0 | 0
2022-01-02 11:30 | 0.41426 | 0 | N/A | 0 | 0
2022-01-02 12:00 | 0.51236 | 0 | N/A | 0 | 0
2022-01-02 12:30 | 0.74091 | 0 | N/A | 0 | 0
2022-01-02 13:00 | 0.82 | 0 | N/A | 0 | 0
2022-01-02 13:30 | 1.7547 | 0 | N/A | 0 | 0
2022-01-02 14:00 | 2.5851 | 0 | N/A | 0 | 0
2022-01-02 14:30 | 2.5434 | 0 | N/A | 0 | 0
2022-01-02 15:00 | 2.8754 | 0 | N/A | 0 | 0
2022-01-02 15:30 | 3.5334 | 0 | N/A | 0 | 0
2022-01-02 16:00 | 3.2775 | 0 | N/A | 0 | 0
2022-01-02 16:30 | 3.3969 | 0 | N/A | 0 | 0
2022-01-02 17:00 | 3.5633 | 0 | N/A | 0 | 0
2022-01-02 17:30 | 4.4667 | 0 | N/A | 0 | 0
2022-01-02 18:00 | 4.6914 | 0 | N/A | 0 | 0
2022-01-02 18:30 | 4.8175 | 0 | N/A | 0 | 0
2022-01-02 19:00 | 5.3717 | 0 | N/A | 0 | 0
2022-01-02 19:30 | 5.3027 | 0 | N/A | 0 | 0
2022-01-02 20:00 | 5.0612 | 0 | N/A | 0 | 0
2022-01-02 20:30 | 4.7824 | 0 | N/A | 0 | 0
2022-01-02 21:00 | 4.4331 | 0 | N/A | 0 | 0
2022-01-02 21:30 | 4.0992 | 0 | N/A | 0 | 0
2022-01-02 22:00 | 3.8512 | 0 | N/A | 0 | 0
2022-01-02 22:30 | 4.1787 | 0 | N/A | 0 | 0
2022-01-02 23:00 | 4.2696 | 0 | N/A | 0 | 0
2022-01-02 23:30 | 3.975 | 0 | N/A | 0 | 0
2022-01-03 | 4.0116 | 0 | N/A | 0 | 0
2022-01-03 00:30 | 4.4114 | 0 | N/A | 0 | 0
2022-01-03 01:00 | 4.4987 | 0 | N/A | 0 | 0
2022-01-03 01:30 | 3.5631 | 0 | N/A | 0 | 0
2022-01-03 02:00 | 2.9118 | 0 | N/A | 0 | 0
2022-01-03 02:30 | 2.8324 | 0 | N/A | 0 | 0
2022-01-03 03:00 | 2.5172 | 0 | N/A | 0 | 0
2022-01-03 03:30 | 2.2705 | 0 | N/A | 0 | 0
2022-01-03 04:00 | 2.1838 | 0 | N/A | 0 | 0
2022-01-03 04:30 | 2.1153 | 0 | N/A | 0 | 0
2022-01-03 05:00 | 2.1124 | 0 | N/A | 0 | 0
2022-01-03 05:30 | 2.1221 | 0 | N/A | 0 | 0
2022-01-03 06:00 | 2.2647 | 0 | N/A | 0 | 0
2022-01-03 06:30 | 2.3942 | 0 | N/A | 0 | 0
2022-01-03 07:00 | 2.4361 | 0 | N/A | 0 | 0
2022-01-03 07:30 | 2.3887 | 0 | N/A | 0 | 0
2022-01-03 08:00 | 2.236 | 0 | N/A | 0 | 0
2022-01-03 08:30 | 1.8102 | 0 | N/A | 0 | 0
2022-01-03 09:00 | 1.4086 | 0 | N/A | 0 | 0
2022-01-03 09:30 | 1.0844 | 0 | N/A | 0 | 0
2022-01-03 10:00 | 0.75047 | 0 | N/A | 0 | 0
2022-01-03 10:30 | -0.94991 | 0 | N/A | 0 | 0
2022-01-03 11:00 | -1.4441 | 0 | N/A | 0 | 0
2022-01-03 11:30 | -1.7976 | 0 | N/A | 0 | 0
2022-01-03 12:00 | -1.9598 | 0 | N/A | 0 | 0
2022-01-03 12:30 | -2.0456 | 0 | N/A | 0 | 0
2022-01-03 13:00 | -2.1514 | 0 | N/A | 0 | 0
2022-01-03 13:30 | -2.2983 | 0 | N/A | 0 | 0
2022-01-03 14:00 | -2.243 | 0 | N/A | 0 | 0
2022-01-03 14:30 | -2.1893 | 0 | N/A | 0 | 0
2022-01-03 15:00 | -2.0891 | 0 | N/A | 0 | 0
2022-01-03 15:30 | -1.9717 | 0 | N/A | 0 | 0
2022-01-03 16:00 | -1.7205 | 0 | N/A | 0 | 0
2022-01-03 16:30 | -1.2867 | 0 | N/A | 0 | 0
2022-01-03 17:00 | -0.6768 | 0 | N/A | 0 | 0
2022-01-03 17:30 | 0.61717 | 0 | N/A | 0 | 0
2022-01-03 18:00 | 1.4206 | 0 | N/A | 0 | 0
2022-01-03 18:30 | 2.2995 | 0 | N/A | 0 | 0
2022-01-03 19:00 | 2.9154 | 0 | N/A | 0 | 0
2022-01-03 19:30 | 3.3527 | 0 | N/A | 0 | 0
2022-01-03 20:00 | 3.6283 | 0 | N/A | 0 | 0
2022-01-03 20:30 | 3.82 | 0 | N/A | 0 | 0
2022-01-03 21:00 | 3.955 | 0 | N/A | 0 | 0
2022-01-03 21:30 | 3.8398 | 0 | N/A | 0 | 0
2022-01-03 22:00 | 3.7106 | 0 | N/A | 0 | 0
2022-01-03 22:30 | 4.0196 | 0 | N/A | 0 | 0
2022-01-03 23:00 | 4.1797 | 0 | N/A | 0 | 0
2022-01-03 23:30 | 3.8392 | 0 | N/A | 0 | 0
2022-01-04 | 3.9077 | 0 | N/A | 0 | 0
2022-01-04 00:30 | 4.2622 | 0 | N/A | 0 | 0
2022-01-04 01:00 | 4.4228 | 0 | N/A | 0 | 0
2022-01-04 01:30 | 3.624 | 0 | N/A | 0 | 0
2022-01-04 02:00 | 3.0466 | 0 | N/A | 0 | 0
2022-01-04 02:30 | 2.9683 | 0 | N/A | 0 | 0
2022-01-04 03:00 | 2.6739 | 0 | N/A | 0 | 0
2022-01-04 03:30 | 2.3423 | 0 | N/A | 0 | 0
2022-01-04 04:00 | 2.2626 | 0 | N/A | 0 | 0
2022-01-04 04:30 | 2.2748 | 0 | N/A | 0 | 0
2022-01-04 05:00 | 2.243 | 0 | N/A | 0 | 0
2022-01-04 05:30 | 2.2988 | 0 | N/A | 0 | 0
2022-01-04 06:00 | 2.4106 | 0 | N/A | 0 | 0
2022-01-04 06:30 | 2.5816 | 0 | N/A | 0 | 0
2022-01-04 07:00 | 2.6822 | 0 | N/A | 0 | 0
2022-01-04 07:30 | 2.9422 | 0 | N/A | 0 | 0
2022-01-04 08:00 | 2.9019 | 0 | N/A | 0 | 0
2022-01-04 08:30 | 2.4292 | 0 | N/A | 0 | 0
2022-01-04 09:00 | 2.2616 | 0 | N/A | 0 | 0
2022-01-04 09:30 | 2.7417 | 0 | N/A | 0 | 0
2022-01-04 10:00 | 2.4026 | 0 | N/A | 0 | 0
2022-01-04 10:30 | 2.5183 | 0 | N/A | 0 | 0
2022-01-04 11:00 | 2.4165 | 0 | N/A | 0 | 0
2022-01-04 11:30 | 2.3411 | 0 | N/A | 0 | 0
2022-01-04 12:00 | 2.3868 | 0 | N/A | 0 | 0
2022-01-04 12:30 | 2.5995 | 0 | N/A | 0 | 0
2022-01-04 13:00 | 3.0605 | 0 | N/A | 0 | 0
2022-01-04 13:30 | 2.7847 | 0 | N/A | 0 | 0
2022-01-04 14:00 | 2.9622 | 0 | N/A | 0 | 0
2022-01-04 14:30 | 3.2028 | 0 | N/A | 0 | 0
2022-01-04 15:00 | 3.3988 | 0 | N/A | 0 | 0
2022-01-04 15:30 | 3.191 | 0 | N/A | 0 | 0
2022-01-04 16:00 | 3.0469 | 0 | N/A | 0 | 0
2022-01-04 16:30 | 2.7404 | 0 | N/A | 0 | 0
2022-01-04 17:00 | 2.9171 | 0 | N/A | 0 | 0
2022-01-04 17:30 | 3.6405 | 0 | N/A | 0 | 0
2022-01-04 18:00 | 4.216 | 0 | N/A | 0 | 0
2022-01-04 18:30 | 4.3959 | 0 | N/A | 0 | 0
2022-01-04 19:00 | 4.618 | 0 | N/A | 0 | 0
2022-01-04 19:30 | 4.5042 | 0 | N/A | 0 | 0
2022-01-04 20:00 | 4.4586 | 0 | N/A | 0 | 0
2022-01-04 20:30 | 4.4094 | 0 | N/A | 0 | 0
2022-01-04 21:00 | 4.3377 | 0 | N/A | 0 | 0
2022-01-04 21:30 | 4.1629 | 0 | N/A | 0 | 0
2022-01-04 22:00 | 3.8744 | 0 | N/A | 0 | 0
2022-01-04 22:30 | 4.1868 | 0 | N/A | 0 | 0
2022-01-04 23:00 | 4.2638 | 0 | N/A | 0 | 0
2022-01-04 23:30 | 0.92494 | 0 | N/A | 0 | 0
2022-01-05 | 0 | 0 | N/A | 0 | 0
2022-01-05 00:30 | 0 | 0 | N/A | 0 | 0
2022-01-05 01:00 | 1.6673 | 0 | N/A | 0 | 0
2022-01-05 01:30 | 5.6702 | 0 | N/A | 0 | 0
2022-01-05 02:00 | 4.731 | 0 | N/A | 0 | 0
2022-01-05 02:30 | 4.8296 | 0 | N/A | 0 | 0
2022-01-05 03:00 | 4.2481 | 0 | N/A | 0 | 0
2022-01-05 03:30 | 3.2477 | 0 | N/A | 0 | 0
2022-01-05 04:00 | 2.7938 | 0 | N/A | 0 | 0
2022-01-05 04:30 | 2.4859 | 0 | N/A | 0 | 0
2022-01-05 05:00 | 2.2988 | 0 | N/A | 0 | 0
2022-01-05 05:30 | 2.3395 | 0 | N/A | 0 | 0
2022-01-05 06:00 | 2.3621 | 0 | N/A | 0 | 0
2022-01-05 06:30 | 2.549 | 0 | N/A | 0 | 0
2022-01-05 07:00 | 2.6572 | 0 | N/A | 0 | 0
2022-01-05 07:30 | 2.818 | 0 | N/A | 0 | 0
2022-01-05 08:00 | 2.8419 | 0 | N/A | 0 | 0
2022-01-05 08:30 | 2.6006 | 0 | N/A | 0 | 0
2022-01-05 09:00 | 2.6736 | 0 | N/A | 0 | 0
2022-01-05 09:30 | 2.6439 | 0 | N/A | 0 | 0
2022-01-05 10:00 | 2.6203 | 0 | N/A | 0 | 0
2022-01-05 10:30 | 2.7294 | 0 | N/A | 0 | 0
2022-01-05 11:00 | 2.9631 | 0 | N/A | 0 | 0
2022-01-05 11:30 | 3.0636 | 0 | N/A | 0 | 0
2022-01-05 12:00 | 2.8755 | 0 | N/A | 0 | 0
2022-01-05 12:30 | 1.9585 | 0 | N/A | 0 | 0
2022-01-05 13:00 | 1.1687 | 0 | N/A | 0 | 0
2022-01-05 13:30 | 0.93473 | 0 | N/A | 0 | 0
2022-01-05 14:00 | 0.8823 | 0 | N/A | 0 | 0
2022-01-05 14:30 | 0.638 | 0 | N/A | 0 | 0
2022-01-05 15:00 | 1.6096 | 0 | N/A | 0 | 0
2022-01-05 15:30 | 2.546 | 0 | N/A | 0 | 0
2022-01-05 16:00 | 3.5196 | 0 | N/A | 0 | 0
2022-01-05 16:30 | 3.9463 | 0 | N/A | 0 | 0
2022-01-05 17:00 | 4.3552 | 0 | N/A | 0 | 0
2022-01-05 17:30 | 4.8838 | 0 | N/A | 0 | 0
2022-01-05 18:00 | 5.0818 | 0 | N/A | 0 | 0
2022-01-05 18:30 | 5.3839 | 0 | N/A | 0 | 0
2022-01-05 19:00 | 6.2911 | 0 | N/A | 0 | 0
2022-01-05 19:30 | 4.8674 | 0 | N/A | 0 | 0
2022-01-05 20:00 | 4.8845 | 0 | N/A | 0 | 0
2022-01-05 20:30 | 4.4969 | 0 | N/A | 0 | 0
2022-01-05 21:00 | 4.0881 | 0 | N/A | 0 | 0
2022-01-05 21:30 | 3.8889 | 0 | N/A | 0 | 0
2022-01-05 22:00 | 3.7129 | 0 | N/A | 0 | 0
2022-01-05 22:30 | 4.0015 | 0 | N/A | 0 | 0
2022-01-05 23:00 | 4.1025 | 0 | N/A | 0 | 0
2022-01-05 23:30 | 3.7504 | 0 | N/A | 0 | 0
2022-01-06 | 3.9132 | 0 | N/A | 0 | 0
2022-01-07 00:30 | 4.4625 | 0 | N/A | 0 | 0
2022-01-07 01:00 | 4.6737 | 0 | N/A | 0 | 0
2022-01-07 01:30 | 3.744 | 0 | N/A | 0 | 0
2022-01-07 02:00 | 3.0661 | 0 | N/A | 0 | 0
2022-01-07 02:30 | 3.0266 | 0 | N/A | 0 | 0
2022-01-07 03:00 | 2.7342 | 0 | N/A | 0 | 0
2022-01-07 03:30 | 2.4693 | 0 | N/A | 0 | 0
2022-01-07 04:00 | 2.2706 | 0 | N/A | 0 | 0
2022-01-07 04:30 | 2.26 | 0 | N/A | 0 | 0
2022-01-07 05:00 | 2.254 | 0 | N/A | 0 | 0
2022-01-07 05:30 | 2.3577 | 0 | N/A | 0 | 0
2022-01-07 06:00 | 2.4064 | 0 | N/A | 0 | 0
2022-01-07 06:30 | 2.4668 | 0 | N/A | 0 | 0
2022-01-07 07:00 | 2.5815 | 0 | N/A | 0 | 0
2022-01-07 07:30 | 2.6203 | 0 | N/A | 0 | 0
2022-01-07 08:00 | 2.4879 | 0 | N/A | 0 | 0
2022-01-07 08:30 | 2.1903 | 0 | N/A | 0 | 0
2022-01-07 09:00 | 2.5361 | 0 | N/A | 0 | 0
2022-01-07 09:30 | 3.0784 | 0 | N/A | 0 | 0
2022-01-07 10:00 | 3.1302 | 0 | N/A | 0 | 0
2022-01-07 10:30 | 3.0538 | 0 | N/A | 0 | 0
2022-01-07 11:00 | 3.3801 | 0 | N/A | 0 | 0
2022-01-07 11:30 | 3.3291 | 0 | N/A | 0 | 0
2022-01-07 12:00 | 2.8705 | 0 | N/A | 0 | 0
2022-01-07 12:30 | 2.8701 | 0 | N/A | 0 | 0
2022-01-07 13:00 | 2.8498 | 0 | N/A | 0 | 0
2022-01-07 13:30 | -0.32804 | 0 | N/A | 0 | 0
2022-01-07 14:00 | 0.77964 | 0 | N/A | 0 | 0
2022-01-07 14:30 | 1.4101 | 0 | N/A | 0 | 0
2022-01-07 15:00 | 2.1573 | 0 | N/A | 0 | 0
2022-01-07 15:30 | 3.3703 | 0 | N/A | 0 | 0
2022-01-07 16:00 | 1.8855 | 0 | N/A | 0 | 0
2022-01-07 16:30 | 2.763 | 0 | N/A | 0 | 0
2022-01-07 17:00 | 4.8552 | 0 | N/A | 0 | 0
2022-01-07 17:30 | 3.857 | 0 | N/A | 0 | 0
2022-01-07 18:00 | 2.6841 | 0 | N/A | 0 | 0
2022-01-07 18:30 | 4.0799 | 0 | N/A | 0 | 0
2022-01-07 19:00 | 4.8109 | 0 | N/A | 0 | 0
2022-01-07 19:30 | 4.1363 | 0 | N/A | 0 | 0
2022-01-07 20:00 | 3.5559 | 0 | N/A | 0 | 0
2022-01-07 20:30 | 3.8016 | 0 | N/A | 0 | 0
2022-01-07 21:00 | 3.9389 | 0 | N/A | 0 | 0
2022-01-07 21:30 | 3.9127 | 0 | N/A | 0 | 0
2022-01-07 22:00 | 3.8351 | 0 | N/A | 0 | 0
2022-01-07 22:30 | 4.1468 | 0 | N/A | 0 | 0
2022-01-07 23:00 | 4.299 | 0 | N/A | 0 | 0
2022-01-07 23:30 | 3.97 | 0 | N/A | 0 | 0
2022-01-08 | 4.0537 | 0 | N/A | 0 | 0
2022-01-08 00:30 | 4.5858 | 0 | N/A | 0 | 0
2022-01-08 01:00 | 4.7475 | 0 | N/A | 0 | 0
2022-01-08 01:30 | 3.8151 | 0 | N/A | 0 | 0
2022-01-08 02:00 | 3.2026 | 0 | N/A | 0 | 0
2022-01-08 02:30 | 3.156 | 0 | N/A | 0 | 0
2022-01-08 03:00 | 2.8348 | 0 | N/A | 0 | 0
2022-01-08 03:30 | 2.5141 | 0 | N/A | 0 | 0
2022-01-08 04:00 | 2.3829 | 0 | N/A | 0 | 0
2022-01-08 04:30 | 2.4131 | 0 | N/A | 0 | 0
2022-01-08 05:00 | 2.3198 | 0 | N/A | 0 | 0
2022-01-08 05:30 | 2.3512 | 0 | N/A | 0 | 0
2022-01-08 06:00 | 2.3898 | 0 | N/A | 0 | 0
2022-01-08 06:30 | 2.5212 | 0 | N/A | 0 | 0
2022-01-08 07:00 | 2.5768 | 0 | N/A | 0 | 0
2022-01-08 07:30 | 2.6826 | 0 | N/A | 0 | 0
2022-01-08 08:00 | 2.6237 | 0 | N/A | 0 | 0
2022-01-08 08:30 | 2.4952 | 0 | N/A | 0 | 0
2022-01-08 09:00 | 2.4673 | 0 | N/A | 0 | 0
2022-01-08 09:30 | 2.2301 | 0 | N/A | 0 | 0
2022-01-08 10:00 | 1.9157 | 0 | N/A | 0 | 0
2022-01-08 10:30 | 1.6419 | 0 | N/A | 0 | 0
2022-01-08 11:00 | 1.7355 | 0 | N/A | 0 | 0
2022-01-08 11:30 | 1.9827 | 0 | N/A | 0 | 0
2022-01-08 12:00 | 2.2396 | 0 | N/A | 0 | 0
2022-01-08 12:30 | 2.1372 | 0 | N/A | 0 | 0
2022-01-08 13:00 | 2.1419 | 0 | N/A | 0 | 0
2022-01-08 13:30 | 2.163 | 0 | N/A | 0 | 0
2022-01-08 14:00 | 1.807 | 0 | N/A | 0 | 0
2022-01-08 14:30 | 2.1458 | 0 | N/A | 0 | 0
2022-01-08 15:00 | 1.6101 | 0 | N/A | 0 | 0
2022-01-08 15:30 | 0.78622 | 0 | N/A | 0 | 0
2022-01-08 16:00 | 0.65832 | 0 | N/A | 0 | 0
2022-01-08 16:30 | 1.1068 | 0 | N/A | 0 | 0
2022-01-08 17:00 | 0.9088 | 0 | N/A | 0 | 0
2022-01-08 17:30 | 1.1755 | 0 | N/A | 0 | 0
2022-01-08 18:00 | 2.2474 | 0 | N/A | 0 | 0
2022-01-08 18:30 | 3.2872 | 0 | N/A | 0 | 0
2022-01-08 19:00 | 3.7458 | 0 | N/A | 0 | 0
2022-01-08 19:30 | 3.8442 | 0 | N/A | 0 | 0
2022-01-08 20:00 | 3.8119 | 0 | N/A | 0 | 0
2022-01-08 20:30 | 3.8617 | 0 | N/A | 0 | 0
2022-01-08 21:00 | 3.7775 | 0 | N/A | 0 | 0
2022-01-08 21:30 | 3.695 | 0 | N/A | 0 | 0
2022-01-08 22:00 | 3.5993 | 0 | N/A | 0 | 0
2022-01-08 22:30 | 3.9358 | 0 | N/A | 0 | 0
2022-01-08 23:00 | 4.1078 | 0 | N/A | 0 | 0
2022-01-08 23:30 | 3.8793 | 0 | N/A | 0 | 0
2022-01-09 | 4.01 | 0 | N/A | 0 | 0
2022-01-09 00:30 | 4.3393 | 0 | N/A | 0 | 0
2022-01-09 01:00 | 4.6 | 0 | N/A | 0 | 0
2022-01-09 01:30 | 3.7804 | 0 | N/A | 0 | 0
2022-01-09 02:00 | 3.0906 | 0 | N/A | 0 | 0
2022-01-09 02:30 | 3.0372 | 0 | N/A | 0 | 0
2022-01-09 03:00 | 2.7601 | 0 | N/A | 0 | 0
2022-01-09 03:30 | 2.3898 | 0 | N/A | 0 | 0
2022-01-09 04:00 | 2.2908 | 0 | N/A | 0 | 0
2022-01-09 04:30 | 2.1917 | 0 | N/A | 0 | 0
2022-01-09 05:00 | 2.2008 | 0 | N/A | 0 | 0
2022-01-09 05:30 | 2.2353 | 0 | N/A | 0 | 0
2022-01-09 06:00 | 2.3485 | 0 | N/A | 0 | 0
2022-01-09 06:30 | 2.3335 | 0 | N/A | 0 | 0
2022-01-09 07:00 | 2.3949 | 0 | N/A | 0 | 0
2022-01-09 07:30 | 2.4344 | 0 | N/A | 0 | 0
2022-01-09 08:00 | 2.292 | 0 | N/A | 0 | 0
2022-01-09 08:30 | 1.8894 | 0 | N/A | 0 | 0
2022-01-09 09:00 | 1.5048 | 0 | N/A | 0 | 0
2022-01-09 09:30 | 1.0282 | 0 | N/A | 0 | 0
2022-01-09 10:00 | 0.67674 | 0 | N/A | 0 | 0
2022-01-09 10:30 | -0.67844 | 0 | N/A | 0 | 0
2022-01-09 11:00 | -0.91074 | 0 | N/A | 0 | 0
2022-01-09 11:30 | -1.2544 | 0 | N/A | 0 | 0
2022-01-09 12:00 | -1.3832 | 0 | N/A | 0 | 0
2022-01-09 12:30 | -1.4972 | 0 | N/A | 0 | 0
2022-01-09 13:00 | -1.477 | 0 | N/A | 0 | 0
2022-01-09 13:30 | -1.4794 | 0 | N/A | 0 | 0
2022-01-09 14:00 | -1.5219 | 0 | N/A | 0 | 0
2022-01-09 14:30 | -1.5805 | 0 | N/A | 0 | 0
2022-01-09 15:00 | -1.4639 | 0 | N/A | 0 | 0
2022-01-09 15:30 | -1.2338 | 0 | N/A | 0 | 0
2022-01-09 16:00 | -0.94455 | 0 | N/A | 0 | 0
2022-01-09 16:30 | -0.46861 | 0 | N/A | 0 | 0
2022-01-09 17:00 | 0.44375 | 0 | N/A | 0 | 0
2022-01-09 17:30 | 1.3092 | 0 | N/A | 0 | 0
2022-01-09 18:00 | 2.3443 | 0 | N/A | 0 | 0
2022-01-09 18:30 | 3.2513 | 0 | N/A | 0 | 0
2022-01-09 19:00 | 3.9446 | 0 | N/A | 0 | 0
2022-01-09 19:30 | 4.3091 | 0 | N/A | 0 | 0
2022-01-09 20:00 | 4.5 | 0 | N/A | 0 | 0
2022-01-09 20:30 | 4.4834 | 0 | N/A | 0 | 0
2022-01-09 21:00 | 4.2618 | 0 | N/A | 0 | 0
2022-01-09 21:30 | 4.1975 | 0 | N/A | 0 | 0
2022-01-09 22:00 | 3.9197 | 0 | N/A | 0 | 0
2022-01-09 22:30 | 4.21 | 0 | N/A | 0 | 0
2022-01-09 23:00 | 4.1969 | 0 | N/A | 0 | 0
2022-01-09 23:30 | 3.8586 | 0 | N/A | 0 | 0
2022-01-10 | 4.0252 | 0 | N/A | 0 | 0
2022-01-10 00:30 | 4.3037 | 0 | N/A | 0 | 0
2022-01-10 01:00 | 4.5113 | 0 | N/A | 0 | 0
2022-01-10 01:30 | 3.782 | 0 | N/A | 0 | 0
2022-01-10 02:00 | 3.1032 | 0 | N/A | 0 | 0
2022-01-10 02:30 | 3.0309 | 0 | N/A | 0 | 0
2022-01-10 03:00 | 2.6272 | 0 | N/A | 0 | 0
2022-01-10 03:30 | 2.3255 | 0 | N/A | 0 | 0
2022-01-10 04:00 | 2.2265 | 0 | N/A | 0 | 0
2022-01-10 04:30 | 2.1909 | 0 | N/A | 0 | 0
2022-01-10 05:00 | 2.2379 | 0 | N/A | 0 | 0
2022-01-10 05:30 | 2.3204 | 0 | N/A | 0 | 0
2022-01-10 06:00 | 2.5302 | 0 | N/A | 0 | 0
2022-01-10 06:30 | 2.7607 | 0 | N/A | 0 | 0
2022-01-10 07:00 | 2.9296 | 0 | N/A | 0 | 0
2022-01-10 07:30 | 3.3109 | 0 | N/A | 0 | 0
2022-01-10 08:00 | 3.0664 | 0 | N/A | 0 | 0
2022-01-10 08:30 | 2.421 | 0 | N/A | 0 | 0
2022-01-10 09:00 | 2.1797 | 0 | N/A | 0 | 0
2022-01-10 09:30 | 1.7197 | 0 | N/A | 0 | 0
2022-01-10 10:00 | 1.093 | 0 | N/A | 0 | 0
2022-01-10 10:30 | 0.44777 | 0 | N/A | 0 | 0
2022-01-10 11:00 | 0.19195 | 0 | N/A | 0 | 0
2022-01-10 11:30 | 0.22333 | 0 | N/A | 0 | 0
2022-01-10 12:00 | 0.1567 | 0 | N/A | 0 | 0
2022-01-10 12:30 | 0.26367 | 0 | N/A | 0 | 0
2022-01-10 13:00 | 0.40679 | 0 | N/A | 0 | 0
2022-01-10 13:30 | 0.30319 | 0 | N/A | 0 | 0
2022-01-10 14:00 | 0.691 | 0 | N/A | 0 | 0
2022-01-10 14:30 | 1.1981 | 0 | N/A | 0 | 0
2022-01-10 15:00 | 1.3514 | 0 | N/A | 0 | 0
2022-01-10 15:30 | 1.8376 | 0 | N/A | 0 | 0
2022-01-10 16:00 | 2.6725 | 0 | N/A | 0 | 0
2022-01-10 16:30 | 3.4607 | 0 | N/A | 0 | 0
2022-01-10 17:00 | 3.5933 | 0 | N/A | 0 | 0
2022-01-10 17:30 | 4.5337 | 0 | N/A | 0 | 0
2022-01-10 18:00 | 5.508 | 0 | N/A | 0 | 0
2022-01-10 18:30 | 5.7234 | 0 | N/A | 0 | 0
2022-01-10 19:00 | 5.9515 | 0 | N/A | 0 | 0
2022-01-10 19:30 | 5.8797 | 0 | N/A | 0 | 0
2022-01-10 20:00 | 5.5556 | 0 | N/A | 0 | 0
2022-01-10 20:30 | 5.4034 | 0 | N/A | 0 | 0
2022-01-10 21:00 | 5.2025 | 0 | N/A | 0 | 0
2022-01-10 21:30 | 4.8863 | 0 | N/A | 0 | 0
2022-01-10 22:00 | 4.4885 | 0 | N/A | 0 | 0
2022-01-10 22:30 | 4.507 | 0 | N/A | 0 | 0
2022-01-10 23:00 | 4.4637 | 0 | N/A | 0 | 0
2022-01-10 23:30 | 4.1795 | 0 | N/A | 0 | 0
2022-01-11 | 4.0616 | 0 | N/A | 0 | 0
2022-01-11 00:30 | 4.3451 | 0 | N/A | 0 | 0
2022-01-11 01:00 | 4.3663 | 0 | N/A | 0 | 0
2022-01-11 01:30 | 3.5192 | 0 | N/A | 0 | 0
2022-01-11 02:00 | 2.8999 | 0 | N/A | 0 | 0
2022-01-11 02:30 | 2.9581 | 0 | N/A | 0 | 0
2022-01-11 03:00 | 2.6781 | 0 | N/A | 0 | 0
2022-01-11 03:30 | 2.3637 | 0 | N/A | 0 | 0
2022-01-11 04:00 | 2.2798 | 0 | N/A | 0 | 0
2022-01-11 04:30 | 2.2451 | 0 | N/A | 0 | 0
2022-01-11 05:00 | 2.248 | 0 | N/A | 0 | 0
2022-01-11 05:30 | 2.4633 | 0 | N/A | 0 | 0
2022-01-11 06:00 | 2.5837 | 0 | N/A | 0 | 0
2022-01-11 06:30 | 2.856 | 0 | N/A | 0 | 0
2022-01-11 07:00 | 3.1725 | 0 | N/A | 0 | 0
2022-01-11 07:30 | 3.5472 | 0 | N/A | 0 | 0
2022-01-11 08:00 | 3.4315 | 0 | N/A | 0 | 0
2022-01-11 08:30 | 3.2935 | 0 | N/A | 0 | 0
2022-01-11 09:00 | 3.26 | 0 | N/A | 0 | 0
2022-01-11 09:30 | 2.092 | 0 | N/A | 0 | 0
2022-01-11 10:00 | 0.59286 | 0 | N/A | 0 | 0
2022-01-11 10:30 | 0.39129 | 0 | N/A | 0 | 0
2022-01-11 11:00 | 0.16014 | 0 | N/A | 0 | 0
2022-01-11 11:30 | -0.12693 | 0 | N/A | 0 | 0
2022-01-11 12:00 | -0.18 | 0 | N/A | 0 | 0
2022-01-11 12:30 | -0.48667 | 0 | N/A | 0 | 0
2022-01-11 13:00 | 0.2361 | 0 | N/A | 0 | 0
2022-01-11 13:30 | 0.079022 | 0 | N/A | 0 | 0
2022-01-11 14:00 | 1.3668 | 0 | N/A | 0 | 0
2022-01-11 14:30 | 2.0353 | 0 | N/A | 0 | 0
2022-01-11 15:00 | 1.6134 | 0 | N/A | 0 | 0
2022-01-11 15:30 | 0.41382 | 0 | N/A | 0 | 0
2022-01-11 16:00 | 0.019437 | 0 | N/A | 0 | 0
2022-01-11 16:30 | 0.55862 | 0 | N/A | 0 | 0
2022-01-11 17:00 | 1.3303 | 0 | N/A | 0 | 0
2022-01-11 17:30 | 2.226 | 0 | N/A | 0 | 0
2022-01-11 18:00 | 3.2677 | 0 | N/A | 0 | 0
2022-01-11 18:30 | 4.1671 | 0 | N/A | 0 | 0
2022-01-11 19:00 | 4.7784 | 0 | N/A | 0 | 0
2022-01-11 19:30 | 5.1284 | 0 | N/A | 0 | 0
2022-01-11 20:00 | 5.2081 | 0 | N/A | 0 | 0
2022-01-11 20:30 | 5.088 | 0 | N/A | 0 | 0
2022-01-11 21:00 | 4.8822 | 0 | N/A | 0 | 0
2022-01-11 21:30 | 4.6209 | 0 | N/A | 0 | 0
2022-01-11 22:00 | 4.2452 | 0 | N/A | 0 | 0
2022-01-11 22:30 | 4.4256 | 0 | N/A | 0 | 0
2022-01-11 23:00 | 4.3929 | 0 | N/A | 0 | 0
2022-01-11 23:30 | 4.023 | 0 | N/A | 0 | 0
2022-01-12 | 3.9983 | 0 | N/A | 0 | 0
2022-01-12 00:30 | 4.4284 | 0 | N/A | 0 | 0
2022-01-12 01:00 | 4.6224 | 0 | N/A | 0 | 0
2022-01-12 01:30 | 3.6915 | 0 | N/A | 0 | 0
2022-01-12 02:00 | 3.081 | 0 | N/A | 0 | 0
2022-01-12 02:30 | 3.0202 | 0 | N/A | 0 | 0
2022-01-12 03:00 | 2.6962 | 0 | N/A | 0 | 0
2022-01-12 03:30 | 2.4829 | 0 | N/A | 0 | 0
2022-01-12 04:00 | 2.3414 | 0 | N/A | 0 | 0
2022-01-12 04:30 | 2.3204 | 0 | N/A | 0 | 0
2022-01-12 05:00 | 2.3261 | 0 | N/A | 0 | 0
2022-01-12 05:30 | 2.4196 | 0 | N/A | 0 | 0
2022-01-12 06:00 | 2.6728 | 0 | N/A | 0 | 0
2022-01-12 06:30 | 3.0379 | 0 | N/A | 0 | 0
2022-01-12 07:00 | 3.4804 | 0 | N/A | 0 | 0
2022-01-12 07:30 | 3.4822 | 0 | N/A | 0 | 0
2022-01-12 08:00 | 3.7916 | 0 | N/A | 0 | 0
2022-01-12 08:30 | 3.652 | 0 | N/A | 0 | 0
2022-01-12 09:00 | 3.479 | 0 | N/A | 0 | 0
2022-01-12 09:30 | 3.2108 | 0 | N/A | 0 | 0
2022-01-12 10:00 | 2.7797 | 0 | N/A | 0 | 0
2022-01-12 10:30 | 2.222 | 0 | N/A | 0 | 0
2022-01-12 11:00 | 1.0128 | 0 | N/A | 0 | 0
2022-01-12 11:30 | 0.1792 | 0 | N/A | 0 | 0
2022-01-12 12:00 | -0.13119 | 0 | N/A | 0 | 0
2022-01-12 12:30 | -0.15297 | 0 | N/A | 0 | 0
2022-01-12 13:00 | -0.33007 | 0 | N/A | 0 | 0
2022-01-12 13:30 | 0.13004 | 0 | N/A | 0 | 0
2022-01-12 14:00 | -0.28002 | 0 | N/A | 0 | 0
2022-01-12 14:30 | -0.12023 | 0 | N/A | 0 | 0
2022-01-12 15:00 | 0.19531 | 0 | N/A | 0 | 0
2022-01-12 15:30 | 1.5072 | 0 | N/A | 0 | 0
2022-01-12 16:00 | 0.85489 | 0 | N/A | 0 | 0
2022-01-12 16:30 | 2.346 | 0 | N/A | 0 | 0
2022-01-12 17:00 | 2.516 | 0 | N/A | 0 | 0
2022-01-12 17:30 | 3.1652 | 0 | N/A | 0 | 0
2022-01-12 18:00 | 4.2152 | 0 | N/A | 0 | 0
2022-01-12 18:30 | 5.1636 | 0 | N/A | 0 | 0
2022-01-12 19:00 | 5.0954 | 0 | N/A | 0 | 0
2022-01-12 19:30 | 4.7902 | 0 | N/A | 0 | 0
2022-01-12 20:00 | 4.7029 | 0 | N/A | 0 | 0
2022-01-12 20:30 | 4.6478 | 0 | N/A | 0 | 0
2022-01-12 21:00 | 4.6758 | 0 | N/A | 0 | 0
2022-01-12 21:30 | 4.4667 | 0 | N/A | 0 | 0
2022-01-12 22:00 | 4.1539 | 0 | N/A | 0 | 0
2022-01-12 22:30 | 4.3207 | 0 | N/A | 0 | 0
2022-01-12 23:00 | 4.307 | 0 | N/A | 0 | 0
2022-01-12 23:30 | 3.9544 | 0 | N/A | 0 | 0
2022-01-13 | 3.959 | 0 | N/A | 0 | 0
2022-01-13 00:30 | 4.3721 | 0 | N/A | 0 | 0
2022-01-13 01:00 | 4.5607 | 0 | N/A | 0 | 0
2022-01-13 01:30 | 3.6534 | 0 | N/A | 0 | 0
2022-01-13 02:00 | 3.0309 | 0 | N/A | 0 | 0
2022-01-13 02:30 | 3.0042 | 0 | N/A | 0 | 0
2022-01-13 03:00 | 2.7123 | 0 | N/A | 0 | 0
2022-01-13 03:30 | 2.4743 | 0 | N/A | 0 | 0
2022-01-13 04:00 | 2.3267 | 0 | N/A | 0 | 0
2022-01-13 04:30 | 2.3604 | 0 | N/A | 0 | 0
2022-01-13 05:00 | 2.3658 | 0 | N/A | 0 | 0
2022-01-13 05:30 | 2.4219 | 0 | N/A | 0 | 0
2022-01-13 06:00 | 2.6226 | 0 | N/A | 0 | 0
2022-01-13 06:30 | 2.8264 | 0 | N/A | 0 | 0
2022-01-13 07:00 | 3.0534 | 0 | N/A | 0 | 0
2022-01-13 07:30 | 3.5176 | 0 | N/A | 0 | 0
2022-01-13 08:00 | 3.4665 | 0 | N/A | 0 | 0
2022-01-13 08:30 | 2.9965 | 0 | N/A | 0 | 0
2022-01-13 09:00 | 2.5899 | 0 | N/A | 0 | 0
2022-01-13 09:30 | 1.9022 | 0 | N/A | 0 | 0
2022-01-13 10:00 | 1.3213 | 0 | N/A | 0 | 0
2022-01-13 10:30 | 1.3604 | 0 | N/A | 0 | 0
2022-01-13 11:00 | 1.2767 | 0 | N/A | 0 | 0
2022-01-13 11:30 | 0.86336 | 0 | N/A | 0 | 0
2022-01-13 12:00 | 1.4067 | 0 | N/A | 0 | 0
2022-01-13 12:30 | 1.4936 | 0 | N/A | 0 | 0
2022-01-13 13:00 | 1.094 | 0 | N/A | 0 | 0
2022-01-13 13:30 | 0.86447 | 0 | N/A | 0 | 0
2022-01-13 14:00 | 1.0555 | 0 | N/A | 0 | 0
2022-01-13 14:30 | 1.0804 | 0 | N/A | 0 | 0
2022-01-13 15:00 | 2.1635 | 0 | N/A | 0 | 0
2022-01-13 15:30 | 3.5017 | 0 | N/A | 0 | 0
2022-01-13 16:00 | 3.8272 | 0 | N/A | 0 | 0
2022-01-13 16:30 | 5.92 | 0 | N/A | 0 | 0
2022-01-13 17:00 | 6.4967 | 0 | N/A | 0 | 0
2022-01-13 17:30 | 5.7528 | 0 | N/A | 0 | 0
2022-01-13 18:00 | 4.9413 | 0 | N/A | 0 | 0
2022-01-13 18:30 | 3.8686 | 0 | N/A | 0 | 0
2022-01-13 19:00 | 4.3841 | 0 | N/A | 0 | 0
2022-01-13 19:30 | 4.7118 | 0 | N/A | 0 | 0
2022-01-13 20:00 | 4.7341 | 0 | N/A | 0 | 0
2022-01-13 20:30 | 4.7414 | 0 | N/A | 0 | 0
2022-01-13 21:00 | 4.7121 | 0 | N/A | 0 | 0
2022-01-13 21:30 | 4.5686 | 0 | N/A | 0 | 0
2022-01-13 22:00 | 4.3152 | 0 | N/A | 0 | 0
2022-01-13 22:30 | 4.4806 | 0 | N/A | 0 | 0
2022-01-13 23:00 | 4.4966 | 0 | N/A | 0 | 0
2022-01-13 23:30 | 4.0454 | 0 | N/A | 0 | 0
2022-01-14 | 4.0315 | 0 | N/A | 0 | 0
2022-01-14 00:30 | 4.3738 | 0 | N/A | 0 | 0
2022-01-14 01:00 | 4.5694 | 0 | N/A | 0 | 0
2022-01-14 01:30 | 3.6507 | 0 | N/A | 0 | 0
2022-01-14 02:00 | 2.9722 | 0 | N/A | 0 | 0
2022-01-14 02:30 | 2.9478 | 0 | N/A | 0 | 0
2022-01-14 03:00 | 2.6976 | 0 | N/A | 0 | 0
2022-01-14 03:30 | 2.4638 | 0 | N/A | 0 | 0
2022-01-14 04:00 | 2.3646 | 0 | N/A | 0 | 0
2022-01-14 04:30 | 2.3005 | 0 | N/A | 0 | 0
2022-01-14 05:00 | 2.3502 | 0 | N/A | 0 | 0
2022-01-14 05:30 | 2.445 | 0 | N/A | 0 | 0
2022-01-14 06:00 | 2.6241 | 0 | N/A | 0 | 0
2022-01-14 06:30 | 2.8962 | 0 | N/A | 0 | 0
2022-01-14 07:00 | 3.1201 | 0 | N/A | 0 | 0
2022-01-14 07:30 | 3.5192 | 0 | N/A | 0 | 0
2022-01-14 08:00 | 3.601 | 0 | N/A | 0 | 0
2022-01-14 08:30 | 3.3564 | 0 | N/A | 0 | 0
2022-01-14 09:00 | 2.5735 | 0 | N/A | 0 | 0
2022-01-14 09:30 | 2.2413 | 0 | N/A | 0 | 0
2022-01-14 10:00 | 1.8932 | 0 | N/A | 0 | 0
2022-01-14 10:30 | 1.7411 | 0 | N/A | 0 | 0
2022-01-14 11:00 | 1.1705 | 0 | N/A | 0 | 0
2022-01-14 11:30 | 0.96 | 0 | N/A | 0 | 0
2022-01-14 12:00 | 1.18 | 0 | N/A | 0 | 0
2022-01-14 12:30 | 1.0967 | 0 | N/A | 0 | 0
2022-01-14 13:00 | 1.4567 | 0 | N/A | 0 | 0
2022-01-14 13:30 | 1.42 | 0 | N/A | 0 | 0
2022-01-14 14:00 | 1.4767 | 0 | N/A | 0 | 0
2022-01-14 14:30 | 1.5001 | 0 | N/A | 0 | 0
2022-01-14 15:00 | 1.5502 | 0 | N/A | 0 | 0
2022-01-14 15:30 | 1.96 | 0 | N/A | 0 | 0
2022-01-14 16:00 | 2.5576 | 0 | N/A | 0 | 0
2022-01-14 16:30 | 3.2733 | 0 | N/A | 0 | 0
2022-01-14 17:00 | 3.5934 | 0 | N/A | 0 | 0
2022-01-14 17:30 | 4.57 | 0 | N/A | 0 | 0
2022-01-14 18:00 | 5.2267 | 0 | N/A | 0 | 0
2022-01-14 18:30 | 6.0803 | 0 | N/A | 0 | 0
2022-01-14 19:00 | 6.6574 | 0 | N/A | 0 | 0
2022-01-14 19:30 | 6.7407 | 0 | N/A | 0 | 0
2022-01-14 20:00 | 6.7417 | 0 | N/A | 0 | 0
2022-01-14 20:30 | 6.4755 | 0 | N/A | 0 | 0
2022-01-14 21:00 | 6.1163 | 0 | N/A | 0 | 0
2022-01-14 21:30 | 5.5692 | 0 | N/A | 0 | 0
2022-01-14 22:00 | 5.0076 | 0 | N/A | 0 | 0
2022-01-14 22:30 | 4.9155 | 0 | N/A | 0 | 0
2022-01-14 23:00 | 4.7735 | 0 | N/A | 0 | 0
2022-01-14 23:30 | 4.2964 | 0 | N/A | 0 | 0
2022-01-15 | 4.218 | 0 | N/A | 0 | 0
2022-01-15 00:30 | 4.5903 | 0 | N/A | 0 | 0
2022-01-15 01:00 | 4.6581 | 0 | N/A | 0 | 0
2022-01-15 01:30 | 3.6912 | 0 | N/A | 0 | 0
2022-01-15 02:00 | 3.0315 | 0 | N/A | 0 | 0
2022-01-15 02:30 | 3.0154 | 0 | N/A | 0 | 0
2022-01-15 03:00 | 2.7523 | 0 | N/A | 0 | 0
2022-01-15 03:30 | 2.5351 | 0 | N/A | 0 | 0
2022-01-15 04:00 | 2.4332 | 0 | N/A | 0 | 0
2022-01-15 04:30 | 2.3754 | 0 | N/A | 0 | 0
2022-01-15 05:00 | 2.3474 | 0 | N/A | 0 | 0
2022-01-15 05:30 | 2.4485 | 0 | N/A | 0 | 0
2022-01-15 06:00 | 2.497 | 0 | N/A | 0 | 0
2022-01-15 06:30 | 2.6505 | 0 | N/A | 0 | 0
2022-01-15 07:00 | 2.746 | 0 | N/A | 0 | 0
2022-01-15 07:30 | 2.8418 | 0 | N/A | 0 | 0
2022-01-15 08:00 | 2.9645 | 0 | N/A | 0 | 0
2022-01-15 08:30 | 2.9961 | 0 | N/A | 0 | 0
2022-01-15 09:00 | 3.0604 | 0 | N/A | 0 | 0
2022-01-15 09:30 | 2.9836 | 0 | N/A | 0 | 0
2022-01-15 10:00 | 3.1522 | 0 | N/A | 0 | 0
2022-01-15 10:30 | 3.1628 | 0 | N/A | 0 | 0
2022-01-15 11:00 | 2.8347 | 0 | N/A | 0 | 0
2022-01-15 11:30 | 2.063 | 0 | N/A | 0 | 0
2022-01-15 12:00 | 1.897 | 0 | N/A | 0 | 0
2022-01-15 12:30 | 1.5447 | 0 | N/A | 0 | 0
2022-01-15 13:00 | 0.60539 | 0 | N/A | 0 | 0
2022-01-15 13:30 | 0.8385 | 0 | N/A | 0 | 0
2022-01-15 14:00 | 0.98299 | 0 | N/A | 0 | 0
2022-01-15 14:30 | 0.69061 | 0 | N/A | 0 | 0
2022-01-15 15:00 | 0.45744 | 0 | N/A | 0 | 0
2022-01-15 15:30 | 0.75869 | 0 | N/A | 0 | 0
2022-01-15 16:00 | 0.78035 | 0 | N/A | 0 | 0
2022-01-15 16:30 | 0.96849 | 0 | N/A | 0 | 0
2022-01-15 17:00 | 1.1553 | 0 | N/A | 0 | 0
2022-01-15 17:30 | 1.9788 | 0 | N/A | 0 | 0
2022-01-15 18:00 | 2.4165 | 0 | N/A | 0 | 0
2022-01-15 18:30 | 2.6424 | 0 | N/A | 0 | 0
2022-01-15 19:00 | 3.1478 | 0 | N/A | 0 | 0
2022-01-15 19:30 | 3.5556 | 0 | N/A | 0 | 0
2022-01-15 20:00 | 3.7236 | 0 | N/A | 0 | 0
2022-01-15 20:30 | 3.8216 | 0 | N/A | 0 | 0
2022-01-15 21:00 | 3.8738 | 0 | N/A | 0 | 0
2022-01-15 21:30 | 3.8763 | 0 | N/A | 0 | 0
2022-01-15 22:00 | 3.8063 | 0 | N/A | 0 | 0
2022-01-15 22:30 | 4.1253 | 0 | N/A | 0 | 0
2022-01-15 23:00 | 4.2316 | 0 | N/A | 0 | 0
2022-01-15 23:30 | 3.9633 | 0 | N/A | 0 | 0
2022-01-16 | 3.999 | 0 | N/A | 0 | 0
2022-01-16 00:30 | 4.4364 | 0 | N/A | 0 | 0
2022-01-16 01:00 | 4.6016 | 0 | N/A | 0 | 0
2022-01-16 01:30 | 3.8039 | 0 | N/A | 0 | 0
2022-01-16 02:00 | 3.0959 | 0 | N/A | 0 | 0
2022-01-16 02:30 | 3.0196 | 0 | N/A | 0 | 0
2022-01-16 03:00 | 2.7644 | 0 | N/A | 0 | 0
2022-01-16 03:30 | 2.4465 | 0 | N/A | 0 | 0
2022-01-16 04:00 | 2.2567 | 0 | N/A | 0 | 0
2022-01-16 04:30 | 2.243 | 0 | N/A | 0 | 0
2022-01-16 05:00 | 2.189 | 0 | N/A | 0 | 0
2022-01-16 05:30 | 2.2132 | 0 | N/A | 0 | 0
2022-01-16 06:00 | 2.2248 | 0 | N/A | 0 | 0
2022-01-16 06:30 | 2.38 | 0 | N/A | 0 | 0
2022-01-16 07:00 | 2.3868 | 0 | N/A | 0 | 0
2022-01-16 07:30 | 2.4109 | 0 | N/A | 0 | 0
2022-01-16 08:00 | 2.1667 | 0 | N/A | 0 | 0
2022-01-16 08:30 | 1.7226 | 0 | N/A | 0 | 0
2022-01-16 09:00 | 1.3516 | 0 | N/A | 0 | 0
2022-01-16 09:30 | 0.9227 | 0 | N/A | 0 | 0
2022-01-16 10:00 | 0.65911 | 0 | N/A | 0 | 0
2022-01-16 10:30 | -0.56617 | 0 | N/A | 0 | 0
2022-01-16 11:00 | -0.60369 | 0 | N/A | 0 | 0
2022-01-16 11:30 | -0.71852 | 0 | N/A | 0 | 0
2022-01-16 12:00 | -0.75027 | 0 | N/A | 0 | 0
2022-01-16 12:30 | -0.79489 | 0 | N/A | 0 | 0
2022-01-16 13:00 | -0.70831 | 0 | N/A | 0 | 0
2022-01-16 13:30 | -0.66374 | 0 | N/A | 0 | 0
2022-01-16 14:00 | -0.38054 | 0 | N/A | 0 | 0
2022-01-16 14:30 | -0.21218 | 0 | N/A | 0 | 0
2022-01-16 15:00 | 0.25406 | 0 | N/A | 0 | 0
2022-01-16 15:30 | 0.7074 | 0 | N/A | 0 | 0
2022-01-16 16:00 | 1.4185 | 0 | N/A | 0 | 0
2022-01-16 16:30 | 2.5812 | 0 | N/A | 0 | 0
2022-01-16 17:00 | 3.9502 | 0 | N/A | 0 | 0
2022-01-16 17:30 | 5.3472 | 0 | N/A | 0 | 0
2022-01-16 18:00 | 5.5708 | 0 | N/A | 0 | 0
2022-01-16 18:30 | 6.2485 | 0 | N/A | 0 | 0
2022-01-16 19:00 | 7.04 | 0 | N/A | 0 | 0
2022-01-16 19:30 | 6.98 | 0 | N/A | 0 | 0
2022-01-16 20:00 | 6.96 | 0 | N/A | 0 | 0
2022-01-16 20:30 | 6.5327 | 0 | N/A | 0 | 0
2022-01-16 21:00 | 6.0939 | 0 | N/A | 0 | 0
2022-01-16 21:30 | 5.571 | 0 | N/A | 0 | 0
2022-01-16 22:00 | 5.1184 | 0 | N/A | 0 | 0
2022-01-16 22:30 | 5.3259 | 0 | N/A | 0 | 0
2022-01-16 23:00 | 5.1513 | 0 | N/A | 0 | 0
2022-01-16 23:30 | 4.5222 | 0 | N/A | 0 | 0
2022-01-17 | 4.3801 | 0 | N/A | 0 | 0
2022-01-17 00:30 | 4.7079 | 0 | N/A | 0 | 0
2022-01-17 01:00 | 4.7309 | 0 | N/A | 0 | 0
2022-01-17 01:30 | 3.7976 | 0 | N/A | 0 | 0
2022-01-17 02:00 | 3.1817 | 0 | N/A | 0 | 0
2022-01-17 02:30 | 3.1479 | 0 | N/A | 0 | 0
2022-01-17 03:00 | 2.8367 | 0 | N/A | 0 | 0
2022-01-17 03:30 | 2.5601 | 0 | N/A | 0 | 0
2022-01-17 04:00 | 2.4555 | 0 | N/A | 0 | 0
2022-01-17 04:30 | 2.5015 | 0 | N/A | 0 | 0
2022-01-17 05:00 | 2.4992 | 0 | N/A | 0 | 0
2022-01-17 05:30 | 2.6023 | 0 | N/A | 0 | 0
2022-01-17 06:00 | 2.7235 | 0 | N/A | 0 | 0
2022-01-17 06:30 | 3.1822 | 0 | N/A | 0 | 0
2022-01-17 07:00 | 3.8602 | 0 | N/A | 0 | 0
2022-01-17 07:30 | 3.5548 | 0 | N/A | 0 | 0
2022-01-17 08:00 | 3.5338 | 0 | N/A | 0 | 0
2022-01-17 08:30 | 3.5533 | 0 | N/A | 0 | 0
2022-01-17 09:00 | 3.1716 | 0 | N/A | 0 | 0
2022-01-17 09:30 | 2.3917 | 0 | N/A | 0 | 0
2022-01-17 10:00 | 2.6382 | 0 | N/A | 0 | 0
2022-01-17 10:30 | 2.3772 | 0 | N/A | 0 | 0
2022-01-17 11:00 | 1.6736 | 0 | N/A | 0 | 0
2022-01-17 11:30 | 1.2785 | 0 | N/A | 0 | 0
2022-01-17 12:00 | 1.0009 | 0 | N/A | 0 | 0
2022-01-17 12:30 | 1.3804 | 0 | N/A | 0 | 0
2022-01-17 13:00 | 1.0773 | 0 | N/A | 0 | 0
2022-01-17 13:30 | 0.72112 | 0 | N/A | 0 | 0
2022-01-17 14:00 | 0.99141 | 0 | N/A | 0 | 0
2022-01-17 14:30 | -0.040277 | 0 | N/A | 0 | 0
2022-01-17 15:00 | -0.32028 | 0 | N/A | 0 | 0
2022-01-17 15:30 | -0.044721 | 0 | N/A | 0 | 0
2022-01-17 16:00 | 0.15333 | 0 | N/A | 0 | 0
2022-01-17 16:30 | 0.40024 | 0 | N/A | 0 | 0
2022-01-17 17:00 | 0.4968 | 0 | N/A | 0 | 0
2022-01-17 17:30 | 1.2317 | 0 | N/A | 0 | 0
2022-01-17 18:00 | 2.3651 | 0 | N/A | 0 | 0
2022-01-17 18:30 | 3.3059 | 0 | N/A | 0 | 0
2022-01-17 19:00 | 3.8955 | 0 | N/A | 0 | 0
2022-01-17 19:30 | 4.2412 | 0 | N/A | 0 | 0
2022-01-17 20:00 | 4.3672 | 0 | N/A | 0 | 0
2022-01-17 20:30 | 4.3734 | 0 | N/A | 0 | 0
2022-01-17 21:00 | 4.3977 | 0 | N/A | 0 | 0
2022-01-17 21:30 | 4.1862 | 0 | N/A | 0 | 0
2022-01-17 22:00 | 3.9747 | 0 | N/A | 0 | 0
2022-01-17 22:30 | 4.2095 | 0 | N/A | 0 | 0
2022-01-17 23:00 | 4.1673 | 0 | N/A | 0 | 0
2022-01-17 23:30 | 3.8719 | 0 | N/A | 0 | 0
2022-01-18 | 3.8717 | 0 | N/A | 0 | 0
2022-01-18 00:30 | 4.3065 | 0 | N/A | 0 | 0
2022-01-18 01:00 | 4.4285 | 0 | N/A | 0 | 0
2022-01-18 01:30 | 3.5906 | 0 | N/A | 0 | 0
2022-01-18 02:00 | 2.9011 | 0 | N/A | 0 | 0
2022-01-18 02:30 | 2.8824 | 0 | N/A | 0 | 0
2022-01-18 03:00 | 2.6463 | 0 | N/A | 0 | 0
2022-01-18 03:30 | 2.3928 | 0 | N/A | 0 | 0
2022-01-18 04:00 | 2.2644 | 0 | N/A | 0 | 0
2022-01-18 04:30 | 2.2521 | 0 | N/A | 0 | 0
2022-01-18 05:00 | 2.2418 | 0 | N/A | 0 | 0
2022-01-18 05:30 | 2.4284 | 0 | N/A | 0 | 0
2022-01-18 06:00 | 2.6045 | 0 | N/A | 0 | 0
2022-01-18 06:30 | 2.9889 | 0 | N/A | 0 | 0
2022-01-18 07:00 | 3.5151 | 0 | N/A | 0 | 0
2022-01-18 07:30 | 3.8998 | 0 | N/A | 0 | 0
2022-01-18 08:00 | 3.7702 | 0 | N/A | 0 | 0
2022-01-18 08:30 | 3.1356 | 0 | N/A | 0 | 0
2022-01-18 09:00 | 2.6052 | 0 | N/A | 0 | 0
2022-01-18 09:30 | 2.465 | 0 | N/A | 0 | 0
2022-01-18 10:00 | 1.9103 | 0 | N/A | 0 | 0
2022-01-18 10:30 | 1.0523 | 0 | N/A | 0 | 0
2022-01-18 11:00 | 0.43329 | 0 | N/A | 0 | 0
2022-01-18 11:30 | 0.17208 | 0 | N/A | 0 | 0
2022-01-18 12:00 | 0.2403 | 0 | N/A | 0 | 0
2022-01-18 12:30 | 0.5998 | 0 | N/A | 0 | 0
2022-01-18 13:00 | 0.51822 | 0 | N/A | 0 | 0
2022-01-18 13:30 | 0.37454 | 0 | N/A | 0 | 0
2022-01-18 14:00 | 0.3956 | 0 | N/A | 0 | 0
2022-01-18 14:30 | 0.19437 | 0 | N/A | 0 | 0
2022-01-18 15:00 | 0.55867 | 0 | N/A | 0 | 0
2022-01-18 15:30 | 0.88827 | 0 | N/A | 0 | 0
2022-01-18 16:00 | 0.9101 | 0 | N/A | 0 | 0
2022-01-18 16:30 | 1.29 | 0 | N/A | 0 | 0
2022-01-18 17:00 | 2.1373 | 0 | N/A | 0 | 0
2022-01-18 17:30 | 2.4295 | 0 | N/A | 0 | 0
2022-01-18 18:00 | 3.257 | 0 | N/A | 0 | 0
2022-01-18 18:30 | 3.7578 | 0 | N/A | 0 | 0
2022-01-18 19:00 | 4.1827 | 0 | N/A | 0 | 0
2022-01-18 19:30 | 4.0379 | 0 | N/A | 0 | 0
2022-01-18 20:00 | 4.1676 | 0 | N/A | 0 | 0
2022-01-18 20:30 | 4.2356 | 0 | N/A | 0 | 0
2022-01-18 21:00 | 4.2638 | 0 | N/A | 0 | 0
2022-01-18 21:30 | 4.1359 | 0 | N/A | 0 | 0
2022-01-18 22:00 | 3.9566 | 0 | N/A | 0 | 0
2022-01-18 22:30 | 4.201 | 0 | N/A | 0 | 0
2022-01-18 23:00 | 4.226 | 0 | N/A | 0 | 0
2022-01-18 23:30 | 3.9632 | 0 | N/A | 0 | 0
2022-01-19 | 4.0239 | 0 | N/A | 0 | 0
2022-01-20 00:30 | 4.2399 | 0 | N/A | 0 | 0
2022-01-20 01:00 | 4.3792 | 0 | N/A | 0 | 0
2022-01-20 01:30 | 3.6218 | 0 | N/A | 0 | 0
2022-01-20 02:00 | 2.9094 | 0 | N/A | 0 | 0
2022-01-20 02:30 | 2.9511 | 0 | N/A | 0 | 0
2022-01-20 03:00 | 2.6779 | 0 | N/A | 0 | 0
2022-01-20 03:30 | 2.3838 | 0 | N/A | 0 | 0
2022-01-20 04:00 | 2.2233 | 0 | N/A | 0 | 0
2022-01-20 04:30 | 2.2398 | 0 | N/A | 0 | 0
2022-01-20 05:00 | 2.2618 | 0 | N/A | 0 | 0
2022-01-20 05:30 | 2.3911 | 0 | N/A | 0 | 0
2022-01-20 06:00 | 2.601 | 0 | N/A | 0 | 0
2022-01-20 06:30 | 3.1676 | 0 | N/A | 0 | 0
2022-01-20 07:00 | 3.7423 | 0 | N/A | 0 | 0
2022-01-20 07:30 | 4.1572 | 0 | N/A | 0 | 0
2022-01-20 08:00 | 3.8209 | 0 | N/A | 0 | 0
2022-01-20 08:30 | 3.1448 | 0 | N/A | 0 | 0
2022-01-20 09:00 | 2.6862 | 0 | N/A | 0 | 0
2022-01-20 09:30 | 1.875 | 0 | N/A | 0 | 0
2022-01-20 10:00 | 1.0247 | 0 | N/A | 0 | 0
2022-01-20 10:30 | 0.34409 | 0 | N/A | 0 | 0
2022-01-20 11:00 | 0.18342 | 0 | N/A | 0 | 0
2022-01-20 11:30 | -0.056667 | 0 | N/A | 0 | 0
2022-01-20 12:00 | -0.20333 | 0 | N/A | 0 | 0
2022-01-20 12:30 | -0.2 | 0 | N/A | 0 | 0
2022-01-20 13:00 | -0.2 | 0 | N/A | 0 | 0
2022-01-20 13:30 | -0.75685 | 0 | N/A | 0 | 0
2022-01-20 14:00 | -0.47854 | 0 | N/A | 0 | 0
2022-01-20 14:30 | -0.42921 | 0 | N/A | 0 | 0
2022-01-20 15:00 | -0.40339 | 0 | N/A | 0 | 0
2022-01-20 15:30 | -0.10022 | 0 | N/A | 0 | 0
2022-01-20 16:00 | 0.13924 | 0 | N/A | 0 | 0
2022-01-20 16:30 | 0.5353 | 0 | N/A | 0 | 0
2022-01-20 17:00 | 0.92247 | 0 | N/A | 0 | 0
2022-01-20 17:30 | 1.5849 | 0 | N/A | 0 | 0
2022-01-20 18:00 | 2.5645 | 0 | N/A | 0 | 0
2022-01-20 18:30 | 3.5364 | 0 | N/A | 0 | 0
2022-01-20 19:00 | 4.311 | 0 | N/A | 0 | 0
2022-01-20 19:30 | 4.6792 | 0 | N/A | 0 | 0
2022-01-20 20:00 | 4.944 | 0 | N/A | 0 | 0
2022-01-20 20:30 | 4.9175 | 0 | N/A | 0 | 0
2022-01-20 21:00 | 4.7896 | 0 | N/A | 0 | 0
2022-01-20 21:30 | 4.5477 | 0 | N/A | 0 | 0
2022-01-20 22:00 | 4.2774 | 0 | N/A | 0 | 0
2022-01-20 22:30 | 4.4278 | 0 | N/A | 0 | 0
2022-01-20 23:00 | 4.3955 | 0 | N/A | 0 | 0
2022-01-20 23:30 | 3.9755 | 0 | N/A | 0 | 0
2022-01-21 | 3.9409 | 0 | N/A | 0 | 0
2022-01-21 00:30 | 4.3983 | 0 | N/A | 0 | 0
2022-01-21 01:00 | 4.463 | 0 | N/A | 0 | 0
2022-01-21 01:30 | 3.5761 | 0 | N/A | 0 | 0
2022-01-21 02:00 | 3.0465 | 0 | N/A | 0 | 0
2022-01-21 02:30 | 2.9656 | 0 | N/A | 0 | 0
2022-01-21 03:00 | 2.676 | 0 | N/A | 0 | 0
2022-01-21 03:30 | 2.4415 | 0 | N/A | 0 | 0
2022-01-21 04:00 | 2.3541 | 0 | N/A | 0 | 0
2022-01-21 04:30 | 2.2808 | 0 | N/A | 0 | 0
2022-01-21 05:00 | 2.3696 | 0 | N/A | 0 | 0
2022-01-21 05:30 | 2.4291 | 0 | N/A | 0 | 0
2022-01-21 06:00 | 2.6363 | 0 | N/A | 0 | 0
2022-01-21 06:30 | 3.0318 | 0 | N/A | 0 | 0
2022-01-21 07:00 | 3.5308 | 0 | N/A | 0 | 0
2022-01-21 07:30 | 3.8427 | 0 | N/A | 0 | 0
2022-01-21 08:00 | 3.7343 | 0 | N/A | 0 | 0
2022-01-21 08:30 | 3.1453 | 0 | N/A | 0 | 0
2022-01-21 09:00 | 2.7275 | 0 | N/A | 0 | 0
2022-01-21 09:30 | 1.9007 | 0 | N/A | 0 | 0
2022-01-21 10:00 | 1.2011 | 0 | N/A | 0 | 0
2022-01-21 10:30 | 0.56366 | 0 | N/A | 0 | 0
2022-01-21 11:00 | 0.29048 | 0 | N/A | 0 | 0
2022-01-21 11:30 | 0.021344 | 0 | N/A | 0 | 0
2022-01-21 12:00 | -0.26183 | 0 | N/A | 0 | 0
2022-01-21 12:30 | -0.52512 | 0 | N/A | 0 | 0
2022-01-21 13:00 | -0.60038 | 0 | N/A | 0 | 0
2022-01-21 13:30 | -0.5257 | 0 | N/A | 0 | 0
2022-01-21 14:00 | -0.45227 | 0 | N/A | 0 | 0
2022-01-21 14:30 | -0.21177 | 0 | N/A | 0 | 0
2022-01-21 15:00 | 0.10138 | 0 | N/A | 0 | 0
2022-01-21 15:30 | 0.34668 | 0 | N/A | 0 | 0
2022-01-21 16:00 | 0.79 | 0 | N/A | 0 | 0
2022-01-21 16:30 | 1.4233 | 0 | N/A | 0 | 0
2022-01-21 17:00 | 2.2036 | 0 | N/A | 0 | 0
2022-01-21 17:30 | 3.1957 | 0 | N/A | 0 | 0
2022-01-21 18:00 | 4.2211 | 0 | N/A | 0 | 0
2022-01-21 18:30 | 5.0037 | 0 | N/A | 0 | 0
2022-01-21 19:00 | 5.7368 | 0 | N/A | 0 | 0
2022-01-21 19:30 | 5.9223 | 0 | N/A | 0 | 0
2022-01-21 20:00 | 6.0068 | 0 | N/A | 0 | 0
2022-01-21 20:30 | 5.8431 | 0 | N/A | 0 | 0
2022-01-21 21:00 | 5.4455 | 0 | N/A | 0 | 0
2022-01-21 21:30 | 5.0827 | 0 | N/A | 0 | 0
2022-01-21 22:00 | 4.6849 | 0 | N/A | 0 | 0
2022-01-21 22:30 | 4.7546 | 0 | N/A | 0 | 0
2022-01-21 23:00 | 4.6068 | 0 | N/A | 0 | 0
2022-01-21 23:30 | 4.1715 | 0 | N/A | 0 | 0
2022-01-22 | 4.1557 | 0 | N/A | 0 | 0
2022-01-22 00:30 | 4.5816 | 0 | N/A | 0 | 0
2022-01-22 01:00 | 4.5864 | 0 | N/A | 0 | 0
2022-01-22 01:30 | 3.6744 | 0 | N/A | 0 | 0
2022-01-22 02:00 | 3.0573 | 0 | N/A | 0 | 0
2022-01-22 02:30 | 3.0327 | 0 | N/A | 0 | 0
2022-01-22 03:00 | 2.8473 | 0 | N/A | 0 | 0
2022-01-22 03:30 | 2.59 | 0 | N/A | 0 | 0
2022-01-22 04:00 | 2.47 | 0 | N/A | 0 | 0
2022-01-22 04:30 | 2.4103 | 0 | N/A | 0 | 0
2022-01-22 05:00 | 2.3735 | 0 | N/A | 0 | 0
2022-01-22 05:30 | 2.3916 | 0 | N/A | 0 | 0
2022-01-22 06:00 | 2.491 | 0 | N/A | 0 | 0
2022-01-22 06:30 | 2.6357 | 0 | N/A | 0 | 0
2022-01-22 07:00 | 2.7298 | 0 | N/A | 0 | 0
2022-01-22 07:30 | 2.747 | 0 | N/A | 0 | 0
2022-01-22 08:00 | 2.6129 | 0 | N/A | 0 | 0
2022-01-22 08:30 | 2.3475 | 0 | N/A | 0 | 0
2022-01-22 09:00 | 1.9301 | 0 | N/A | 0 | 0
2022-01-22 09:30 | 1.3713 | 0 | N/A | 0 | 0
2022-01-22 10:00 | 0.7798 | 0 | N/A | 0 | 0
2022-01-22 10:30 | 0.36347 | 0 | N/A | 0 | 0
2022-01-22 11:00 | -0.19678 | 0 | N/A | 0 | 0
2022-01-22 11:30 | -0.3504 | 0 | N/A | 0 | 0
2022-01-22 12:00 | -0.32745 | 0 | N/A | 0 | 0
2022-01-22 12:30 | -0.29762 | 0 | N/A | 0 | 0
2022-01-22 13:00 | -0.19678 | 0 | N/A | 0 | 0
2022-01-22 13:30 | -0.13 | 0 | N/A | 0 | 0
2022-01-22 14:00 | -0.01 | 0 | N/A | 0 | 0
2022-01-22 14:30 | 0.23333 | 0 | N/A | 0 | 0
2022-01-22 15:00 | 0.52667 | 0 | N/A | 0 | 0
2022-01-22 15:30 | 0.97333 | 0 | N/A | 0 | 0
2022-01-22 16:00 | 1.49 | 0 | N/A | 0 | 0
2022-01-22 16:30 | 2.1178 | 0 | N/A | 0 | 0
2022-01-22 17:00 | 2.9172 | 0 | N/A | 0 | 0
2022-01-22 17:30 | 3.9193 | 0 | N/A | 0 | 0
2022-01-22 18:00 | 5.24 | 0 | N/A | 0 | 0
2022-01-22 18:30 | 5.9974 | 0 | N/A | 0 | 0
2022-01-22 19:00 | 6.315 | 0 | N/A | 0 | 0
2022-01-22 19:30 | 6.484 | 0 | N/A | 0 | 0
2022-01-22 20:00 | 6.4921 | 0 | N/A | 0 | 0
2022-01-22 20:30 | 6.0546 | 0 | N/A | 0 | 0
2022-01-22 21:00 | 5.6475 | 0 | N/A | 0 | 0
2022-01-22 21:30 | 5.2724 | 0 | N/A | 0 | 0
2022-01-22 22:00 | 4.812 | 0 | N/A | 0 | 0
2022-01-22 22:30 | 4.9503 | 0 | N/A | 0 | 0
2022-01-22 23:00 | 4.8622 | 0 | N/A | 0 | 0
2022-01-22 23:30 | 4.4181 | 0 | N/A | 0 | 0
2022-01-23 | 4.3292 | 0 | N/A | 0 | 0
2022-01-23 00:30 | 4.6791 | 0 | N/A | 0 | 0
2022-01-23 01:00 | 4.7688 | 0 | N/A | 0 | 0
2022-01-23 01:30 | 3.8081 | 0 | N/A | 0 | 0
2022-01-23 02:00 | 3.1126 | 0 | N/A | 0 | 0
2022-01-23 02:30 | 3.0944 | 0 | N/A | 0 | 0
2022-01-23 03:00 | 2.8039 | 0 | N/A | 0 | 0
2022-01-23 03:30 | 2.4735 | 0 | N/A | 0 | 0
2022-01-23 04:00 | 2.4159 | 0 | N/A | 0 | 0
2022-01-23 04:30 | 2.3416 | 0 | N/A | 0 | 0
2022-01-23 05:00 | 2.3059 | 0 | N/A | 0 | 0
2022-01-23 05:30 | 2.3291 | 0 | N/A | 0 | 0
2022-01-23 06:00 | 2.4216 | 0 | N/A | 0 | 0
2022-01-23 06:30 | 2.5392 | 0 | N/A | 0 | 0
2022-01-23 07:00 | 2.5623 | 0 | N/A | 0 | 0
2022-01-23 07:30 | 2.5413 | 0 | N/A | 0 | 0
2022-01-23 08:00 | 2.354 | 0 | N/A | 0 | 0
2022-01-23 08:30 | 2.0541 | 0 | N/A | 0 | 0
2022-01-23 09:00 | 1.7728 | 0 | N/A | 0 | 0
2022-01-23 09:30 | 1.3566 | 0 | N/A | 0 | 0
2022-01-23 10:00 | 1.0403 | 0 | N/A | 0 | 0
2022-01-23 10:30 | 0.79202 | 0 | N/A | 0 | 0
2022-01-23 11:00 | 0.66537 | 0 | N/A | 0 | 0
2022-01-23 11:30 | 0.52582 | 0 | N/A | 0 | 0
2022-01-23 12:00 | 0.57281 | 0 | N/A | 0 | 0
2022-01-23 12:30 | 0.68089 | 0 | N/A | 0 | 0
2022-01-23 13:00 | 1.434 | 0 | N/A | 0 | 0
2022-01-23 13:30 | 1.4367 | 0 | N/A | 0 | 0
2022-01-23 14:00 | 1.9074 | 0 | N/A | 0 | 0
2022-01-23 14:30 | 2.106 | 0 | N/A | 0 | 0
2022-01-23 15:00 | 2.3352 | 0 | N/A | 0 | 0
2022-01-23 15:30 | 3.3247 | 0 | N/A | 0 | 0
2022-01-23 16:00 | 3.5508 | 0 | N/A | 0 | 0
2022-01-23 16:30 | 4.71 | 0 | N/A | 0 | 0
2022-01-23 17:00 | 5.4967 | 0 | N/A | 0 | 0
2022-01-23 17:30 | 5.9306 | 0 | N/A | 0 | 0
2022-01-23 18:00 | 6.3767 | 0 | N/A | 0 | 0
2022-01-23 18:30 | 7.3734 | 0 | N/A | 0 | 0
2022-01-23 19:00 | 7.5633 | 0 | N/A | 0 | 0
2022-01-23 19:30 | 7.2133 | 0 | N/A | 0 | 0
2022-01-23 20:00 | 6.8668 | 0 | N/A | 0 | 0
2022-01-23 20:30 | 6.4658 | 0 | N/A | 0 | 0
2022-01-23 21:00 | 6.1354 | 0 | N/A | 0 | 0
2022-01-23 21:30 | 5.7582 | 0 | N/A | 0 | 0
2022-01-23 22:00 | 5.2374 | 0 | N/A | 0 | 0
2022-01-23 22:30 | 5.1829 | 0 | N/A | 0 | 0
2022-01-23 23:00 | 5.0243 | 0 | N/A | 0 | 0
2022-01-23 23:30 | 4.5526 | 0 | N/A | 0 | 0
2022-01-24 | 4.4874 | 0 | N/A | 0 | 0
2022-01-24 00:30 | 4.7194 | 0 | N/A | 0 | 0
2022-01-24 01:00 | 4.7915 | 0 | N/A | 0 | 0
2022-01-24 01:30 | 3.8514 | 0 | N/A | 0 | 0
2022-01-24 02:00 | 3.1958 | 0 | N/A | 0 | 0
2022-01-24 02:30 | 3.1934 | 0 | N/A | 0 | 0
2022-01-24 03:00 | 2.9006 | 0 | N/A | 0 | 0
2022-01-24 03:30 | 2.6873 | 0 | N/A | 0 | 0
2022-01-24 04:00 | 2.5788 | 0 | N/A | 0 | 0
2022-01-24 04:30 | 2.5546 | 0 | N/A | 0 | 0
2022-01-24 05:00 | 2.603 | 0 | N/A | 0 | 0
2022-01-24 05:30 | 2.6974 | 0 | N/A | 0 | 0
2022-01-24 06:00 | 2.8569 | 0 | N/A | 0 | 0
2022-01-24 06:30 | 3.2063 | 0 | N/A | 0 | 0
2022-01-24 07:00 | 3.6567 | 0 | N/A | 0 | 0
2022-01-24 07:30 | 4.0667 | 0 | N/A | 0 | 0
2022-01-24 08:00 | 3.9995 | 0 | N/A | 0 | 0
2022-01-24 08:30 | 3.8357 | 0 | N/A | 0 | 0
2022-01-24 09:00 | 3.5767 | 0 | N/A | 0 | 0
2022-01-24 09:30 | 3.0987 | 0 | N/A | 0 | 0
2022-01-24 10:00 | 3.0279 | 0 | N/A | 0 | 0
2022-01-24 10:30 | 2.4818 | 0 | N/A | 0 | 0
2022-01-24 11:00 | 2.4918 | 0 | N/A | 0 | 0
2022-01-24 11:30 | 2.3384 | 0 | N/A | 0 | 0
2022-01-24 12:00 | 1.5426 | 0 | N/A | 0 | 0
2022-01-24 12:30 | 2.2543 | 0 | N/A | 0 | 0
2022-01-24 13:00 | 2.4439 | 0 | N/A | 0 | 0
2022-01-24 13:30 | 2.7614 | 0 | N/A | 0 | 0
2022-01-24 14:00 | 2.8738 | 0 | N/A | 0 | 0
2022-01-24 14:30 | 3.1488 | 0 | N/A | 0 | 0
2022-01-24 15:00 | 3.5888 | 0 | N/A | 0 | 0
2022-01-24 15:30 | 4.7712 | 0 | N/A | 0 | 0
2022-01-24 16:00 | 4.8361 | 0 | N/A | 0 | 0
2022-01-24 16:30 | 5.1865 | 0 | N/A | 0 | 0
2022-01-24 17:00 | 5.5238 | 0 | N/A | 0 | 0
2022-01-24 17:30 | 6.7647 | 0 | N/A | 0 | 0
2022-01-24 18:00 | 8.0963 | 0 | N/A | 0 | 0
2022-01-24 18:30 | 8.3523 | 0 | N/A | 0 | 0
2022-01-24 19:00 | 9.4379 | 0 | N/A | 0 | 0
2022-01-24 19:30 | 8.8551 | 0 | N/A | 0 | 0
2022-01-24 20:00 | 8.3435 | 0 | N/A | 0 | 0
2022-01-24 20:30 | 7.8635 | 0 | N/A | 0 | 0
2022-01-24 21:00 | 7.2667 | 0 | N/A | 0 | 0
2022-01-24 21:30 | 6.6306 | 0 | N/A | 0 | 0
2022-01-24 22:00 | 5.9504 | 0 | N/A | 0 | 0
2022-01-24 22:30 | 5.7739 | 0 | N/A | 0 | 0
2022-01-24 23:00 | 5.4381 | 0 | N/A | 0 | 0
2022-01-24 23:30 | 4.7144 | 0 | N/A | 0 | 0
2022-01-25 | 4.543 | 0 | N/A | 0 | 0
2022-01-25 00:30 | 4.993 | 0 | N/A | 0 | 0
2022-01-25 01:00 | 4.8201 | 0 | N/A | 0 | 0
2022-01-25 01:30 | 3.8341 | 0 | N/A | 0 | 0
2022-01-25 02:00 | 3.2757 | 0 | N/A | 0 | 0
2022-01-25 02:30 | 3.268 | 0 | N/A | 0 | 0
2022-01-25 03:00 | 3.0221 | 0 | N/A | 0 | 0
2022-01-25 03:30 | 2.8896 | 0 | N/A | 0 | 0
2022-01-25 04:00 | 2.7704 | 0 | N/A | 0 | 0
2022-01-25 04:30 | 2.809 | 0 | N/A | 0 | 0
2022-01-25 05:00 | 2.7927 | 0 | N/A | 0 | 0
2022-01-25 05:30 | 2.8896 | 0 | N/A | 0 | 0
2022-01-25 06:00 | 3.1562 | 0 | N/A | 0 | 0
2022-01-25 06:30 | 3.9443 | 0 | N/A | 0 | 0
2022-01-25 07:00 | 4.3556 | 0 | N/A | 0 | 0
2022-01-25 07:30 | 4.7281 | 0 | N/A | 0 | 0
2022-01-25 08:00 | 4.7517 | 0 | N/A | 0 | 0
2022-01-25 08:30 | 4.44 | 0 | N/A | 0 | 0
2022-01-25 09:00 | 4.0535 | 0 | N/A | 0 | 0
2022-01-25 09:30 | 3.846 | 0 | N/A | 0 | 0
2022-01-25 10:00 | 3.4453 | 0 | N/A | 0 | 0
2022-01-25 10:30 | 3.1088 | 0 | N/A | 0 | 0
2022-01-25 11:00 | 3.1278 | 0 | N/A | 0 | 0
2022-01-25 11:30 | 3.2908 | 0 | N/A | 0 | 0
2022-01-25 12:00 | 4.2953 | 0 | N/A | 0 | 0
2022-01-25 12:30 | 5.1287 | 0 | N/A | 0 | 0
2022-01-25 13:00 | 5.0572 | 0 | N/A | 0 | 0
2022-01-25 13:30 | 4.7591 | 0 | N/A | 0 | 0
2022-01-25 14:00 | 3.9947 | 0 | N/A | 0 | 0
2022-01-25 14:30 | 4.4316 | 0 | N/A | 0 | 0
2022-01-25 15:00 | 5.9842 | 0 | N/A | 0 | 0
2022-01-25 15:30 | 5.2493 | 0 | N/A | 0 | 0
2022-01-25 16:00 | 5.5281 | 0 | N/A | 0 | 0
2022-01-25 16:30 | 6.8172 | 0 | N/A | 0 | 0
2022-01-25 17:00 | 6.9634 | 0 | N/A | 0 | 0
2022-01-25 17:30 | 6.6662 | 0 | N/A | 0 | 0
2022-01-25 18:00 | 7.44 | 0 | N/A | 0 | 0
2022-01-25 18:30 | 8.1095 | 0 | N/A | 0 | 0
2022-01-25 19:00 | 8.4356 | 0 | N/A | 0 | 0
2022-01-25 19:30 | 8.3612 | 0 | N/A | 0 | 0
2022-01-25 20:00 | 8.0675 | 0 | N/A | 0 | 0
2022-01-25 20:30 | 7.4633 | 0 | N/A | 0 | 0
2022-01-25 21:00 | 6.9701 | 0 | N/A | 0 | 0
2022-01-25 21:30 | 6.3811 | 0 | N/A | 0 | 0
2022-01-25 22:00 | 5.8144 | 0 | N/A | 0 | 0
2022-01-25 22:30 | 5.7297 | 0 | N/A | 0 | 0
2022-01-25 23:00 | 5.4512 | 0 | N/A | 0 | 0
2022-01-25 23:30 | 4.8704 | 0 | N/A | 0 | 0
2022-01-26 | 4.7005 | 0 | N/A | 0 | 0
2022-01-26 00:30 | 5.0593 | 0 | N/A | 0 | 0
2022-01-26 01:00 | 4.9011 | 0 | N/A | 0 | 0
2022-01-26 01:30 | 4.0004 | 0 | N/A | 0 | 0
2022-01-26 02:00 | 3.3177 | 0 | N/A | 0 | 0
2022-01-26 02:30 | 3.3107 | 0 | N/A | 0 | 0
2022-01-26 03:00 | 3.0399 | 0 | N/A | 0 | 0
2022-01-26 03:30 | 2.7835 | 0 | N/A | 0 | 0
2022-01-26 04:00 | 2.7181 | 0 | N/A | 0 | 0
2022-01-26 04:30 | 2.7137 | 0 | N/A | 0 | 0
2022-01-26 05:00 | 2.668 | 0 | N/A | 0 | 0
2022-01-26 05:30 | 2.7537 | 0 | N/A | 0 | 0
2022-01-26 06:00 | 2.8374 | 0 | N/A | 0 | 0
2022-01-26 06:30 | 3.0147 | 0 | N/A | 0 | 0
2022-01-26 07:00 | 3.0293 | 0 | N/A | 0 | 0
2022-01-26 07:30 | 3.1268 | 0 | N/A | 0 | 0
2022-01-26 08:00 | 3.094 | 0 | N/A | 0 | 0
2022-01-26 08:30 | 2.8248 | 0 | N/A | 0 | 0
2022-01-26 09:00 | 2.5685 | 0 | N/A | 0 | 0
2022-01-26 09:30 | 2.4112 | 0 | N/A | 0 | 0
2022-01-26 10:00 | 2.1727 | 0 | N/A | 0 | 0
2022-01-26 10:30 | 2.0257 | 0 | N/A | 0 | 0
2022-01-26 11:00 | 1.9939 | 0 | N/A | 0 | 0
2022-01-26 11:30 | 2.0433 | 0 | N/A | 0 | 0
2022-01-26 12:00 | 2.16 | 0 | N/A | 0 | 0
2022-01-26 12:30 | 2.39 | 0 | N/A | 0 | 0
2022-01-26 13:00 | 2.61 | 0 | N/A | 0 | 0
2022-01-26 13:30 | 2.7234 | 0 | N/A | 0 | 0
2022-01-26 14:00 | 3.1177 | 0 | N/A | 0 | 0
2022-01-26 14:30 | 3.503 | 0 | N/A | 0 | 0
2022-01-26 15:00 | 3.8802 | 0 | N/A | 0 | 0
2022-01-26 15:30 | 4.5873 | 0 | N/A | 0 | 0
2022-01-26 16:00 | 5.4373 | 0 | N/A | 0 | 0
2022-01-26 16:30 | 7.1678 | 0 | N/A | 0 | 0
2022-01-26 17:00 | 8.2861 | 0 | N/A | 0 | 0
2022-01-26 17:30 | 8.7355 | 0 | N/A | 0 | 0
2022-01-26 18:00 | 8.5859 | 0 | N/A | 0 | 0
2022-01-26 18:30 | 7.8134 | 0 | N/A | 0 | 0
2022-01-26 19:00 | 7.0871 | 0 | N/A | 0 | 0
2022-01-26 19:30 | 6.4935 | 0 | N/A | 0 | 0
2022-01-26 20:00 | 5.8832 | 0 | N/A | 0 | 0
2022-01-26 20:30 | 5.6041 | 0 | N/A | 0 | 0
2022-01-26 21:00 | 5.5319 | 0 | N/A | 0 | 0
2022-01-26 21:30 | 5.1917 | 0 | N/A | 0 | 0
2022-01-26 22:00 | 4.8731 | 0 | N/A | 0 | 0
2022-01-26 22:30 | 4.8957 | 0 | N/A | 0 | 0
2022-01-26 23:00 | 4.8097 | 0 | N/A | 0 | 0
2022-01-26 23:30 | 4.4232 | 0 | N/A | 0 | 0
2022-01-27 | 4.3691 | 0 | N/A | 0 | 0
2022-01-27 00:30 | 4.8368 | 0 | N/A | 0 | 0
2022-01-27 01:00 | 4.8363 | 0 | N/A | 0 | 0
2022-01-27 01:30 | 3.8842 | 0 | N/A | 0 | 0
2022-01-27 02:00 | 3.2533 | 0 | N/A | 0 | 0
2022-01-27 02:30 | 3.1886 | 0 | N/A | 0 | 0
2022-01-27 03:00 | 3.0033 | 0 | N/A | 0 | 0
2022-01-27 03:30 | 2.8119 | 0 | N/A | 0 | 0
2022-01-27 04:00 | 2.6757 | 0 | N/A | 0 | 0
2022-01-27 04:30 | 2.6745 | 0 | N/A | 0 | 0
2022-01-27 05:00 | 2.7493 | 0 | N/A | 0 | 0
2022-01-27 05:30 | 2.8796 | 0 | N/A | 0 | 0
2022-01-27 06:00 | 3.1514 | 0 | N/A | 0 | 0
2022-01-27 06:30 | 3.4917 | 0 | N/A | 0 | 0
2022-01-27 07:00 | 4.2181 | 0 | N/A | 0 | 0
2022-01-27 07:30 | 4.704 | 0 | N/A | 0 | 0
2022-01-27 08:00 | 4.6802 | 0 | N/A | 0 | 0
2022-01-27 08:30 | 4.3471 | 0 | N/A | 0 | 0
2022-01-27 09:00 | 4.1 | 0 | N/A | 0 | 0
2022-01-27 09:30 | 3.6955 | 0 | N/A | 0 | 0
2022-01-27 10:00 | 3.3613 | 0 | N/A | 0 | 0
2022-01-27 10:30 | 3.468 | 0 | N/A | 0 | 0
2022-01-27 11:00 | 3.4033 | 0 | N/A | 0 | 0
2022-01-27 11:30 | 3.3628 | 0 | N/A | 0 | 0
2022-01-27 12:00 | 2.8131 | 0 | N/A | 0 | 0
2022-01-27 12:30 | 2.8115 | 0 | N/A | 0 | 0
2022-01-27 13:00 | 3.2883 | 0 | N/A | 0 | 0
2022-01-27 13:30 | 3.4441 | 0 | N/A | 0 | 0
2022-01-27 14:00 | 4.1473 | 0 | N/A | 0 | 0
2022-01-27 14:30 | 4.486 | 0 | N/A | 0 | 0
2022-01-27 15:00 | 4.254 | 0 | N/A | 0 | 0
2022-01-27 15:30 | 4.6948 | 0 | N/A | 0 | 0
2022-01-27 16:00 | 4.8378 | 0 | N/A | 0 | 0
2022-01-27 16:30 | 5.3386 | 0 | N/A | 0 | 0
2022-01-27 17:00 | 5.755 | 0 | N/A | 0 | 0
2022-01-27 17:30 | 6.9795 | 0 | N/A | 0 | 0
2022-01-27 18:00 | 8.8764 | 0 | N/A | 0 | 0
2022-01-27 18:30 | 9.5584 | 0 | N/A | 0 | 0
2022-01-27 19:00 | 9.3872 | 0 | N/A | 0 | 0
2022-01-27 19:30 | 8.6569 | 0 | N/A | 0 | 0
2022-01-27 20:00 | 7.8234 | 0 | N/A | 0 | 0
2022-01-27 20:30 | 6.5868 | 0 | N/A | 0 | 0
2022-01-27 21:00 | 6.3587 | 0 | N/A | 0 | 0
2022-01-27 21:30 | 5.8373 | 0 | N/A | 0 | 0
2022-01-27 22:00 | 5.3422 | 0 | N/A | 0 | 0
2022-01-27 22:30 | 5.3272 | 0 | N/A | 0 | 0
2022-01-27 23:00 | 5.031 | 0 | N/A | 0 | 0
2022-01-27 23:30 | 4.4956 | 0 | N/A | 0 | 0
2022-01-28 | 4.4969 | 0 | N/A | 0 | 0
2022-01-28 00:30 | 4.8805 | 0 | N/A | 0 | 0
2022-01-28 01:00 | 4.7612 | 0 | N/A | 0 | 0
2022-01-28 01:30 | 3.8404 | 0 | N/A | 0 | 0
2022-01-28 02:00 | 3.266 | 0 | N/A | 0 | 0
2022-01-28 02:30 | 3.319 | 0 | N/A | 0 | 0
2022-01-28 03:00 | 3.1247 | 0 | N/A | 0 | 0
2022-01-28 03:30 | 2.8223 | 0 | N/A | 0 | 0
2022-01-28 04:00 | 2.7739 | 0 | N/A | 0 | 0
2022-01-28 04:30 | 2.8064 | 0 | N/A | 0 | 0
2022-01-28 05:00 | 2.8411 | 0 | N/A | 0 | 0
2022-01-28 05:30 | 2.9446 | 0 | N/A | 0 | 0
2022-01-28 06:00 | 3.1973 | 0 | N/A | 0 | 0
2022-01-28 06:30 | 3.9832 | 0 | N/A | 0 | 0
2022-01-28 07:00 | 4.3408 | 0 | N/A | 0 | 0
2022-01-28 07:30 | 4.7951 | 0 | N/A | 0 | 0
2022-01-28 08:00 | 4.837 | 0 | N/A | 0 | 0
2022-01-28 08:30 | 4.4571 | 0 | N/A | 0 | 0
2022-01-28 09:00 | 4.3834 | 0 | N/A | 0 | 0
2022-01-28 09:30 | 4.2011 | 0 | N/A | 0 | 0
2022-01-28 10:00 | 4.207 | 0 | N/A | 0 | 0
2022-01-28 10:30 | 3.7871 | 0 | N/A | 0 | 0
2022-01-28 11:00 | 3.8663 | 0 | N/A | 0 | 0
2022-01-28 11:30 | 4.8382 | 0 | N/A | 0 | 0
2022-01-28 12:00 | 5.4251 | 0 | N/A | 0 | 0
2022-01-28 12:30 | 5.6339 | 0 | N/A | 0 | 0
2022-01-28 13:00 | 6.791 | 0 | N/A | 0 | 0
2022-01-28 13:30 | 6.4736 | 0 | N/A | 0 | 0
2022-01-28 14:00 | 5.4685 | 0 | N/A | 0 | 0
2022-01-28 14:30 | 4.852 | 0 | N/A | 0 | 0
2022-01-28 15:00 | 4.9186 | 0 | N/A | 0 | 0
2022-01-28 15:30 | 4.7113 | 0 | N/A | 0 | 0
2022-01-28 16:00 | 3.4203 | 0 | N/A | 0 | 0
2022-01-28 16:30 | 3.5012 | 0 | N/A | 0 | 0
2022-01-28 17:00 | 2.7626 | 0 | N/A | 0 | 0
2022-01-28 17:30 | 3.292 | 0 | N/A | 0 | 0
2022-01-28 18:00 | 4.5649 | 0 | N/A | 0 | 0
2022-01-28 18:30 | 4.8658 | 0 | N/A | 0 | 0
2022-01-28 19:00 | 4.6009 | 0 | N/A | 0 | 0
2022-01-28 19:30 | 4.2859 | 0 | N/A | 0 | 0
2022-01-28 20:00 | 4.5309 | 0 | N/A | 0 | 0
2022-01-28 20:30 | 4.4302 | 0 | N/A | 0 | 0
2022-01-28 21:00 | 4.4985 | 0 | N/A | 0 | 0
2022-01-28 21:30 | 4.3854 | 0 | N/A | 0 | 0
2022-01-28 22:00 | 4.0962 | 0 | N/A | 0 | 0
2022-01-28 22:30 | 4.3839 | 0 | N/A | 0 | 0
2022-01-28 23:00 | 4.3142 | 0 | N/A | 0 | 0
2022-01-28 23:30 | 3.8485 | 0 | N/A | 0 | 0
2022-01-29 | 3.9368 | 0 | N/A | 0 | 0
2022-01-29 00:30 | 4.4153 | 0 | N/A | 0 | 0
2022-01-29 01:00 | 4.5643 | 0 | N/A | 0 | 0
2022-01-29 01:30 | 3.6036 | 0 | N/A | 0 | 0
2022-01-29 02:00 | 2.9867 | 0 | N/A | 0 | 0
2022-01-29 02:30 | 2.925 | 0 | N/A | 0 | 0
2022-01-29 03:00 | 2.6796 | 0 | N/A | 0 | 0
2022-01-29 03:30 | 2.3984 | 0 | N/A | 0 | 0
2022-01-29 04:00 | 2.3559 | 0 | N/A | 0 | 0
2022-01-29 04:30 | 2.3619 | 0 | N/A | 0 | 0
2022-01-29 05:00 | 2.2705 | 0 | N/A | 0 | 0
2022-01-29 05:30 | 2.3454 | 0 | N/A | 0 | 0
2022-01-29 06:00 | 2.4373 | 0 | N/A | 0 | 0
2022-01-29 06:30 | 2.7136 | 0 | N/A | 0 | 0
2022-01-29 07:00 | 2.8051 | 0 | N/A | 0 | 0
2022-01-29 07:30 | 2.9578 | 0 | N/A | 0 | 0
2022-01-29 08:00 | 3.0529 | 0 | N/A | 0 | 0
2022-01-29 08:30 | 3.0578 | 0 | N/A | 0 | 0
2022-01-29 09:00 | 3.0618 | 0 | N/A | 0 | 0
2022-01-29 09:30 | 3.0609 | 0 | N/A | 0 | 0
2022-01-29 10:00 | 2.4511 | 0 | N/A | 0 | 0
2022-01-29 10:30 | 2.315 | 0 | N/A | 0 | 0
2022-01-29 11:00 | 2.3968 | 0 | N/A | 0 | 0
2022-01-29 11:30 | 2.1951 | 0 | N/A | 0 | 0
2022-01-29 12:00 | 2.0954 | 0 | N/A | 0 | 0
2022-01-29 12:30 | 2.0233 | 0 | N/A | 0 | 0
2022-01-29 13:00 | 1.7375 | 0 | N/A | 0 | 0
2022-01-29 13:30 | 1.5444 | 0 | N/A | 0 | 0
2022-01-29 14:00 | 1.1835 | 0 | N/A | 0 | 0
2022-01-29 14:30 | 0.82058 | 0 | N/A | 0 | 0
2022-01-29 15:00 | 0.63232 | 0 | N/A | 0 | 0
2022-01-29 15:30 | 0.60315 | 0 | N/A | 0 | 0
2022-01-29 16:00 | -0.52631 | 0 | N/A | 0 | 0
2022-01-29 16:30 | -0.52717 | 0 | N/A | 0 | 0
2022-01-29 17:00 | 0.55307 | 0 | N/A | 0 | 0
2022-01-29 17:30 | 0.99267 | 0 | N/A | 0 | 0
2022-01-29 18:00 | 1.8873 | 0 | N/A | 0 | 0
2022-01-29 18:30 | 2.7329 | 0 | N/A | 0 | 0
2022-01-29 19:00 | 3.2929 | 0 | N/A | 0 | 0
2022-01-29 19:30 | 3.8698 | 0 | N/A | 0 | 0
2022-01-29 20:00 | 4.0252 | 0 | N/A | 0 | 0
2022-01-29 20:30 | 3.9535 | 0 | N/A | 0 | 0
2022-01-29 21:00 | 3.8761 | 0 | N/A | 0 | 0
2022-01-29 21:30 | 3.7698 | 0 | N/A | 0 | 0
2022-01-29 22:00 | 3.6505 | 0 | N/A | 0 | 0
2022-01-29 22:30 | 4.0504 | 0 | N/A | 0 | 0
2022-01-29 23:00 | 4.2115 | 0 | N/A | 0 | 0
2022-01-29 23:30 | 3.9259 | 0 | N/A | 0 | 0
2022-01-30 | 3.9842 | 0 | N/A | 0 | 0
2022-01-30 00:30 | 4.3333 | 0 | N/A | 0 | 0
2022-01-30 01:00 | 4.5939 | 0 | N/A | 0 | 0
2022-01-30 01:30 | 3.7507 | 0 | N/A | 0 | 0
2022-01-30 02:00 | 3.055 | 0 | N/A | 0 | 0
2022-01-30 02:30 | 2.9804 | 0 | N/A | 0 | 0
2022-01-30 03:00 | 2.7068 | 0 | N/A | 0 | 0
2022-01-30 03:30 | 2.3933 | 0 | N/A | 0 | 0
2022-01-30 04:00 | 2.269 | 0 | N/A | 0 | 0
2022-01-30 04:30 | 2.2617 | 0 | N/A | 0 | 0
2022-01-30 05:00 | 2.2073 | 0 | N/A | 0 | 0
2022-01-30 05:30 | 2.2212 | 0 | N/A | 0 | 0
2022-01-30 06:00 | 2.248 | 0 | N/A | 0 | 0
2022-01-30 06:30 | 2.4073 | 0 | N/A | 0 | 0
2022-01-30 07:00 | 2.4619 | 0 | N/A | 0 | 0
2022-01-30 07:30 | 2.6663 | 0 | N/A | 0 | 0
2022-01-30 08:00 | 2.6315 | 0 | N/A | 0 | 0
2022-01-30 08:30 | 2.4834 | 0 | N/A | 0 | 0
2022-01-30 09:00 | 2.3875 | 0 | N/A | 0 | 0
2022-01-30 09:30 | 2.315 | 0 | N/A | 0 | 0
2022-01-30 10:00 | 2.5182 | 0 | N/A | 0 | 0
2022-01-30 10:30 | 2.3664 | 0 | N/A | 0 | 0
2022-01-30 11:00 | 2.2084 | 0 | N/A | 0 | 0
2022-01-30 11:30 | 1.776 | 0 | N/A | 0 | 0
2022-01-30 12:00 | 1.5075 | 0 | N/A | 0 | 0
2022-01-30 12:30 | 1.4947 | 0 | N/A | 0 | 0
2022-01-30 13:00 | 1.0886 | 0 | N/A | 0 | 0
2022-01-30 13:30 | 0.54269 | 0 | N/A | 0 | 0
2022-01-30 14:00 | 0.45852 | 0 | N/A | 0 | 0
2022-01-30 14:30 | -0.31672 | 0 | N/A | 0 | 0
2022-01-30 15:00 | -0.37548 | 0 | N/A | 0 | 0
2022-01-30 15:30 | -0.32056 | 0 | N/A | 0 | 0
2022-01-30 16:00 | 0.44515 | 0 | N/A | 0 | 0
2022-01-30 16:30 | 1.1095 | 0 | N/A | 0 | 0
2022-01-30 17:00 | 2.2758 | 0 | N/A | 0 | 0
2022-01-30 17:30 | 3.5408 | 0 | N/A | 0 | 0
2022-01-30 18:00 | 4.594 | 0 | N/A | 0 | 0
2022-01-30 18:30 | 5.0832 | 0 | N/A | 0 | 0
2022-01-30 19:00 | 5.4773 | 0 | N/A | 0 | 0
2022-01-30 19:30 | 5.891 | 0 | N/A | 0 | 0
2022-01-30 20:00 | 5.8297 | 0 | N/A | 0 | 0
2022-01-30 20:30 | 5.5212 | 0 | N/A | 0 | 0
2022-01-30 21:00 | 5.1465 | 0 | N/A | 0 | 0
2022-01-30 21:30 | 4.8949 | 0 | N/A | 0 | 0
2022-01-30 22:00 | 4.5448 | 0 | N/A | 0 | 0
2022-01-30 22:30 | 4.7617 | 0 | N/A | 0 | 0
2022-01-30 23:00 | 4.6727 | 0 | N/A | 0 | 0
2022-01-30 23:30 | 4.2882 | 0 | N/A | 0 | 0
2022-01-31 | 4.2624 | 0 | N/A | 0 | 0
2022-01-31 00:30 | 4.6969 | 0 | N/A | 0 | 0
2022-01-31 01:00 | 4.8432 | 0 | N/A | 0 | 0
2022-01-31 01:30 | 3.9401 | 0 | N/A | 0 | 0
2022-01-31 02:00 | 3.1744 | 0 | N/A | 0 | 0
2022-01-31 02:30 | 3.1257 | 0 | N/A | 0 | 0
2022-01-31 03:00 | 2.9233 | 0 | N/A | 0 | 0
2022-01-31 03:30 | 2.6018 | 0 | N/A | 0 | 0
2022-01-31 04:00 | 2.5131 | 0 | N/A | 0 | 0
2022-01-31 04:30 | 2.549 | 0 | N/A | 0 | 0
2022-01-31 05:00 | 2.5416 | 0 | N/A | 0 | 0
2022-01-31 05:30 | 2.5936 | 0 | N/A | 0 | 0
2022-01-31 06:00 | 2.8777 | 0 | N/A | 0 | 0
2022-01-31 06:30 | 3.2266 | 0 | N/A | 0 | 0
2022-01-31 07:00 | 3.9856 | 0 | N/A | 0 | 0
2022-01-31 07:30 | 4.3663 | 0 | N/A | 0 | 0
2022-01-31 08:00 | 4.45 | 0 | N/A | 0 | 0
2022-01-31 08:30 | 3.7695 | 0 | N/A | 0 | 0
2022-01-31 09:00 | 3.3473 | 0 | N/A | 0 | 0
2022-01-31 09:30 | 2.8336 | 0 | N/A | 0 | 0
2022-01-31 10:00 | 2.37 | 0 | N/A | 0 | 0
2022-01-31 10:30 | 1.8909 | 0 | N/A | 0 | 0
2022-01-31 11:00 | 2.0568 | 0 | N/A | 0 | 0
2022-01-31 11:30 | 2.2016 | 0 | N/A | 0 | 0
2022-01-31 12:00 | 2.279 | 0 | N/A | 0 | 0
2022-01-31 12:30 | 2.5191 | 0 | N/A | 0 | 0
2022-01-31 13:00 | 2.3746 | 0 | N/A | 0 | 0
2022-01-31 13:30 | 2.4053 | 0 | N/A | 0 | 0
2022-01-31 14:00 | 2.7429 | 0 | N/A | 0 | 0
2022-01-31 14:30 | 2.7866 | 0 | N/A | 0 | 0
2022-01-31 15:00 | 3.0844 | 0 | N/A | 0 | 0
2022-01-31 15:30 | 3.4584 | 0 | N/A | 0 | 0
2022-01-31 16:00 | 3.7943 | 0 | N/A | 0 | 0
2022-01-31 16:30 | 4.228 | 0 | N/A | 0 | 0
2022-01-31 17:00 | 4.7935 | 0 | N/A | 0 | 0
2022-01-31 17:30 | 5.4604 | 0 | N/A | 0 | 0
2022-01-31 18:00 | 6.6644 | 0 | N/A | 0 | 0
2022-01-31 18:30 | 7.571 | 0 | N/A | 0 | 0
2022-01-31 19:00 | 8.2172 | 0 | N/A | 0 | 0
2022-01-31 19:30 | 8.51 | 0 | N/A | 0 | 0
2022-01-31 20:00 | 8.42 | 0 | N/A | 0 | 0
2022-01-31 20:30 | 7.98 | 0 | N/A | 0 | 0
2022-01-31 21:00 | 7.2 | 0 | N/A | 0 | 0
2022-01-31 21:30 | 6.4949 | 0 | N/A | 0 | 0
2022-01-31 22:00 | 5.8514 | 0 | N/A | 0 | 0
2022-01-31 22:30 | 5.6311 | 0 | N/A | 0 | 0
2022-01-31 23:00 | 5.3087 | 0 | N/A | 0 | 0
2022-01-31 23:30 | 4.5823 | 0 | N/A | 0 | 0
2022-02-01 | 4.3317 | 0 | N/A | 0 | 0
2022-02-03 00:30 | 4.4229 | 0 | N/A | 0 | 0
2022-02-03 01:00 | 4.6591 | 0 | N/A | 0 | 0
2022-02-03 01:30 | 3.706 | 0 | N/A | 0 | 0
2022-02-03 02:00 | 3.0119 | 0 | N/A | 0 | 0
2022-02-03 02:30 | 2.96 | 0 | N/A | 0 | 0
2022-02-03 03:00 | 2.7084 | 0 | N/A | 0 | 0
2022-02-03 03:30 | 2.4895 | 0 | N/A | 0 | 0
2022-02-03 04:00 | 2.4022 | 0 | N/A | 0 | 0
2022-02-03 04:30 | 2.3999 | 0 | N/A | 0 | 0
2022-02-03 05:00 | 2.491 | 0 | N/A | 0 | 0
2022-02-03 05:30 | 2.6187 | 0 | N/A | 0 | 0
2022-02-03 06:00 | 2.9262 | 0 | N/A | 0 | 0
2022-02-03 06:30 | 3.6831 | 0 | N/A | 0 | 0
2022-02-03 07:00 | 4.3765 | 0 | N/A | 0 | 0
2022-02-03 07:30 | 5.1793 | 0 | N/A | 0 | 0
2022-02-03 08:00 | 5.327 | 0 | N/A | 0 | 0
2022-02-03 08:30 | 4.7593 | 0 | N/A | 0 | 0
2022-02-03 09:00 | 4.2933 | 0 | N/A | 0 | 0
2022-02-03 09:30 | 3.9931 | 0 | N/A | 0 | 0
2022-02-03 10:00 | 4.0052 | 0 | N/A | 0 | 0
2022-02-03 10:30 | 3.6783 | 0 | N/A | 0 | 0
2022-02-03 11:00 | 3.8724 | 0 | N/A | 0 | 0
2022-02-03 11:30 | 3.0181 | 0 | N/A | 0 | 0
2022-02-03 12:00 | 2.7549 | 0 | N/A | 0 | 0
2022-02-03 12:30 | 2.0965 | 0 | N/A | 0 | 0
2022-02-03 13:00 | 1.8144 | 0 | N/A | 0 | 0
2022-02-03 13:30 | 2.0823 | 0 | N/A | 0 | 0
2022-02-03 14:00 | 2.2557 | 0 | N/A | 0 | 0
2022-02-03 14:30 | 2.0573 | 0 | N/A | 0 | 0
2022-02-03 15:00 | 1.47 | 0 | N/A | 0 | 0
2022-02-03 15:30 | 2.7326 | 0 | N/A | 0 | 0
2022-02-03 16:00 | 2.2977 | 0 | N/A | 0 | 0
2022-02-03 16:30 | 2.2621 | 0 | N/A | 0 | 0
2022-02-03 17:00 | 2.9111 | 0 | N/A | 0 | 0
2022-02-03 17:30 | 2.9072 | 0 | N/A | 0 | 0
2022-02-03 18:00 | 3.6481 | 0 | N/A | 0 | 0
2022-02-03 18:30 | 4.5702 | 0 | N/A | 0 | 0
2022-02-03 19:00 | 4.8108 | 0 | N/A | 0 | 0
2022-02-03 19:30 | 4.7831 | 0 | N/A | 0 | 0
2022-02-03 20:00 | 4.9092 | 0 | N/A | 0 | 0
2022-02-03 20:30 | 5.0607 | 0 | N/A | 0 | 0
2022-02-03 21:00 | 5.0944 | 0 | N/A | 0 | 0
2022-02-03 21:30 | 4.9588 | 0 | N/A | 0 | 0
2022-02-03 22:00 | 4.582 | 0 | N/A | 0 | 0
2022-02-03 22:30 | 4.7048 | 0 | N/A | 0 | 0
2022-02-03 23:00 | 4.7179 | 0 | N/A | 0 | 0
2022-02-03 23:30 | 4.4003 | 0 | N/A | 0 | 0
2022-02-04 | 4.3843 | 0 | N/A | 0 | 0
2022-02-04 00:30 | 4.6194 | 0 | N/A | 0 | 0
2022-02-04 01:00 | 4.8311 | 0 | N/A | 0 | 0
2022-02-04 01:30 | 4.0085 | 0 | N/A | 0 | 0
2022-02-04 02:00 | 3.3278 | 0 | N/A | 0 | 0
2022-02-04 02:30 | 3.2264 | 0 | N/A | 0 | 0
2022-02-04 03:00 | 2.9811 | 0 | N/A | 0 | 0
2022-02-04 03:30 | 2.6426 | 0 | N/A | 0 | 0
2022-02-04 04:00 | 2.4969 | 0 | N/A | 0 | 0
2022-02-04 04:30 | 2.4722 | 0 | N/A | 0 | 0
2022-02-04 05:00 | 2.494 | 0 | N/A | 0 | 0
2022-02-04 05:30 | 2.7074 | 0 | N/A | 0 | 0
2022-02-04 06:00 | 2.9526 | 0 | N/A | 0 | 0
2022-02-04 06:30 | 3.7673 | 0 | N/A | 0 | 0
2022-02-04 07:00 | 4.3713 | 0 | N/A | 0 | 0
2022-02-04 07:30 | 5.1348 | 0 | N/A | 0 | 0
2022-02-04 08:00 | 4.9604 | 0 | N/A | 0 | 0
2022-02-04 08:30 | 3.6783 | 0 | N/A | 0 | 0
2022-02-04 09:00 | 3.2394 | 0 | N/A | 0 | 0
2022-02-04 09:30 | 2.6831 | 0 | N/A | 0 | 0
2022-02-04 10:00 | 2.0813 | 0 | N/A | 0 | 0
2022-02-04 10:30 | 1.7319 | 0 | N/A | 0 | 0
2022-02-04 11:00 | 1.4127 | 0 | N/A | 0 | 0
2022-02-04 11:30 | 0.54573 | 0 | N/A | 0 | 0
2022-02-04 12:00 | 0.55907 | 0 | N/A | 0 | 0
2022-02-04 12:30 | 0.23507 | 0 | N/A | 0 | 0
2022-02-04 13:00 | -0.40848 | 0 | N/A | 0 | 0
2022-02-04 13:30 | -0.54309 | 0 | N/A | 0 | 0
2022-02-04 14:00 | -0.79961 | 0 | N/A | 0 | 0
2022-02-04 14:30 | -0.79717 | 0 | N/A | 0 | 0
2022-02-04 15:00 | -0.8196 | 0 | N/A | 0 | 0
2022-02-04 15:30 | -0.8911 | 0 | N/A | 0 | 0
2022-02-04 16:00 | -1.2755 | 0 | N/A | 0 | 0
2022-02-04 16:30 | -1.0465 | 0 | N/A | 0 | 0
2022-02-04 17:00 | -0.66966 | 0 | N/A | 0 | 0
2022-02-04 17:30 | 0.5709 | 0 | N/A | 0 | 0
2022-02-04 18:00 | 1.4479 | 0 | N/A | 0 | 0
2022-02-04 18:30 | 2.0724 | 0 | N/A | 0 | 0
2022-02-04 19:00 | 2.8288 | 0 | N/A | 0 | 0
2022-02-04 19:30 | 3.5507 | 0 | N/A | 0 | 0
2022-02-04 20:00 | 3.8848 | 0 | N/A | 0 | 0
2022-02-04 20:30 | 4.1914 | 0 | N/A | 0 | 0
2022-02-04 21:00 | 4.2756 | 0 | N/A | 0 | 0
2022-02-04 21:30 | 4.2176 | 0 | N/A | 0 | 0
2022-02-04 22:00 | 3.9752 | 0 | N/A | 0 | 0
2022-02-04 22:30 | 4.1943 | 0 | N/A | 0 | 0
2022-02-04 23:00 | 4.3233 | 0 | N/A | 0 | 0
2022-02-04 23:30 | 3.9964 | 0 | N/A | 0 | 0
2022-02-05 | 4.019 | 0 | N/A | 0 | 0
2022-02-05 00:30 | 4.3117 | 0 | N/A | 0 | 0
2022-02-05 01:00 | 4.441 | 0 | N/A | 0 | 0
2022-02-05 01:30 | 3.6011 | 0 | N/A | 0 | 0
2022-02-05 02:00 | 3.0331 | 0 | N/A | 0 | 0
2022-02-05 02:30 | 2.9848 | 0 | N/A | 0 | 0
2022-02-05 03:00 | 2.6619 | 0 | N/A | 0 | 0
2022-02-05 03:30 | 2.4388 | 0 | N/A | 0 | 0
2022-02-05 04:00 | 2.3452 | 0 | N/A | 0 | 0
2022-02-05 04:30 | 2.3198 | 0 | N/A | 0 | 0
2022-02-05 05:00 | 2.2969 | 0 | N/A | 0 | 0
2022-02-05 05:30 | 2.3485 | 0 | N/A | 0 | 0
2022-02-05 06:00 | 2.4851 | 0 | N/A | 0 | 0
2022-02-05 06:30 | 2.7357 | 0 | N/A | 0 | 0
2022-02-05 07:00 | 2.895 | 0 | N/A | 0 | 0
2022-02-05 07:30 | 3.134 | 0 | N/A | 0 | 0
2022-02-05 08:00 | 3.0288 | 0 | N/A | 0 | 0
2022-02-05 08:30 | 2.575 | 0 | N/A | 0 | 0
2022-02-05 09:00 | 2.1684 | 0 | N/A | 0 | 0
2022-02-05 09:30 | 1.683 | 0 | N/A | 0 | 0
2022-02-05 10:00 | 1.0106 | 0 | N/A | 0 | 0
2022-02-05 10:30 | 0.62405 | 0 | N/A | 0 | 0
2022-02-05 11:00 | -0.51157 | 0 | N/A | 0 | 0
2022-02-05 11:30 | 0.56946 | 0 | N/A | 0 | 0
2022-02-05 12:00 | 0.59481 | 0 | N/A | 0 | 0
2022-02-05 12:30 | 0.6346 | 0 | N/A | 0 | 0
2022-02-05 13:00 | 0.91255 | 0 | N/A | 0 | 0
2022-02-05 13:30 | 0.69208 | 0 | N/A | 0 | 0
2022-02-05 14:00 | 1.1794 | 0 | N/A | 0 | 0
2022-02-05 14:30 | 2.0555 | 0 | N/A | 0 | 0
2022-02-05 15:00 | 1.8651 | 0 | N/A | 0 | 0
2022-02-05 15:30 | 1.4165 | 0 | N/A | 0 | 0
2022-02-05 16:00 | 1.9976 | 0 | N/A | 0 | 0
2022-02-05 16:30 | 1.6103 | 0 | N/A | 0 | 0
2022-02-05 17:00 | 1.582 | 0 | N/A | 0 | 0
2022-02-05 17:30 | 1.1093 | 0 | N/A | 0 | 0
2022-02-05 18:00 | 2.3528 | 0 | N/A | 0 | 0
2022-02-05 18:30 | 2.985 | 0 | N/A | 0 | 0
2022-02-05 19:00 | 3.3189 | 0 | N/A | 0 | 0
2022-02-05 19:30 | 3.9288 | 0 | N/A | 0 | 0
2022-02-05 20:00 | 4.1405 | 0 | N/A | 0 | 0
2022-02-05 20:30 | 4.0269 | 0 | N/A | 0 | 0
2022-02-05 21:00 | 3.985 | 0 | N/A | 0 | 0
2022-02-05 21:30 | 3.8553 | 0 | N/A | 0 | 0
2022-02-05 22:00 | 3.6932 | 0 | N/A | 0 | 0
2022-02-05 22:30 | 4.0149 | 0 | N/A | 0 | 0
2022-02-05 23:00 | 4.1943 | 0 | N/A | 0 | 0
2022-02-05 23:30 | 3.9506 | 0 | N/A | 0 | 0
2022-02-06 | 4.0535 | 0 | N/A | 0 | 0
2022-02-06 00:30 | 4.4473 | 0 | N/A | 0 | 0
2022-02-06 01:00 | 4.5972 | 0 | N/A | 0 | 0
2022-02-06 01:30 | 3.8136 | 0 | N/A | 0 | 0
2022-02-06 02:00 | 3.1835 | 0 | N/A | 0 | 0
2022-02-06 02:30 | 3.136 | 0 | N/A | 0 | 0
2022-02-06 03:00 | 2.8597 | 0 | N/A | 0 | 0
2022-02-06 03:30 | 2.5661 | 0 | N/A | 0 | 0
2022-02-06 04:00 | 2.4373 | 0 | N/A | 0 | 0
2022-02-06 04:30 | 2.3693 | 0 | N/A | 0 | 0
2022-02-06 05:00 | 2.3118 | 0 | N/A | 0 | 0
2022-02-06 05:30 | 2.3001 | 0 | N/A | 0 | 0
2022-02-06 06:00 | 2.4047 | 0 | N/A | 0 | 0
2022-02-06 06:30 | 2.5644 | 0 | N/A | 0 | 0
2022-02-06 07:00 | 2.6604 | 0 | N/A | 0 | 0
2022-02-06 07:30 | 2.7865 | 0 | N/A | 0 | 0
2022-02-06 08:00 | 2.6862 | 0 | N/A | 0 | 0
2022-02-06 08:30 | 2.2631 | 0 | N/A | 0 | 0
2022-02-06 09:00 | 1.9724 | 0 | N/A | 0 | 0
2022-02-06 09:30 | 1.5274 | 0 | N/A | 0 | 0
2022-02-06 10:00 | 0.96268 | 0 | N/A | 0 | 0
2022-02-06 10:30 | 0.63934 | 0 | N/A | 0 | 0
2022-02-06 11:00 | -0.55607 | 0 | N/A | 0 | 0
2022-02-06 11:30 | -0.73313 | 0 | N/A | 0 | 0
2022-02-06 12:00 | -0.90434 | 0 | N/A | 0 | 0
2022-02-06 12:30 | -0.95627 | 0 | N/A | 0 | 0
2022-02-06 13:00 | -0.60157 | 0 | N/A | 0 | 0
2022-02-06 13:30 | -0.35347 | 0 | N/A | 0 | 0
2022-02-06 14:00 | 0.77153 | 0 | N/A | 0 | 0
2022-02-06 14:30 | 0.54459 | 0 | N/A | 0 | 0
2022-02-06 15:00 | 0.85001 | 0 | N/A | 0 | 0
2022-02-06 15:30 | 1.0585 | 0 | N/A | 0 | 0
2022-02-06 16:00 | 1.2453 | 0 | N/A | 0 | 0
2022-02-06 16:30 | 1.2699 | 0 | N/A | 0 | 0
2022-02-06 17:00 | 1.4666 | 0 | N/A | 0 | 0
2022-02-06 17:30 | 2.6513 | 0 | N/A | 0 | 0
2022-02-06 18:00 | 3.117 | 0 | N/A | 0 | 0
2022-02-06 18:30 | 3.7827 | 0 | N/A | 0 | 0
2022-02-06 19:00 | 4.4191 | 0 | N/A | 0 | 0
2022-02-06 19:30 | 4.7749 | 0 | N/A | 0 | 0
2022-02-06 20:00 | 4.8852 | 0 | N/A | 0 | 0
2022-02-06 20:30 | 4.738 | 0 | N/A | 0 | 0
2022-02-06 21:00 | 4.5935 | 0 | N/A | 0 | 0
2022-02-06 21:30 | 4.3345 | 0 | N/A | 0 | 0
2022-02-06 22:00 | 3.955 | 0 | N/A | 0 | 0
2022-02-06 22:30 | 4.1898 | 0 | N/A | 0 | 0
2022-02-06 23:00 | 4.231 | 0 | N/A | 0 | 0
2022-02-06 23:30 | 3.9838 | 0 | N/A | 0 | 0
2022-02-07 | 4.0235 | 0 | N/A | 0 | 0
2022-02-07 00:30 | 4.4597 | 0 | N/A | 0 | 0
2022-02-07 01:00 | 4.665 | 0 | N/A | 0 | 0
2022-02-07 01:30 | 3.7684 | 0 | N/A | 0 | 0
2022-02-07 02:00 | 3.2034 | 0 | N/A | 0 | 0
2022-02-07 02:30 | 3.0627 | 0 | N/A | 0 | 0
2022-02-07 03:00 | 2.8067 | 0 | N/A | 0 | 0
2022-02-07 03:30 | 2.5506 | 0 | N/A | 0 | 0
2022-02-07 04:00 | 2.3809 | 0 | N/A | 0 | 0
2022-02-07 04:30 | 2.3281 | 0 | N/A | 0 | 0
2022-02-07 05:00 | 2.3853 | 0 | N/A | 0 | 0
2022-02-07 05:30 | 2.5736 | 0 | N/A | 0 | 0
2022-02-07 06:00 | 2.8249 | 0 | N/A | 0 | 0
2022-02-07 06:30 | 3.4716 | 0 | N/A | 0 | 0
2022-02-07 07:00 | 4.287 | 0 | N/A | 0 | 0
2022-02-07 07:30 | 4.7858 | 0 | N/A | 0 | 0
2022-02-07 08:00 | 4.7991 | 0 | N/A | 0 | 0
2022-02-07 08:30 | 4.0245 | 0 | N/A | 0 | 0
2022-02-07 09:00 | 3.4447 | 0 | N/A | 0 | 0
2022-02-07 09:30 | 2.5951 | 0 | N/A | 0 | 0
2022-02-07 10:00 | 1.7191 | 0 | N/A | 0 | 0
2022-02-07 10:30 | 1.0348 | 0 | N/A | 0 | 0
2022-02-07 11:00 | 0.50158 | 0 | N/A | 0 | 0
2022-02-07 11:30 | 0.3541 | 0 | N/A | 0 | 0
2022-02-07 12:00 | 0.096724 | 0 | N/A | 0 | 0
2022-02-07 12:30 | -0.048074 | 0 | N/A | 0 | 0
2022-02-07 13:00 | -0.20177 | 0 | N/A | 0 | 0
2022-02-07 13:30 | -0.31248 | 0 | N/A | 0 | 0
2022-02-07 14:00 | -0.20616 | 0 | N/A | 0 | 0
2022-02-07 14:30 | 0.22706 | 0 | N/A | 0 | 0
2022-02-07 15:00 | 0.32993 | 0 | N/A | 0 | 0
2022-02-07 15:30 | 0.60569 | 0 | N/A | 0 | 0
2022-02-07 16:00 | 0.92015 | 0 | N/A | 0 | 0
2022-02-07 16:30 | 1.0837 | 0 | N/A | 0 | 0
2022-02-07 17:00 | 1.6437 | 0 | N/A | 0 | 0
2022-02-07 17:30 | 2.5282 | 0 | N/A | 0 | 0
2022-02-07 18:00 | 3.5153 | 0 | N/A | 0 | 0
2022-02-07 18:30 | 4.3948 | 0 | N/A | 0 | 0
2022-02-07 19:00 | 4.8624 | 0 | N/A | 0 | 0
2022-02-07 19:30 | 5.172 | 0 | N/A | 0 | 0
2022-02-07 20:00 | 5.1849 | 0 | N/A | 0 | 0
2022-02-07 20:30 | 5.0631 | 0 | N/A | 0 | 0
2022-02-07 21:00 | 4.8456 | 0 | N/A | 0 | 0
2022-02-07 21:30 | 4.5203 | 0 | N/A | 0 | 0
2022-02-07 22:00 | 4.2032 | 0 | N/A | 0 | 0
2022-02-07 22:30 | 4.3036 | 0 | N/A | 0 | 0
2022-02-07 23:00 | 4.2114 | 0 | N/A | 0 | 0
2022-02-07 23:30 | 3.784 | 0 | N/A | 0 | 0
2022-02-08 | 3.8459 | 0 | N/A | 0 | 0
2022-02-08 00:30 | 4.233 | 0 | N/A | 0 | 0
2022-02-08 01:00 | 4.3153 | 0 | N/A | 0 | 0
2022-02-08 01:30 | 3.3489 | 0 | N/A | 0 | 0
2022-02-08 02:00 | 2.8106 | 0 | N/A | 0 | 0
2022-02-08 02:30 | 2.7596 | 0 | N/A | 0 | 0
2022-02-08 03:00 | 2.5535 | 0 | N/A | 0 | 0
2022-02-08 03:30 | 2.2823 | 0 | N/A | 0 | 0
2022-02-08 04:00 | 2.2958 | 0 | N/A | 0 | 0
2022-02-08 04:30 | 2.3112 | 0 | N/A | 0 | 0
2022-02-08 05:00 | 2.3301 | 0 | N/A | 0 | 0
2022-02-08 05:30 | 2.4987 | 0 | N/A | 0 | 0
2022-02-08 06:00 | 2.8021 | 0 | N/A | 0 | 0
2022-02-08 06:30 | 3.3878 | 0 | N/A | 0 | 0
2022-02-08 07:00 | 4.0416 | 0 | N/A | 0 | 0
2022-02-08 07:30 | 4.639 | 0 | N/A | 0 | 0
2022-02-08 08:00 | 4.7047 | 0 | N/A | 0 | 0
2022-02-08 08:30 | 3.9389 | 0 | N/A | 0 | 0
2022-02-08 09:00 | 3.2349 | 0 | N/A | 0 | 0
2022-02-08 09:30 | 2.5799 | 0 | N/A | 0 | 0
2022-02-08 10:00 | 1.4397 | 0 | N/A | 0 | 0
2022-02-08 10:30 | 0.95037 | 0 | N/A | 0 | 0
2022-02-08 11:00 | 0.56668 | 0 | N/A | 0 | 0
2022-02-08 11:30 | 0.1467 | 0 | N/A | 0 | 0
2022-02-08 12:00 | -0.25142 | 0 | N/A | 0 | 0
2022-02-08 12:30 | -0.28002 | 0 | N/A | 0 | 0
2022-02-08 13:00 | -0.43372 | 0 | N/A | 0 | 0
2022-02-08 13:30 | -0.43431 | 0 | N/A | 0 | 0
2022-02-08 14:00 | -0.39543 | 0 | N/A | 0 | 0
2022-02-08 14:30 | -0.24518 | 0 | N/A | 0 | 0
2022-02-08 15:00 | 0.16344 | 0 | N/A | 0 | 0
2022-02-08 15:30 | 0.19847 | 0 | N/A | 0 | 0
2022-02-08 16:00 | 0.44687 | 0 | N/A | 0 | 0
2022-02-08 16:30 | 0.80351 | 0 | N/A | 0 | 0
2022-02-08 17:00 | 1.5258 | 0 | N/A | 0 | 0
2022-02-08 17:30 | 2.528 | 0 | N/A | 0 | 0
2022-02-08 18:00 | 3.6607 | 0 | N/A | 0 | 0
2022-02-08 18:30 | 4.5965 | 0 | N/A | 0 | 0
2022-02-08 19:00 | 5.2599 | 0 | N/A | 0 | 0
2022-02-08 19:30 | 5.7772 | 0 | N/A | 0 | 0
2022-02-08 20:00 | 5.7883 | 0 | N/A | 0 | 0
2022-02-08 20:30 | 5.5714 | 0 | N/A | 0 | 0
2022-02-08 21:00 | 5.2913 | 0 | N/A | 0 | 0
2022-02-08 21:30 | 4.9125 | 0 | N/A | 0 | 0
2022-02-08 22:00 | 4.41 | 0 | N/A | 0 | 0
2022-02-08 22:30 | 4.4257 | 0 | N/A | 0 | 0
2022-02-08 23:00 | 4.2333 | 0 | N/A | 0 | 0
2022-02-08 23:30 | 3.7308 | 0 | N/A | 0 | 0
2022-02-09 | 3.7147 | 0 | N/A | 0 | 0
2022-02-10 00:30 | 4.261 | 0 | N/A | 0 | 0
2022-02-10 01:00 | 4.376 | 0 | N/A | 0 | 0
2022-02-10 01:30 | 3.4212 | 0 | N/A | 0 | 0
2022-02-10 02:00 | 2.8481 | 0 | N/A | 0 | 0
2022-02-10 02:30 | 2.863 | 0 | N/A | 0 | 0
2022-02-10 03:00 | 2.5491 | 0 | N/A | 0 | 0
2022-02-10 03:30 | 2.3169 | 0 | N/A | 0 | 0
2022-02-10 04:00 | 2.2669 | 0 | N/A | 0 | 0
2022-02-10 04:30 | 2.2145 | 0 | N/A | 0 | 0
2022-02-10 05:00 | 2.3098 | 0 | N/A | 0 | 0
2022-02-10 05:30 | 2.5192 | 0 | N/A | 0 | 0
2022-02-10 06:00 | 2.7526 | 0 | N/A | 0 | 0
2022-02-10 06:30 | 3.2163 | 0 | N/A | 0 | 0
2022-02-10 07:00 | 3.7141 | 0 | N/A | 0 | 0
2022-02-10 07:30 | 4.352 | 0 | N/A | 0 | 0
2022-02-10 08:00 | 4.2581 | 0 | N/A | 0 | 0
2022-02-10 08:30 | 3.9072 | 0 | N/A | 0 | 0
2022-02-10 09:00 | 3.6299 | 0 | N/A | 0 | 0
2022-02-10 09:30 | 4.0833 | 0 | N/A | 0 | 0
2022-02-10 10:00 | 3.9353 | 0 | N/A | 0 | 0
2022-02-10 10:30 | 2.4554 | 0 | N/A | 0 | 0
2022-02-10 11:00 | 2.2575 | 0 | N/A | 0 | 0
2022-02-10 11:30 | 1.9279 | 0 | N/A | 0 | 0
2022-02-10 12:00 | 2.1338 | 0 | N/A | 0 | 0
2022-02-10 12:30 | 1.9347 | 0 | N/A | 0 | 0
2022-02-10 13:00 | 1.1361 | 0 | N/A | 0 | 0
2022-02-10 13:30 | 1.0638 | 0 | N/A | 0 | 0
2022-02-10 14:00 | 1.2773 | 0 | N/A | 0 | 0
2022-02-10 14:30 | 0.059628 | 0 | N/A | 0 | 0
2022-02-10 15:00 | 0.3908 | 0 | N/A | 0 | 0
2022-02-10 15:30 | 0.62816 | 0 | N/A | 0 | 0
2022-02-10 16:00 | 0.63311 | 0 | N/A | 0 | 0
2022-02-10 16:30 | 0.326 | 0 | N/A | 0 | 0
2022-02-10 17:00 | 0.37257 | 0 | N/A | 0 | 0
2022-02-10 17:30 | 1.1397 | 0 | N/A | 0 | 0
2022-02-10 18:00 | 2.0648 | 0 | N/A | 0 | 0
2022-02-10 18:30 | 2.9529 | 0 | N/A | 0 | 0
2022-02-10 19:00 | 3.5896 | 0 | N/A | 0 | 0
2022-02-10 19:30 | 4.0065 | 0 | N/A | 0 | 0
2022-02-10 20:00 | 4.2306 | 0 | N/A | 0 | 0
2022-02-10 20:30 | 4.3675 | 0 | N/A | 0 | 0
2022-02-10 21:00 | 4.4557 | 0 | N/A | 0 | 0
2022-02-10 21:30 | 4.1982 | 0 | N/A | 0 | 0
2022-02-10 22:00 | 4.0088 | 0 | N/A | 0 | 0
2022-02-10 22:30 | 4.2697 | 0 | N/A | 0 | 0
2022-02-10 23:00 | 4.3005 | 0 | N/A | 0 | 0
2022-02-10 23:30 | 3.8775 | 0 | N/A | 0 | 0
2022-02-11 | 3.8261 | 0 | N/A | 0 | 0
2022-02-11 00:30 | 4.2339 | 0 | N/A | 0 | 0
2022-02-11 01:00 | 4.5077 | 0 | N/A | 0 | 0
2022-02-11 01:30 | 3.6465 | 0 | N/A | 0 | 0
2022-02-11 02:00 | 2.9268 | 0 | N/A | 0 | 0
2022-02-11 02:30 | 2.8827 | 0 | N/A | 0 | 0
2022-02-11 03:00 | 2.6048 | 0 | N/A | 0 | 0
2022-02-11 03:30 | 2.4061 | 0 | N/A | 0 | 0
2022-02-11 04:00 | 2.3439 | 0 | N/A | 0 | 0
2022-02-11 04:30 | 2.2761 | 0 | N/A | 0 | 0
2022-02-11 05:00 | 2.3339 | 0 | N/A | 0 | 0
2022-02-11 05:30 | 2.5736 | 0 | N/A | 0 | 0
2022-02-11 06:00 | 2.9086 | 0 | N/A | 0 | 0
2022-02-11 06:30 | 3.6077 | 0 | N/A | 0 | 0
2022-02-11 07:00 | 4.3597 | 0 | N/A | 0 | 0
2022-02-11 07:30 | 5.1002 | 0 | N/A | 0 | 0
2022-02-11 08:00 | 5.0877 | 0 | N/A | 0 | 0
2022-02-11 08:30 | 4.2351 | 0 | N/A | 0 | 0
2022-02-11 09:00 | 4.1195 | 0 | N/A | 0 | 0
2022-02-11 09:30 | 3.4934 | 0 | N/A | 0 | 0
2022-02-11 10:00 | 3.1957 | 0 | N/A | 0 | 0
2022-02-11 10:30 | 1.8808 | 0 | N/A | 0 | 0
2022-02-11 11:00 | 2.3665 | 0 | N/A | 0 | 0
2022-02-11 11:30 | 3.1142 | 0 | N/A | 0 | 0
2022-02-11 12:00 | 2.1621 | 0 | N/A | 0 | 0
2022-02-11 12:30 | 1.4844 | 0 | N/A | 0 | 0
2022-02-11 13:00 | 0.6361 | 0 | N/A | 0 | 0
2022-02-11 13:30 | 0.72945 | 0 | N/A | 0 | 0
2022-02-11 14:00 | 0.27891 | 0 | N/A | 0 | 0
2022-02-11 14:30 | 0.57801 | 0 | N/A | 0 | 0
2022-02-11 15:00 | 1.2048 | 0 | N/A | 0 | 0
2022-02-11 15:30 | -0.58524 | 0 | N/A | 0 | 0
2022-02-11 16:00 | -0.84509 | 0 | N/A | 0 | 0
2022-02-11 16:30 | 0.67952 | 0 | N/A | 0 | 0
2022-02-11 17:00 | -0.60378 | 0 | N/A | 0 | 0
2022-02-11 17:30 | 0.53487 | 0 | N/A | 0 | 0
2022-02-11 18:00 | 1.2826 | 0 | N/A | 0 | 0
2022-02-11 18:30 | 2.121 | 0 | N/A | 0 | 0
2022-02-11 19:00 | 2.961 | 0 | N/A | 0 | 0
2022-02-11 19:30 | 3.5274 | 0 | N/A | 0 | 0
2022-02-11 20:00 | 3.8991 | 0 | N/A | 0 | 0
2022-02-11 20:30 | 4.1405 | 0 | N/A | 0 | 0
2022-02-11 21:00 | 4.331 | 0 | N/A | 0 | 0
2022-02-11 21:30 | 4.1992 | 0 | N/A | 0 | 0
2022-02-11 22:00 | 4.0078 | 0 | N/A | 0 | 0
2022-02-11 22:30 | 4.2025 | 0 | N/A | 0 | 0
2022-02-11 23:00 | 4.3393 | 0 | N/A | 0 | 0
2022-02-11 23:30 | 4.056 | 0 | N/A | 0 | 0
2022-02-12 | 3.9995 | 0 | N/A | 0 | 0
2022-02-12 00:30 | 4.4377 | 0 | N/A | 0 | 0
2022-02-12 01:00 | 4.6267 | 0 | N/A | 0 | 0
2022-02-12 01:30 | 3.6255 | 0 | N/A | 0 | 0
2022-02-12 02:00 | 2.9793 | 0 | N/A | 0 | 0
2022-02-12 02:30 | 2.9396 | 0 | N/A | 0 | 0
2022-02-12 03:00 | 2.6357 | 0 | N/A | 0 | 0
2022-02-12 03:30 | 2.3659 | 0 | N/A | 0 | 0
2022-02-12 04:00 | 2.2893 | 0 | N/A | 0 | 0
2022-02-12 04:30 | 2.2405 | 0 | N/A | 0 | 0
2022-02-12 05:00 | 2.2314 | 0 | N/A | 0 | 0
2022-02-12 05:30 | 2.2706 | 0 | N/A | 0 | 0
2022-02-12 06:00 | 2.4271 | 0 | N/A | 0 | 0
2022-02-12 06:30 | 2.7391 | 0 | N/A | 0 | 0
2022-02-12 07:00 | 2.8395 | 0 | N/A | 0 | 0
2022-02-12 07:30 | 3.0911 | 0 | N/A | 0 | 0
2022-02-12 08:00 | 3.1506 | 0 | N/A | 0 | 0
2022-02-12 08:30 | 2.5868 | 0 | N/A | 0 | 0
2022-02-12 09:00 | 2.2018 | 0 | N/A | 0 | 0
2022-02-12 09:30 | 1.6428 | 0 | N/A | 0 | 0
2022-02-12 10:00 | 0.98311 | 0 | N/A | 0 | 0
2022-02-12 10:30 | 0.58792 | 0 | N/A | 0 | 0
2022-02-12 11:00 | -0.56382 | 0 | N/A | 0 | 0
2022-02-12 11:30 | -0.80748 | 0 | N/A | 0 | 0
2022-02-12 12:00 | -0.51051 | 0 | N/A | 0 | 0
2022-02-12 12:30 | -0.82899 | 0 | N/A | 0 | 0
2022-02-12 13:00 | -0.79911 | 0 | N/A | 0 | 0
2022-02-12 13:30 | -0.59867 | 0 | N/A | 0 | 0
2022-02-12 14:00 | -0.54557 | 0 | N/A | 0 | 0
2022-02-12 14:30 | -0.65388 | 0 | N/A | 0 | 0
2022-02-12 15:00 | -0.38787 | 0 | N/A | 0 | 0
2022-02-12 15:30 | -0.22559 | 0 | N/A | 0 | 0
2022-02-12 16:00 | 0.34197 | 0 | N/A | 0 | 0
2022-02-12 16:30 | 0.71872 | 0 | N/A | 0 | 0
2022-02-12 17:00 | 1.4343 | 0 | N/A | 0 | 0
2022-02-12 17:30 | 2.0641 | 0 | N/A | 0 | 0
2022-02-12 18:00 | 3.0354 | 0 | N/A | 0 | 0
2022-02-12 18:30 | 3.7859 | 0 | N/A | 0 | 0
2022-02-12 19:00 | 4.4426 | 0 | N/A | 0 | 0
2022-02-12 19:30 | 4.8375 | 0 | N/A | 0 | 0
2022-02-12 20:00 | 4.8841 | 0 | N/A | 0 | 0
2022-02-12 20:30 | 4.718 | 0 | N/A | 0 | 0
2022-02-12 21:00 | 4.526 | 0 | N/A | 0 | 0
2022-02-12 21:30 | 4.28 | 0 | N/A | 0 | 0
2022-02-12 22:00 | 3.9172 | 0 | N/A | 0 | 0
2022-02-12 22:30 | 4.2337 | 0 | N/A | 0 | 0
2022-02-12 23:00 | 4.216 | 0 | N/A | 0 | 0
2022-02-12 23:30 | 3.9976 | 0 | N/A | 0 | 0
2022-02-13 | 4.0006 | 0 | N/A | 0 | 0
2022-02-13 00:30 | 4.4076 | 0 | N/A | 0 | 0
2022-02-13 01:00 | 4.5464 | 0 | N/A | 0 | 0
2022-02-13 01:30 | 3.6365 | 0 | N/A | 0 | 0
2022-02-13 02:00 | 2.9663 | 0 | N/A | 0 | 0
2022-02-13 02:30 | 2.9297 | 0 | N/A | 0 | 0
2022-02-13 03:00 | 2.596 | 0 | N/A | 0 | 0
2022-02-13 03:30 | 2.4622 | 0 | N/A | 0 | 0
2022-02-13 04:00 | 2.2995 | 0 | N/A | 0 | 0
2022-02-13 04:30 | 2.2123 | 0 | N/A | 0 | 0
2022-02-13 05:00 | 2.257 | 0 | N/A | 0 | 0
2022-02-13 05:30 | 2.2063 | 0 | N/A | 0 | 0
2022-02-13 06:00 | 2.2719 | 0 | N/A | 0 | 0
2022-02-13 06:30 | 2.45 | 0 | N/A | 0 | 0
2022-02-13 07:00 | 2.5973 | 0 | N/A | 0 | 0
2022-02-13 07:30 | 2.6867 | 0 | N/A | 0 | 0
2022-02-13 08:00 | 2.6668 | 0 | N/A | 0 | 0
2022-02-13 08:30 | 2.3246 | 0 | N/A | 0 | 0
2022-02-13 09:00 | 1.9561 | 0 | N/A | 0 | 0
2022-02-13 09:30 | 1.5294 | 0 | N/A | 0 | 0
2022-02-13 10:00 | 0.94921 | 0 | N/A | 0 | 0
2022-02-13 10:30 | 0.7347 | 0 | N/A | 0 | 0
2022-02-13 11:00 | -0.47834 | 0 | N/A | 0 | 0
2022-02-13 11:30 | -0.49118 | 0 | N/A | 0 | 0
2022-02-13 12:00 | -0.46392 | 0 | N/A | 0 | 0
2022-02-13 12:30 | 0.60818 | 0 | N/A | 0 | 0
2022-02-13 13:00 | 0.68878 | 0 | N/A | 0 | 0
2022-02-13 13:30 | 1.0746 | 0 | N/A | 0 | 0
2022-02-13 14:00 | 1.519 | 0 | N/A | 0 | 0
2022-02-13 14:30 | 2.014 | 0 | N/A | 0 | 0
2022-02-13 15:00 | 1.6795 | 0 | N/A | 0 | 0
2022-02-13 15:30 | 1.3697 | 0 | N/A | 0 | 0
2022-02-13 16:00 | 1.6887 | 0 | N/A | 0 | 0
2022-02-13 16:30 | 2.3783 | 0 | N/A | 0 | 0
2022-02-13 17:00 | 3.2914 | 0 | N/A | 0 | 0
2022-02-13 17:30 | 4.0552 | 0 | N/A | 0 | 0
2022-02-13 18:00 | 5.3935 | 0 | N/A | 0 | 0
2022-02-13 18:30 | 6.1533 | 0 | N/A | 0 | 0
2022-02-13 19:00 | 6.9706 | 0 | N/A | 0 | 0
2022-02-13 19:30 | 6.983 | 0 | N/A | 0 | 0
2022-02-13 20:00 | 6.4099 | 0 | N/A | 0 | 0
2022-02-13 20:30 | 5.8482 | 0 | N/A | 0 | 0
2022-02-13 21:00 | 5.3667 | 0 | N/A | 0 | 0
2022-02-13 21:30 | 4.9801 | 0 | N/A | 0 | 0
2022-02-13 22:00 | 4.5198 | 0 | N/A | 0 | 0
2022-02-13 22:30 | 4.601 | 0 | N/A | 0 | 0
2022-02-13 23:00 | 4.4707 | 0 | N/A | 0 | 0
2022-02-13 23:30 | 4.1126 | 0 | N/A | 0 | 0
2022-02-14 | 4.1753 | 0 | N/A | 0 | 0
2022-02-15 00:30 | 4.4525 | 0 | N/A | 0 | 0
2022-02-15 01:00 | 4.4901 | 0 | N/A | 0 | 0
2022-02-15 01:30 | 3.5259 | 0 | N/A | 0 | 0
2022-02-15 02:00 | 2.9757 | 0 | N/A | 0 | 0
2022-02-15 02:30 | 2.9641 | 0 | N/A | 0 | 0
2022-02-15 03:00 | 2.6986 | 0 | N/A | 0 | 0
2022-02-15 03:30 | 2.5036 | 0 | N/A | 0 | 0
2022-02-15 04:00 | 2.4379 | 0 | N/A | 0 | 0
2022-02-15 04:30 | 2.469 | 0 | N/A | 0 | 0
2022-02-15 05:00 | 2.4815 | 0 | N/A | 0 | 0
2022-02-15 05:30 | 2.6883 | 0 | N/A | 0 | 0
2022-02-15 06:00 | 3.0232 | 0 | N/A | 0 | 0
2022-02-15 06:30 | 3.3539 | 0 | N/A | 0 | 0
2022-02-15 07:00 | 4.1461 | 0 | N/A | 0 | 0
2022-02-15 07:30 | 4.9015 | 0 | N/A | 0 | 0
2022-02-15 08:00 | 5.0698 | 0 | N/A | 0 | 0
2022-02-15 08:30 | 4.6833 | 0 | N/A | 0 | 0
2022-02-15 09:00 | 4.3504 | 0 | N/A | 0 | 0
2022-02-15 09:30 | 3.7934 | 0 | N/A | 0 | 0
2022-02-15 10:00 | 2.9089 | 0 | N/A | 0 | 0
2022-02-15 10:30 | 1.8709 | 0 | N/A | 0 | 0
2022-02-15 11:00 | 1.4025 | 0 | N/A | 0 | 0
2022-02-15 11:30 | 0.35335 | 0 | N/A | 0 | 0
2022-02-15 12:00 | 0.1666 | 0 | N/A | 0 | 0
2022-02-15 12:30 | -0.068638 | 0 | N/A | 0 | 0
2022-02-15 13:00 | -0.73001 | 0 | N/A | 0 | 0
2022-02-15 13:30 | -0.50028 | 0 | N/A | 0 | 0
2022-02-15 14:00 | -0.4681 | 0 | N/A | 0 | 0
2022-02-15 14:30 | -0.22373 | 0 | N/A | 0 | 0
2022-02-15 15:00 | 0.11353 | 0 | N/A | 0 | 0
2022-02-15 15:30 | 0.32085 | 0 | N/A | 0 | 0
2022-02-15 16:00 | 0.82003 | 0 | N/A | 0 | 0
2022-02-15 16:30 | 1.4399 | 0 | N/A | 0 | 0
2022-02-15 17:00 | 2.0687 | 0 | N/A | 0 | 0
2022-02-15 17:30 | 3.0423 | 0 | N/A | 0 | 0
2022-02-15 18:00 | 4.1361 | 0 | N/A | 0 | 0
2022-02-15 18:30 | 5.5239 | 0 | N/A | 0 | 0
2022-02-15 19:00 | 5.3353 | 0 | N/A | 0 | 0
2022-02-15 19:30 | 5.4834 | 0 | N/A | 0 | 0
2022-02-15 20:00 | 5.2909 | 0 | N/A | 0 | 0
2022-02-15 20:30 | 5.2538 | 0 | N/A | 0 | 0
2022-02-15 21:00 | 5.0114 | 0 | N/A | 0 | 0
2022-02-15 21:30 | 4.6878 | 0 | N/A | 0 | 0
2022-02-15 22:00 | 4.1889 | 0 | N/A | 0 | 0
2022-02-15 22:30 | 4.3126 | 0 | N/A | 0 | 0
2022-02-15 23:00 | 4.2538 | 0 | N/A | 0 | 0
2022-02-15 23:30 | 3.7125 | 0 | N/A | 0 | 0
2022-02-16 | 3.7448 | 0 | N/A | 0 | 0
2022-02-17 00:30 | 4.1978 | 0 | N/A | 0 | 0
2022-02-17 01:00 | 4.4297 | 0 | N/A | 0 | 0
2022-02-17 01:30 | 3.5227 | 0 | N/A | 0 | 0
2022-02-17 02:00 | 2.8621 | 0 | N/A | 0 | 0
2022-02-17 02:30 | 2.8524 | 0 | N/A | 0 | 0
2022-02-17 03:00 | 2.5977 | 0 | N/A | 0 | 0
2022-02-17 03:30 | 2.3243 | 0 | N/A | 0 | 0
2022-02-17 04:00 | 2.2957 | 0 | N/A | 0 | 0
2022-02-17 04:30 | 2.3227 | 0 | N/A | 0 | 0
2022-02-17 05:00 | 2.396 | 0 | N/A | 0 | 0
2022-02-17 05:30 | 2.5201 | 0 | N/A | 0 | 0
2022-02-17 06:00 | 2.6993 | 0 | N/A | 0 | 0
2022-02-17 06:30 | 3.1244 | 0 | N/A | 0 | 0
2022-02-17 07:00 | 3.8476 | 0 | N/A | 0 | 0
2022-02-17 07:30 | 4.7117 | 0 | N/A | 0 | 0
2022-02-17 08:00 | 5.032 | 0 | N/A | 0 | 0
2022-02-17 08:30 | 4.3845 | 0 | N/A | 0 | 0
2022-02-17 09:00 | 3.7 | 0 | N/A | 0 | 0
2022-02-17 09:30 | 2.8893 | 0 | N/A | 0 | 0
2022-02-17 10:00 | 1.726 | 0 | N/A | 0 | 0
2022-02-17 10:30 | 1.1606 | 0 | N/A | 0 | 0
2022-02-17 11:00 | 1.7094 | 0 | N/A | 0 | 0
2022-02-17 11:30 | 1.8673 | 0 | N/A | 0 | 0
2022-02-17 12:00 | 2.1582 | 0 | N/A | 0 | 0
2022-02-17 12:30 | 1.8045 | 0 | N/A | 0 | 0
2022-02-17 13:00 | 1.2499 | 0 | N/A | 0 | 0
2022-02-17 13:30 | 1.6632 | 0 | N/A | 0 | 0
2022-02-17 14:00 | 2.3556 | 0 | N/A | 0 | 0
2022-02-17 14:30 | 2.8309 | 0 | N/A | 0 | 0
2022-02-17 15:00 | 2.1449 | 0 | N/A | 0 | 0
2022-02-17 15:30 | 1.5251 | 0 | N/A | 0 | 0
2022-02-17 16:00 | 1.157 | 0 | N/A | 0 | 0
2022-02-17 16:30 | 0.27811 | 0 | N/A | 0 | 0
2022-02-17 17:00 | 0.29307 | 0 | N/A | 0 | 0
2022-02-17 17:30 | 1.0521 | 0 | N/A | 0 | 0
2022-02-17 18:00 | 2.0609 | 0 | N/A | 0 | 0
2022-02-17 18:30 | 3.0195 | 0 | N/A | 0 | 0
2022-02-17 19:00 | 3.9294 | 0 | N/A | 0 | 0
2022-02-17 19:30 | 4.2069 | 0 | N/A | 0 | 0
2022-02-17 20:00 | 4.4966 | 0 | N/A | 0 | 0
2022-02-17 20:30 | 4.6177 | 0 | N/A | 0 | 0
2022-02-17 21:00 | 4.589 | 0 | N/A | 0 | 0
2022-02-17 21:30 | 4.3475 | 0 | N/A | 0 | 0
2022-02-17 22:00 | 4.0505 | 0 | N/A | 0 | 0
2022-02-17 22:30 | 4.1648 | 0 | N/A | 0 | 0
2022-02-17 23:00 | 4.2607 | 0 | N/A | 0 | 0
2022-02-17 23:30 | 3.8418 | 0 | N/A | 0 | 0
2022-02-18 | 3.8314 | 0 | N/A | 0 | 0
2022-02-18 00:30 | 4.2584 | 0 | N/A | 0 | 0
2022-02-18 01:00 | 4.4141 | 0 | N/A | 0 | 0
2022-02-18 01:30 | 3.5728 | 0 | N/A | 0 | 0
2022-02-18 02:00 | 2.9675 | 0 | N/A | 0 | 0
2022-02-18 02:30 | 2.8637 | 0 | N/A | 0 | 0
2022-02-18 03:00 | 2.6122 | 0 | N/A | 0 | 0
2022-02-18 03:30 | 2.384 | 0 | N/A | 0 | 0
2022-02-18 04:00 | 2.2946 | 0 | N/A | 0 | 0
2022-02-18 04:30 | 2.4045 | 0 | N/A | 0 | 0
2022-02-18 05:00 | 2.4194 | 0 | N/A | 0 | 0
2022-02-18 05:30 | 2.5514 | 0 | N/A | 0 | 0
2022-02-18 06:00 | 2.7998 | 0 | N/A | 0 | 0
2022-02-18 06:30 | 3.1918 | 0 | N/A | 0 | 0
2022-02-18 07:00 | 4.1224 | 0 | N/A | 0 | 0
2022-02-18 07:30 | 4.6492 | 0 | N/A | 0 | 0
2022-02-18 08:00 | 5.1044 | 0 | N/A | 0 | 0
2022-02-18 08:30 | 4.7607 | 0 | N/A | 0 | 0
2022-02-18 09:00 | 4.2612 | 0 | N/A | 0 | 0
2022-02-18 09:30 | 3.8357 | 0 | N/A | 0 | 0
2022-02-18 10:00 | 2.5915 | 0 | N/A | 0 | 0
2022-02-18 10:30 | 2.1776 | 0 | N/A | 0 | 0
2022-02-18 11:00 | 2.6767 | 0 | N/A | 0 | 0
2022-02-18 11:30 | 2.4994 | 0 | N/A | 0 | 0
2022-02-18 12:00 | 2.6655 | 0 | N/A | 0 | 0
2022-02-18 12:30 | 1.8369 | 0 | N/A | 0 | 0
2022-02-18 13:00 | 2.457 | 0 | N/A | 0 | 0
2022-02-18 13:30 | 1.7024 | 0 | N/A | 0 | 0
2022-02-18 14:00 | 1.8204 | 0 | N/A | 0 | 0
2022-02-18 14:30 | 1.1785 | 0 | N/A | 0 | 0
2022-02-18 15:00 | 0.90338 | 0 | N/A | 0 | 0
2022-02-18 15:30 | 0.48847 | 0 | N/A | 0 | 0
2022-02-18 16:00 | 0.5155 | 0 | N/A | 0 | 0
2022-02-18 16:30 | 0.98813 | 0 | N/A | 0 | 0
2022-02-18 17:00 | 1.6781 | 0 | N/A | 0 | 0
2022-02-18 17:30 | 1.935 | 0 | N/A | 0 | 0
2022-02-18 18:00 | 2.1032 | 0 | N/A | 0 | 0
2022-02-18 18:30 | 3.2419 | 0 | N/A | 0 | 0
2022-02-18 19:00 | 3.3763 | 0 | N/A | 0 | 0
2022-02-18 19:30 | 3.7225 | 0 | N/A | 0 | 0
2022-02-18 20:00 | 4.0657 | 0 | N/A | 0 | 0
2022-02-18 20:30 | 4.2389 | 0 | N/A | 0 | 0
2022-02-18 21:00 | 4.3533 | 0 | N/A | 0 | 0
2022-02-18 21:30 | 4.2411 | 0 | N/A | 0 | 0
2022-02-18 22:00 | 4.0084 | 0 | N/A | 0 | 0
2022-02-18 22:30 | 4.3038 | 0 | N/A | 0 | 0
2022-02-18 23:00 | 4.3968 | 0 | N/A | 0 | 0
2022-02-18 23:30 | 3.9801 | 0 | N/A | 0 | 0
2022-02-19 | 3.9754 | 0 | N/A | 0 | 0
2022-02-19 00:30 | 4.4106 | 0 | N/A | 0 | 0
2022-02-19 01:00 | 4.662 | 0 | N/A | 0 | 0
2022-02-19 01:30 | 3.7477 | 0 | N/A | 0 | 0
2022-02-19 02:00 | 3.1352 | 0 | N/A | 0 | 0
2022-02-19 02:30 | 3.1324 | 0 | N/A | 0 | 0
2022-02-19 03:00 | 2.7728 | 0 | N/A | 0 | 0
2022-02-19 03:30 | 2.506 | 0 | N/A | 0 | 0
2022-02-19 04:00 | 2.3707 | 0 | N/A | 0 | 0
2022-02-19 04:30 | 2.35 | 0 | N/A | 0 | 0
2022-02-19 05:00 | 2.3839 | 0 | N/A | 0 | 0
2022-02-19 05:30 | 2.4492 | 0 | N/A | 0 | 0
2022-02-19 06:00 | 2.4642 | 0 | N/A | 0 | 0
2022-02-19 06:30 | 2.7039 | 0 | N/A | 0 | 0
2022-02-19 07:00 | 2.8959 | 0 | N/A | 0 | 0
2022-02-19 07:30 | 3.2175 | 0 | N/A | 0 | 0
2022-02-19 08:00 | 3.1887 | 0 | N/A | 0 | 0
2022-02-19 08:30 | 2.8773 | 0 | N/A | 0 | 0
2022-02-19 09:00 | 2.4871 | 0 | N/A | 0 | 0
2022-02-19 09:30 | 1.8057 | 0 | N/A | 0 | 0
2022-02-19 10:00 | 1.0867 | 0 | N/A | 0 | 0
2022-02-19 10:30 | 0.65667 | 0 | N/A | 0 | 0
2022-02-19 11:00 | -0.67943 | 0 | N/A | 0 | 0
2022-02-19 11:30 | -0.99593 | 0 | N/A | 0 | 0
2022-02-19 12:00 | -1.322 | 0 | N/A | 0 | 0
2022-02-19 12:30 | -1.4483 | 0 | N/A | 0 | 0
2022-02-19 13:00 | -1.6444 | 0 | N/A | 0 | 0
2022-02-19 13:30 | -1.7874 | 0 | N/A | 0 | 0
2022-02-19 14:00 | -1.8646 | 0 | N/A | 0 | 0
2022-02-19 14:30 | -1.8007 | 0 | N/A | 0 | 0
2022-02-19 15:00 | -1.7054 | 0 | N/A | 0 | 0
2022-02-19 15:30 | -1.5203 | 0 | N/A | 0 | 0
2022-02-19 16:00 | -1.1758 | 0 | N/A | 0 | 0
2022-02-19 16:30 | -0.64544 | 0 | N/A | 0 | 0
2022-02-19 17:00 | 0.43549 | 0 | N/A | 0 | 0
2022-02-19 17:30 | 1.1218 | 0 | N/A | 0 | 0
2022-02-19 18:00 | 2.0973 | 0 | N/A | 0 | 0
2022-02-19 18:30 | 3.0715 | 0 | N/A | 0 | 0
2022-02-19 19:00 | 3.7393 | 0 | N/A | 0 | 0
2022-02-19 19:30 | 4.1226 | 0 | N/A | 0 | 0
2022-02-19 20:00 | 4.3111 | 0 | N/A | 0 | 0
2022-02-19 20:30 | 4.2283 | 0 | N/A | 0 | 0
2022-02-19 21:00 | 4.0858 | 0 | N/A | 0 | 0
2022-02-19 21:30 | 3.9236 | 0 | N/A | 0 | 0
2022-02-19 22:00 | 3.6841 | 0 | N/A | 0 | 0
2022-02-19 22:30 | 4.0975 | 0 | N/A | 0 | 0
2022-02-19 23:00 | 4.2002 | 0 | N/A | 0 | 0
2022-02-19 23:30 | 3.8539 | 0 | N/A | 0 | 0
2022-02-20 | 3.8701 | 0 | N/A | 0 | 0
2022-02-20 00:30 | 4.2754 | 0 | N/A | 0 | 0
2022-02-20 01:00 | 4.4716 | 0 | N/A | 0 | 0
2022-02-20 01:30 | 3.6662 | 0 | N/A | 0 | 0
2022-02-20 02:00 | 3.0649 | 0 | N/A | 0 | 0
2022-02-20 02:30 | 2.9683 | 0 | N/A | 0 | 0
2022-02-20 03:00 | 2.7111 | 0 | N/A | 0 | 0
2022-02-20 03:30 | 2.3987 | 0 | N/A | 0 | 0
2022-02-20 04:00 | 2.2573 | 0 | N/A | 0 | 0
2022-02-20 04:30 | 2.2128 | 0 | N/A | 0 | 0
2022-02-20 05:00 | 2.1907 | 0 | N/A | 0 | 0
2022-02-20 05:30 | 2.2538 | 0 | N/A | 0 | 0
2022-02-20 06:00 | 2.1851 | 0 | N/A | 0 | 0
2022-02-20 06:30 | 2.3363 | 0 | N/A | 0 | 0
2022-02-20 07:00 | 2.4448 | 0 | N/A | 0 | 0
2022-02-20 07:30 | 2.6892 | 0 | N/A | 0 | 0
2022-02-20 08:00 | 2.608 | 0 | N/A | 0 | 0
2022-02-20 08:30 | 2.4568 | 0 | N/A | 0 | 0
2022-02-20 09:00 | 2.1836 | 0 | N/A | 0 | 0
2022-02-20 09:30 | 1.6519 | 0 | N/A | 0 | 0
2022-02-20 10:00 | 1.3248 | 0 | N/A | 0 | 0
2022-02-20 10:30 | 0.93203 | 0 | N/A | 0 | 0
2022-02-20 11:00 | -0.65355 | 0 | N/A | 0 | 0
2022-02-20 11:30 | -0.91263 | 0 | N/A | 0 | 0
2022-02-20 12:00 | -0.58383 | 0 | N/A | 0 | 0
2022-02-20 12:30 | 0.57529 | 0 | N/A | 0 | 0
2022-02-20 13:00 | 0.55909 | 0 | N/A | 0 | 0
2022-02-20 13:30 | -0.84964 | 0 | N/A | 0 | 0
2022-02-20 14:00 | -1.1646 | 0 | N/A | 0 | 0
2022-02-20 14:30 | -1.3416 | 0 | N/A | 0 | 0
2022-02-20 15:00 | -1.1472 | 0 | N/A | 0 | 0
2022-02-20 15:30 | 0.51294 | 0 | N/A | 0 | 0
2022-02-20 16:00 | 0.56508 | 0 | N/A | 0 | 0
2022-02-20 16:30 | 0.53654 | 0 | N/A | 0 | 0
2022-02-20 17:00 | 1.7772 | 0 | N/A | 0 | 0
2022-02-20 17:30 | 2.5797 | 0 | N/A | 0 | 0
2022-02-20 18:00 | 2.9241 | 0 | N/A | 0 | 0
2022-02-20 18:30 | 3.4282 | 0 | N/A | 0 | 0
2022-02-20 19:00 | 3.6334 | 0 | N/A | 0 | 0
2022-02-20 19:30 | 3.7454 | 0 | N/A | 0 | 0
2022-02-20 20:00 | 4.1397 | 0 | N/A | 0 | 0
2022-02-20 20:30 | 4.2976 | 0 | N/A | 0 | 0
2022-02-20 21:00 | 4.2434 | 0 | N/A | 0 | 0
2022-02-20 21:30 | 4.0122 | 0 | N/A | 0 | 0
2022-02-20 22:00 | 3.6674 | 0 | N/A | 0 | 0
2022-02-20 22:30 | 4.0481 | 0 | N/A | 0 | 0
2022-02-20 23:00 | 4.1222 | 0 | N/A | 0 | 0
2022-02-20 23:30 | 3.9598 | 0 | N/A | 0 | 0
2022-02-21 | 3.9954 | 0 | N/A | 0 | 0
2022-02-21 00:30 | 4.3429 | 0 | N/A | 0 | 0
2022-02-21 01:00 | 4.6355 | 0 | N/A | 0 | 0
2022-02-21 01:30 | 3.8439 | 0 | N/A | 0 | 0
2022-02-21 02:00 | 3.2098 | 0 | N/A | 0 | 0
2022-02-21 02:30 | 3.156 | 0 | N/A | 0 | 0
2022-02-21 03:00 | 2.8653 | 0 | N/A | 0 | 0
2022-02-21 03:30 | 2.5617 | 0 | N/A | 0 | 0
2022-02-21 04:00 | 2.4124 | 0 | N/A | 0 | 0
2022-02-21 04:30 | 2.4734 | 0 | N/A | 0 | 0
2022-02-21 05:00 | 2.4642 | 0 | N/A | 0 | 0
2022-02-21 05:30 | 2.6084 | 0 | N/A | 0 | 0
2022-02-21 06:00 | 2.8477 | 0 | N/A | 0 | 0
2022-02-21 06:30 | 3.3036 | 0 | N/A | 0 | 0
2022-02-21 07:00 | 4.1778 | 0 | N/A | 0 | 0
2022-02-21 07:30 | 4.9962 | 0 | N/A | 0 | 0
2022-02-21 08:00 | 5.1378 | 0 | N/A | 0 | 0
2022-02-21 08:30 | 4.2164 | 0 | N/A | 0 | 0
2022-02-21 09:00 | 3.5497 | 0 | N/A | 0 | 0
2022-02-21 09:30 | 2.6851 | 0 | N/A | 0 | 0
2022-02-21 10:00 | 1.6339 | 0 | N/A | 0 | 0
2022-02-21 10:30 | 0.82188 | 0 | N/A | 0 | 0
2022-02-21 11:00 | 1.1403 | 0 | N/A | 0 | 0
2022-02-21 11:30 | 1.2182 | 0 | N/A | 0 | 0
2022-02-21 12:00 | 0.8477 | 0 | N/A | 0 | 0
2022-02-21 12:30 | 1.262 | 0 | N/A | 0 | 0
2022-02-21 13:00 | 0.5398 | 0 | N/A | 0 | 0
2022-02-21 13:30 | 0.25944 | 0 | N/A | 0 | 0
2022-02-21 14:00 | -0.24938 | 0 | N/A | 0 | 0
2022-02-21 14:30 | -0.52244 | 0 | N/A | 0 | 0
2022-02-21 15:00 | -0.33287 | 0 | N/A | 0 | 0
2022-02-21 15:30 | -0.82641 | 0 | N/A | 0 | 0
2022-02-21 16:00 | 0.39115 | 0 | N/A | 0 | 0
2022-02-21 16:30 | -0.46896 | 0 | N/A | 0 | 0
2022-02-21 17:00 | 0.48116 | 0 | N/A | 0 | 0
2022-02-21 17:30 | 1.097 | 0 | N/A | 0 | 0
2022-02-21 18:00 | 2.2025 | 0 | N/A | 0 | 0
2022-02-21 18:30 | 3.3527 | 0 | N/A | 0 | 0
2022-02-21 19:00 | 3.7811 | 0 | N/A | 0 | 0
2022-02-21 19:30 | 4.26 | 0 | N/A | 0 | 0
2022-02-21 20:00 | 4.4538 | 0 | N/A | 0 | 0
2022-02-21 20:30 | 4.5538 | 0 | N/A | 0 | 0
2022-02-21 21:00 | 4.527 | 0 | N/A | 0 | 0
2022-02-21 21:30 | 4.416 | 0 | N/A | 0 | 0
2022-02-21 22:00 | 4.1195 | 0 | N/A | 0 | 0
2022-02-21 22:30 | 4.2137 | 0 | N/A | 0 | 0
2022-02-21 23:00 | 4.1992 | 0 | N/A | 0 | 0
2022-02-21 23:30 | 3.8456 | 0 | N/A | 0 | 0
2022-02-22 | 3.8482 | 0 | N/A | 0 | 0
2022-02-23 00:30 | 4.2107 | 0 | N/A | 0 | 0
2022-02-23 01:00 | 4.4276 | 0 | N/A | 0 | 0
2022-02-23 01:30 | 3.528 | 0 | N/A | 0 | 0
2022-02-23 02:00 | 2.9334 | 0 | N/A | 0 | 0
2022-02-23 02:30 | 2.8328 | 0 | N/A | 0 | 0
2022-02-23 03:00 | 2.69 | 0 | N/A | 0 | 0
2022-02-23 03:30 | 2.4299 | 0 | N/A | 0 | 0
2022-02-23 04:00 | 2.3206 | 0 | N/A | 0 | 0
2022-02-23 04:30 | 2.3856 | 0 | N/A | 0 | 0
2022-02-23 05:00 | 2.4195 | 0 | N/A | 0 | 0
2022-02-23 05:30 | 2.5974 | 0 | N/A | 0 | 0
2022-02-23 06:00 | 2.8354 | 0 | N/A | 0 | 0
2022-02-23 06:30 | 3.3407 | 0 | N/A | 0 | 0
2022-02-23 07:00 | 3.7474 | 0 | N/A | 0 | 0
2022-02-23 07:30 | 4.4056 | 0 | N/A | 0 | 0
2022-02-23 08:00 | 4.4254 | 0 | N/A | 0 | 0
2022-02-23 08:30 | 3.6821 | 0 | N/A | 0 | 0
2022-02-23 09:00 | 3.0212 | 0 | N/A | 0 | 0
2022-02-23 09:30 | 2.369 | 0 | N/A | 0 | 0
2022-02-23 10:00 | 1.5539 | 0 | N/A | 0 | 0
2022-02-23 10:30 | 0.96506 | 0 | N/A | 0 | 0
2022-02-23 11:00 | 0.42492 | 0 | N/A | 0 | 0
2022-02-23 11:30 | 0.0033333 | 0 | N/A | 0 | 0
2022-02-23 12:00 | -0.13667 | 0 | N/A | 0 | 0
2022-02-23 12:30 | -0.1867 | 0 | N/A | 0 | 0
2022-02-23 13:00 | 0.15839 | 0 | N/A | 0 | 0
2022-02-23 13:30 | 1.2634 | 0 | N/A | 0 | 0
2022-02-23 14:00 | 1.4267 | 0 | N/A | 0 | 0
2022-02-23 14:30 | 1.2034 | 0 | N/A | 0 | 0
2022-02-23 15:00 | 1.9303 | 0 | N/A | 0 | 0
2022-02-23 15:30 | 3.0503 | 0 | N/A | 0 | 0
2022-02-23 16:00 | 3.9306 | 0 | N/A | 0 | 0
2022-02-23 16:30 | 4.8776 | 0 | N/A | 0 | 0
2022-02-23 17:00 | 5.5071 | 0 | N/A | 0 | 0
2022-02-23 17:30 | 5.2635 | 0 | N/A | 0 | 0
2022-02-23 18:00 | 6.0641 | 0 | N/A | 0 | 0
2022-02-23 18:30 | 5.8809 | 0 | N/A | 0 | 0
2022-02-23 19:00 | 5.6408 | 0 | N/A | 0 | 0
2022-02-23 19:30 | 5.4717 | 0 | N/A | 0 | 0
2022-02-23 20:00 | 5.2813 | 0 | N/A | 0 | 0
2022-02-23 20:30 | 5.2463 | 0 | N/A | 0 | 0
2022-02-23 21:00 | 5.0389 | 0 | N/A | 0 | 0
2022-02-23 21:30 | 4.7453 | 0 | N/A | 0 | 0
2022-02-23 22:00 | 4.3393 | 0 | N/A | 0 | 0
2022-02-23 22:30 | 4.3827 | 0 | N/A | 0 | 0
2022-02-23 23:00 | 4.2618 | 0 | N/A | 0 | 0
2022-02-23 23:30 | 3.7855 | 0 | N/A | 0 | 0
2022-02-24 | 3.7746 | 0 | N/A | 0 | 0
2022-02-24 00:30 | 4.2413 | 0 | N/A | 0 | 0
2022-02-24 01:00 | 4.4393 | 0 | N/A | 0 | 0
2022-02-24 01:30 | 3.5766 | 0 | N/A | 0 | 0
2022-02-24 02:00 | 2.9167 | 0 | N/A | 0 | 0
2022-02-24 02:30 | 2.8766 | 0 | N/A | 0 | 0
2022-02-24 03:00 | 2.5874 | 0 | N/A | 0 | 0
2022-02-24 03:30 | 2.3869 | 0 | N/A | 0 | 0
2022-02-24 04:00 | 2.3361 | 0 | N/A | 0 | 0
2022-02-24 04:30 | 2.3766 | 0 | N/A | 0 | 0
2022-02-24 05:00 | 2.4267 | 0 | N/A | 0 | 0
2022-02-24 05:30 | 2.5045 | 0 | N/A | 0 | 0
2022-02-24 06:00 | 2.7793 | 0 | N/A | 0 | 0
2022-02-24 06:30 | 3.1899 | 0 | N/A | 0 | 0
2022-02-24 07:00 | 3.6491 | 0 | N/A | 0 | 0
2022-02-24 07:30 | 4.6825 | 0 | N/A | 0 | 0
2022-02-24 08:00 | 4.7485 | 0 | N/A | 0 | 0
2022-02-24 08:30 | 4.3049 | 0 | N/A | 0 | 0
2022-02-24 09:00 | 3.8961 | 0 | N/A | 0 | 0
2022-02-24 09:30 | 2.7487 | 0 | N/A | 0 | 0
2022-02-24 10:00 | 1.4468 | 0 | N/A | 0 | 0
2022-02-24 10:30 | 1.0263 | 0 | N/A | 0 | 0
2022-02-24 11:00 | 0.82677 | 0 | N/A | 0 | 0
2022-02-24 11:30 | 0.51735 | 0 | N/A | 0 | 0
2022-02-24 12:00 | 0.32441 | 0 | N/A | 0 | 0
2022-02-24 12:30 | 0.2709 | 0 | N/A | 0 | 0
2022-02-24 13:00 | 0.20923 | 0 | N/A | 0 | 0
2022-02-24 13:30 | 0.27378 | 0 | N/A | 0 | 0
2022-02-24 14:00 | 0.33283 | 0 | N/A | 0 | 0
2022-02-24 14:30 | 0.41027 | 0 | N/A | 0 | 0
2022-02-24 15:00 | 0.73021 | 0 | N/A | 0 | 0
2022-02-24 15:30 | 0.55909 | 0 | N/A | 0 | 0
2022-02-24 16:00 | 0.84683 | 0 | N/A | 0 | 0
2022-02-24 16:30 | 1.65 | 0 | N/A | 0 | 0
2022-02-24 17:00 | 2.3267 | 0 | N/A | 0 | 0
2022-02-24 17:30 | 3.2001 | 0 | N/A | 0 | 0
2022-02-24 18:00 | 4.2474 | 0 | N/A | 0 | 0
2022-02-24 18:30 | 4.8813 | 0 | N/A | 0 | 0
2022-02-24 19:00 | 5.3936 | 0 | N/A | 0 | 0
2022-02-24 19:30 | 5.6368 | 0 | N/A | 0 | 0
2022-02-24 20:00 | 5.5078 | 0 | N/A | 0 | 0
2022-02-24 20:30 | 5.2366 | 0 | N/A | 0 | 0
2022-02-24 21:00 | 5.1042 | 0 | N/A | 0 | 0
2022-02-24 21:30 | 4.6275 | 0 | N/A | 0 | 0
2022-02-24 22:00 | 4.2476 | 0 | N/A | 0 | 0
2022-02-24 22:30 | 4.347 | 0 | N/A | 0 | 0
2022-02-24 23:00 | 4.2538 | 0 | N/A | 0 | 0
2022-02-24 23:30 | 3.8361 | 0 | N/A | 0 | 0
2022-02-25 | 3.7836 | 0 | N/A | 0 | 0
2022-02-25 00:30 | 4.2722 | 0 | N/A | 0 | 0
2022-02-25 01:00 | 4.3453 | 0 | N/A | 0 | 0
2022-02-25 01:30 | 3.4617 | 0 | N/A | 0 | 0
2022-02-25 02:00 | 2.8801 | 0 | N/A | 0 | 0
2022-02-25 02:30 | 2.884 | 0 | N/A | 0 | 0
2022-02-25 03:00 | 2.5614 | 0 | N/A | 0 | 0
2022-02-25 03:30 | 2.3589 | 0 | N/A | 0 | 0
2022-02-25 04:00 | 2.241 | 0 | N/A | 0 | 0
2022-02-25 04:30 | 2.3598 | 0 | N/A | 0 | 0
2022-02-25 05:00 | 2.412 | 0 | N/A | 0 | 0
2022-02-25 05:30 | 2.5966 | 0 | N/A | 0 | 0
2022-02-25 06:00 | 2.7774 | 0 | N/A | 0 | 0
2022-02-25 06:30 | 3.2931 | 0 | N/A | 0 | 0
2022-02-25 07:00 | 3.9067 | 0 | N/A | 0 | 0
2022-02-25 07:30 | 4.8735 | 0 | N/A | 0 | 0
2022-02-25 08:00 | 5.1125 | 0 | N/A | 0 | 0
2022-02-25 08:30 | 4.8293 | 0 | N/A | 0 | 0
2022-02-25 09:00 | 4.6596 | 0 | N/A | 0 | 0
2022-02-25 09:30 | 4.321 | 0 | N/A | 0 | 0
2022-02-25 10:00 | 3.5489 | 0 | N/A | 0 | 0
2022-02-25 10:30 | 2.8695 | 0 | N/A | 0 | 0
2022-02-25 11:00 | 1.7974 | 0 | N/A | 0 | 0
2022-02-25 11:30 | 0.98955 | 0 | N/A | 0 | 0
2022-02-25 12:00 | 0.49644 | 0 | N/A | 0 | 0
2022-02-25 12:30 | -0.20069 | 0 | N/A | 0 | 0
2022-02-25 13:00 | -0.42824 | 0 | N/A | 0 | 0
2022-02-25 13:30 | -0.93343 | 0 | N/A | 0 | 0
2022-02-25 14:00 | -0.90002 | 0 | N/A | 0 | 0
2022-02-25 14:30 | -1.3586 | 0 | N/A | 0 | 0
2022-02-25 15:00 | -1.5107 | 0 | N/A | 0 | 0
2022-02-25 15:30 | -1.3481 | 0 | N/A | 0 | 0
2022-02-25 16:00 | -1.1283 | 0 | N/A | 0 | 0
2022-02-25 16:30 | -0.68471 | 0 | N/A | 0 | 0
2022-02-25 17:00 | -0.30668 | 0 | N/A | 0 | 0
2022-02-25 17:30 | 1.1272 | 0 | N/A | 0 | 0
2022-02-25 18:00 | 2.0689 | 0 | N/A | 0 | 0
2022-02-25 18:30 | 2.5649 | 0 | N/A | 0 | 0
2022-02-25 19:00 | 3.4806 | 0 | N/A | 0 | 0
2022-02-25 19:30 | 3.87 | 0 | N/A | 0 | 0
2022-02-25 20:00 | 4.2107 | 0 | N/A | 0 | 0
2022-02-25 20:30 | 4.2486 | 0 | N/A | 0 | 0
2022-02-25 21:00 | 4.2962 | 0 | N/A | 0 | 0
2022-02-25 21:30 | 4.1243 | 0 | N/A | 0 | 0
2022-02-25 22:00 | 3.822 | 0 | N/A | 0 | 0
2022-02-25 22:30 | 4.1065 | 0 | N/A | 0 | 0
2022-02-25 23:00 | 4.1813 | 0 | N/A | 0 | 0
2022-02-25 23:30 | 3.8475 | 0 | N/A | 0 | 0
2022-02-26 | 3.9406 | 0 | N/A | 0 | 0
2022-02-26 00:30 | 4.2658 | 0 | N/A | 0 | 0
2022-02-26 01:00 | 4.361 | 0 | N/A | 0 | 0
2022-02-26 01:30 | 3.3947 | 0 | N/A | 0 | 0
2022-02-26 02:00 | 2.8032 | 0 | N/A | 0 | 0
2022-02-26 02:30 | 2.7912 | 0 | N/A | 0 | 0
2022-02-26 03:00 | 2.5355 | 0 | N/A | 0 | 0
2022-02-26 03:30 | 2.2764 | 0 | N/A | 0 | 0
2022-02-26 04:00 | 2.2232 | 0 | N/A | 0 | 0
2022-02-26 04:30 | 2.21 | 0 | N/A | 0 | 0
2022-02-26 05:00 | 2.2495 | 0 | N/A | 0 | 0
2022-02-26 05:30 | 2.254 | 0 | N/A | 0 | 0
2022-02-26 06:00 | 2.3703 | 0 | N/A | 0 | 0
2022-02-26 06:30 | 2.6262 | 0 | N/A | 0 | 0
2022-02-26 07:00 | 2.8597 | 0 | N/A | 0 | 0
2022-02-26 07:30 | 3.0254 | 0 | N/A | 0 | 0
2022-02-26 08:00 | 3.2761 | 0 | N/A | 0 | 0
2022-02-26 08:30 | 3.1721 | 0 | N/A | 0 | 0
2022-02-26 09:00 | 2.9757 | 0 | N/A | 0 | 0
2022-02-26 09:30 | 2.7291 | 0 | N/A | 0 | 0
2022-02-26 10:00 | 2.269 | 0 | N/A | 0 | 0
2022-02-26 10:30 | 1.692 | 0 | N/A | 0 | 0
2022-02-26 11:00 | 1.1551 | 0 | N/A | 0 | 0
2022-02-26 11:30 | 0.57655 | 0 | N/A | 0 | 0
2022-02-26 12:00 | -0.70174 | 0 | N/A | 0 | 0
2022-02-26 12:30 | -1.0549 | 0 | N/A | 0 | 0
2022-02-26 13:00 | -1.1314 | 0 | N/A | 0 | 0
2022-02-26 13:30 | -1.1481 | 0 | N/A | 0 | 0
2022-02-26 14:00 | -1.1351 | 0 | N/A | 0 | 0
2022-02-26 14:30 | -1.1212 | 0 | N/A | 0 | 0
2022-02-26 15:00 | -0.79269 | 0 | N/A | 0 | 0
2022-02-26 15:30 | -0.51 | 0 | N/A | 0 | 0
2022-02-26 16:00 | -0.3161 | 0 | N/A | 0 | 0
2022-02-26 16:30 | 0.42527 | 0 | N/A | 0 | 0
2022-02-26 17:00 | 1.1021 | 0 | N/A | 0 | 0
2022-02-26 17:30 | 1.951 | 0 | N/A | 0 | 0
2022-02-26 18:00 | 2.9587 | 0 | N/A | 0 | 0
2022-02-26 18:30 | 3.7176 | 0 | N/A | 0 | 0
2022-02-26 19:00 | 4.3053 | 0 | N/A | 0 | 0
2022-02-26 19:30 | 4.7019 | 0 | N/A | 0 | 0
2022-02-26 20:00 | 4.8079 | 0 | N/A | 0 | 0
2022-02-26 20:30 | 4.612 | 0 | N/A | 0 | 0
2022-02-26 21:00 | 4.4481 | 0 | N/A | 0 | 0
2022-02-26 21:30 | 4.1335 | 0 | N/A | 0 | 0
2022-02-26 22:00 | 3.8576 | 0 | N/A | 0 | 0
2022-02-26 22:30 | 4.1683 | 0 | N/A | 0 | 0
2022-02-26 23:00 | 4.158 | 0 | N/A | 0 | 0
2022-02-26 23:30 | 3.9873 | 0 | N/A | 0 | 0
2022-02-27 | 4.1285 | 0 | N/A | 0 | 0
2022-02-27 00:30 | 4.4656 | 0 | N/A | 0 | 0
2022-02-27 01:00 | 4.5974 | 0 | N/A | 0 | 0
2022-02-27 01:30 | 3.7706 | 0 | N/A | 0 | 0
2022-02-27 02:00 | 3.1202 | 0 | N/A | 0 | 0
2022-02-27 02:30 | 3.0906 | 0 | N/A | 0 | 0
2022-02-27 03:00 | 2.7546 | 0 | N/A | 0 | 0
2022-02-27 03:30 | 2.4818 | 0 | N/A | 0 | 0
2022-02-27 04:00 | 2.3452 | 0 | N/A | 0 | 0
2022-02-27 04:30 | 2.3196 | 0 | N/A | 0 | 0
2022-02-27 05:00 | 2.327 | 0 | N/A | 0 | 0
2022-02-27 05:30 | 2.3121 | 0 | N/A | 0 | 0
2022-02-27 06:00 | 2.3479 | 0 | N/A | 0 | 0
2022-02-27 06:30 | 2.4669 | 0 | N/A | 0 | 0
2022-02-27 07:00 | 2.5786 | 0 | N/A | 0 | 0
2022-02-27 07:30 | 2.7618 | 0 | N/A | 0 | 0
2022-02-27 08:00 | 2.7447 | 0 | N/A | 0 | 0
2022-02-27 08:30 | 2.5601 | 0 | N/A | 0 | 0
2022-02-27 09:00 | 2.2497 | 0 | N/A | 0 | 0
2022-02-27 09:30 | 1.6399 | 0 | N/A | 0 | 0
2022-02-27 10:00 | 1.4286 | 0 | N/A | 0 | 0
2022-02-27 10:30 | 1.2134 | 0 | N/A | 0 | 0
2022-02-27 11:00 | 1.7128 | 0 | N/A | 0 | 0
2022-02-27 11:30 | 1.6191 | 0 | N/A | 0 | 0
2022-02-27 12:00 | -0.54406 | 0 | N/A | 0 | 0
2022-02-27 12:30 | -0.77964 | 0 | N/A | 0 | 0
2022-02-27 13:00 | -0.44102 | 0 | N/A | 0 | 0
2022-02-27 13:30 | 0.45305 | 0 | N/A | 0 | 0
2022-02-27 14:00 | 0.54676 | 0 | N/A | 0 | 0
2022-02-27 14:30 | -0.29562 | 0 | N/A | 0 | 0
2022-02-27 15:00 | 0.87821 | 0 | N/A | 0 | 0
2022-02-27 15:30 | 2.8294 | 0 | N/A | 0 | 0
2022-02-27 16:00 | 2.8635 | 0 | N/A | 0 | 0
2022-02-27 16:30 | 3.253 | 0 | N/A | 0 | 0
2022-02-27 17:00 | 3.2589 | 0 | N/A | 0 | 0
2022-02-27 17:30 | 3.5731 | 0 | N/A | 0 | 0
2022-02-27 18:00 | 4.242 | 0 | N/A | 0 | 0
2022-02-27 18:30 | 4.727 | 0 | N/A | 0 | 0
2022-02-27 19:00 | 5.1045 | 0 | N/A | 0 | 0
2022-02-27 19:30 | 5.0751 | 0 | N/A | 0 | 0
2022-02-27 20:00 | 4.8895 | 0 | N/A | 0 | 0
2022-02-27 20:30 | 4.6142 | 0 | N/A | 0 | 0
2022-02-27 21:00 | 4.4393 | 0 | N/A | 0 | 0
2022-02-27 21:30 | 4.074 | 0 | N/A | 0 | 0
2022-02-27 22:00 | 3.7736 | 0 | N/A | 0 | 0
2022-02-27 22:30 | 4.0617 | 0 | N/A | 0 | 0
2022-02-27 23:00 | 4.1257 | 0 | N/A | 0 | 0
2022-02-27 23:30 | 3.7885 | 0 | N/A | 0 | 0
2022-02-28 | 4.0263 | 0 | N/A | 0 | 0
2022-02-28 00:30 | 4.2793 | 0 | N/A | 0 | 0
2022-02-28 01:00 | 4.5011 | 0 | N/A | 0 | 0
2022-02-28 01:30 | 3.7116 | 0 | N/A | 0 | 0
2022-02-28 02:00 | 3.1011 | 0 | N/A | 0 | 0
2022-02-28 02:30 | 3.0168 | 0 | N/A | 0 | 0
2022-02-28 03:00 | 2.7923 | 0 | N/A | 0 | 0
2022-02-28 03:30 | 2.4708 | 0 | N/A | 0 | 0
2022-02-28 04:00 | 2.3172 | 0 | N/A | 0 | 0
2022-02-28 04:30 | 2.3896 | 0 | N/A | 0 | 0
2022-02-28 05:00 | 2.4017 | 0 | N/A | 0 | 0
2022-02-28 05:30 | 2.4809 | 0 | N/A | 0 | 0
2022-02-28 06:00 | 2.7395 | 0 | N/A | 0 | 0
2022-02-28 06:30 | 3.2931 | 0 | N/A | 0 | 0
2022-02-28 07:00 | 3.7707 | 0 | N/A | 0 | 0
2022-02-28 07:30 | 4.7552 | 0 | N/A | 0 | 0
2022-02-28 08:00 | 5.1364 | 0 | N/A | 0 | 0
2022-02-28 08:30 | 4.6539 | 0 | N/A | 0 | 0
2022-02-28 09:00 | 4.283 | 0 | N/A | 0 | 0
2022-02-28 09:30 | 3.6976 | 0 | N/A | 0 | 0
2022-02-28 10:00 | 2.7664 | 0 | N/A | 0 | 0
2022-02-28 10:30 | 1.9521 | 0 | N/A | 0 | 0
2022-02-28 11:00 | 1.6775 | 0 | N/A | 0 | 0
2022-02-28 11:30 | 1.0725 | 0 | N/A | 0 | 0
2022-02-28 12:00 | 0.12333 | 0 | N/A | 0 | 0
2022-02-28 12:30 | 0.0055556 | 0 | N/A | 0 | 0
2022-02-28 13:00 | -0.076956 | 0 | N/A | 0 | 0
2022-02-28 13:30 | -0.28783 | 0 | N/A | 0 | 0
2022-02-28 14:00 | -0.28831 | 0 | N/A | 0 | 0
2022-02-28 14:30 | 0.0834 | 0 | N/A | 0 | 0
2022-02-28 15:00 | 0.1674 | 0 | N/A | 0 | 0
2022-02-28 15:30 | 0.31531 | 0 | N/A | 0 | 0
2022-02-28 16:00 | 0.68667 | 0 | N/A | 0 | 0
2022-02-28 16:30 | 0.8103 | 0 | N/A | 0 | 0
2022-02-28 17:00 | 1.5097 | 0 | N/A | 0 | 0
2022-02-28 17:30 | 2.568 | 0 | N/A | 0 | 0
2022-02-28 18:00 | 4.085 | 0 | N/A | 0 | 0
2022-02-28 18:30 | 5.0707 | 0 | N/A | 0 | 0
2022-02-28 19:00 | 5.2683 | 0 | N/A | 0 | 0
2022-02-28 19:30 | 5.236 | 0 | N/A | 0 | 0
2022-02-28 20:00 | 5.1189 | 0 | N/A | 0 | 0
2022-02-28 20:30 | 5.0012 | 0 | N/A | 0 | 0
2022-02-28 21:00 | 4.7977 | 0 | N/A | 0 | 0
2022-02-28 21:30 | 4.3753 | 0 | N/A | 0 | 0
2022-02-28 22:00 | 4.0857 | 0 | N/A | 0 | 0
2022-02-28 22:30 | 4.2034 | 0 | N/A | 0 | 0
2022-02-28 23:00 | 4.2015 | 0 | N/A | 0 | 0
2022-02-28 23:30 | 3.7141 | 0 | N/A | 0 | 0
2022-03-01 | 3.7821 | 0 | N/A | 0 | 0
2022-03-01 00:30 | 4.2224 | 0 | N/A | 0 | 0
2022-03-01 01:00 | 4.2505 | 0 | N/A | 0 | 0
2022-03-01 01:30 | 3.4565 | 0 | N/A | 0 | 0
2022-03-01 02:00 | 2.8356 | 0 | N/A | 0 | 0
2022-03-01 02:30 | 2.8445 | 0 | N/A | 0 | 0
2022-03-01 03:00 | 2.5106 | 0 | N/A | 0 | 0
2022-03-01 03:30 | 2.3438 | 0 | N/A | 0 | 0
2022-03-01 04:00 | 2.2782 | 0 | N/A | 0 | 0
2022-03-01 04:30 | 2.4074 | 0 | N/A | 0 | 0
2022-03-01 05:00 | 2.4651 | 0 | N/A | 0 | 0
2022-03-01 05:30 | 2.6196 | 0 | N/A | 0 | 0
2022-03-01 06:00 | 2.8545 | 0 | N/A | 0 | 0
2022-03-01 06:30 | 3.3373 | 0 | N/A | 0 | 0
2022-03-01 07:00 | 3.6318 | 0 | N/A | 0 | 0
2022-03-01 07:30 | 4.5274 | 0 | N/A | 0 | 0
2022-03-01 08:00 | 5.0492 | 0 | N/A | 0 | 0
2022-03-01 08:30 | 4.8033 | 0 | N/A | 0 | 0
2022-03-01 09:00 | 4.706 | 0 | N/A | 0 | 0
2022-03-01 09:30 | 4.7427 | 0 | N/A | 0 | 0
2022-03-01 10:00 | 4.5079 | 0 | N/A | 0 | 0
2022-03-01 10:30 | 4.5555 | 0 | N/A | 0 | 0
2022-03-01 11:00 | 4.0872 | 0 | N/A | 0 | 0
2022-03-01 11:30 | 4.2321 | 0 | N/A | 0 | 0
2022-03-01 12:00 | 4.8188 | 0 | N/A | 0 | 0
2022-03-01 12:30 | 4.6294 | 0 | N/A | 0 | 0
2022-03-01 13:00 | 3.4116 | 0 | N/A | 0 | 0
2022-03-01 13:30 | 3.568 | 0 | N/A | 0 | 0
2022-03-01 14:00 | 3.796 | 0 | N/A | 0 | 0
2022-03-01 14:30 | 3.6731 | 0 | N/A | 0 | 0
2022-03-01 15:00 | 3.6523 | 0 | N/A | 0 | 0
2022-03-01 15:30 | 3.9262 | 0 | N/A | 0 | 0
2022-03-01 16:00 | 3.2084 | 0 | N/A | 0 | 0
2022-03-01 16:30 | 2.9195 | 0 | N/A | 0 | 0
2022-03-01 17:00 | 3.4788 | 0 | N/A | 0 | 0
2022-03-01 17:30 | 3.0739 | 0 | N/A | 0 | 0
2022-03-01 18:00 | 3.2406 | 0 | N/A | 0 | 0
2022-03-01 18:30 | 4.007 | 0 | N/A | 0 | 0
2022-03-01 19:00 | 4.4004 | 0 | N/A | 0 | 0
2022-03-01 19:30 | 4.5106 | 0 | N/A | 0 | 0
2022-03-01 20:00 | 4.6455 | 0 | N/A | 0 | 0
2022-03-01 20:30 | 4.7085 | 0 | N/A | 0 | 0
2022-03-01 21:00 | 4.5736 | 0 | N/A | 0 | 0
2022-03-01 21:30 | 4.2841 | 0 | N/A | 0 | 0
2022-03-01 22:00 | 3.9338 | 0 | N/A | 0 | 0
2022-03-01 22:30 | 4.164 | 0 | N/A | 0 | 0
2022-03-01 23:00 | 4.2054 | 0 | N/A | 0 | 0
2022-03-01 23:30 | 3.8614 | 0 | N/A | 0 | 0
2022-03-02 | 3.782 | 0 | N/A | 0 | 0
2022-03-02 00:30 | 4.2612 | 0 | N/A | 0 | 0
2022-03-02 01:00 | 4.4584 | 0 | N/A | 0 | 0
2022-03-02 01:30 | 3.5663 | 0 | N/A | 0 | 0
2022-03-02 02:00 | 2.8937 | 0 | N/A | 0 | 0
2022-03-02 02:30 | 2.8914 | 0 | N/A | 0 | 0
2022-03-02 03:00 | 2.614 | 0 | N/A | 0 | 0
2022-03-02 03:30 | 2.3396 | 0 | N/A | 0 | 0
2022-03-02 04:00 | 2.3018 | 0 | N/A | 0 | 0
2022-03-02 04:30 | 2.3516 | 0 | N/A | 0 | 0
2022-03-02 05:00 | 2.3954 | 0 | N/A | 0 | 0
2022-03-02 05:30 | 2.5215 | 0 | N/A | 0 | 0
2022-03-02 06:00 | 2.8547 | 0 | N/A | 0 | 0
2022-03-02 06:30 | 3.299 | 0 | N/A | 0 | 0
2022-03-02 07:00 | 3.7832 | 0 | N/A | 0 | 0
2022-03-02 07:30 | 4.3999 | 0 | N/A | 0 | 0
2022-03-02 08:00 | 4.7154 | 0 | N/A | 0 | 0
2022-03-02 08:30 | 4.3499 | 0 | N/A | 0 | 0
2022-03-02 09:00 | 4.0836 | 0 | N/A | 0 | 0
2022-03-02 09:30 | 3.8257 | 0 | N/A | 0 | 0
2022-03-02 10:00 | 3.3717 | 0 | N/A | 0 | 0
2022-03-02 10:30 | 2.5725 | 0 | N/A | 0 | 0
2022-03-02 11:00 | 1.8758 | 0 | N/A | 0 | 0
2022-03-02 11:30 | 1.4408 | 0 | N/A | 0 | 0
2022-03-02 12:00 | 1.5074 | 0 | N/A | 0 | 0
2022-03-02 12:30 | 0.97054 | 0 | N/A | 0 | 0
2022-03-02 13:00 | 1.2178 | 0 | N/A | 0 | 0
2022-03-02 13:30 | 1.5221 | 0 | N/A | 0 | 0
2022-03-02 14:00 | 2.5646 | 0 | N/A | 0 | 0
2022-03-02 14:30 | 2.7726 | 0 | N/A | 0 | 0
2022-03-02 15:00 | 2.2677 | 0 | N/A | 0 | 0
2022-03-02 15:30 | 1.8719 | 0 | N/A | 0 | 0
2022-03-02 16:00 | 0.49189 | 0 | N/A | 0 | 0
2022-03-02 16:30 | 1.1449 | 0 | N/A | 0 | 0
2022-03-02 17:00 | 1.5338 | 0 | N/A | 0 | 0
2022-03-02 17:30 | 2.2827 | 0 | N/A | 0 | 0
2022-03-02 18:00 | 3.3248 | 0 | N/A | 0 | 0
2022-03-02 18:30 | 4.2661 | 0 | N/A | 0 | 0
2022-03-02 19:00 | 5.0984 | 0 | N/A | 0 | 0
2022-03-02 19:30 | 5.1978 | 0 | N/A | 0 | 0
2022-03-02 20:00 | 5.2518 | 0 | N/A | 0 | 0
2022-03-02 20:30 | 5.1476 | 0 | N/A | 0 | 0
2022-03-02 21:00 | 4.9901 | 0 | N/A | 0 | 0
2022-03-02 21:30 | 4.6962 | 0 | N/A | 0 | 0
2022-03-02 22:00 | 4.3397 | 0 | N/A | 0 | 0
2022-03-02 22:30 | 4.3651 | 0 | N/A | 0 | 0
2022-03-02 23:00 | 4.364 | 0 | N/A | 0 | 0
2022-03-02 23:30 | 3.8481 | 0 | N/A | 0 | 0
2022-03-03 | 3.8698 | 0 | N/A | 0 | 0
2022-03-04 00:30 | 4.414 | 0 | N/A | 0 | 0
2022-03-04 01:00 | 4.4167 | 0 | N/A | 0 | 0
2022-03-04 01:30 | 3.5604 | 0 | N/A | 0 | 0
2022-03-04 02:00 | 2.9464 | 0 | N/A | 0 | 0
2022-03-04 02:30 | 2.8408 | 0 | N/A | 0 | 0
2022-03-04 03:00 | 2.6468 | 0 | N/A | 0 | 0
2022-03-04 03:30 | 2.406 | 0 | N/A | 0 | 0
2022-03-04 04:00 | 2.356 | 0 | N/A | 0 | 0
2022-03-04 04:30 | 2.3976 | 0 | N/A | 0 | 0
2022-03-04 05:00 | 2.4094 | 0 | N/A | 0 | 0
2022-03-04 05:30 | 2.5644 | 0 | N/A | 0 | 0
2022-03-04 06:00 | 2.7529 | 0 | N/A | 0 | 0
2022-03-04 06:30 | 3.2455 | 0 | N/A | 0 | 0
2022-03-04 07:00 | 3.66 | 0 | N/A | 0 | 0
2022-03-04 07:30 | 4.5905 | 0 | N/A | 0 | 0
2022-03-04 08:00 | 4.7989 | 0 | N/A | 0 | 0
2022-03-04 08:30 | 4.2727 | 0 | N/A | 0 | 0
2022-03-04 09:00 | 3.7384 | 0 | N/A | 0 | 0
2022-03-04 09:30 | 3.7219 | 0 | N/A | 0 | 0
2022-03-04 10:00 | 3.0149 | 0 | N/A | 0 | 0
2022-03-04 10:30 | 2.6147 | 0 | N/A | 0 | 0
2022-03-04 11:00 | 3.0243 | 0 | N/A | 0 | 0
2022-03-04 11:30 | 2.8001 | 0 | N/A | 0 | 0
2022-03-04 12:00 | 3.1303 | 0 | N/A | 0 | 0
2022-03-04 12:30 | 2.8257 | 0 | N/A | 0 | 0
2022-03-04 13:00 | 1.6006 | 0 | N/A | 0 | 0
2022-03-04 13:30 | 2.52 | 0 | N/A | 0 | 0
2022-03-04 14:00 | 3.4502 | 0 | N/A | 0 | 0
2022-03-04 14:30 | 2.4017 | 0 | N/A | 0 | 0
2022-03-04 15:00 | 3.1245 | 0 | N/A | 0 | 0
2022-03-04 15:30 | 3.9569 | 0 | N/A | 0 | 0
2022-03-04 16:00 | 4.0971 | 0 | N/A | 0 | 0
2022-03-04 16:30 | 4.4278 | 0 | N/A | 0 | 0
2022-03-04 17:00 | 4.6302 | 0 | N/A | 0 | 0
2022-03-04 17:30 | 4.8393 | 0 | N/A | 0 | 0
2022-03-04 18:00 | 5.1403 | 0 | N/A | 0 | 0
2022-03-04 18:30 | 5.1292 | 0 | N/A | 0 | 0
2022-03-04 19:00 | 5.1474 | 0 | N/A | 0 | 0
2022-03-04 19:30 | 5.0059 | 0 | N/A | 0 | 0
2022-03-04 20:00 | 4.971 | 0 | N/A | 0 | 0
2022-03-04 20:30 | 4.916 | 0 | N/A | 0 | 0
2022-03-04 21:00 | 4.6468 | 0 | N/A | 0 | 0
2022-03-04 21:30 | 4.3162 | 0 | N/A | 0 | 0
2022-03-04 22:00 | 4.0154 | 0 | N/A | 0 | 0
2022-03-04 22:30 | 4.254 | 0 | N/A | 0 | 0
2022-03-04 23:00 | 4.3461 | 0 | N/A | 0 | 0
2022-03-04 23:30 | 3.9319 | 0 | N/A | 0 | 0
2022-03-05 | 3.9022 | 0 | N/A | 0 | 0
2022-03-05 00:30 | 4.4864 | 0 | N/A | 0 | 0
2022-03-05 01:00 | 4.5422 | 0 | N/A | 0 | 0
2022-03-05 01:30 | 3.5798 | 0 | N/A | 0 | 0
2022-03-05 02:00 | 2.8777 | 0 | N/A | 0 | 0
2022-03-05 02:30 | 2.9009 | 0 | N/A | 0 | 0
2022-03-05 03:00 | 2.6202 | 0 | N/A | 0 | 0
2022-03-05 03:30 | 2.4227 | 0 | N/A | 0 | 0
2022-03-05 04:00 | 2.29 | 0 | N/A | 0 | 0
2022-03-05 04:30 | 2.3017 | 0 | N/A | 0 | 0
2022-03-05 05:00 | 2.3004 | 0 | N/A | 0 | 0
2022-03-05 05:30 | 2.3616 | 0 | N/A | 0 | 0
2022-03-05 06:00 | 2.4301 | 0 | N/A | 0 | 0
2022-03-05 06:30 | 2.6326 | 0 | N/A | 0 | 0
2022-03-05 07:00 | 2.8103 | 0 | N/A | 0 | 0
2022-03-05 07:30 | 3.1003 | 0 | N/A | 0 | 0
2022-03-05 08:00 | 3.2825 | 0 | N/A | 0 | 0
2022-03-05 08:30 | 3.4693 | 0 | N/A | 0 | 0
2022-03-05 09:00 | 3.6314 | 0 | N/A | 0 | 0
2022-03-05 09:30 | 3.539 | 0 | N/A | 0 | 0
2022-03-05 10:00 | 3.2573 | 0 | N/A | 0 | 0
2022-03-05 10:30 | 3.5553 | 0 | N/A | 0 | 0
2022-03-05 11:00 | 3.2152 | 0 | N/A | 0 | 0
2022-03-05 11:30 | 3.2945 | 0 | N/A | 0 | 0
2022-03-05 12:00 | 3.5432 | 0 | N/A | 0 | 0
2022-03-05 12:30 | 2.8903 | 0 | N/A | 0 | 0
2022-03-05 13:00 | 3.749 | 0 | N/A | 0 | 0
2022-03-05 13:30 | 3.4215 | 0 | N/A | 0 | 0
2022-03-05 14:00 | 3.1575 | 0 | N/A | 0 | 0
2022-03-05 14:30 | 1.6514 | 0 | N/A | 0 | 0
2022-03-05 15:00 | 0.74226 | 0 | N/A | 0 | 0
2022-03-05 15:30 | 1.2475 | 0 | N/A | 0 | 0
2022-03-05 16:00 | 2.4123 | 0 | N/A | 0 | 0
2022-03-05 16:30 | 2.7011 | 0 | N/A | 0 | 0
2022-03-05 17:00 | 3.5238 | 0 | N/A | 0 | 0
2022-03-05 17:30 | 3.5961 | 0 | N/A | 0 | 0
2022-03-05 18:00 | 3.7656 | 0 | N/A | 0 | 0
2022-03-05 18:30 | 4.0257 | 0 | N/A | 0 | 0
2022-03-05 19:00 | 4.392 | 0 | N/A | 0 | 0
2022-03-05 19:30 | 4.3943 | 0 | N/A | 0 | 0
2022-03-05 20:00 | 4.5894 | 0 | N/A | 0 | 0
2022-03-05 20:30 | 4.4577 | 0 | N/A | 0 | 0
2022-03-05 21:00 | 4.2735 | 0 | N/A | 0 | 0
2022-03-05 21:30 | 4.025 | 0 | N/A | 0 | 0
2022-03-05 22:00 | 3.729 | 0 | N/A | 0 | 0
2022-03-05 22:30 | 4.2194 | 0 | N/A | 0 | 0
2022-03-05 23:00 | 4.343 | 0 | N/A | 0 | 0
2022-03-05 23:30 | 4.0366 | 0 | N/A | 0 | 0
2022-03-06 | 4.1029 | 0 | N/A | 0 | 0
2022-03-06 00:30 | 4.4833 | 0 | N/A | 0 | 0
2022-03-06 01:00 | 4.7123 | 0 | N/A | 0 | 0
2022-03-06 01:30 | 3.8439 | 0 | N/A | 0 | 0
2022-03-06 02:00 | 3.1403 | 0 | N/A | 0 | 0
2022-03-06 02:30 | 3.0802 | 0 | N/A | 0 | 0
2022-03-06 03:00 | 2.7868 | 0 | N/A | 0 | 0
2022-03-06 03:30 | 2.5255 | 0 | N/A | 0 | 0
2022-03-06 04:00 | 2.3708 | 0 | N/A | 0 | 0
2022-03-06 04:30 | 2.3134 | 0 | N/A | 0 | 0
2022-03-06 05:00 | 2.3007 | 0 | N/A | 0 | 0
2022-03-06 05:30 | 2.3461 | 0 | N/A | 0 | 0
2022-03-06 06:00 | 2.4169 | 0 | N/A | 0 | 0
2022-03-06 06:30 | 2.6013 | 0 | N/A | 0 | 0
2022-03-06 07:00 | 2.6897 | 0 | N/A | 0 | 0
2022-03-06 07:30 | 2.9572 | 0 | N/A | 0 | 0
2022-03-06 08:00 | 3.1897 | 0 | N/A | 0 | 0
2022-03-06 08:30 | 3.3084 | 0 | N/A | 0 | 0
2022-03-06 09:00 | 3.4741 | 0 | N/A | 0 | 0
2022-03-06 09:30 | 3.6082 | 0 | N/A | 0 | 0
2022-03-06 10:00 | 3.4796 | 0 | N/A | 0 | 0
2022-03-06 10:30 | 3.7339 | 0 | N/A | 0 | 0
2022-03-06 11:00 | 3.7122 | 0 | N/A | 0 | 0
2022-03-06 11:30 | 3.3883 | 0 | N/A | 0 | 0
2022-03-06 12:00 | 2.6654 | 0 | N/A | 0 | 0
2022-03-06 12:30 | 2.5801 | 0 | N/A | 0 | 0
2022-03-06 13:00 | 2.9543 | 0 | N/A | 0 | 0
2022-03-06 13:30 | 3.0151 | 0 | N/A | 0 | 0
2022-03-06 14:00 | 2.5387 | 0 | N/A | 0 | 0
2022-03-06 14:30 | 2.6548 | 0 | N/A | 0 | 0
2022-03-06 15:00 | 2.6226 | 0 | N/A | 0 | 0
2022-03-06 15:30 | 2.4169 | 0 | N/A | 0 | 0
2022-03-06 16:00 | 2.77 | 0 | N/A | 0 | 0
2022-03-06 16:30 | 3.5444 | 0 | N/A | 0 | 0
2022-03-06 17:00 | 3.1306 | 0 | N/A | 0 | 0
2022-03-06 17:30 | 4.2806 | 0 | N/A | 0 | 0
2022-03-06 18:00 | 5.1035 | 0 | N/A | 0 | 0
2022-03-06 18:30 | 5.2795 | 0 | N/A | 0 | 0
2022-03-06 19:00 | 5.3991 | 0 | N/A | 0 | 0
2022-03-06 19:30 | 5.3359 | 0 | N/A | 0 | 0
2022-03-06 20:00 | 5.2597 | 0 | N/A | 0 | 0
2022-03-06 20:30 | 5.1398 | 0 | N/A | 0 | 0
2022-03-06 21:00 | 4.9394 | 0 | N/A | 0 | 0
2022-03-06 21:30 | 4.5172 | 0 | N/A | 0 | 0
2022-03-06 22:00 | 4.154 | 0 | N/A | 0 | 0
2022-03-06 22:30 | 4.3371 | 0 | N/A | 0 | 0
2022-03-06 23:00 | 4.4297 | 0 | N/A | 0 | 0
2022-03-06 23:30 | 4.0754 | 0 | N/A | 0 | 0
2022-03-07 | 4.1603 | 0 | N/A | 0 | 0
2022-03-08 00:30 | 4.515 | 0 | N/A | 0 | 0
2022-03-08 01:00 | 4.7872 | 0 | N/A | 0 | 0
2022-03-08 01:30 | 3.8629 | 0 | N/A | 0 | 0
2022-03-08 02:00 | 3.3278 | 0 | N/A | 0 | 0
2022-03-08 02:30 | 3.2224 | 0 | N/A | 0 | 0
2022-03-08 03:00 | 2.8728 | 0 | N/A | 0 | 0
2022-03-08 03:30 | 2.5887 | 0 | N/A | 0 | 0
2022-03-08 04:00 | 2.4851 | 0 | N/A | 0 | 0
2022-03-08 04:30 | 2.4805 | 0 | N/A | 0 | 0
2022-03-08 05:00 | 2.5059 | 0 | N/A | 0 | 0
2022-03-08 05:30 | 2.7946 | 0 | N/A | 0 | 0
2022-03-08 06:00 | 3.056 | 0 | N/A | 0 | 0
2022-03-08 06:30 | 3.5829 | 0 | N/A | 0 | 0
2022-03-08 07:00 | 4.1235 | 0 | N/A | 0 | 0
2022-03-08 07:30 | 4.8832 | 0 | N/A | 0 | 0
2022-03-08 08:00 | 5.3245 | 0 | N/A | 0 | 0
2022-03-08 08:30 | 4.8829 | 0 | N/A | 0 | 0
2022-03-08 09:00 | 4.5409 | 0 | N/A | 0 | 0
2022-03-08 09:30 | 3.8121 | 0 | N/A | 0 | 0
2022-03-08 10:00 | 3.352 | 0 | N/A | 0 | 0
2022-03-08 10:30 | 2.5541 | 0 | N/A | 0 | 0
2022-03-08 11:00 | 1.9922 | 0 | N/A | 0 | 0
2022-03-08 11:30 | 1.9881 | 0 | N/A | 0 | 0
2022-03-08 12:00 | 2.1052 | 0 | N/A | 0 | 0
2022-03-08 12:30 | 2.2723 | 0 | N/A | 0 | 0
2022-03-08 13:00 | 2.3724 | 0 | N/A | 0 | 0
2022-03-08 13:30 | 2.4172 | 0 | N/A | 0 | 0
2022-03-08 14:00 | 2.4743 | 0 | N/A | 0 | 0
2022-03-08 14:30 | 2.5084 | 0 | N/A | 0 | 0
2022-03-08 15:00 | 2.0646 | 0 | N/A | 0 | 0
2022-03-08 15:30 | 1.4548 | 0 | N/A | 0 | 0
2022-03-08 16:00 | 1.8436 | 0 | N/A | 0 | 0
2022-03-08 16:30 | 1.8471 | 0 | N/A | 0 | 0
2022-03-08 17:00 | 2.9754 | 0 | N/A | 0 | 0
2022-03-08 17:30 | 3.86 | 0 | N/A | 0 | 0
2022-03-08 18:00 | 4.3146 | 0 | N/A | 0 | 0
2022-03-08 18:30 | 4.7241 | 0 | N/A | 0 | 0
2022-03-08 19:00 | 5.4324 | 0 | N/A | 0 | 0
2022-03-08 19:30 | 5.4701 | 0 | N/A | 0 | 0
2022-03-08 20:00 | 5.6954 | 0 | N/A | 0 | 0
2022-03-08 20:30 | 5.634 | 0 | N/A | 0 | 0
2022-03-08 21:00 | 5.2356 | 0 | N/A | 0 | 0
2022-03-08 21:30 | 4.9925 | 0 | N/A | 0 | 0
2022-03-08 22:00 | 4.529 | 0 | N/A | 0 | 0
2022-03-08 22:30 | 4.6344 | 0 | N/A | 0 | 0
2022-03-08 23:00 | 4.6458 | 0 | N/A | 0 | 0
2022-03-08 23:30 | 4.2753 | 0 | N/A | 0 | 0
2022-03-09 | 4.1741 | 0 | N/A | 0 | 0
2022-03-12 00:30 | 4.3925 | 0 | N/A | 0 | 0
2022-03-12 01:00 | 4.6376 | 0 | N/A | 0 | 0
2022-03-12 01:30 | 3.8187 | 0 | N/A | 0 | 0
2022-03-12 02:00 | 3.1223 | 0 | N/A | 0 | 0
2022-03-12 02:30 | 3.0238 | 0 | N/A | 0 | 0
2022-03-12 03:00 | 2.768 | 0 | N/A | 0 | 0
2022-03-12 03:30 | 2.5722 | 0 | N/A | 0 | 0
2022-03-12 04:00 | 2.4663 | 0 | N/A | 0 | 0
2022-03-12 04:30 | 2.3677 | 0 | N/A | 0 | 0
2022-03-12 05:00 | 2.3932 | 0 | N/A | 0 | 0
2022-03-12 05:30 | 2.3839 | 0 | N/A | 0 | 0
2022-03-12 06:00 | 2.6076 | 0 | N/A | 0 | 0
2022-03-12 06:30 | 2.9198 | 0 | N/A | 0 | 0
2022-03-12 07:00 | 3.071 | 0 | N/A | 0 | 0
2022-03-12 07:30 | 3.4237 | 0 | N/A | 0 | 0
2022-03-12 08:00 | 3.5534 | 0 | N/A | 0 | 0
2022-03-12 08:30 | 3.174 | 0 | N/A | 0 | 0
2022-03-12 09:00 | 3.2066 | 0 | N/A | 0 | 0
2022-03-12 09:30 | 2.7526 | 0 | N/A | 0 | 0
2022-03-12 10:00 | 1.4227 | 0 | N/A | 0 | 0
2022-03-12 10:30 | 0.86513 | 0 | N/A | 0 | 0
2022-03-12 11:00 | -0.66895 | 0 | N/A | 0 | 0
2022-03-12 11:30 | -0.99548 | 0 | N/A | 0 | 0
2022-03-12 12:00 | -1.139 | 0 | N/A | 0 | 0
2022-03-12 12:30 | -1.3861 | 0 | N/A | 0 | 0
2022-03-12 13:00 | -1.5838 | 0 | N/A | 0 | 0
2022-03-12 13:30 | -1.7633 | 0 | N/A | 0 | 0
2022-03-12 14:00 | -1.8667 | 0 | N/A | 0 | 0
2022-03-12 14:30 | -1.8366 | 0 | N/A | 0 | 0
2022-03-12 15:00 | -1.6795 | 0 | N/A | 0 | 0
2022-03-12 15:30 | -1.4531 | 0 | N/A | 0 | 0
2022-03-12 16:00 | -1.1392 | 0 | N/A | 0 | 0
2022-03-12 16:30 | -0.74132 | 0 | N/A | 0 | 0
2022-03-12 17:00 | 0.52642 | 0 | N/A | 0 | 0
2022-03-12 17:30 | 1.2652 | 0 | N/A | 0 | 0
2022-03-12 18:00 | 2.1831 | 0 | N/A | 0 | 0
2022-03-12 18:30 | 3.013 | 0 | N/A | 0 | 0
2022-03-12 19:00 | 3.7021 | 0 | N/A | 0 | 0
2022-03-12 19:30 | 4.0053 | 0 | N/A | 0 | 0
2022-03-12 20:00 | 4.1029 | 0 | N/A | 0 | 0
2022-03-12 20:30 | 4.0994 | 0 | N/A | 0 | 0
2022-03-12 21:00 | 3.9801 | 0 | N/A | 0 | 0
2022-03-12 21:30 | 3.7515 | 0 | N/A | 0 | 0
2022-03-12 22:00 | 3.5159 | 0 | N/A | 0 | 0
2022-03-12 22:30 | 3.9433 | 0 | N/A | 0 | 0
2022-03-12 23:00 | 4.0497 | 0 | N/A | 0 | 0
2022-03-12 23:30 | 3.8523 | 0 | N/A | 0 | 0
2022-03-13 | 3.876 | 0 | N/A | 0 | 0
2022-03-13 00:30 | 4.2493 | 0 | N/A | 0 | 0
2022-03-13 01:00 | 4.4577 | 0 | N/A | 0 | 0
2022-03-13 01:30 | 3.7075 | 0 | N/A | 0 | 0
2022-03-13 02:00 | 3.1779 | 0 | N/A | 0 | 0
2022-03-13 02:30 | 3.1137 | 0 | N/A | 0 | 0
2022-03-13 03:00 | 2.828 | 0 | N/A | 0 | 0
2022-03-13 03:30 | 2.4955 | 0 | N/A | 0 | 0
2022-03-13 04:00 | 2.3445 | 0 | N/A | 0 | 0
2022-03-13 04:30 | 2.2901 | 0 | N/A | 0 | 0
2022-03-13 05:00 | 2.2231 | 0 | N/A | 0 | 0
2022-03-13 05:30 | 2.279 | 0 | N/A | 0 | 0
2022-03-13 06:00 | 2.3408 | 0 | N/A | 0 | 0
2022-03-13 06:30 | 2.4986 | 0 | N/A | 0 | 0
2022-03-13 07:00 | 2.6954 | 0 | N/A | 0 | 0
2022-03-13 07:30 | 2.9903 | 0 | N/A | 0 | 0
2022-03-13 08:00 | 3.0613 | 0 | N/A | 0 | 0
2022-03-13 08:30 | 2.7296 | 0 | N/A | 0 | 0
2022-03-13 09:00 | 2.39 | 0 | N/A | 0 | 0
2022-03-13 09:30 | 1.8894 | 0 | N/A | 0 | 0
2022-03-13 10:00 | 1.3179 | 0 | N/A | 0 | 0
2022-03-13 10:30 | 0.81038 | 0 | N/A | 0 | 0
2022-03-13 11:00 | -0.62198 | 0 | N/A | 0 | 0
2022-03-13 11:30 | -0.79218 | 0 | N/A | 0 | 0
2022-03-13 12:00 | -0.94057 | 0 | N/A | 0 | 0
2022-03-13 12:30 | -1.2015 | 0 | N/A | 0 | 0
2022-03-13 13:00 | -1.5235 | 0 | N/A | 0 | 0
2022-03-13 13:30 | -1.7834 | 0 | N/A | 0 | 0
2022-03-13 14:00 | -1.796 | 0 | N/A | 0 | 0
2022-03-13 14:30 | -1.6967 | 0 | N/A | 0 | 0
2022-03-13 15:00 | -1.4679 | 0 | N/A | 0 | 0
2022-03-13 15:30 | -1.0702 | 0 | N/A | 0 | 0
2022-03-13 16:00 | -0.4491 | 0 | N/A | 0 | 0
2022-03-13 16:30 | 0.67021 | 0 | N/A | 0 | 0
2022-03-13 17:00 | 1.4151 | 0 | N/A | 0 | 0
2022-03-13 17:30 | 1.9333 | 0 | N/A | 0 | 0
2022-03-13 18:00 | 2.8357 | 0 | N/A | 0 | 0
2022-03-13 18:30 | 3.7438 | 0 | N/A | 0 | 0
2022-03-13 19:00 | 4.2842 | 0 | N/A | 0 | 0
2022-03-13 19:30 | 4.6076 | 0 | N/A | 0 | 0
2022-03-13 20:00 | 4.5415 | 0 | N/A | 0 | 0
2022-03-13 20:30 | 4.3686 | 0 | N/A | 0 | 0
2022-03-13 21:00 | 4.1553 | 0 | N/A | 0 | 0
2022-03-13 21:30 | 3.9166 | 0 | N/A | 0 | 0
2022-03-13 22:00 | 3.6996 | 0 | N/A | 0 | 0
2022-03-13 22:30 | 3.9533 | 0 | N/A | 0 | 0
2022-03-13 23:00 | 4.049 | 0 | N/A | 0 | 0
2022-03-13 23:30 | 3.8435 | 0 | N/A | 0 | 0
2022-03-14 | 3.8758 | 0 | N/A | 0 | 0
2022-03-14 00:30 | 4.2537 | 0 | N/A | 0 | 0
2022-03-14 01:00 | 4.4337 | 0 | N/A | 0 | 0
2022-03-14 01:30 | 3.6214 | 0 | N/A | 0 | 0
2022-03-14 02:00 | 3.0518 | 0 | N/A | 0 | 0
2022-03-14 02:30 | 2.8933 | 0 | N/A | 0 | 0
2022-03-14 03:00 | 2.7216 | 0 | N/A | 0 | 0
2022-03-14 03:30 | 2.3941 | 0 | N/A | 0 | 0
2022-03-14 04:00 | 2.2679 | 0 | N/A | 0 | 0
2022-03-14 04:30 | 2.2162 | 0 | N/A | 0 | 0
2022-03-14 05:00 | 2.2275 | 0 | N/A | 0 | 0
2022-03-14 05:30 | 2.3533 | 0 | N/A | 0 | 0
2022-03-14 06:00 | 2.4225 | 0 | N/A | 0 | 0
2022-03-14 06:30 | 2.5615 | 0 | N/A | 0 | 0
2022-03-14 07:00 | 2.6707 | 0 | N/A | 0 | 0
2022-03-14 07:30 | 2.8482 | 0 | N/A | 0 | 0
2022-03-14 08:00 | 2.8551 | 0 | N/A | 0 | 0
2022-03-14 08:30 | 2.642 | 0 | N/A | 0 | 0
2022-03-14 09:00 | 2.3193 | 0 | N/A | 0 | 0
2022-03-14 09:30 | 1.868 | 0 | N/A | 0 | 0
2022-03-14 10:00 | 1.3535 | 0 | N/A | 0 | 0
2022-03-14 10:30 | 0.95689 | 0 | N/A | 0 | 0
2022-03-14 11:00 | 0.60828 | 0 | N/A | 0 | 0
2022-03-14 11:30 | -0.67053 | 0 | N/A | 0 | 0
2022-03-14 12:00 | -0.79512 | 0 | N/A | 0 | 0
2022-03-14 12:30 | -0.57837 | 0 | N/A | 0 | 0
2022-03-14 13:00 | 0.46154 | 0 | N/A | 0 | 0
2022-03-14 13:30 | 0.438 | 0 | N/A | 0 | 0
2022-03-14 14:00 | 0.63879 | 0 | N/A | 0 | 0
2022-03-14 14:30 | 0.52379 | 0 | N/A | 0 | 0
2022-03-14 15:00 | 0.71743 | 0 | N/A | 0 | 0
2022-03-14 15:30 | 1.1303 | 0 | N/A | 0 | 0
2022-03-14 16:00 | 2.9746 | 0 | N/A | 0 | 0
2022-03-14 16:30 | 2.4469 | 0 | N/A | 0 | 0
2022-03-14 17:00 | 3.7096 | 0 | N/A | 0 | 0
2022-03-14 17:30 | 4.8638 | 0 | N/A | 0 | 0
2022-03-14 18:00 | 5.3393 | 0 | N/A | 0 | 0
2022-03-14 18:30 | 5.2484 | 0 | N/A | 0 | 0
2022-03-14 19:00 | 5.0591 | 0 | N/A | 0 | 0
2022-03-14 19:30 | 5.1176 | 0 | N/A | 0 | 0
2022-03-14 20:00 | 5.0705 | 0 | N/A | 0 | 0
2022-03-14 20:30 | 4.904 | 0 | N/A | 0 | 0
2022-03-14 21:00 | 4.5797 | 0 | N/A | 0 | 0
2022-03-14 21:30 | 4.2009 | 0 | N/A | 0 | 0
2022-03-14 22:00 | 3.9315 | 0 | N/A | 0 | 0
2022-03-14 22:30 | 4.044 | 0 | N/A | 0 | 0
2022-03-14 23:00 | 4.143 | 0 | N/A | 0 | 0
2022-03-14 23:30 | 3.9461 | 0 | N/A | 0 | 0
2022-03-15 | 3.9283 | 0 | N/A | 0 | 0
2022-03-15 00:30 | 4.2909 | 0 | N/A | 0 | 0
2022-03-15 01:00 | 4.4545 | 0 | N/A | 0 | 0
2022-03-15 01:30 | 3.7431 | 0 | N/A | 0 | 0
2022-03-15 02:00 | 3.155 | 0 | N/A | 0 | 0
2022-03-15 02:30 | 3.0128 | 0 | N/A | 0 | 0
2022-03-15 03:00 | 2.7826 | 0 | N/A | 0 | 0
2022-03-15 03:30 | 2.5141 | 0 | N/A | 0 | 0
2022-03-15 04:00 | 2.3181 | 0 | N/A | 0 | 0
2022-03-15 04:30 | 2.2416 | 0 | N/A | 0 | 0
2022-03-15 05:00 | 2.3211 | 0 | N/A | 0 | 0
2022-03-15 05:30 | 2.4934 | 0 | N/A | 0 | 0
2022-03-15 06:00 | 2.818 | 0 | N/A | 0 | 0
2022-03-15 06:30 | 3.1818 | 0 | N/A | 0 | 0
2022-03-15 07:00 | 3.5875 | 0 | N/A | 0 | 0
2022-03-15 07:30 | 4.3622 | 0 | N/A | 0 | 0
2022-03-15 08:00 | 4.4656 | 0 | N/A | 0 | 0
2022-03-15 08:30 | 3.7635 | 0 | N/A | 0 | 0
2022-03-15 09:00 | 3.4286 | 0 | N/A | 0 | 0
2022-03-15 09:30 | 3.5615 | 0 | N/A | 0 | 0
2022-03-15 10:00 | 3.375 | 0 | N/A | 0 | 0
2022-03-15 10:30 | 2.9199 | 0 | N/A | 0 | 0
2022-03-15 11:00 | 3.0575 | 0 | N/A | 0 | 0
2022-03-15 11:30 | 3.2448 | 0 | N/A | 0 | 0
2022-03-15 12:00 | 3.941 | 0 | N/A | 0 | 0
2022-03-15 12:30 | 3.4631 | 0 | N/A | 0 | 0
2022-03-15 13:00 | 3.0496 | 0 | N/A | 0 | 0
2022-03-15 13:30 | 2.8098 | 0 | N/A | 0 | 0
2022-03-15 14:00 | 2.7243 | 0 | N/A | 0 | 0
2022-03-15 14:30 | 3.0092 | 0 | N/A | 0 | 0
2022-03-15 15:00 | 2.3106 | 0 | N/A | 0 | 0
2022-03-15 15:30 | 2.3161 | 0 | N/A | 0 | 0
2022-03-15 16:00 | 2.6574 | 0 | N/A | 0 | 0
2022-03-15 16:30 | 1.494 | 0 | N/A | 0 | 0
2022-03-15 17:00 | 1.4374 | 0 | N/A | 0 | 0
2022-03-15 17:30 | 2.5071 | 0 | N/A | 0 | 0
2022-03-15 18:00 | 3.4321 | 0 | N/A | 0 | 0
2022-03-15 18:30 | 4.133 | 0 | N/A | 0 | 0
2022-03-15 19:00 | 4.6498 | 0 | N/A | 0 | 0
2022-03-15 19:30 | 4.7676 | 0 | N/A | 0 | 0
2022-03-15 20:00 | 4.9205 | 0 | N/A | 0 | 0
2022-03-15 20:30 | 4.9239 | 0 | N/A | 0 | 0
2022-03-15 21:00 | 4.6657 | 0 | N/A | 0 | 0
2022-03-15 21:30 | 4.3392 | 0 | N/A | 0 | 0
2022-03-15 22:00 | 4.0197 | 0 | N/A | 0 | 0
2022-03-15 22:30 | 4.1701 | 0 | N/A | 0 | 0
2022-03-15 23:00 | 4.1195 | 0 | N/A | 0 | 0
2022-03-15 23:30 | 3.79 | 0 | N/A | 0 | 0
2022-03-16 | 3.8264 | 0 | N/A | 0 | 0
2022-03-18 00:30 | 4.4899 | 0 | N/A | 0 | 0
2022-03-18 01:00 | 4.5345 | 0 | N/A | 0 | 0
2022-03-18 01:30 | 3.6515 | 0 | N/A | 0 | 0
2022-03-18 02:00 | 3.0318 | 0 | N/A | 0 | 0
2022-03-18 02:30 | 3.0109 | 0 | N/A | 0 | 0
2022-03-18 03:00 | 2.731 | 0 | N/A | 0 | 0
2022-03-18 03:30 | 2.4613 | 0 | N/A | 0 | 0
2022-03-18 04:00 | 2.3887 | 0 | N/A | 0 | 0
2022-03-18 04:30 | 2.4049 | 0 | N/A | 0 | 0
2022-03-18 05:00 | 2.3903 | 0 | N/A | 0 | 0
2022-03-18 05:30 | 2.6228 | 0 | N/A | 0 | 0
2022-03-18 06:00 | 2.8801 | 0 | N/A | 0 | 0
2022-03-18 06:30 | 3.3544 | 0 | N/A | 0 | 0
2022-03-18 07:00 | 3.7348 | 0 | N/A | 0 | 0
2022-03-18 07:30 | 4.5486 | 0 | N/A | 0 | 0
2022-03-18 08:00 | 5.0416 | 0 | N/A | 0 | 0
2022-03-18 08:30 | 4.538 | 0 | N/A | 0 | 0
2022-03-18 09:00 | 4.2558 | 0 | N/A | 0 | 0
2022-03-18 09:30 | 4.0141 | 0 | N/A | 0 | 0
2022-03-18 10:00 | 4.082 | 0 | N/A | 0 | 0
2022-03-18 10:30 | 3.5583 | 0 | N/A | 0 | 0
2022-03-18 11:00 | 2.7903 | 0 | N/A | 0 | 0
2022-03-18 11:30 | 2.8414 | 0 | N/A | 0 | 0
2022-03-18 12:00 | 1.8845 | 0 | N/A | 0 | 0
2022-03-18 12:30 | 1.8076 | 0 | N/A | 0 | 0
2022-03-18 13:00 | 1.2224 | 0 | N/A | 0 | 0
2022-03-18 13:30 | 1.871 | 0 | N/A | 0 | 0
2022-03-18 14:00 | 1.296 | 0 | N/A | 0 | 0
2022-03-18 14:30 | 0.88887 | 0 | N/A | 0 | 0
2022-03-18 15:00 | 1.0628 | 0 | N/A | 0 | 0
2022-03-18 15:30 | 0.51461 | 0 | N/A | 0 | 0
2022-03-18 16:00 | 0.96624 | 0 | N/A | 0 | 0
2022-03-18 16:30 | 1.506 | 0 | N/A | 0 | 0
2022-03-18 17:00 | 2.4046 | 0 | N/A | 0 | 0
2022-03-18 17:30 | 3.0099 | 0 | N/A | 0 | 0
2022-03-18 18:00 | 3.4741 | 0 | N/A | 0 | 0
2022-03-18 18:30 | 3.7827 | 0 | N/A | 0 | 0
2022-03-18 19:00 | 4.1701 | 0 | N/A | 0 | 0
2022-03-18 19:30 | 4.4617 | 0 | N/A | 0 | 0
2022-03-18 20:00 | 4.5923 | 0 | N/A | 0 | 0
2022-03-18 20:30 | 4.6718 | 0 | N/A | 0 | 0
2022-03-18 21:00 | 4.4293 | 0 | N/A | 0 | 0
2022-03-18 21:30 | 4.2367 | 0 | N/A | 0 | 0
2022-03-18 22:00 | 3.9996 | 0 | N/A | 0 | 0
2022-03-18 22:30 | 4.2571 | 0 | N/A | 0 | 0
2022-03-18 23:00 | 4.3343 | 0 | N/A | 0 | 0
2022-03-18 23:30 | 4.0342 | 0 | N/A | 0 | 0
2022-03-19 | 4.0215 | 0 | N/A | 0 | 0
2022-03-19 00:30 | 4.48 | 0 | N/A | 0 | 0
2022-03-19 01:00 | 4.7977 | 0 | N/A | 0 | 0
2022-03-19 01:30 | 3.9438 | 0 | N/A | 0 | 0
2022-03-19 02:00 | 3.1739 | 0 | N/A | 0 | 0
2022-03-19 02:30 | 3.1223 | 0 | N/A | 0 | 0
2022-03-19 03:00 | 2.8065 | 0 | N/A | 0 | 0
2022-03-19 03:30 | 2.5875 | 0 | N/A | 0 | 0
2022-03-19 04:00 | 2.4433 | 0 | N/A | 0 | 0
2022-03-19 04:30 | 2.3795 | 0 | N/A | 0 | 0
2022-03-19 05:00 | 2.3089 | 0 | N/A | 0 | 0
2022-03-19 05:30 | 2.3884 | 0 | N/A | 0 | 0
2022-03-19 06:00 | 2.4686 | 0 | N/A | 0 | 0
2022-03-19 06:30 | 2.6294 | 0 | N/A | 0 | 0
2022-03-19 07:00 | 2.8057 | 0 | N/A | 0 | 0
2022-03-19 07:30 | 3.1344 | 0 | N/A | 0 | 0
2022-03-19 08:00 | 3.4165 | 0 | N/A | 0 | 0
2022-03-19 08:30 | 3.1757 | 0 | N/A | 0 | 0
2022-03-19 09:00 | 2.7833 | 0 | N/A | 0 | 0
2022-03-19 09:30 | 2.1962 | 0 | N/A | 0 | 0
2022-03-19 10:00 | 1.5601 | 0 | N/A | 0 | 0
2022-03-19 10:30 | 1.0443 | 0 | N/A | 0 | 0
2022-03-19 11:00 | 0.61711 | 0 | N/A | 0 | 0
2022-03-19 11:30 | -0.69273 | 0 | N/A | 0 | 0
2022-03-19 12:00 | -0.98118 | 0 | N/A | 0 | 0
2022-03-19 12:30 | -1.2454 | 0 | N/A | 0 | 0
2022-03-19 13:00 | -1.44 | 0 | N/A | 0 | 0
2022-03-19 13:30 | -1.6187 | 0 | N/A | 0 | 0
2022-03-19 14:00 | -1.6758 | 0 | N/A | 0 | 0
2022-03-19 14:30 | -1.5326 | 0 | N/A | 0 | 0
2022-03-19 15:00 | -1.2945 | 0 | N/A | 0 | 0
2022-03-19 15:30 | -1.0963 | 0 | N/A | 0 | 0
2022-03-19 16:00 | -0.73504 | 0 | N/A | 0 | 0
2022-03-19 16:30 | -0.45377 | 0 | N/A | 0 | 0
2022-03-19 17:00 | 0.92087 | 0 | N/A | 0 | 0
2022-03-19 17:30 | 1.8689 | 0 | N/A | 0 | 0
2022-03-19 18:00 | 2.9421 | 0 | N/A | 0 | 0
2022-03-19 18:30 | 3.7016 | 0 | N/A | 0 | 0
2022-03-19 19:00 | 4.3078 | 0 | N/A | 0 | 0
2022-03-19 19:30 | 4.5671 | 0 | N/A | 0 | 0
2022-03-19 20:00 | 4.5084 | 0 | N/A | 0 | 0
2022-03-19 20:30 | 4.3529 | 0 | N/A | 0 | 0
2022-03-19 21:00 | 4.1251 | 0 | N/A | 0 | 0
2022-03-19 21:30 | 3.9081 | 0 | N/A | 0 | 0
2022-03-19 22:00 | 3.6752 | 0 | N/A | 0 | 0
2022-03-19 22:30 | 4.021 | 0 | N/A | 0 | 0
2022-03-19 23:00 | 4.1108 | 0 | N/A | 0 | 0
2022-03-19 23:30 | 3.828 | 0 | N/A | 0 | 0
2022-03-20 | 3.8588 | 0 | N/A | 0 | 0
2022-03-20 00:30 | 4.2344 | 0 | N/A | 0 | 0
2022-03-20 01:00 | 4.3824 | 0 | N/A | 0 | 0
2022-03-20 01:30 | 3.6685 | 0 | N/A | 0 | 0
2022-03-20 02:00 | 3.091 | 0 | N/A | 0 | 0
2022-03-20 02:30 | 2.9736 | 0 | N/A | 0 | 0
2022-03-20 03:00 | 2.7391 | 0 | N/A | 0 | 0
2022-03-20 03:30 | 2.4269 | 0 | N/A | 0 | 0
2022-03-20 04:00 | 2.2706 | 0 | N/A | 0 | 0
2022-03-20 04:30 | 2.2273 | 0 | N/A | 0 | 0
2022-03-20 05:00 | 2.1792 | 0 | N/A | 0 | 0
2022-03-20 05:30 | 2.2264 | 0 | N/A | 0 | 0
2022-03-20 06:00 | 2.3014 | 0 | N/A | 0 | 0
2022-03-20 06:30 | 2.5209 | 0 | N/A | 0 | 0
2022-03-20 07:00 | 2.6336 | 0 | N/A | 0 | 0
2022-03-20 07:30 | 2.9329 | 0 | N/A | 0 | 0
2022-03-20 08:00 | 3.0103 | 0 | N/A | 0 | 0
2022-03-20 08:30 | 2.5002 | 0 | N/A | 0 | 0
2022-03-20 09:00 | 2.7417 | 0 | N/A | 0 | 0
2022-03-20 09:30 | 2.8399 | 0 | N/A | 0 | 0
2022-03-20 10:00 | 1.6462 | 0 | N/A | 0 | 0
2022-03-20 10:30 | 1.3326 | 0 | N/A | 0 | 0
2022-03-20 11:00 | 0.8414 | 0 | N/A | 0 | 0
2022-03-20 11:30 | 0.66303 | 0 | N/A | 0 | 0
2022-03-20 12:00 | 0.71118 | 0 | N/A | 0 | 0
2022-03-20 12:30 | 0.58926 | 0 | N/A | 0 | 0
2022-03-20 13:00 | -0.81585 | 0 | N/A | 0 | 0
2022-03-20 13:30 | -1.056 | 0 | N/A | 0 | 0
2022-03-20 14:00 | -0.61994 | 0 | N/A | 0 | 0
2022-03-20 14:30 | 0.7189 | 0 | N/A | 0 | 0
2022-03-20 15:00 | 2.1494 | 0 | N/A | 0 | 0
2022-03-20 15:30 | 2.6379 | 0 | N/A | 0 | 0
2022-03-20 16:00 | 2.6146 | 0 | N/A | 0 | 0
2022-03-20 16:30 | 2.2395 | 0 | N/A | 0 | 0
2022-03-20 17:00 | 1.5727 | 0 | N/A | 0 | 0
2022-03-20 17:30 | 2.3486 | 0 | N/A | 0 | 0
2022-03-20 18:00 | 3.2492 | 0 | N/A | 0 | 0
2022-03-20 18:30 | 4.216 | 0 | N/A | 0 | 0
2022-03-20 19:00 | 4.8254 | 0 | N/A | 0 | 0
2022-03-20 19:30 | 4.951 | 0 | N/A | 0 | 0
2022-03-20 20:00 | 4.9035 | 0 | N/A | 0 | 0
2022-03-20 20:30 | 4.6866 | 0 | N/A | 0 | 0
2022-03-20 21:00 | 4.4932 | 0 | N/A | 0 | 0
2022-03-20 21:30 | 4.113 | 0 | N/A | 0 | 0
2022-03-20 22:00 | 3.7577 | 0 | N/A | 0 | 0
2022-03-20 22:30 | 4.002 | 0 | N/A | 0 | 0
2022-03-20 23:00 | 4.0327 | 0 | N/A | 0 | 0
2022-03-20 23:30 | 3.7643 | 0 | N/A | 0 | 0
2022-03-21 | 3.8254 | 0 | N/A | 0 | 0
2022-03-21 00:30 | 4.2968 | 0 | N/A | 0 | 0
2022-03-21 01:00 | 4.5496 | 0 | N/A | 0 | 0
2022-03-21 01:30 | 3.7624 | 0 | N/A | 0 | 0
2022-03-21 02:00 | 3.184 | 0 | N/A | 0 | 0
2022-03-21 02:30 | 3.0825 | 0 | N/A | 0 | 0
2022-03-21 03:00 | 2.7789 | 0 | N/A | 0 | 0
2022-03-21 03:30 | 2.5046 | 0 | N/A | 0 | 0
2022-03-21 04:00 | 2.3854 | 0 | N/A | 0 | 0
2022-03-21 04:30 | 2.3235 | 0 | N/A | 0 | 0
2022-03-21 05:00 | 2.3561 | 0 | N/A | 0 | 0
2022-03-21 05:30 | 2.5601 | 0 | N/A | 0 | 0
2022-03-21 06:00 | 2.8536 | 0 | N/A | 0 | 0
2022-03-21 06:30 | 3.3943 | 0 | N/A | 0 | 0
2022-03-21 07:00 | 3.9133 | 0 | N/A | 0 | 0
2022-03-21 07:30 | 4.8461 | 0 | N/A | 0 | 0
2022-03-21 08:00 | 5.2927 | 0 | N/A | 0 | 0
2022-03-21 08:30 | 4.7228 | 0 | N/A | 0 | 0
2022-03-21 09:00 | 3.9047 | 0 | N/A | 0 | 0
2022-03-21 09:30 | 3.2189 | 0 | N/A | 0 | 0
2022-03-21 10:00 | 2.5727 | 0 | N/A | 0 | 0
2022-03-21 10:30 | 1.7666 | 0 | N/A | 0 | 0
2022-03-21 11:00 | 1.1937 | 0 | N/A | 0 | 0
2022-03-21 11:30 | 0.72667 | 0 | N/A | 0 | 0
2022-03-21 12:00 | 0.37406 | 0 | N/A | 0 | 0
2022-03-21 12:30 | 0.26386 | 0 | N/A | 0 | 0
2022-03-21 13:00 | -0.37024 | 0 | N/A | 0 | 0
2022-03-21 13:30 | -0.30341 | 0 | N/A | 0 | 0
2022-03-21 14:00 | -0.2119 | 0 | N/A | 0 | 0
2022-03-21 14:30 | 0.15391 | 0 | N/A | 0 | 0
2022-03-21 15:00 | 0.30641 | 0 | N/A | 0 | 0
2022-03-21 15:30 | 0.6467 | 0 | N/A | 0 | 0
2022-03-21 16:00 | 1.2333 | 0 | N/A | 0 | 0
2022-03-21 16:30 | 1.7785 | 0 | N/A | 0 | 0
2022-03-21 17:00 | 2.2441 | 0 | N/A | 0 | 0
2022-03-21 17:30 | 3.3629 | 0 | N/A | 0 | 0
2022-03-21 18:00 | 4.558 | 0 | N/A | 0 | 0
2022-03-21 18:30 | 5.1208 | 0 | N/A | 0 | 0
2022-03-21 19:00 | 5.6352 | 0 | N/A | 0 | 0
2022-03-21 19:30 | 5.4458 | 0 | N/A | 0 | 0
2022-03-21 20:00 | 5.2049 | 0 | N/A | 0 | 0
2022-03-21 20:30 | 5.0243 | 0 | N/A | 0 | 0
2022-03-21 21:00 | 4.7057 | 0 | N/A | 0 | 0
2022-03-21 21:30 | 4.3046 | 0 | N/A | 0 | 0
2022-03-21 22:00 | 3.959 | 0 | N/A | 0 | 0
2022-03-21 22:30 | 4.0888 | 0 | N/A | 0 | 0
2022-03-21 23:00 | 4.078 | 0 | N/A | 0 | 0
2022-03-21 23:30 | 3.7887 | 0 | N/A | 0 | 0
2022-03-22 | 3.7778 | 0 | N/A | 0 | 0
2022-03-22 00:30 | 4.1617 | 0 | N/A | 0 | 0
2022-03-22 01:00 | 4.3999 | 0 | N/A | 0 | 0
2022-03-22 01:30 | 3.5943 | 0 | N/A | 0 | 0
2022-03-22 02:00 | 2.9932 | 0 | N/A | 0 | 0
2022-03-22 02:30 | 2.9077 | 0 | N/A | 0 | 0
2022-03-22 03:00 | 2.6818 | 0 | N/A | 0 | 0
2022-03-22 03:30 | 2.4655 | 0 | N/A | 0 | 0
2022-03-22 04:00 | 2.3273 | 0 | N/A | 0 | 0
2022-03-22 04:30 | 2.3646 | 0 | N/A | 0 | 0
2022-03-22 05:00 | 2.3465 | 0 | N/A | 0 | 0
2022-03-22 05:30 | 2.527 | 0 | N/A | 0 | 0
2022-03-22 06:00 | 2.7756 | 0 | N/A | 0 | 0
2022-03-22 06:30 | 3.3173 | 0 | N/A | 0 | 0
2022-03-22 07:00 | 3.6727 | 0 | N/A | 0 | 0
2022-03-22 07:30 | 4.5524 | 0 | N/A | 0 | 0
2022-03-22 08:00 | 5.0045 | 0 | N/A | 0 | 0
2022-03-22 08:30 | 4.3425 | 0 | N/A | 0 | 0
2022-03-22 09:00 | 4.3636 | 0 | N/A | 0 | 0
2022-03-22 09:30 | 4.1537 | 0 | N/A | 0 | 0
2022-03-22 10:00 | 3.8863 | 0 | N/A | 0 | 0
2022-03-22 10:30 | 3.2811 | 0 | N/A | 0 | 0
2022-03-22 11:00 | 2.3899 | 0 | N/A | 0 | 0
2022-03-22 11:30 | 2.8473 | 0 | N/A | 0 | 0
2022-03-22 12:00 | 2.3944 | 0 | N/A | 0 | 0
2022-03-22 12:30 | 3.3702 | 0 | N/A | 0 | 0
2022-03-22 13:00 | 3.6253 | 0 | N/A | 0 | 0
2022-03-22 13:30 | 3.4865 | 0 | N/A | 0 | 0
2022-03-22 14:00 | 3.7071 | 0 | N/A | 0 | 0
2022-03-22 14:30 | 3.0261 | 0 | N/A | 0 | 0
2022-03-22 15:00 | 2.7477 | 0 | N/A | 0 | 0
2022-03-22 15:30 | 2.5176 | 0 | N/A | 0 | 0
2022-03-22 16:00 | 3.2814 | 0 | N/A | 0 | 0
2022-03-22 16:30 | 3.7978 | 0 | N/A | 0 | 0
2022-03-22 17:00 | 3.9208 | 0 | N/A | 0 | 0
2022-03-22 17:30 | 4.3193 | 0 | N/A | 0 | 0
2022-03-22 18:00 | 4.9183 | 0 | N/A | 0 | 0
2022-03-22 18:30 | 5.2468 | 0 | N/A | 0 | 0
2022-03-22 19:00 | 5.4477 | 0 | N/A | 0 | 0
2022-03-22 19:30 | 5.3841 | 0 | N/A | 0 | 0
2022-03-22 20:00 | 5.3008 | 0 | N/A | 0 | 0
2022-03-22 20:30 | 5.1206 | 0 | N/A | 0 | 0
2022-03-22 21:00 | 4.8228 | 0 | N/A | 0 | 0
2022-03-22 21:30 | 4.4663 | 0 | N/A | 0 | 0
2022-03-22 22:00 | 4.092 | 0 | N/A | 0 | 0
2022-03-22 22:30 | 4.1765 | 0 | N/A | 0 | 0
2022-03-22 23:00 | 4.2701 | 0 | N/A | 0 | 0
2022-03-22 23:30 | 3.9332 | 0 | N/A | 0 | 0
2022-03-23 | 3.9946 | 0 | N/A | 0 | 0
2022-03-23 00:30 | 4.442 | 0 | N/A | 0 | 0
2022-03-23 01:00 | 4.7134 | 0 | N/A | 0 | 0
2022-03-23 01:30 | 3.9243 | 0 | N/A | 0 | 0
2022-03-23 02:00 | 3.284 | 0 | N/A | 0 | 0
2022-03-23 02:30 | 3.1916 | 0 | N/A | 0 | 0
2022-03-23 03:00 | 2.87 | 0 | N/A | 0 | 0
2022-03-23 03:30 | 2.6536 | 0 | N/A | 0 | 0
2022-03-23 04:00 | 2.5537 | 0 | N/A | 0 | 0
2022-03-23 04:30 | 2.5164 | 0 | N/A | 0 | 0
2022-03-23 05:00 | 2.5568 | 0 | N/A | 0 | 0
2022-03-23 05:30 | 2.6646 | 0 | N/A | 0 | 0
2022-03-23 06:00 | 2.9594 | 0 | N/A | 0 | 0
2022-03-23 06:30 | 3.5041 | 0 | N/A | 0 | 0
2022-03-23 07:00 | 4.125 | 0 | N/A | 0 | 0
2022-03-23 07:30 | 5.219 | 0 | N/A | 0 | 0
2022-03-23 08:00 | 5.8287 | 0 | N/A | 0 | 0
2022-03-23 08:30 | 4.8859 | 0 | N/A | 0 | 0
2022-03-23 09:00 | 4.2057 | 0 | N/A | 0 | 0
2022-03-23 09:30 | 3.742 | 0 | N/A | 0 | 0
2022-03-23 10:00 | 3.0789 | 0 | N/A | 0 | 0
2022-03-23 10:30 | 1.8958 | 0 | N/A | 0 | 0
2022-03-23 11:00 | 1.6115 | 0 | N/A | 0 | 0
2022-03-23 11:30 | 2.628 | 0 | N/A | 0 | 0
2022-03-23 12:00 | 3.391 | 0 | N/A | 0 | 0
2022-03-23 12:30 | 2.9048 | 0 | N/A | 0 | 0
2022-03-23 13:00 | 2.8616 | 0 | N/A | 0 | 0
2022-03-23 13:30 | 2.1212 | 0 | N/A | 0 | 0
2022-03-23 14:00 | 1.7182 | 0 | N/A | 0 | 0
2022-03-23 14:30 | 1.697 | 0 | N/A | 0 | 0
2022-03-23 15:00 | 1.2059 | 0 | N/A | 0 | 0
2022-03-23 15:30 | 1.3683 | 0 | N/A | 0 | 0
2022-03-23 16:00 | 2.0344 | 0 | N/A | 0 | 0
2022-03-23 16:30 | 2.4657 | 0 | N/A | 0 | 0
2022-03-23 17:00 | 2.74 | 0 | N/A | 0 | 0
2022-03-23 17:30 | 3.3277 | 0 | N/A | 0 | 0
2022-03-23 18:00 | 3.9192 | 0 | N/A | 0 | 0
2022-03-23 18:30 | 4.5989 | 0 | N/A | 0 | 0
2022-03-23 19:00 | 4.8974 | 0 | N/A | 0 | 0
2022-03-23 19:30 | 5.1358 | 0 | N/A | 0 | 0
2022-03-23 20:00 | 5.2975 | 0 | N/A | 0 | 0
2022-03-23 20:30 | 5.3501 | 0 | N/A | 0 | 0
2022-03-23 21:00 | 5.1206 | 0 | N/A | 0 | 0
2022-03-23 21:30 | 4.8791 | 0 | N/A | 0 | 0
2022-03-23 22:00 | 4.5021 | 0 | N/A | 0 | 0
2022-03-23 22:30 | 4.5798 | 0 | N/A | 0 | 0
2022-03-23 23:00 | 4.6055 | 0 | N/A | 0 | 0
2022-03-23 23:30 | 4.2137 | 0 | N/A | 0 | 0
2022-03-24 | 4.322 | 0 | N/A | 0 | 0
2022-03-27 00:30 | 4.2429 | 0 | N/A | 0 | 0
2022-03-27 01:00 | 4.4919 | 0 | N/A | 0 | 0
2022-03-27 01:30 | 3.7197 | 0 | N/A | 0 | 0
2022-03-27 02:00 | 3.1472 | 0 | N/A | 0 | 0
2022-03-27 02:30 | 3.0642 | 0 | N/A | 0 | 0
2022-03-27 03:00 | 2.7414 | 0 | N/A | 0 | 0
2022-03-27 03:30 | 2.4389 | 0 | N/A | 0 | 0
2022-03-27 04:00 | 2.2744 | 0 | N/A | 0 | 0
2022-03-27 04:30 | 2.2351 | 0 | N/A | 0 | 0
2022-03-27 05:00 | 2.1712 | 0 | N/A | 0 | 0
2022-03-27 05:30 | 2.2566 | 0 | N/A | 0 | 0
2022-03-27 06:00 | 2.3352 | 0 | N/A | 0 | 0
2022-03-27 06:30 | 2.5523 | 0 | N/A | 0 | 0
2022-03-27 07:00 | 2.6664 | 0 | N/A | 0 | 0
2022-03-27 07:30 | 3.0021 | 0 | N/A | 0 | 0
2022-03-27 08:00 | 3.2027 | 0 | N/A | 0 | 0
2022-03-27 08:30 | 3.0475 | 0 | N/A | 0 | 0
2022-03-27 09:00 | 2.705 | 0 | N/A | 0 | 0
2022-03-27 09:30 | 2.2572 | 0 | N/A | 0 | 0
2022-03-27 10:00 | 1.6736 | 0 | N/A | 0 | 0
2022-03-27 10:30 | 1.0537 | 0 | N/A | 0 | 0
2022-03-27 11:00 | 0.6825 | 0 | N/A | 0 | 0
2022-03-27 11:30 | -0.67775 | 0 | N/A | 0 | 0
2022-03-27 12:00 | -0.89862 | 0 | N/A | 0 | 0
2022-03-27 12:30 | -1.0793 | 0 | N/A | 0 | 0
2022-03-27 13:00 | -1.2871 | 0 | N/A | 0 | 0
2022-03-27 13:30 | -1.4131 | 0 | N/A | 0 | 0
2022-03-27 14:00 | -1.245 | 0 | N/A | 0 | 0
2022-03-27 14:30 | -1.0252 | 0 | N/A | 0 | 0
2022-03-27 15:00 | -0.67991 | 0 | N/A | 0 | 0
2022-03-27 15:30 | -0.52028 | 0 | N/A | 0 | 0
2022-03-27 16:00 | 0.49683 | 0 | N/A | 0 | 0
2022-03-27 16:30 | 0.90746 | 0 | N/A | 0 | 0
2022-03-27 17:00 | 1.9656 | 0 | N/A | 0 | 0
2022-03-27 17:30 | 2.8376 | 0 | N/A | 0 | 0
2022-03-27 18:00 | 3.7545 | 0 | N/A | 0 | 0
2022-03-27 18:30 | 4.4746 | 0 | N/A | 0 | 0
2022-03-27 19:00 | 4.9637 | 0 | N/A | 0 | 0
2022-03-27 19:30 | 5.1608 | 0 | N/A | 0 | 0
2022-03-27 20:00 | 5.0985 | 0 | N/A | 0 | 0
2022-03-27 20:30 | 4.6214 | 0 | N/A | 0 | 0
2022-03-27 21:00 | 4.3494 | 0 | N/A | 0 | 0
2022-03-27 21:30 | 4.0628 | 0 | N/A | 0 | 0
2022-03-27 22:00 | 3.7011 | 0 | N/A | 0 | 0
2022-03-27 22:30 | 3.9437 | 0 | N/A | 0 | 0
2022-03-27 23:00 | 4.0109 | 0 | N/A | 0 | 0
2022-03-27 23:30 | 3.7424 | 0 | N/A | 0 | 0
2022-03-28 | 3.8259 | 0 | N/A | 0 | 0
2022-03-28 00:30 | 4.2252 | 0 | N/A | 0 | 0
2022-03-28 01:00 | 4.3911 | 0 | N/A | 0 | 0
2022-03-28 01:30 | 3.6882 | 0 | N/A | 0 | 0
2022-03-28 02:00 | 3.0855 | 0 | N/A | 0 | 0
2022-03-28 02:30 | 2.9925 | 0 | N/A | 0 | 0
2022-03-28 03:00 | 2.7545 | 0 | N/A | 0 | 0
2022-03-28 03:30 | 2.4157 | 0 | N/A | 0 | 0
2022-03-28 04:00 | 2.2461 | 0 | N/A | 0 | 0
2022-03-28 04:30 | 2.2038 | 0 | N/A | 0 | 0
2022-03-28 05:00 | 2.269 | 0 | N/A | 0 | 0
2022-03-28 05:30 | 2.433 | 0 | N/A | 0 | 0
2022-03-28 06:00 | 2.6831 | 0 | N/A | 0 | 0
2022-03-28 06:30 | 3.159 | 0 | N/A | 0 | 0
2022-03-28 07:00 | 3.4886 | 0 | N/A | 0 | 0
2022-03-28 07:30 | 4.5986 | 0 | N/A | 0 | 0
2022-03-28 08:00 | 5.0958 | 0 | N/A | 0 | 0
2022-03-28 08:30 | 4.7493 | 0 | N/A | 0 | 0
2022-03-28 09:00 | 4.5428 | 0 | N/A | 0 | 0
2022-03-28 09:30 | 4.3245 | 0 | N/A | 0 | 0
2022-03-28 10:00 | 4.1891 | 0 | N/A | 0 | 0
2022-03-28 10:30 | 3.2597 | 0 | N/A | 0 | 0
2022-03-28 11:00 | 3.0724 | 0 | N/A | 0 | 0
2022-03-28 11:30 | 2.0162 | 0 | N/A | 0 | 0
2022-03-28 12:00 | 0.38163 | 0 | N/A | 0 | 0
2022-03-28 12:30 | -0.12824 | 0 | N/A | 0 | 0
2022-03-28 13:00 | -0.13437 | 0 | N/A | 0 | 0
2022-03-28 13:30 | -0.39735 | 0 | N/A | 0 | 0
2022-03-28 14:00 | -0.73334 | 0 | N/A | 0 | 0
2022-03-28 14:30 | -0.36014 | 0 | N/A | 0 | 0
2022-03-28 15:00 | 0.22161 | 0 | N/A | 0 | 0
2022-03-28 15:30 | 0.78035 | 0 | N/A | 0 | 0
2022-03-28 16:00 | 1.1777 | 0 | N/A | 0 | 0
2022-03-28 16:30 | 1.4232 | 0 | N/A | 0 | 0
2022-03-28 17:00 | 1.8231 | 0 | N/A | 0 | 0
2022-03-28 17:30 | 3.1278 | 0 | N/A | 0 | 0
2022-03-28 18:00 | 3.9223 | 0 | N/A | 0 | 0
2022-03-28 18:30 | 4.4374 | 0 | N/A | 0 | 0
2022-03-28 19:00 | 4.7503 | 0 | N/A | 0 | 0
2022-03-28 19:30 | 5.0411 | 0 | N/A | 0 | 0
2022-03-28 20:00 | 5.062 | 0 | N/A | 0 | 0
2022-03-28 20:30 | 4.8742 | 0 | N/A | 0 | 0
2022-03-28 21:00 | 4.5249 | 0 | N/A | 0 | 0
2022-03-28 21:30 | 4.1764 | 0 | N/A | 0 | 0
2022-03-28 22:00 | 3.8969 | 0 | N/A | 0 | 0
2022-03-28 22:30 | 4.0989 | 0 | N/A | 0 | 0
2022-03-28 23:00 | 4.1385 | 0 | N/A | 0 | 0
2022-03-28 23:30 | 3.8392 | 0 | N/A | 0 | 0
2022-03-29 | 3.8731 | 0 | N/A | 0 | 0
2022-03-29 00:30 | 4.2325 | 0 | N/A | 0 | 0
2022-03-29 01:00 | 4.5161 | 0 | N/A | 0 | 0
2022-03-29 01:30 | 3.5807 | 0 | N/A | 0 | 0
2022-03-29 02:00 | 2.8877 | 0 | N/A | 0 | 0
2022-03-29 02:30 | 2.8062 | 0 | N/A | 0 | 0
2022-03-29 03:00 | 2.6126 | 0 | N/A | 0 | 0
2022-03-29 03:30 | 2.3693 | 0 | N/A | 0 | 0
2022-03-29 04:00 | 2.2343 | 0 | N/A | 0 | 0
2022-03-29 04:30 | 2.2709 | 0 | N/A | 0 | 0
2022-03-29 05:00 | 2.3204 | 0 | N/A | 0 | 0
2022-03-29 05:30 | 2.4585 | 0 | N/A | 0 | 0
2022-03-29 06:00 | 2.6997 | 0 | N/A | 0 | 0
2022-03-29 06:30 | 3.2424 | 0 | N/A | 0 | 0
2022-03-29 07:00 | 3.795 | 0 | N/A | 0 | 0
2022-03-29 07:30 | 4.6978 | 0 | N/A | 0 | 0
2022-03-29 08:00 | 5.1454 | 0 | N/A | 0 | 0
2022-03-29 08:30 | 4.5759 | 0 | N/A | 0 | 0
2022-03-29 09:00 | 4.3063 | 0 | N/A | 0 | 0
2022-03-29 09:30 | 3.9398 | 0 | N/A | 0 | 0
2022-03-29 10:00 | 3.6893 | 0 | N/A | 0 | 0
2022-03-29 10:30 | 2.8219 | 0 | N/A | 0 | 0
2022-03-29 11:00 | 2.1119 | 0 | N/A | 0 | 0
2022-03-29 11:30 | 1.4114 | 0 | N/A | 0 | 0
2022-03-29 12:00 | 0.85255 | 0 | N/A | 0 | 0
2022-03-29 12:30 | 0.35036 | 0 | N/A | 0 | 0
2022-03-29 13:00 | -0.23898 | 0 | N/A | 0 | 0
2022-03-29 13:30 | -0.50804 | 0 | N/A | 0 | 0
2022-03-29 14:00 | -0.34387 | 0 | N/A | 0 | 0
2022-03-29 14:30 | 0.15723 | 0 | N/A | 0 | 0
2022-03-29 15:00 | 0.24884 | 0 | N/A | 0 | 0
2022-03-29 15:30 | 0.64111 | 0 | N/A | 0 | 0
2022-03-29 16:00 | 0.70317 | 0 | N/A | 0 | 0
2022-03-29 16:30 | 0.59666 | 0 | N/A | 0 | 0
2022-03-29 17:00 | 1.1533 | 0 | N/A | 0 | 0
2022-03-29 17:30 | 2.3398 | 0 | N/A | 0 | 0
2022-03-29 18:00 | 3.5432 | 0 | N/A | 0 | 0
2022-03-29 18:30 | 4.349 | 0 | N/A | 0 | 0
2022-03-29 19:00 | 4.8257 | 0 | N/A | 0 | 0
2022-03-29 19:30 | 4.9944 | 0 | N/A | 0 | 0
2022-03-29 20:00 | 5.0756 | 0 | N/A | 0 | 0
2022-03-29 20:30 | 4.9621 | 0 | N/A | 0 | 0
2022-03-29 21:00 | 4.6134 | 0 | N/A | 0 | 0
2022-03-29 21:30 | 4.2856 | 0 | N/A | 0 | 0
2022-03-29 22:00 | 3.9996 | 0 | N/A | 0 | 0
2022-03-29 22:30 | 4.1854 | 0 | N/A | 0 | 0
2022-03-29 23:00 | 4.2226 | 0 | N/A | 0 | 0
2022-03-29 23:30 | 3.9068 | 0 | N/A | 0 | 0
2022-03-30 | 3.8421 | 0 | N/A | 0 | 0
2022-03-30 00:30 | 4.2825 | 0 | N/A | 0 | 0
2022-03-30 01:00 | 4.5585 | 0 | N/A | 0 | 0
2022-03-30 01:30 | 3.7568 | 0 | N/A | 0 | 0
2022-03-30 02:00 | 3.1583 | 0 | N/A | 0 | 0
2022-03-30 02:30 | 3.0349 | 0 | N/A | 0 | 0
2022-03-30 03:00 | 2.8145 | 0 | N/A | 0 | 0
2022-03-30 03:30 | 2.5163 | 0 | N/A | 0 | 0
2022-03-30 04:00 | 2.4312 | 0 | N/A | 0 | 0
2022-03-30 04:30 | 2.3428 | 0 | N/A | 0 | 0
2022-03-30 05:00 | 2.3701 | 0 | N/A | 0 | 0
2022-03-30 05:30 | 2.5029 | 0 | N/A | 0 | 0
2022-03-30 06:00 | 2.8118 | 0 | N/A | 0 | 0
2022-03-30 06:30 | 3.3637 | 0 | N/A | 0 | 0
2022-03-30 07:00 | 3.8424 | 0 | N/A | 0 | 0
2022-03-30 07:30 | 5.0047 | 0 | N/A | 0 | 0
2022-03-30 08:00 | 5.5848 | 0 | N/A | 0 | 0
2022-03-30 08:30 | 5.1231 | 0 | N/A | 0 | 0
2022-03-30 09:00 | 4.1319 | 0 | N/A | 0 | 0
2022-03-30 09:30 | 3.8943 | 0 | N/A | 0 | 0
2022-03-30 10:00 | 3.227 | 0 | N/A | 0 | 0
2022-03-30 10:30 | 3.2121 | 0 | N/A | 0 | 0
2022-03-30 11:00 | 2.3133 | 0 | N/A | 0 | 0
2022-03-30 11:30 | 2.1231 | 0 | N/A | 0 | 0
2022-03-30 12:00 | 2.3843 | 0 | N/A | 0 | 0
2022-03-30 12:30 | 1.4903 | 0 | N/A | 0 | 0
2022-03-30 13:00 | 0.91304 | 0 | N/A | 0 | 0
2022-03-30 13:30 | 1.5024 | 0 | N/A | 0 | 0
2022-03-30 14:00 | 1.4374 | 0 | N/A | 0 | 0
2022-03-30 14:30 | 1.5001 | 0 | N/A | 0 | 0
2022-03-30 15:00 | 1.6491 | 0 | N/A | 0 | 0
2022-03-30 15:30 | 2.1547 | 0 | N/A | 0 | 0
2022-03-30 16:00 | 2.2843 | 0 | N/A | 0 | 0
2022-03-30 16:30 | 1.7147 | 0 | N/A | 0 | 0
2022-03-30 17:00 | 2.9884 | 0 | N/A | 0 | 0
2022-03-30 17:30 | 2.9624 | 0 | N/A | 0 | 0
2022-03-30 18:00 | 4.1908 | 0 | N/A | 0 | 0
2022-03-30 18:30 | 4.9254 | 0 | N/A | 0 | 0
2022-03-30 19:00 | 5.3172 | 0 | N/A | 0 | 0
2022-03-30 19:30 | 5.4115 | 0 | N/A | 0 | 0
2022-03-30 20:00 | 5.4931 | 0 | N/A | 0 | 0
2022-03-30 20:30 | 5.4594 | 0 | N/A | 0 | 0
2022-03-30 21:00 | 5.1682 | 0 | N/A | 0 | 0
2022-03-30 21:30 | 4.8384 | 0 | N/A | 0 | 0
2022-03-30 22:00 | 4.5303 | 0 | N/A | 0 | 0
2022-03-30 22:30 | 4.6461 | 0 | N/A | 0 | 0
2022-03-30 23:00 | 4.5527 | 0 | N/A | 0 | 0
2022-03-30 23:30 | 4.2421 | 0 | N/A | 0 | 0
2022-03-31 | 4.2735 | 0 | N/A | 0 | 0
2022-03-31 00:30 | 4.6851 | 0 | N/A | 0 | 0
2022-03-31 01:00 | 4.916 | 0 | N/A | 0 | 0
2022-03-31 01:30 | 4.1314 | 0 | N/A | 0 | 0
2022-03-31 02:00 | 3.3829 | 0 | N/A | 0 | 0
2022-03-31 02:30 | 3.3232 | 0 | N/A | 0 | 0
2022-03-31 03:00 | 3.1005 | 0 | N/A | 0 | 0
2022-03-31 03:30 | 2.7615 | 0 | N/A | 0 | 0
2022-03-31 04:00 | 2.655 | 0 | N/A | 0 | 0
2022-03-31 04:30 | 2.6074 | 0 | N/A | 0 | 0
2022-03-31 05:00 | 2.6508 | 0 | N/A | 0 | 0
2022-03-31 05:30 | 2.8151 | 0 | N/A | 0 | 0
2022-03-31 06:00 | 3.1408 | 0 | N/A | 0 | 0
2022-03-31 06:30 | 3.7368 | 0 | N/A | 0 | 0
2022-03-31 07:00 | 4.3279 | 0 | N/A | 0 | 0
2022-03-31 07:30 | 5.8674 | 0 | N/A | 0 | 0
2022-03-31 08:00 | 6.2981 | 0 | N/A | 0 | 0
2022-03-31 08:30 | 5.8149 | 0 | N/A | 0 | 0
2022-03-31 09:00 | 5.6533 | 0 | N/A | 0 | 0
2022-03-31 09:30 | 5.5065 | 0 | N/A | 0 | 0
2022-03-31 10:00 | 5.1091 | 0 | N/A | 0 | 0
2022-03-31 10:30 | 5.0823 | 0 | N/A | 0 | 0
2022-03-31 11:00 | 4.8123 | 0 | N/A | 0 | 0
2022-03-31 11:30 | 4.4255 | 0 | N/A | 0 | 0
2022-03-31 12:00 | 3.9087 | 0 | N/A | 0 | 0
2022-03-31 12:30 | 3.8644 | 0 | N/A | 0 | 0
2022-03-31 13:00 | 3.5331 | 0 | N/A | 0 | 0
2022-03-31 13:30 | 2.8861 | 0 | N/A | 0 | 0
2022-03-31 14:00 | 3.5059 | 0 | N/A | 0 | 0
2022-03-31 14:30 | 4.1068 | 0 | N/A | 0 | 0
2022-03-31 15:00 | 4.0667 | 0 | N/A | 0 | 0
2022-03-31 15:30 | 3.6927 | 0 | N/A | 0 | 0
2022-03-31 16:00 | 3.2978 | 0 | N/A | 0 | 0
2022-03-31 16:30 | 3.5482 | 0 | N/A | 0 | 0
2022-03-31 17:00 | 3.9034 | 0 | N/A | 0 | 0
2022-03-31 17:30 | 4.5584 | 0 | N/A | 0 | 0
2022-03-31 18:00 | 5.3581 | 0 | N/A | 0 | 0
2022-03-31 18:30 | 5.5574 | 0 | N/A | 0 | 0
2022-03-31 19:00 | 5.919 | 0 | N/A | 0 | 0
2022-03-31 19:30 | 6.2817 | 0 | N/A | 0 | 0
2022-03-31 20:00 | 6.5685 | 0 | N/A | 0 | 0
2022-03-31 20:30 | 6.4415 | 0 | N/A | 0 | 0
2022-03-31 21:00 | 6.0538 | 0 | N/A | 0 | 0
2022-03-31 21:30 | 5.6474 | 0 | N/A | 0 | 0
2022-03-31 22:00 | 5.2339 | 0 | N/A | 0 | 0
2022-03-31 22:30 | 5.1979 | 0 | N/A | 0 | 0
2022-03-31 23:00 | 5.1337 | 0 | N/A | 0 | 0
2022-03-31 23:30 | 4.7645 | 0 | N/A | 0 | 0
2022-04-01 | 4.6781 | 0 | N/A | 0 | 0
2022-04-01 00:30 | 4.9312 | 0 | N/A | 0 | 0
2022-04-01 01:00 | 5.2331 | 0 | N/A | 0 | 0
2022-04-01 01:30 | 4.4434 | 0 | N/A | 0 | 0
2022-04-01 02:00 | 3.8687 | 0 | N/A | 0 | 0
2022-04-01 02:30 | 3.7241 | 0 | N/A | 0 | 0
2022-04-01 03:00 | 3.4627 | 0 | N/A | 0 | 0
2022-04-01 03:30 | 3.053 | 0 | N/A | 0 | 0
2022-04-01 04:00 | 2.8318 | 0 | N/A | 0 | 0
2022-04-01 04:30 | 2.7844 | 0 | N/A | 0 | 0
2022-04-01 05:00 | 2.8217 | 0 | N/A | 0 | 0
2022-04-01 05:30 | 2.961 | 0 | N/A | 0 | 0
2022-04-01 06:00 | 3.3014 | 0 | N/A | 0 | 0
2022-04-01 06:30 | 3.968 | 0 | N/A | 0 | 0
2022-04-01 07:00 | 4.6434 | 0 | N/A | 0 | 0
2022-04-01 07:30 | 5.7019 | 0 | N/A | 0 | 0
2022-04-01 08:00 | 6.1689 | 0 | N/A | 0 | 0
2022-04-01 08:30 | 5.5898 | 0 | N/A | 0 | 0
2022-04-01 09:00 | 4.6234 | 0 | N/A | 0 | 0
2022-04-01 09:30 | 3.8828 | 0 | N/A | 0 | 0
2022-04-01 10:00 | 3.1076 | 0 | N/A | 0 | 0
2022-04-01 10:30 | 1.9753 | 0 | N/A | 0 | 0
2022-04-01 11:00 | 2.5404 | 0 | N/A | 0 | 0
2022-04-01 11:30 | 2.0101 | 0 | N/A | 0 | 0
2022-04-01 12:00 | 1.8356 | 0 | N/A | 0 | 0
2022-04-01 12:30 | 1.717 | 0 | N/A | 0 | 0
2022-04-01 13:00 | 1.5769 | 0 | N/A | 0 | 0
2022-04-01 13:30 | 1.5622 | 0 | N/A | 0 | 0
2022-04-01 14:00 | 1.4584 | 0 | N/A | 0 | 0
2022-04-01 14:30 | 2.0979 | 0 | N/A | 0 | 0
2022-04-01 15:00 | 1.979 | 0 | N/A | 0 | 0
2022-04-01 15:30 | 1.6855 | 0 | N/A | 0 | 0
2022-04-01 16:00 | 1.2988 | 0 | N/A | 0 | 0
2022-04-01 16:30 | 1.6818 | 0 | N/A | 0 | 0
2022-04-01 17:00 | 2.5336 | 0 | N/A | 0 | 0
2022-04-01 17:30 | 3.0262 | 0 | N/A | 0 | 0
2022-04-01 18:00 | 4.1622 | 0 | N/A | 0 | 0
2022-04-01 18:30 | 4.7334 | 0 | N/A | 0 | 0
2022-04-01 19:00 | 5.3153 | 0 | N/A | 0 | 0
2022-04-01 19:30 | 5.7683 | 0 | N/A | 0 | 0
2022-04-01 20:00 | 5.9555 | 0 | N/A | 0 | 0
2022-04-01 20:30 | 6.0218 | 0 | N/A | 0 | 0
2022-04-01 21:00 | 5.7978 | 0 | N/A | 0 | 0
2022-04-01 21:30 | 5.391 | 0 | N/A | 0 | 0
2022-04-01 22:00 | 5.0016 | 0 | N/A | 0 | 0
2022-04-01 22:30 | 5.0198 | 0 | N/A | 0 | 0
2022-04-01 23:00 | 5.0497 | 0 | N/A | 0 | 0
2022-04-01 23:30 | 4.6499 | 0 | N/A | 0 | 0
2022-04-02 | 4.6691 | 0 | N/A | 0 | 0
2022-04-02 00:30 | 5.1456 | 0 | N/A | 0 | 0
2022-04-02 01:00 | 5.174 | 0 | N/A | 0 | 0
2022-04-02 01:30 | 4.377 | 0 | N/A | 0 | 0
2022-04-02 02:00 | 3.6358 | 0 | N/A | 0 | 0
2022-04-02 02:30 | 3.5744 | 0 | N/A | 0 | 0
2022-04-02 03:00 | 3.3041 | 0 | N/A | 0 | 0
2022-04-02 03:30 | 2.9107 | 0 | N/A | 0 | 0
2022-04-02 04:00 | 2.7283 | 0 | N/A | 0 | 0
2022-04-02 04:30 | 2.6748 | 0 | N/A | 0 | 0
2022-04-02 05:00 | 2.655 | 0 | N/A | 0 | 0
2022-04-02 05:30 | 2.7029 | 0 | N/A | 0 | 0
2022-04-02 06:00 | 2.7827 | 0 | N/A | 0 | 0
2022-04-02 06:30 | 3.077 | 0 | N/A | 0 | 0
2022-04-02 07:00 | 3.3459 | 0 | N/A | 0 | 0
2022-04-02 07:30 | 3.7597 | 0 | N/A | 0 | 0
2022-04-02 08:00 | 4.0619 | 0 | N/A | 0 | 0
2022-04-02 08:30 | 4.1959 | 0 | N/A | 0 | 0
2022-04-02 09:00 | 4.4525 | 0 | N/A | 0 | 0
2022-04-02 09:30 | 4.651 | 0 | N/A | 0 | 0
2022-04-02 10:00 | 4.5405 | 0 | N/A | 0 | 0
2022-04-02 10:30 | 4.3728 | 0 | N/A | 0 | 0
2022-04-02 11:00 | 3.9021 | 0 | N/A | 0 | 0
2022-04-02 11:30 | 3.863 | 0 | N/A | 0 | 0
2022-04-02 12:00 | 4.1407 | 0 | N/A | 0 | 0
2022-04-02 12:30 | 3.838 | 0 | N/A | 0 | 0
2022-04-02 13:00 | 3.8217 | 0 | N/A | 0 | 0
2022-04-02 13:30 | 3.8995 | 0 | N/A | 0 | 0
2022-04-02 14:00 | 3.9407 | 0 | N/A | 0 | 0
2022-04-02 14:30 | 4.2309 | 0 | N/A | 0 | 0
2022-04-02 15:00 | 4.4993 | 0 | N/A | 0 | 0
2022-04-02 15:30 | 4.3506 | 0 | N/A | 0 | 0
2022-04-02 16:00 | 3.9261 | 0 | N/A | 0 | 0
2022-04-02 16:30 | 4.0172 | 0 | N/A | 0 | 0
2022-04-02 17:00 | 4.3165 | 0 | N/A | 0 | 0
2022-04-02 17:30 | 4.8932 | 0 | N/A | 0 | 0
2022-04-02 18:00 | 5.5627 | 0 | N/A | 0 | 0
2022-04-02 18:30 | 5.9289 | 0 | N/A | 0 | 0
2022-04-02 19:00 | 5.9804 | 0 | N/A | 0 | 0
2022-04-02 19:30 | 5.8258 | 0 | N/A | 0 | 0
2022-04-02 20:00 | 5.7384 | 0 | N/A | 0 | 0
2022-04-02 20:30 | 5.4419 | 0 | N/A | 0 | 0
2022-04-02 21:00 | 5.1091 | 0 | N/A | 0 | 0
2022-04-02 21:30 | 4.9056 | 0 | N/A | 0 | 0
2022-04-02 22:00 | 4.6369 | 0 | N/A | 0 | 0
2022-04-02 22:30 | 4.8761 | 0 | N/A | 0 | 0
2022-04-02 23:00 | 4.9248 | 0 | N/A | 0 | 0
2022-04-02 23:30 | 4.5813 | 0 | N/A | 0 | 0
2022-04-03 | 4.6423 | 0 | N/A | 0 | 0
2022-04-04 00:30 | 4.485 | 0 | N/A | 0 | 0
2022-04-04 01:00 | 3.6905 | 0 | N/A | 0 | 0
2022-04-04 01:30 | 3.5915 | 0 | N/A | 0 | 0
2022-04-04 02:00 | 3.2696 | 0 | N/A | 0 | 0
2022-04-04 02:30 | 2.8634 | 0 | N/A | 0 | 0
2022-04-04 03:00 | 2.651 | 0 | N/A | 0 | 0
2022-04-04 03:30 | 2.5432 | 0 | N/A | 0 | 0
2022-04-04 04:00 | 2.4708 | 0 | N/A | 0 | 0
2022-04-04 04:30 | 2.5245 | 0 | N/A | 0 | 0
2022-04-04 05:00 | 2.5688 | 0 | N/A | 0 | 0
2022-04-04 05:30 | 2.7778 | 0 | N/A | 0 | 0
2022-04-04 06:00 | 3.1124 | 0 | N/A | 0 | 0
2022-04-04 06:30 | 3.7161 | 0 | N/A | 0 | 0
2022-04-04 07:00 | 4.5041 | 0 | N/A | 0 | 0
2022-04-04 07:30 | 5.1203 | 0 | N/A | 0 | 0
2022-04-04 08:00 | 5.4038 | 0 | N/A | 0 | 0
2022-04-04 08:30 | 5.2095 | 0 | N/A | 0 | 0
2022-04-04 09:00 | 4.7323 | 0 | N/A | 0 | 0
2022-04-04 09:30 | 4.6429 | 0 | N/A | 0 | 0
2022-04-04 10:00 | 4.4384 | 0 | N/A | 0 | 0
2022-04-04 10:30 | 3.6515 | 0 | N/A | 0 | 0
2022-04-04 11:00 | 3.4669 | 0 | N/A | 0 | 0
2022-04-04 11:30 | 3.5504 | 0 | N/A | 0 | 0
2022-04-04 12:00 | 4.0908 | 0 | N/A | 0 | 0
2022-04-04 12:30 | 3.9944 | 0 | N/A | 0 | 0
2022-04-04 13:00 | 3.7261 | 0 | N/A | 0 | 0
2022-04-04 13:30 | 4.4375 | 0 | N/A | 0 | 0
2022-04-04 14:00 | 4.5134 | 0 | N/A | 0 | 0
2022-04-04 14:30 | 4.6102 | 0 | N/A | 0 | 0
2022-04-04 15:00 | 4.495 | 0 | N/A | 0 | 0
2022-04-04 15:30 | 3.5598 | 0 | N/A | 0 | 0
2022-04-04 16:00 | 3.1169 | 0 | N/A | 0 | 0
2022-04-04 16:30 | 3.7155 | 0 | N/A | 0 | 0
2022-04-04 17:00 | 4.1904 | 0 | N/A | 0 | 0
2022-04-04 17:30 | 4.8821 | 0 | N/A | 0 | 0
2022-04-04 18:00 | 5.7972 | 0 | N/A | 0 | 0
2022-04-04 18:30 | 6.4859 | 0 | N/A | 0 | 0
2022-04-04 19:00 | 6.7825 | 0 | N/A | 0 | 0
2022-04-04 19:30 | 6.6535 | 0 | N/A | 0 | 0
2022-04-04 20:00 | 6.3543 | 0 | N/A | 0 | 0
2022-04-04 20:30 | 5.9847 | 0 | N/A | 0 | 0
2022-04-04 21:00 | 5.6767 | 0 | N/A | 0 | 0
2022-04-04 21:30 | 6.0216 | 0 | N/A | 0 | 0
2022-04-04 22:00 | 5.9992 | 0 | N/A | 0 | 0
2022-04-04 22:30 | 5.4263 | 0 | N/A | 0 | 0
2022-04-04 23:00 | 5.318 | 0 | N/A | 0 | 0
2022-04-04 23:30 | 5.4849 | 0 | N/A | 0 | 0
2022-04-05 | 5.6971 | 0 | N/A | 0 | 0
2022-04-07 00:30 | 4.39 | 0 | N/A | 0 | 0
2022-04-07 01:00 | 3.7538 | 0 | N/A | 0 | 0
2022-04-07 01:30 | 3.669 | 0 | N/A | 0 | 0
2022-04-07 02:00 | 3.3008 | 0 | N/A | 0 | 0
2022-04-07 02:30 | 2.9458 | 0 | N/A | 0 | 0
2022-04-07 03:00 | 2.7337 | 0 | N/A | 0 | 0
2022-04-07 03:30 | 2.661 | 0 | N/A | 0 | 0
2022-04-07 04:00 | 2.5954 | 0 | N/A | 0 | 0
2022-04-07 04:30 | 2.6469 | 0 | N/A | 0 | 0
2022-04-07 05:00 | 2.69 | 0 | N/A | 0 | 0
2022-04-07 05:30 | 2.8288 | 0 | N/A | 0 | 0
2022-04-07 06:00 | 3.2806 | 0 | N/A | 0 | 0
2022-04-07 06:30 | 3.8434 | 0 | N/A | 0 | 0
2022-04-07 07:00 | 4.612 | 0 | N/A | 0 | 0
2022-04-07 07:30 | 5.0029 | 0 | N/A | 0 | 0
2022-04-07 08:00 | 5.4762 | 0 | N/A | 0 | 0
2022-04-07 08:30 | 5.3928 | 0 | N/A | 0 | 0
2022-04-07 09:00 | 4.9459 | 0 | N/A | 0 | 0
2022-04-07 09:30 | 4.3032 | 0 | N/A | 0 | 0
2022-04-07 10:00 | 3.5029 | 0 | N/A | 0 | 0
2022-04-07 10:30 | 2.7052 | 0 | N/A | 0 | 0
2022-04-07 11:00 | 2.5088 | 0 | N/A | 0 | 0
2022-04-07 11:30 | 1.4473 | 0 | N/A | 0 | 0
2022-04-07 12:00 | 1.5541 | 0 | N/A | 0 | 0
2022-04-07 12:30 | 1.8304 | 0 | N/A | 0 | 0
2022-04-07 13:00 | 2.5817 | 0 | N/A | 0 | 0
2022-04-07 13:30 | 2.7846 | 0 | N/A | 0 | 0
2022-04-07 14:00 | 2.7979 | 0 | N/A | 0 | 0
2022-04-07 14:30 | 2.3121 | 0 | N/A | 0 | 0
2022-04-07 15:00 | 2.3698 | 0 | N/A | 0 | 0
2022-04-07 15:30 | 2.1144 | 0 | N/A | 0 | 0
2022-04-07 16:00 | 2.2262 | 0 | N/A | 0 | 0
2022-04-07 16:30 | 2.4552 | 0 | N/A | 0 | 0
2022-04-07 17:00 | 3.2969 | 0 | N/A | 0 | 0
2022-04-07 17:30 | 4.3127 | 0 | N/A | 0 | 0
2022-04-07 18:00 | 5.0887 | 0 | N/A | 0 | 0
2022-04-07 18:30 | 5.7932 | 0 | N/A | 0 | 0
2022-04-07 19:00 | 6.0943 | 0 | N/A | 0 | 0
2022-04-07 19:30 | 6.0211 | 0 | N/A | 0 | 0
2022-04-07 20:00 | 5.9546 | 0 | N/A | 0 | 0
2022-04-07 20:30 | 5.7239 | 0 | N/A | 0 | 0
2022-04-07 21:00 | 5.3605 | 0 | N/A | 0 | 0
2022-04-07 21:30 | 5.5182 | 0 | N/A | 0 | 0
2022-04-07 22:00 | 5.6198 | 0 | N/A | 0 | 0
2022-04-07 22:30 | 5.0413 | 0 | N/A | 0 | 0
2022-04-07 23:00 | 4.9925 | 0 | N/A | 0 | 0
2022-04-07 23:30 | 5.1455 | 0 | N/A | 0 | 0
2022-04-08 | 5.3841 | 0 | N/A | 0 | 0
2022-04-08 00:30 | 4.4175 | 0 | N/A | 0 | 0
2022-04-08 01:00 | 3.6336 | 0 | N/A | 0 | 0
2022-04-08 01:30 | 3.5249 | 0 | N/A | 0 | 0
2022-04-08 02:00 | 3.2358 | 0 | N/A | 0 | 0
2022-04-08 02:30 | 2.8975 | 0 | N/A | 0 | 0
2022-04-08 03:00 | 2.6837 | 0 | N/A | 0 | 0
2022-04-08 03:30 | 2.6505 | 0 | N/A | 0 | 0
2022-04-08 04:00 | 2.5644 | 0 | N/A | 0 | 0
2022-04-08 04:30 | 2.6074 | 0 | N/A | 0 | 0
2022-04-08 05:00 | 2.6371 | 0 | N/A | 0 | 0
2022-04-08 05:30 | 2.7796 | 0 | N/A | 0 | 0
2022-04-08 06:00 | 3.1794 | 0 | N/A | 0 | 0
2022-04-08 06:30 | 4.1275 | 0 | N/A | 0 | 0
2022-04-08 07:00 | 4.7667 | 0 | N/A | 0 | 0
2022-04-08 07:30 | 5.0153 | 0 | N/A | 0 | 0
2022-04-08 08:00 | 4.8451 | 0 | N/A | 0 | 0
2022-04-08 08:30 | 4.6548 | 0 | N/A | 0 | 0
2022-04-08 09:00 | 3.5318 | 0 | N/A | 0 | 0
2022-04-08 09:30 | 2.3378 | 0 | N/A | 0 | 0
2022-04-08 10:00 | 2.278 | 0 | N/A | 0 | 0
2022-04-08 10:30 | 2.103 | 0 | N/A | 0 | 0
2022-04-08 11:00 | 2.076 | 0 | N/A | 0 | 0
2022-04-08 11:30 | 1.5618 | 0 | N/A | 0 | 0
2022-04-08 12:00 | 0.34647 | 0 | N/A | 0 | 0
2022-04-08 12:30 | 0.50373 | 0 | N/A | 0 | 0
2022-04-08 13:00 | 1.1346 | 0 | N/A | 0 | 0
2022-04-08 13:30 | 1.1108 | 0 | N/A | 0 | 0
2022-04-08 14:00 | 1.5572 | 0 | N/A | 0 | 0
2022-04-08 14:30 | 1.8341 | 0 | N/A | 0 | 0
2022-04-08 15:00 | 2.6182 | 0 | N/A | 0 | 0
2022-04-08 15:30 | 3.4026 | 0 | N/A | 0 | 0
2022-04-08 16:00 | 3.7679 | 0 | N/A | 0 | 0
2022-04-08 16:30 | 3.8461 | 0 | N/A | 0 | 0
2022-04-08 17:00 | 3.9023 | 0 | N/A | 0 | 0
2022-04-08 17:30 | 4.2856 | 0 | N/A | 0 | 0
2022-04-08 18:00 | 4.8919 | 0 | N/A | 0 | 0
2022-04-08 18:30 | 5.2674 | 0 | N/A | 0 | 0
2022-04-08 19:00 | 5.3704 | 0 | N/A | 0 | 0
2022-04-08 19:30 | 5.1611 | 0 | N/A | 0 | 0
2022-04-08 20:00 | 5.0276 | 0 | N/A | 0 | 0
2022-04-08 20:30 | 4.847 | 0 | N/A | 0 | 0
2022-04-08 21:00 | 4.6657 | 0 | N/A | 0 | 0
2022-04-08 21:30 | 5.0176 | 0 | N/A | 0 | 0
2022-04-08 22:00 | 5.0771 | 0 | N/A | 0 | 0
2022-04-08 22:30 | 4.7376 | 0 | N/A | 0 | 0
2022-04-08 23:00 | 4.6602 | 0 | N/A | 0 | 0
2022-04-08 23:30 | 4.9421 | 0 | N/A | 0 | 0
2022-04-09 | 5.0814 | 0 | N/A | 0 | 0
2022-04-09 00:30 | 4.1813 | 0 | N/A | 0 | 0
2022-04-09 01:00 | 3.4954 | 0 | N/A | 0 | 0
2022-04-09 01:30 | 3.4523 | 0 | N/A | 0 | 0
2022-04-09 02:00 | 3.1336 | 0 | N/A | 0 | 0
2022-04-09 02:30 | 2.6928 | 0 | N/A | 0 | 0
2022-04-09 03:00 | 2.554 | 0 | N/A | 0 | 0
2022-04-09 03:30 | 2.4805 | 0 | N/A | 0 | 0
2022-04-09 04:00 | 2.4209 | 0 | N/A | 0 | 0
2022-04-09 04:30 | 2.4312 | 0 | N/A | 0 | 0
2022-04-09 05:00 | 2.4419 | 0 | N/A | 0 | 0
2022-04-09 05:30 | 2.5031 | 0 | N/A | 0 | 0
2022-04-09 06:00 | 2.6332 | 0 | N/A | 0 | 0
2022-04-09 06:30 | 2.8674 | 0 | N/A | 0 | 0
2022-04-09 07:00 | 3.0455 | 0 | N/A | 0 | 0
2022-04-09 07:30 | 3.0815 | 0 | N/A | 0 | 0
2022-04-09 08:00 | 2.9514 | 0 | N/A | 0 | 0
2022-04-09 08:30 | 3.409 | 0 | N/A | 0 | 0
2022-04-09 09:00 | 3.1012 | 0 | N/A | 0 | 0
2022-04-09 09:30 | 2.5737 | 0 | N/A | 0 | 0
2022-04-09 10:00 | 2.5962 | 0 | N/A | 0 | 0
2022-04-09 10:30 | 2.6373 | 0 | N/A | 0 | 0
2022-04-09 11:00 | 2.7924 | 0 | N/A | 0 | 0
2022-04-09 11:30 | 2.4308 | 0 | N/A | 0 | 0
2022-04-09 12:00 | 1.5996 | 0 | N/A | 0 | 0
2022-04-09 12:30 | 1.1822 | 0 | N/A | 0 | 0
2022-04-09 13:00 | 1.8821 | 0 | N/A | 0 | 0
2022-04-09 13:30 | 1.6997 | 0 | N/A | 0 | 0
2022-04-09 14:00 | 0.77615 | 0 | N/A | 0 | 0
2022-04-09 14:30 | 0.56105 | 0 | N/A | 0 | 0
2022-04-09 15:00 | 0.66236 | 0 | N/A | 0 | 0
2022-04-09 15:30 | 0.91129 | 0 | N/A | 0 | 0
2022-04-09 16:00 | 2.0599 | 0 | N/A | 0 | 0
2022-04-09 16:30 | 2.2508 | 0 | N/A | 0 | 0
2022-04-09 17:00 | 2.9418 | 0 | N/A | 0 | 0
2022-04-09 17:30 | 3.8499 | 0 | N/A | 0 | 0
2022-04-09 18:00 | 4.6639 | 0 | N/A | 0 | 0
2022-04-09 18:30 | 5.205 | 0 | N/A | 0 | 0
2022-04-09 19:00 | 5.3849 | 0 | N/A | 0 | 0
2022-04-09 19:30 | 5.0509 | 0 | N/A | 0 | 0
2022-04-09 20:00 | 4.8345 | 0 | N/A | 0 | 0
2022-04-09 20:30 | 4.4697 | 0 | N/A | 0 | 0
2022-04-09 21:00 | 4.2314 | 0 | N/A | 0 | 0
2022-04-09 21:30 | 4.5724 | 0 | N/A | 0 | 0
2022-04-09 22:00 | 4.7182 | 0 | N/A | 0 | 0
2022-04-09 22:30 | 4.3963 | 0 | N/A | 0 | 0
2022-04-09 23:00 | 4.4425 | 0 | N/A | 0 | 0
2022-04-09 23:30 | 4.8169 | 0 | N/A | 0 | 0
2022-04-10 | 5.1054 | 0 | N/A | 0 | 0
2022-04-10 00:30 | 4.3029 | 0 | N/A | 0 | 0
2022-04-10 01:00 | 3.6095 | 0 | N/A | 0 | 0
2022-04-10 01:30 | 3.4912 | 0 | N/A | 0 | 0
2022-04-10 02:00 | 3.0657 | 0 | N/A | 0 | 0
2022-04-10 02:30 | 2.7491 | 0 | N/A | 0 | 0
2022-04-10 03:00 | 2.5316 | 0 | N/A | 0 | 0
2022-04-10 03:30 | 2.3927 | 0 | N/A | 0 | 0
2022-04-10 04:00 | 2.3475 | 0 | N/A | 0 | 0
2022-04-10 04:30 | 2.3669 | 0 | N/A | 0 | 0
2022-04-10 05:00 | 2.2932 | 0 | N/A | 0 | 0
2022-04-10 05:30 | 2.3549 | 0 | N/A | 0 | 0
2022-04-10 06:00 | 2.45 | 0 | N/A | 0 | 0
2022-04-10 06:30 | 2.6761 | 0 | N/A | 0 | 0
2022-04-10 07:00 | 2.8633 | 0 | N/A | 0 | 0
2022-04-10 07:30 | 2.8605 | 0 | N/A | 0 | 0
2022-04-10 08:00 | 2.9147 | 0 | N/A | 0 | 0
2022-04-10 08:30 | 2.9561 | 0 | N/A | 0 | 0
2022-04-10 09:00 | 2.7607 | 0 | N/A | 0 | 0
2022-04-10 09:30 | 2.3761 | 0 | N/A | 0 | 0
2022-04-10 10:00 | 1.5367 | 0 | N/A | 0 | 0
2022-04-10 10:30 | 0.98268 | 0 | N/A | 0 | 0
2022-04-10 11:00 | -0.6708 | 0 | N/A | 0 | 0
2022-04-10 11:30 | -0.96944 | 0 | N/A | 0 | 0
2022-04-10 12:00 | -1.1312 | 0 | N/A | 0 | 0
2022-04-10 12:30 | -1.1374 | 0 | N/A | 0 | 0
2022-04-10 13:00 | -1.0929 | 0 | N/A | 0 | 0
2022-04-10 13:30 | -1.0121 | 0 | N/A | 0 | 0
2022-04-10 14:00 | -0.65021 | 0 | N/A | 0 | 0
2022-04-10 14:30 | -0.56337 | 0 | N/A | 0 | 0
2022-04-10 15:00 | 0.66641 | 0 | N/A | 0 | 0
2022-04-10 15:30 | 1.8295 | 0 | N/A | 0 | 0
2022-04-10 16:00 | 2.6829 | 0 | N/A | 0 | 0
2022-04-10 16:30 | 3.054 | 0 | N/A | 0 | 0
2022-04-10 17:00 | 3.6122 | 0 | N/A | 0 | 0
2022-04-10 17:30 | 4.7446 | 0 | N/A | 0 | 0
2022-04-10 18:00 | 5.2303 | 0 | N/A | 0 | 0
2022-04-10 18:30 | 5.5668 | 0 | N/A | 0 | 0
2022-04-10 19:00 | 5.5886 | 0 | N/A | 0 | 0
2022-04-10 19:30 | 5.2031 | 0 | N/A | 0 | 0
2022-04-10 20:00 | 4.8081 | 0 | N/A | 0 | 0
2022-04-10 20:30 | 4.3937 | 0 | N/A | 0 | 0
2022-04-10 21:00 | 4.0752 | 0 | N/A | 0 | 0
2022-04-10 21:30 | 4.4359 | 0 | N/A | 0 | 0
2022-04-10 22:00 | 4.5452 | 0 | N/A | 0 | 0
2022-04-10 22:30 | 4.3023 | 0 | N/A | 0 | 0
2022-04-10 23:00 | 4.369 | 0 | N/A | 0 | 0
2022-04-10 23:30 | 4.5733 | 0 | N/A | 0 | 0
2022-04-11 | 4.8277 | 0 | N/A | 0 | 0
2022-04-11 00:30 | 4.0528 | 0 | N/A | 0 | 0
2022-04-11 01:00 | 3.4526 | 0 | N/A | 0 | 0
2022-04-11 01:30 | 3.2944 | 0 | N/A | 0 | 0
2022-04-11 02:00 | 2.9393 | 0 | N/A | 0 | 0
2022-04-11 02:30 | 2.5295 | 0 | N/A | 0 | 0
2022-04-11 03:00 | 2.4269 | 0 | N/A | 0 | 0
2022-04-11 03:30 | 2.35 | 0 | N/A | 0 | 0
2022-04-11 04:00 | 2.3434 | 0 | N/A | 0 | 0
2022-04-11 04:30 | 2.3946 | 0 | N/A | 0 | 0
2022-04-11 05:00 | 2.4642 | 0 | N/A | 0 | 0
2022-04-11 05:30 | 2.658 | 0 | N/A | 0 | 0
2022-04-11 06:00 | 2.9448 | 0 | N/A | 0 | 0
2022-04-11 06:30 | 3.3794 | 0 | N/A | 0 | 0
2022-04-11 07:00 | 3.6997 | 0 | N/A | 0 | 0
2022-04-11 07:30 | 4.0733 | 0 | N/A | 0 | 0
2022-04-11 08:00 | 4.545 | 0 | N/A | 0 | 0
2022-04-11 08:30 | 5 | 0 | N/A | 0 | 0
2022-04-11 09:00 | 4.9301 | 0 | N/A | 0 | 0
2022-04-11 09:30 | 4.4865 | 0 | N/A | 0 | 0
2022-04-11 10:00 | 3.7351 | 0 | N/A | 0 | 0
2022-04-11 10:30 | 2.1336 | 0 | N/A | 0 | 0
2022-04-11 11:00 | 2.0299 | 0 | N/A | 0 | 0
2022-04-11 11:30 | 2.1493 | 0 | N/A | 0 | 0
2022-04-11 12:00 | 3.0377 | 0 | N/A | 0 | 0
2022-04-11 12:30 | 1.9416 | 0 | N/A | 0 | 0
2022-04-11 13:00 | 1.5533 | 0 | N/A | 0 | 0
2022-04-11 13:30 | 1.1183 | 0 | N/A | 0 | 0
2022-04-11 14:00 | 0.64722 | 0 | N/A | 0 | 0
2022-04-11 14:30 | 1.165 | 0 | N/A | 0 | 0
2022-04-11 15:00 | 1.2451 | 0 | N/A | 0 | 0
2022-04-11 15:30 | 1.4524 | 0 | N/A | 0 | 0
2022-04-11 16:00 | 1.934 | 0 | N/A | 0 | 0
2022-04-11 16:30 | 2.3719 | 0 | N/A | 0 | 0
2022-04-11 17:00 | 2.9041 | 0 | N/A | 0 | 0
2022-04-11 17:30 | 4.1113 | 0 | N/A | 0 | 0
2022-04-11 18:00 | 5.4575 | 0 | N/A | 0 | 0
2022-04-11 18:30 | 6.2572 | 0 | N/A | 0 | 0
2022-04-11 19:00 | 6.4246 | 0 | N/A | 0 | 0
2022-04-11 19:30 | 6.1705 | 0 | N/A | 0 | 0
2022-04-11 20:00 | 5.9063 | 0 | N/A | 0 | 0
2022-04-11 20:30 | 5.6696 | 0 | N/A | 0 | 0
2022-04-11 21:00 | 5.3737 | 0 | N/A | 0 | 0
2022-04-11 21:30 | 5.6627 | 0 | N/A | 0 | 0
2022-04-11 22:00 | 5.7042 | 0 | N/A | 0 | 0
2022-04-11 22:30 | 5.2476 | 0 | N/A | 0 | 0
2022-04-11 23:00 | 5.0842 | 0 | N/A | 0 | 0
2022-04-11 23:30 | 5.4304 | 0 | N/A | 0 | 0
2022-04-12 | 5.6286 | 0 | N/A | 0 | 0
2022-04-12 00:30 | 4.8397 | 0 | N/A | 0 | 0
2022-04-12 01:00 | 4.109 | 0 | N/A | 0 | 0
2022-04-12 01:30 | 3.9094 | 0 | N/A | 0 | 0
2022-04-12 02:00 | 3.5679 | 0 | N/A | 0 | 0
2022-04-12 02:30 | 3.1977 | 0 | N/A | 0 | 0
2022-04-12 03:00 | 3.0573 | 0 | N/A | 0 | 0
2022-04-12 03:30 | 2.9179 | 0 | N/A | 0 | 0
2022-04-12 04:00 | 2.8146 | 0 | N/A | 0 | 0
2022-04-12 04:30 | 2.8477 | 0 | N/A | 0 | 0
2022-04-12 05:00 | 2.8969 | 0 | N/A | 0 | 0
2022-04-12 05:30 | 3.1262 | 0 | N/A | 0 | 0
2022-04-12 06:00 | 3.5634 | 0 | N/A | 0 | 0
2022-04-12 06:30 | 4.2154 | 0 | N/A | 0 | 0
2022-04-12 07:00 | 4.5664 | 0 | N/A | 0 | 0
2022-04-12 07:30 | 4.9353 | 0 | N/A | 0 | 0
2022-04-12 08:00 | 5.4852 | 0 | N/A | 0 | 0
2022-04-12 08:30 | 5.3464 | 0 | N/A | 0 | 0
2022-04-12 09:00 | 4.5728 | 0 | N/A | 0 | 0
2022-04-12 09:30 | 3.811 | 0 | N/A | 0 | 0
2022-04-12 10:00 | 2.8215 | 0 | N/A | 0 | 0
2022-04-12 10:30 | 3.0985 | 0 | N/A | 0 | 0
2022-04-12 11:00 | 3.2679 | 0 | N/A | 0 | 0
2022-04-12 11:30 | 2.4034 | 0 | N/A | 0 | 0
2022-04-12 12:00 | 1.3598 | 0 | N/A | 0 | 0
2022-04-12 12:30 | 0.44614 | 0 | N/A | 0 | 0
2022-04-12 13:00 | -0.27131 | 0 | N/A | 0 | 0
2022-04-12 13:30 | -0.71361 | 0 | N/A | 0 | 0
2022-04-12 14:00 | -0.43748 | 0 | N/A | 0 | 0
2022-04-12 14:30 | 0.37431 | 0 | N/A | 0 | 0
2022-04-12 15:00 | 0.84885 | 0 | N/A | 0 | 0
2022-04-12 15:30 | 1.3886 | 0 | N/A | 0 | 0
2022-04-12 16:00 | 1.8415 | 0 | N/A | 0 | 0
2022-04-12 16:30 | 2.6774 | 0 | N/A | 0 | 0
2022-04-12 17:00 | 3.222 | 0 | N/A | 0 | 0
2022-04-12 17:30 | 4.4506 | 0 | N/A | 0 | 0
2022-04-12 18:00 | 5.8007 | 0 | N/A | 0 | 0
2022-04-12 18:30 | 6.5449 | 0 | N/A | 0 | 0
2022-04-12 19:00 | 6.734 | 0 | N/A | 0 | 0
2022-04-12 19:30 | 6.5563 | 0 | N/A | 0 | 0
2022-04-12 20:00 | 6.3259 | 0 | N/A | 0 | 0
2022-04-12 20:30 | 6.0426 | 0 | N/A | 0 | 0
2022-04-12 21:00 | 5.7027 | 0 | N/A | 0 | 0
2022-04-12 21:30 | 5.8692 | 0 | N/A | 0 | 0
2022-04-12 22:00 | 5.8445 | 0 | N/A | 0 | 0
2022-04-12 22:30 | 5.1933 | 0 | N/A | 0 | 0
2022-04-12 23:00 | 5.0899 | 0 | N/A | 0 | 0
2022-04-12 23:30 | 5.3466 | 0 | N/A | 0 | 0
2022-04-13 | 5.5617 | 0 | N/A | 0 | 0
2022-04-15 00:30 | 4.3411 | 0 | N/A | 0 | 0
2022-04-15 01:00 | 3.5867 | 0 | N/A | 0 | 0
2022-04-15 01:30 | 3.4016 | 0 | N/A | 0 | 0
2022-04-15 02:00 | 3.1344 | 0 | N/A | 0 | 0
2022-04-15 02:30 | 2.7083 | 0 | N/A | 0 | 0
2022-04-15 03:00 | 2.503 | 0 | N/A | 0 | 0
2022-04-15 03:30 | 2.3857 | 0 | N/A | 0 | 0
2022-04-15 04:00 | 2.3291 | 0 | N/A | 0 | 0
2022-04-15 04:30 | 2.334 | 0 | N/A | 0 | 0
2022-04-15 05:00 | 2.3491 | 0 | N/A | 0 | 0
2022-04-15 05:30 | 2.4151 | 0 | N/A | 0 | 0
2022-04-15 06:00 | 2.485 | 0 | N/A | 0 | 0
2022-04-15 06:30 | 2.6112 | 0 | N/A | 0 | 0
2022-04-15 07:00 | 2.6961 | 0 | N/A | 0 | 0
2022-04-15 07:30 | 2.7484 | 0 | N/A | 0 | 0
2022-04-15 08:00 | 2.7245 | 0 | N/A | 0 | 0
2022-04-15 08:30 | 2.5105 | 0 | N/A | 0 | 0
2022-04-15 09:00 | 2.4913 | 0 | N/A | 0 | 0
2022-04-15 09:30 | 2.5174 | 0 | N/A | 0 | 0
2022-04-15 10:00 | 1.5872 | 0 | N/A | 0 | 0
2022-04-15 10:30 | 1.2036 | 0 | N/A | 0 | 0
2022-04-15 11:00 | 1.2754 | 0 | N/A | 0 | 0
2022-04-15 11:30 | 0.79 | 0 | N/A | 0 | 0
2022-04-15 12:00 | -0.77702 | 0 | N/A | 0 | 0
2022-04-15 12:30 | -0.83507 | 0 | N/A | 0 | 0
2022-04-15 13:00 | -0.81358 | 0 | N/A | 0 | 0
2022-04-15 13:30 | -0.79311 | 0 | N/A | 0 | 0
2022-04-15 14:00 | 0.79901 | 0 | N/A | 0 | 0
2022-04-15 14:30 | 1.1362 | 0 | N/A | 0 | 0
2022-04-15 15:00 | 1.601 | 0 | N/A | 0 | 0
2022-04-15 15:30 | 2.0737 | 0 | N/A | 0 | 0
2022-04-15 16:00 | 2.5762 | 0 | N/A | 0 | 0
2022-04-15 16:30 | 2.6978 | 0 | N/A | 0 | 0
2022-04-15 17:00 | 3.1898 | 0 | N/A | 0 | 0
2022-04-15 17:30 | 3.8056 | 0 | N/A | 0 | 0
2022-04-15 18:00 | 4.4525 | 0 | N/A | 0 | 0
2022-04-15 18:30 | 4.7572 | 0 | N/A | 0 | 0
2022-04-15 19:00 | 4.6779 | 0 | N/A | 0 | 0
2022-04-15 19:30 | 4.4133 | 0 | N/A | 0 | 0
2022-04-15 20:00 | 4.2041 | 0 | N/A | 0 | 0
2022-04-15 20:30 | 4.0532 | 0 | N/A | 0 | 0
2022-04-15 21:00 | 3.8564 | 0 | N/A | 0 | 0
2022-04-15 21:30 | 4.222 | 0 | N/A | 0 | 0
2022-04-15 22:00 | 4.4211 | 0 | N/A | 0 | 0
2022-04-15 22:30 | 4.1094 | 0 | N/A | 0 | 0
2022-04-15 23:00 | 4.1296 | 0 | N/A | 0 | 0
2022-04-15 23:30 | 4.6478 | 0 | N/A | 0 | 0
2022-04-16 | 4.8265 | 0 | N/A | 0 | 0
2022-04-16 00:30 | 4.0965 | 0 | N/A | 0 | 0
2022-04-16 01:00 | 3.4806 | 0 | N/A | 0 | 0
2022-04-16 01:30 | 3.3942 | 0 | N/A | 0 | 0
2022-04-16 02:00 | 3.0386 | 0 | N/A | 0 | 0
2022-04-16 02:30 | 2.6775 | 0 | N/A | 0 | 0
2022-04-16 03:00 | 2.5122 | 0 | N/A | 0 | 0
2022-04-16 03:30 | 2.3558 | 0 | N/A | 0 | 0
2022-04-16 04:00 | 2.3248 | 0 | N/A | 0 | 0
2022-04-16 04:30 | 2.3176 | 0 | N/A | 0 | 0
2022-04-16 05:00 | 2.3336 | 0 | N/A | 0 | 0
2022-04-16 05:30 | 2.4855 | 0 | N/A | 0 | 0
2022-04-16 06:00 | 2.5677 | 0 | N/A | 0 | 0
2022-04-16 06:30 | 2.7837 | 0 | N/A | 0 | 0
2022-04-16 07:00 | 2.9185 | 0 | N/A | 0 | 0
2022-04-16 07:30 | 2.8364 | 0 | N/A | 0 | 0
2022-04-16 08:00 | 2.6956 | 0 | N/A | 0 | 0
2022-04-16 08:30 | 2.4449 | 0 | N/A | 0 | 0
2022-04-16 09:00 | 1.9524 | 0 | N/A | 0 | 0
2022-04-16 09:30 | 1.4306 | 0 | N/A | 0 | 0
2022-04-16 10:00 | 0.88726 | 0 | N/A | 0 | 0
2022-04-16 10:30 | -0.7053 | 0 | N/A | 0 | 0
2022-04-16 11:00 | -0.86575 | 0 | N/A | 0 | 0
2022-04-16 11:30 | -1.1572 | 0 | N/A | 0 | 0
2022-04-16 12:00 | -1.3689 | 0 | N/A | 0 | 0
2022-04-16 12:30 | -1.3306 | 0 | N/A | 0 | 0
2022-04-16 13:00 | -1.3179 | 0 | N/A | 0 | 0
2022-04-16 13:30 | -1.258 | 0 | N/A | 0 | 0
2022-04-16 14:00 | -1.0793 | 0 | N/A | 0 | 0
2022-04-16 14:30 | -0.82043 | 0 | N/A | 0 | 0
2022-04-16 15:00 | -0.60093 | 0 | N/A | 0 | 0
2022-04-16 15:30 | 0.73824 | 0 | N/A | 0 | 0
2022-04-16 16:00 | 1.2629 | 0 | N/A | 0 | 0
2022-04-16 16:30 | 2.048 | 0 | N/A | 0 | 0
2022-04-16 17:00 | 2.8873 | 0 | N/A | 0 | 0
2022-04-16 17:30 | 3.7384 | 0 | N/A | 0 | 0
2022-04-16 18:00 | 4.4393 | 0 | N/A | 0 | 0
2022-04-16 18:30 | 4.6953 | 0 | N/A | 0 | 0
2022-04-16 19:00 | 4.669 | 0 | N/A | 0 | 0
2022-04-16 19:30 | 4.4287 | 0 | N/A | 0 | 0
2022-04-16 20:00 | 4.1943 | 0 | N/A | 0 | 0
2022-04-16 20:30 | 3.8783 | 0 | N/A | 0 | 0
2022-04-16 21:00 | 3.7117 | 0 | N/A | 0 | 0
2022-04-16 21:30 | 4.0964 | 0 | N/A | 0 | 0
2022-04-16 22:00 | 4.1814 | 0 | N/A | 0 | 0
2022-04-16 22:30 | 4.0019 | 0 | N/A | 0 | 0
2022-04-16 23:00 | 4.0972 | 0 | N/A | 0 | 0
2022-04-16 23:30 | 4.4075 | 0 | N/A | 0 | 0
2022-04-17 | 4.6038 | 0 | N/A | 0 | 0
2022-04-17 00:30 | 3.8272 | 0 | N/A | 0 | 0
2022-04-17 01:00 | 3.2395 | 0 | N/A | 0 | 0
2022-04-17 01:30 | 3.1571 | 0 | N/A | 0 | 0
2022-04-17 02:00 | 2.8641 | 0 | N/A | 0 | 0
2022-04-17 02:30 | 2.4746 | 0 | N/A | 0 | 0
2022-04-17 03:00 | 2.3021 | 0 | N/A | 0 | 0
2022-04-17 03:30 | 2.214 | 0 | N/A | 0 | 0
2022-04-17 04:00 | 2.126 | 0 | N/A | 0 | 0
2022-04-17 04:30 | 2.1211 | 0 | N/A | 0 | 0
2022-04-17 05:00 | 2.101 | 0 | N/A | 0 | 0
2022-04-17 05:30 | 2.2198 | 0 | N/A | 0 | 0
2022-04-17 06:00 | 2.2889 | 0 | N/A | 0 | 0
2022-04-17 06:30 | 2.4875 | 0 | N/A | 0 | 0
2022-04-17 07:00 | 2.5334 | 0 | N/A | 0 | 0
2022-04-17 07:30 | 2.4885 | 0 | N/A | 0 | 0
2022-04-17 08:00 | 2.5171 | 0 | N/A | 0 | 0
2022-04-17 08:30 | 2.5339 | 0 | N/A | 0 | 0
2022-04-17 09:00 | 2.4536 | 0 | N/A | 0 | 0
2022-04-17 09:30 | 1.5996 | 0 | N/A | 0 | 0
2022-04-17 10:00 | 0.87431 | 0 | N/A | 0 | 0
2022-04-17 10:30 | -0.762 | 0 | N/A | 0 | 0
2022-04-17 11:00 | -0.83556 | 0 | N/A | 0 | 0
2022-04-17 11:30 | -1.0114 | 0 | N/A | 0 | 0
2022-04-17 12:00 | -0.96803 | 0 | N/A | 0 | 0
2022-04-17 12:30 | -0.99206 | 0 | N/A | 0 | 0
2022-04-17 13:00 | -0.97801 | 0 | N/A | 0 | 0
2022-04-17 13:30 | -0.99941 | 0 | N/A | 0 | 0
2022-04-17 14:00 | -0.68646 | 0 | N/A | 0 | 0
2022-04-17 14:30 | 0.69385 | 0 | N/A | 0 | 0
2022-04-17 15:00 | 1.5089 | 0 | N/A | 0 | 0
2022-04-17 15:30 | 2.1864 | 0 | N/A | 0 | 0
2022-04-17 16:00 | 2.4282 | 0 | N/A | 0 | 0
2022-04-17 16:30 | 3.222 | 0 | N/A | 0 | 0
2022-04-17 17:00 | 3.693 | 0 | N/A | 0 | 0
2022-04-17 17:30 | 4.1647 | 0 | N/A | 0 | 0
2022-04-17 18:00 | 4.7212 | 0 | N/A | 0 | 0
2022-04-17 18:30 | 4.9145 | 0 | N/A | 0 | 0
2022-04-17 19:00 | 4.8174 | 0 | N/A | 0 | 0
2022-04-17 19:30 | 4.4715 | 0 | N/A | 0 | 0
2022-04-17 20:00 | 4.1341 | 0 | N/A | 0 | 0
2022-04-17 20:30 | 3.9229 | 0 | N/A | 0 | 0
2022-04-17 21:00 | 3.7243 | 0 | N/A | 0 | 0
2022-04-17 21:30 | 4.1297 | 0 | N/A | 0 | 0
2022-04-17 22:00 | 4.2453 | 0 | N/A | 0 | 0
2022-04-17 22:30 | 4.052 | 0 | N/A | 0 | 0
2022-04-17 23:00 | 4.1821 | 0 | N/A | 0 | 0
2022-04-17 23:30 | 4.6163 | 0 | N/A | 0 | 0
2022-04-18 | 4.7487 | 0 | N/A | 0 | 0
2022-04-18 00:30 | 3.9859 | 0 | N/A | 0 | 0
2022-04-18 01:00 | 3.3436 | 0 | N/A | 0 | 0
2022-04-18 01:30 | 3.2247 | 0 | N/A | 0 | 0
2022-04-18 02:00 | 2.8816 | 0 | N/A | 0 | 0
2022-04-18 02:30 | 2.5269 | 0 | N/A | 0 | 0
2022-04-18 03:00 | 2.3573 | 0 | N/A | 0 | 0
2022-04-18 03:30 | 2.2592 | 0 | N/A | 0 | 0
2022-04-18 04:00 | 2.1695 | 0 | N/A | 0 | 0
2022-04-18 04:30 | 2.1741 | 0 | N/A | 0 | 0
2022-04-18 05:00 | 2.1964 | 0 | N/A | 0 | 0
2022-04-18 05:30 | 2.3632 | 0 | N/A | 0 | 0
2022-04-18 06:00 | 2.43 | 0 | N/A | 0 | 0
2022-04-18 06:30 | 2.5297 | 0 | N/A | 0 | 0
2022-04-18 07:00 | 2.6437 | 0 | N/A | 0 | 0
2022-04-18 07:30 | 2.7206 | 0 | N/A | 0 | 0
2022-04-18 08:00 | 3.0426 | 0 | N/A | 0 | 0
2022-04-18 08:30 | 3.3477 | 0 | N/A | 0 | 0
2022-04-18 09:00 | 3.5028 | 0 | N/A | 0 | 0
2022-04-18 09:30 | 3.8212 | 0 | N/A | 0 | 0
2022-04-18 10:00 | 3.8658 | 0 | N/A | 0 | 0
2022-04-18 10:30 | 4.001 | 0 | N/A | 0 | 0
2022-04-18 11:00 | 3.4359 | 0 | N/A | 0 | 0
2022-04-18 11:30 | 3.2312 | 0 | N/A | 0 | 0
2022-04-18 12:00 | 2.5615 | 0 | N/A | 0 | 0
2022-04-18 12:30 | 3.2285 | 0 | N/A | 0 | 0
2022-04-18 13:00 | 3.4628 | 0 | N/A | 0 | 0
2022-04-18 13:30 | 3.5378 | 0 | N/A | 0 | 0
2022-04-18 14:00 | 3.8494 | 0 | N/A | 0 | 0
2022-04-18 14:30 | 3.9628 | 0 | N/A | 0 | 0
2022-04-18 15:00 | 4.1886 | 0 | N/A | 0 | 0
2022-04-18 15:30 | 4.5192 | 0 | N/A | 0 | 0
2022-04-18 16:00 | 4.7291 | 0 | N/A | 0 | 0
2022-04-18 16:30 | 5.0291 | 0 | N/A | 0 | 0
2022-04-18 17:00 | 5.4831 | 0 | N/A | 0 | 0
2022-04-18 17:30 | 5.9688 | 0 | N/A | 0 | 0
2022-04-18 18:00 | 6.5056 | 0 | N/A | 0 | 0
2022-04-18 18:30 | 6.5932 | 0 | N/A | 0 | 0
2022-04-18 19:00 | 6.2715 | 0 | N/A | 0 | 0
2022-04-18 19:30 | 5.9682 | 0 | N/A | 0 | 0
2022-04-18 20:00 | 5.6437 | 0 | N/A | 0 | 0
2022-04-18 20:30 | 5.3705 | 0 | N/A | 0 | 0
2022-04-18 21:00 | 5.0052 | 0 | N/A | 0 | 0
2022-04-18 21:30 | 5.3392 | 0 | N/A | 0 | 0
2022-04-18 22:00 | 5.36 | 0 | N/A | 0 | 0
2022-04-18 22:30 | 4.8474 | 0 | N/A | 0 | 0
2022-04-18 23:00 | 4.7784 | 0 | N/A | 0 | 0
2022-04-18 23:30 | 4.9716 | 0 | N/A | 0 | 0
2022-04-19 | 5.1461 | 0 | N/A | 0 | 0
2022-04-20 00:30 | 5.1775 | 0 | N/A | 0 | 0
2022-04-20 01:00 | 4.3948 | 0 | N/A | 0 | 0
2022-04-20 01:30 | 4.2766 | 0 | N/A | 0 | 0
2022-04-20 02:00 | 3.9447 | 0 | N/A | 0 | 0
2022-04-20 02:30 | 3.4775 | 0 | N/A | 0 | 0
2022-04-20 03:00 | 3.2113 | 0 | N/A | 0 | 0
2022-04-20 03:30 | 3.038 | 0 | N/A | 0 | 0
2022-04-20 04:00 | 2.909 | 0 | N/A | 0 | 0
2022-04-20 04:30 | 2.9547 | 0 | N/A | 0 | 0
2022-04-20 05:00 | 2.9855 | 0 | N/A | 0 | 0
2022-04-20 05:30 | 3.1574 | 0 | N/A | 0 | 0
2022-04-20 06:00 | 3.6096 | 0 | N/A | 0 | 0
2022-04-20 06:30 | 4.141 | 0 | N/A | 0 | 0
2022-04-20 07:00 | 4.5489 | 0 | N/A | 0 | 0
2022-04-20 07:30 | 4.708 | 0 | N/A | 0 | 0
2022-04-20 08:00 | 5.6089 | 0 | N/A | 0 | 0
2022-04-20 08:30 | 5.9995 | 0 | N/A | 0 | 0
2022-04-20 09:00 | 5.6261 | 0 | N/A | 0 | 0
2022-04-20 09:30 | 5.5932 | 0 | N/A | 0 | 0
2022-04-20 10:00 | 5.3542 | 0 | N/A | 0 | 0
2022-04-20 10:30 | 4.7477 | 0 | N/A | 0 | 0
2022-04-20 11:00 | 4.3998 | 0 | N/A | 0 | 0
2022-04-20 11:30 | 2.6401 | 0 | N/A | 0 | 0
2022-04-20 12:00 | 3.2923 | 0 | N/A | 0 | 0
2022-04-20 12:30 | 3.6906 | 0 | N/A | 0 | 0
2022-04-20 13:00 | 3.1283 | 0 | N/A | 0 | 0
2022-04-20 13:30 | 3.3805 | 0 | N/A | 0 | 0
2022-04-20 14:00 | 2.9659 | 0 | N/A | 0 | 0
2022-04-20 14:30 | 3.5794 | 0 | N/A | 0 | 0
2022-04-20 15:00 | 3.7761 | 0 | N/A | 0 | 0
2022-04-20 15:30 | 3.4476 | 0 | N/A | 0 | 0
2022-04-20 16:00 | 3.2026 | 0 | N/A | 0 | 0
2022-04-20 16:30 | 4.2214 | 0 | N/A | 0 | 0
2022-04-20 17:00 | 4.7391 | 0 | N/A | 0 | 0
2022-04-20 17:30 | 5.4526 | 0 | N/A | 0 | 0
2022-04-20 18:00 | 6.3944 | 0 | N/A | 0 | 0
2022-04-20 18:30 | 7.0144 | 0 | N/A | 0 | 0
2022-04-20 19:00 | 7.0366 | 0 | N/A | 0 | 0
2022-04-20 19:30 | 6.7613 | 0 | N/A | 0 | 0
2022-04-20 20:00 | 6.5719 | 0 | N/A | 0 | 0
2022-04-20 20:30 | 6.3185 | 0 | N/A | 0 | 0
2022-04-20 21:00 | 5.9963 | 0 | N/A | 0 | 0
2022-04-20 21:30 | 6.3163 | 0 | N/A | 0 | 0
2022-04-20 22:00 | 6.289 | 0 | N/A | 0 | 0
2022-04-20 22:30 | 5.7128 | 0 | N/A | 0 | 0
2022-04-20 23:00 | 5.6949 | 0 | N/A | 0 | 0
2022-04-20 23:30 | 5.8677 | 0 | N/A | 0 | 0
2022-04-21 | 5.9761 | 0 | N/A | 0 | 0
2022-04-21 00:30 | 5.1422 | 0 | N/A | 0 | 0
2022-04-21 01:00 | 4.2536 | 0 | N/A | 0 | 0
2022-04-21 01:30 | 4.0953 | 0 | N/A | 0 | 0
2022-04-21 02:00 | 3.7937 | 0 | N/A | 0 | 0
2022-04-21 02:30 | 3.4094 | 0 | N/A | 0 | 0
2022-04-21 03:00 | 3.1598 | 0 | N/A | 0 | 0
2022-04-21 03:30 | 2.9698 | 0 | N/A | 0 | 0
2022-04-21 04:00 | 2.9063 | 0 | N/A | 0 | 0
2022-04-21 04:30 | 2.9083 | 0 | N/A | 0 | 0
2022-04-21 05:00 | 2.9567 | 0 | N/A | 0 | 0
2022-04-21 05:30 | 3.1401 | 0 | N/A | 0 | 0
2022-04-21 06:00 | 3.5091 | 0 | N/A | 0 | 0
2022-04-21 06:30 | 4.0221 | 0 | N/A | 0 | 0
2022-04-21 07:00 | 4.4397 | 0 | N/A | 0 | 0
2022-04-21 07:30 | 4.7533 | 0 | N/A | 0 | 0
2022-04-21 08:00 | 4.9121 | 0 | N/A | 0 | 0
2022-04-21 08:30 | 4.9434 | 0 | N/A | 0 | 0
2022-04-21 09:00 | 4.7431 | 0 | N/A | 0 | 0
2022-04-21 09:30 | 4.474 | 0 | N/A | 0 | 0
2022-04-21 10:00 | 4.3984 | 0 | N/A | 0 | 0
2022-04-21 10:30 | 3.905 | 0 | N/A | 0 | 0
2022-04-21 11:00 | 3.7458 | 0 | N/A | 0 | 0
2022-04-21 11:30 | 3.7603 | 0 | N/A | 0 | 0
2022-04-21 12:00 | 3.7002 | 0 | N/A | 0 | 0
2022-04-21 12:30 | 4.0503 | 0 | N/A | 0 | 0
2022-04-21 13:00 | 4.0846 | 0 | N/A | 0 | 0
2022-04-21 13:30 | 4.6053 | 0 | N/A | 0 | 0
2022-04-21 14:00 | 4.1298 | 0 | N/A | 0 | 0
2022-04-21 14:30 | 4.6662 | 0 | N/A | 0 | 0
2022-04-21 15:00 | 4.7885 | 0 | N/A | 0 | 0
2022-04-21 15:30 | 5.0151 | 0 | N/A | 0 | 0
2022-04-21 16:00 | 5.0359 | 0 | N/A | 0 | 0
2022-04-21 16:30 | 4.9083 | 0 | N/A | 0 | 0
2022-04-21 17:00 | 5.515 | 0 | N/A | 0 | 0
2022-04-21 17:30 | 6.3061 | 0 | N/A | 0 | 0
2022-04-21 18:00 | 7.1425 | 0 | N/A | 0 | 0
2022-04-21 18:30 | 7.6162 | 0 | N/A | 0 | 0
2022-04-21 19:00 | 7.6436 | 0 | N/A | 0 | 0
2022-04-21 19:30 | 7.3695 | 0 | N/A | 0 | 0
2022-04-21 20:00 | 7.0229 | 0 | N/A | 0 | 0
2022-04-21 20:30 | 6.749 | 0 | N/A | 0 | 0
2022-04-21 21:00 | 6.3929 | 0 | N/A | 0 | 0
2022-04-21 21:30 | 6.5523 | 0 | N/A | 0 | 0
2022-04-21 22:00 | 6.4913 | 0 | N/A | 0 | 0
2022-04-21 22:30 | 5.9041 | 0 | N/A | 0 | 0
2022-04-21 23:00 | 5.646 | 0 | N/A | 0 | 0
2022-04-21 23:30 | 5.9124 | 0 | N/A | 0 | 0
2022-04-22 | 5.9705 | 0 | N/A | 0 | 0
2022-04-22 00:30 | 5.218 | 0 | N/A | 0 | 0
2022-04-22 01:00 | 4.4668 | 0 | N/A | 0 | 0
2022-04-22 01:30 | 4.2646 | 0 | N/A | 0 | 0
2022-04-22 02:00 | 3.8734 | 0 | N/A | 0 | 0
2022-04-22 02:30 | 3.4348 | 0 | N/A | 0 | 0
2022-04-22 03:00 | 3.2051 | 0 | N/A | 0 | 0
2022-04-22 03:30 | 3.0524 | 0 | N/A | 0 | 0
2022-04-22 04:00 | 2.9151 | 0 | N/A | 0 | 0
2022-04-22 04:30 | 2.927 | 0 | N/A | 0 | 0
2022-04-22 05:00 | 2.9946 | 0 | N/A | 0 | 0
2022-04-22 05:30 | 3.1779 | 0 | N/A | 0 | 0
2022-04-22 06:00 | 3.5473 | 0 | N/A | 0 | 0
2022-04-22 06:30 | 4.133 | 0 | N/A | 0 | 0
2022-04-22 07:00 | 4.4797 | 0 | N/A | 0 | 0
2022-04-22 07:30 | 4.8158 | 0 | N/A | 0 | 0
2022-04-22 08:00 | 4.8621 | 0 | N/A | 0 | 0
2022-04-22 08:30 | 4.6951 | 0 | N/A | 0 | 0
2022-04-22 09:00 | 4.0683 | 0 | N/A | 0 | 0
2022-04-22 09:30 | 3.1803 | 0 | N/A | 0 | 0
2022-04-22 10:00 | 2.7003 | 0 | N/A | 0 | 0
2022-04-22 10:30 | 2.3606 | 0 | N/A | 0 | 0
2022-04-22 11:00 | 1.3197 | 0 | N/A | 0 | 0
2022-04-22 11:30 | 0.91349 | 0 | N/A | 0 | 0
2022-04-22 12:00 | 0.47391 | 0 | N/A | 0 | 0
2022-04-22 12:30 | 0.51152 | 0 | N/A | 0 | 0
2022-04-22 13:00 | 1.0442 | 0 | N/A | 0 | 0
2022-04-22 13:30 | 1.1576 | 0 | N/A | 0 | 0
2022-04-22 14:00 | 0.9708 | 0 | N/A | 0 | 0
2022-04-22 14:30 | 1.5022 | 0 | N/A | 0 | 0
2022-04-22 15:00 | 1.177 | 0 | N/A | 0 | 0
2022-04-22 15:30 | 1.7799 | 0 | N/A | 0 | 0
2022-04-22 16:00 | 2.6084 | 0 | N/A | 0 | 0
2022-04-22 16:30 | 3.4175 | 0 | N/A | 0 | 0
2022-04-22 17:00 | 4.1038 | 0 | N/A | 0 | 0
2022-04-22 17:30 | 5.1154 | 0 | N/A | 0 | 0
2022-04-22 18:00 | 6.1075 | 0 | N/A | 0 | 0
2022-04-22 18:30 | 6.7897 | 0 | N/A | 0 | 0
2022-04-22 19:00 | 6.9684 | 0 | N/A | 0 | 0
2022-04-22 19:30 | 6.8168 | 0 | N/A | 0 | 0
2022-04-22 20:00 | 6.6591 | 0 | N/A | 0 | 0
2022-04-22 20:30 | 6.5034 | 0 | N/A | 0 | 0
2022-04-22 21:00 | 6.292 | 0 | N/A | 0 | 0
2022-04-22 21:30 | 6.6109 | 0 | N/A | 0 | 0
2022-04-22 22:00 | 6.7667 | 0 | N/A | 0 | 0
2022-04-22 22:30 | 6.1052 | 0 | N/A | 0 | 0
2022-04-22 23:00 | 6.003 | 0 | N/A | 0 | 0
2022-04-22 23:30 | 6.1327 | 0 | N/A | 0 | 0
2022-04-23 | 6.1877 | 0 | N/A | 0 | 0
2022-04-23 00:30 | 5.4012 | 0 | N/A | 0 | 0
2022-04-23 01:00 | 4.7484 | 0 | N/A | 0 | 0
2022-04-23 01:30 | 4.5508 | 0 | N/A | 0 | 0
2022-04-23 02:00 | 4.0897 | 0 | N/A | 0 | 0
2022-04-23 02:30 | 3.7083 | 0 | N/A | 0 | 0
2022-04-23 03:00 | 3.5197 | 0 | N/A | 0 | 0
2022-04-23 03:30 | 3.3007 | 0 | N/A | 0 | 0
2022-04-23 04:00 | 3.2509 | 0 | N/A | 0 | 0
2022-04-23 04:30 | 3.1756 | 0 | N/A | 0 | 0
2022-04-23 05:00 | 3.1885 | 0 | N/A | 0 | 0
2022-04-23 05:30 | 3.2753 | 0 | N/A | 0 | 0
2022-04-23 06:00 | 3.5007 | 0 | N/A | 0 | 0
2022-04-23 06:30 | 3.8386 | 0 | N/A | 0 | 0
2022-04-23 07:00 | 4.0929 | 0 | N/A | 0 | 0
2022-04-23 07:30 | 4.1612 | 0 | N/A | 0 | 0
2022-04-23 08:00 | 4.4675 | 0 | N/A | 0 | 0
2022-04-23 08:30 | 4.6646 | 0 | N/A | 0 | 0
2022-04-23 09:00 | 3.9393 | 0 | N/A | 0 | 0
2022-04-23 09:30 | 3.0875 | 0 | N/A | 0 | 0
2022-04-23 10:00 | 2.2985 | 0 | N/A | 0 | 0
2022-04-23 10:30 | 1.4733 | 0 | N/A | 0 | 0
2022-04-23 11:00 | 0.86107 | 0 | N/A | 0 | 0
2022-04-23 11:30 | 0.67067 | 0 | N/A | 0 | 0
2022-04-23 12:00 | -0.76624 | 0 | N/A | 0 | 0
2022-04-23 12:30 | -0.8914 | 0 | N/A | 0 | 0
2022-04-23 13:00 | -0.90608 | 0 | N/A | 0 | 0
2022-04-23 13:30 | -0.8307 | 0 | N/A | 0 | 0
2022-04-23 14:00 | -0.82906 | 0 | N/A | 0 | 0
2022-04-23 14:30 | -0.76105 | 0 | N/A | 0 | 0
2022-04-23 15:00 | 0.78504 | 0 | N/A | 0 | 0
2022-04-23 15:30 | 1.2151 | 0 | N/A | 0 | 0
2022-04-23 16:00 | 1.8653 | 0 | N/A | 0 | 0
2022-04-23 16:30 | 2.5338 | 0 | N/A | 0 | 0
2022-04-23 17:00 | 3.6587 | 0 | N/A | 0 | 0
2022-04-23 17:30 | 4.6791 | 0 | N/A | 0 | 0
2022-04-23 18:00 | 5.6427 | 0 | N/A | 0 | 0
2022-04-23 18:30 | 6.224 | 0 | N/A | 0 | 0
2022-04-23 19:00 | 6.3235 | 0 | N/A | 0 | 0
2022-04-23 19:30 | 6.068 | 0 | N/A | 0 | 0
2022-04-23 20:00 | 5.8978 | 0 | N/A | 0 | 0
2022-04-23 20:30 | 5.6729 | 0 | N/A | 0 | 0
2022-04-23 21:00 | 5.4386 | 0 | N/A | 0 | 0
2022-04-23 21:30 | 5.7738 | 0 | N/A | 0 | 0
2022-04-23 22:00 | 5.8501 | 0 | N/A | 0 | 0
2022-04-23 22:30 | 5.425 | 0 | N/A | 0 | 0
2022-04-23 23:00 | 5.4435 | 0 | N/A | 0 | 0
2022-04-23 23:30 | 5.6376 | 0 | N/A | 0 | 0
2022-04-24 | 5.7399 | 0 | N/A | 0 | 0
2022-04-24 00:30 | 4.9934 | 0 | N/A | 0 | 0
2022-04-24 01:00 | 4.3707 | 0 | N/A | 0 | 0
2022-04-24 01:30 | 4.2892 | 0 | N/A | 0 | 0
2022-04-24 02:00 | 3.8875 | 0 | N/A | 0 | 0
2022-04-24 02:30 | 3.4525 | 0 | N/A | 0 | 0
2022-04-24 03:00 | 3.1773 | 0 | N/A | 0 | 0
2022-04-24 03:30 | 3.0157 | 0 | N/A | 0 | 0
2022-04-24 04:00 | 2.9648 | 0 | N/A | 0 | 0
2022-04-24 04:30 | 2.8612 | 0 | N/A | 0 | 0
2022-04-24 05:00 | 2.8771 | 0 | N/A | 0 | 0
2022-04-24 05:30 | 2.9821 | 0 | N/A | 0 | 0
2022-04-24 06:00 | 3.0893 | 0 | N/A | 0 | 0
2022-04-24 06:30 | 3.4829 | 0 | N/A | 0 | 0
2022-04-24 07:00 | 3.6937 | 0 | N/A | 0 | 0
2022-04-24 07:30 | 3.6968 | 0 | N/A | 0 | 0
2022-04-24 08:00 | 3.7263 | 0 | N/A | 0 | 0
2022-04-24 08:30 | 3.486 | 0 | N/A | 0 | 0
2022-04-24 09:00 | 2.9581 | 0 | N/A | 0 | 0
2022-04-24 09:30 | 2.2854 | 0 | N/A | 0 | 0
2022-04-24 10:00 | 1.5664 | 0 | N/A | 0 | 0
2022-04-24 10:30 | 1.05 | 0 | N/A | 0 | 0
2022-04-24 11:00 | 0.74394 | 0 | N/A | 0 | 0
2022-04-24 11:30 | -0.76185 | 0 | N/A | 0 | 0
2022-04-24 12:00 | -1.0378 | 0 | N/A | 0 | 0
2022-04-24 12:30 | -1.0832 | 0 | N/A | 0 | 0
2022-04-24 13:00 | -1.0318 | 0 | N/A | 0 | 0
2022-04-24 13:30 | -1.02 | 0 | N/A | 0 | 0
2022-04-24 14:00 | -0.96208 | 0 | N/A | 0 | 0
2022-04-24 14:30 | -0.73663 | 0 | N/A | 0 | 0
2022-04-24 15:00 | 0.7073 | 0 | N/A | 0 | 0
2022-04-24 15:30 | 1.0124 | 0 | N/A | 0 | 0
2022-04-24 16:00 | 1.6513 | 0 | N/A | 0 | 0
2022-04-24 16:30 | 2.5072 | 0 | N/A | 0 | 0
2022-04-24 17:00 | 3.5095 | 0 | N/A | 0 | 0
2022-04-24 17:30 | 4.7041 | 0 | N/A | 0 | 0
2022-04-24 18:00 | 5.7891 | 0 | N/A | 0 | 0
2022-04-24 18:30 | 6.3201 | 0 | N/A | 0 | 0
2022-04-24 19:00 | 6.3795 | 0 | N/A | 0 | 0
2022-04-24 19:30 | 6.0996 | 0 | N/A | 0 | 0
2022-04-24 20:00 | 5.8606 | 0 | N/A | 0 | 0
2022-04-24 20:30 | 5.571 | 0 | N/A | 0 | 0
2022-04-24 21:00 | 5.3452 | 0 | N/A | 0 | 0
2022-04-24 21:30 | 5.7183 | 0 | N/A | 0 | 0
2022-04-24 22:00 | 5.8071 | 0 | N/A | 0 | 0
2022-04-24 22:30 | 5.5165 | 0 | N/A | 0 | 0
2022-04-24 23:00 | 5.4197 | 0 | N/A | 0 | 0
2022-04-24 23:30 | 5.5541 | 0 | N/A | 0 | 0
2022-04-25 | 5.7772 | 0 | N/A | 0 | 0
2022-04-25 00:30 | 4.9373 | 0 | N/A | 0 | 0
2022-04-25 01:00 | 4.3152 | 0 | N/A | 0 | 0
2022-04-25 01:30 | 4.2051 | 0 | N/A | 0 | 0
2022-04-25 02:00 | 3.84 | 0 | N/A | 0 | 0
2022-04-25 02:30 | 3.4266 | 0 | N/A | 0 | 0
2022-04-25 03:00 | 3.1526 | 0 | N/A | 0 | 0
2022-04-25 03:30 | 3.0209 | 0 | N/A | 0 | 0
2022-04-25 04:00 | 2.9621 | 0 | N/A | 0 | 0
2022-04-25 04:30 | 2.9242 | 0 | N/A | 0 | 0
2022-04-25 05:00 | 3.0402 | 0 | N/A | 0 | 0
2022-04-25 05:30 | 3.1464 | 0 | N/A | 0 | 0
2022-04-25 06:00 | 3.2437 | 0 | N/A | 0 | 0
2022-04-25 06:30 | 3.507 | 0 | N/A | 0 | 0
2022-04-25 07:00 | 3.743 | 0 | N/A | 0 | 0
2022-04-25 07:30 | 3.6668 | 0 | N/A | 0 | 0
2022-04-25 08:00 | 3.7403 | 0 | N/A | 0 | 0
2022-04-25 08:30 | 3.5755 | 0 | N/A | 0 | 0
2022-04-25 09:00 | 3.2047 | 0 | N/A | 0 | 0
2022-04-25 09:30 | 2.5679 | 0 | N/A | 0 | 0
2022-04-25 10:00 | 1.7921 | 0 | N/A | 0 | 0
2022-04-25 10:30 | 1.0419 | 0 | N/A | 0 | 0
2022-04-25 11:00 | 0.643 | 0 | N/A | 0 | 0
2022-04-25 11:30 | -0.72361 | 0 | N/A | 0 | 0
2022-04-25 12:00 | -0.8908 | 0 | N/A | 0 | 0
2022-04-25 12:30 | 0.7167 | 0 | N/A | 0 | 0
2022-04-25 13:00 | -0.73552 | 0 | N/A | 0 | 0
2022-04-25 13:30 | 0.69897 | 0 | N/A | 0 | 0
2022-04-25 14:00 | -0.7513 | 0 | N/A | 0 | 0
2022-04-25 14:30 | 0.78035 | 0 | N/A | 0 | 0
2022-04-25 15:00 | 1.2225 | 0 | N/A | 0 | 0
2022-04-25 15:30 | 2.249 | 0 | N/A | 0 | 0
2022-04-25 16:00 | 2.4708 | 0 | N/A | 0 | 0
2022-04-25 16:30 | 3.3341 | 0 | N/A | 0 | 0
2022-04-25 17:00 | 4.1027 | 0 | N/A | 0 | 0
2022-04-25 17:30 | 4.8859 | 0 | N/A | 0 | 0
2022-04-25 18:00 | 5.7272 | 0 | N/A | 0 | 0
2022-04-25 18:30 | 6.3977 | 0 | N/A | 0 | 0
2022-04-25 19:00 | 6.3912 | 0 | N/A | 0 | 0
2022-04-25 19:30 | 6.0522 | 0 | N/A | 0 | 0
2022-04-25 20:00 | 5.8511 | 0 | N/A | 0 | 0
2022-04-25 20:30 | 5.588 | 0 | N/A | 0 | 0
2022-04-25 21:00 | 5.2051 | 0 | N/A | 0 | 0
2022-04-25 21:30 | 5.5008 | 0 | N/A | 0 | 0
2022-04-25 22:00 | 5.515 | 0 | N/A | 0 | 0
2022-04-25 22:30 | 5.099 | 0 | N/A | 0 | 0
2022-04-25 23:00 | 5.0181 | 0 | N/A | 0 | 0
2022-04-25 23:30 | 5.2019 | 0 | N/A | 0 | 0
2022-04-26 | 5.4579 | 0 | N/A | 0 | 0
2022-04-26 00:30 | 4.8118 | 0 | N/A | 0 | 0
2022-04-26 01:00 | 4.1851 | 0 | N/A | 0 | 0
2022-04-26 01:30 | 3.9836 | 0 | N/A | 0 | 0
2022-04-26 02:00 | 3.6693 | 0 | N/A | 0 | 0
2022-04-26 02:30 | 3.2385 | 0 | N/A | 0 | 0
2022-04-26 03:00 | 2.9729 | 0 | N/A | 0 | 0
2022-04-26 03:30 | 2.8966 | 0 | N/A | 0 | 0
2022-04-26 04:00 | 2.8235 | 0 | N/A | 0 | 0
2022-04-26 04:30 | 2.7355 | 0 | N/A | 0 | 0
2022-04-26 05:00 | 2.797 | 0 | N/A | 0 | 0
2022-04-26 05:30 | 3.073 | 0 | N/A | 0 | 0
2022-04-26 06:00 | 3.4739 | 0 | N/A | 0 | 0
2022-04-26 06:30 | 4.3067 | 0 | N/A | 0 | 0
2022-04-26 07:00 | 4.8598 | 0 | N/A | 0 | 0
2022-04-26 07:30 | 5.1063 | 0 | N/A | 0 | 0
2022-04-26 08:00 | 5.0139 | 0 | N/A | 0 | 0
2022-04-26 08:30 | 4.623 | 0 | N/A | 0 | 0
2022-04-26 09:00 | 3.5908 | 0 | N/A | 0 | 0
2022-04-26 09:30 | 2.5989 | 0 | N/A | 0 | 0
2022-04-26 10:00 | 1.7876 | 0 | N/A | 0 | 0
2022-04-26 10:30 | 1.1185 | 0 | N/A | 0 | 0
2022-04-26 11:00 | 0.56382 | 0 | N/A | 0 | 0
2022-04-26 11:30 | 0.44806 | 0 | N/A | 0 | 0
2022-04-26 12:00 | -0.27427 | 0 | N/A | 0 | 0
2022-04-26 12:30 | -0.42354 | 0 | N/A | 0 | 0
2022-04-26 13:00 | -0.30203 | 0 | N/A | 0 | 0
2022-04-26 13:30 | 0.67812 | 0 | N/A | 0 | 0
2022-04-26 14:00 | 1.7167 | 0 | N/A | 0 | 0
2022-04-26 14:30 | 2.6691 | 0 | N/A | 0 | 0
2022-04-26 15:00 | 2.9015 | 0 | N/A | 0 | 0
2022-04-26 15:30 | 3.1642 | 0 | N/A | 0 | 0
2022-04-26 16:00 | 3.3542 | 0 | N/A | 0 | 0
2022-04-26 16:30 | 3.9151 | 0 | N/A | 0 | 0
2022-04-26 17:00 | 4.5227 | 0 | N/A | 0 | 0
2022-04-26 17:30 | 5.4203 | 0 | N/A | 0 | 0
2022-04-26 18:00 | 6.0962 | 0 | N/A | 0 | 0
2022-04-26 18:30 | 6.5269 | 0 | N/A | 0 | 0
2022-04-26 19:00 | 6.3896 | 0 | N/A | 0 | 0
2022-04-26 19:30 | 6.0732 | 0 | N/A | 0 | 0
2022-04-26 20:00 | 5.828 | 0 | N/A | 0 | 0
2022-04-26 20:30 | 5.541 | 0 | N/A | 0 | 0
2022-04-26 21:00 | 5.2154 | 0 | N/A | 0 | 0
2022-04-26 21:30 | 5.3726 | 0 | N/A | 0 | 0
2022-04-26 22:00 | 5.4257 | 0 | N/A | 0 | 0
2022-04-26 22:30 | 4.871 | 0 | N/A | 0 | 0
2022-04-26 23:00 | 4.8066 | 0 | N/A | 0 | 0
2022-04-26 23:30 | 4.9704 | 0 | N/A | 0 | 0
2022-04-27 | 5.2174 | 0 | N/A | 0 | 0
2022-04-27 00:30 | 4.3585 | 0 | N/A | 0 | 0
2022-04-27 01:00 | 3.6899 | 0 | N/A | 0 | 0
2022-04-27 01:30 | 3.5882 | 0 | N/A | 0 | 0
2022-04-27 02:00 | 3.3497 | 0 | N/A | 0 | 0
2022-04-27 02:30 | 2.9453 | 0 | N/A | 0 | 0
2022-04-27 03:00 | 2.7372 | 0 | N/A | 0 | 0
2022-04-27 03:30 | 2.6508 | 0 | N/A | 0 | 0
2022-04-27 04:00 | 2.5385 | 0 | N/A | 0 | 0
2022-04-27 04:30 | 2.5265 | 0 | N/A | 0 | 0
2022-04-27 05:00 | 2.6069 | 0 | N/A | 0 | 0
2022-04-27 05:30 | 2.7642 | 0 | N/A | 0 | 0
2022-04-27 06:00 | 3.0556 | 0 | N/A | 0 | 0
2022-04-27 06:30 | 3.7736 | 0 | N/A | 0 | 0
2022-04-27 07:00 | 4.322 | 0 | N/A | 0 | 0
2022-04-27 07:30 | 4.5564 | 0 | N/A | 0 | 0
2022-04-27 08:00 | 4.9122 | 0 | N/A | 0 | 0
2022-04-27 08:30 | 4.7357 | 0 | N/A | 0 | 0
2022-04-27 09:00 | 4.3714 | 0 | N/A | 0 | 0
2022-04-27 09:30 | 3.457 | 0 | N/A | 0 | 0
2022-04-27 10:00 | 3.2109 | 0 | N/A | 0 | 0
2022-04-27 10:30 | 2.8011 | 0 | N/A | 0 | 0
2022-04-27 11:00 | 3.1167 | 0 | N/A | 0 | 0
2022-04-27 11:30 | 3.3762 | 0 | N/A | 0 | 0
2022-04-27 12:00 | 3.3325 | 0 | N/A | 0 | 0
2022-04-27 12:30 | 3.2907 | 0 | N/A | 0 | 0
2022-04-27 13:00 | 3.3408 | 0 | N/A | 0 | 0
2022-04-27 13:30 | 3.6326 | 0 | N/A | 0 | 0
2022-04-27 14:00 | 2.3122 | 0 | N/A | 0 | 0
2022-04-27 14:30 | 1.4866 | 0 | N/A | 0 | 0
2022-04-27 15:00 | 1.936 | 0 | N/A | 0 | 0
2022-04-27 15:30 | 2.8385 | 0 | N/A | 0 | 0
2022-04-27 16:00 | 3.8165 | 0 | N/A | 0 | 0
2022-04-27 16:30 | 4.3198 | 0 | N/A | 0 | 0
2022-04-27 17:00 | 4.8716 | 0 | N/A | 0 | 0
2022-04-27 17:30 | 5.4374 | 0 | N/A | 0 | 0
2022-04-27 18:00 | 6.0656 | 0 | N/A | 0 | 0
2022-04-27 18:30 | 6.5961 | 0 | N/A | 0 | 0
2022-04-27 19:00 | 6.4279 | 0 | N/A | 0 | 0
2022-04-27 19:30 | 6.098 | 0 | N/A | 0 | 0
2022-04-27 20:00 | 5.7994 | 0 | N/A | 0 | 0
2022-04-27 20:30 | 5.487 | 0 | N/A | 0 | 0
2022-04-27 21:00 | 5.2241 | 0 | N/A | 0 | 0
2022-04-27 21:30 | 5.6023 | 0 | N/A | 0 | 0
2022-04-27 22:00 | 5.5332 | 0 | N/A | 0 | 0
2022-04-27 22:30 | 4.9441 | 0 | N/A | 0 | 0
2022-04-27 23:00 | 4.8182 | 0 | N/A | 0 | 0
2022-04-27 23:30 | 5.1683 | 0 | N/A | 0 | 0
2022-04-28 | 5.4438 | 0 | N/A | 0 | 0
2022-04-29 00:30 | 4.5946 | 0 | N/A | 0 | 0
2022-04-29 01:00 | 3.9706 | 0 | N/A | 0 | 0
2022-04-29 01:30 | 3.7949 | 0 | N/A | 0 | 0
2022-04-29 02:00 | 3.4606 | 0 | N/A | 0 | 0
2022-04-29 02:30 | 3.0344 | 0 | N/A | 0 | 0
2022-04-29 03:00 | 2.8357 | 0 | N/A | 0 | 0
2022-04-29 03:30 | 2.7551 | 0 | N/A | 0 | 0
2022-04-29 04:00 | 2.6848 | 0 | N/A | 0 | 0
2022-04-29 04:30 | 2.6253 | 0 | N/A | 0 | 0
2022-04-29 05:00 | 2.6579 | 0 | N/A | 0 | 0
2022-04-29 05:30 | 2.8215 | 0 | N/A | 0 | 0
2022-04-29 06:00 | 3.1581 | 0 | N/A | 0 | 0
2022-04-29 06:30 | 3.8182 | 0 | N/A | 0 | 0
2022-04-29 07:00 | 4.322 | 0 | N/A | 0 | 0
2022-04-29 07:30 | 4.3604 | 0 | N/A | 0 | 0
2022-04-29 08:00 | 4.742 | 0 | N/A | 0 | 0
2022-04-29 08:30 | 4.7836 | 0 | N/A | 0 | 0
2022-04-29 09:00 | 4.8631 | 0 | N/A | 0 | 0
2022-04-29 09:30 | 4.7391 | 0 | N/A | 0 | 0
2022-04-29 10:00 | 4.3263 | 0 | N/A | 0 | 0
2022-04-29 10:30 | 4.1362 | 0 | N/A | 0 | 0
2022-04-29 11:00 | 4.1333 | 0 | N/A | 0 | 0
2022-04-29 11:30 | 4.2933 | 0 | N/A | 0 | 0
2022-04-29 12:00 | 4.0841 | 0 | N/A | 0 | 0
2022-04-29 12:30 | 3.9938 | 0 | N/A | 0 | 0
2022-04-29 13:00 | 3.7751 | 0 | N/A | 0 | 0
2022-04-29 13:30 | 3.8575 | 0 | N/A | 0 | 0
2022-04-29 14:00 | 3.9999 | 0 | N/A | 0 | 0
2022-04-29 14:30 | 4.0845 | 0 | N/A | 0 | 0
2022-04-29 15:00 | 4.1441 | 0 | N/A | 0 | 0
2022-04-29 15:30 | 4.4596 | 0 | N/A | 0 | 0
2022-04-29 16:00 | 4.6642 | 0 | N/A | 0 | 0
2022-04-29 16:30 | 5.2295 | 0 | N/A | 0 | 0
2022-04-29 17:00 | 5.6366 | 0 | N/A | 0 | 0
2022-04-29 17:30 | 6.1997 | 0 | N/A | 0 | 0
2022-04-29 18:00 | 6.6784 | 0 | N/A | 0 | 0
2022-04-29 18:30 | 6.8376 | 0 | N/A | 0 | 0
2022-04-29 19:00 | 6.5832 | 0 | N/A | 0 | 0
2022-04-29 19:30 | 6.2998 | 0 | N/A | 0 | 0
2022-04-29 20:00 | 6.0104 | 0 | N/A | 0 | 0
2022-04-29 20:30 | 5.799 | 0 | N/A | 0 | 0
2022-04-29 21:00 | 5.523 | 0 | N/A | 0 | 0
2022-04-29 21:30 | 5.7158 | 0 | N/A | 0 | 0
2022-04-29 22:00 | 5.7321 | 0 | N/A | 0 | 0
2022-04-29 22:30 | 5.3217 | 0 | N/A | 0 | 0
2022-04-29 23:00 | 5.2146 | 0 | N/A | 0 | 0
2022-04-29 23:30 | 5.4758 | 0 | N/A | 0 | 0
2022-04-30 | 5.7518 | 0 | N/A | 0 | 0
2022-04-30 00:30 | 4.8727 | 0 | N/A | 0 | 0
2022-04-30 01:00 | 4.1035 | 0 | N/A | 0 | 0
2022-04-30 01:30 | 4.0421 | 0 | N/A | 0 | 0
2022-04-30 02:00 | 3.7408 | 0 | N/A | 0 | 0
2022-04-30 02:30 | 3.2722 | 0 | N/A | 0 | 0
2022-04-30 03:00 | 3.0214 | 0 | N/A | 0 | 0
2022-04-30 03:30 | 2.8941 | 0 | N/A | 0 | 0
2022-04-30 04:00 | 2.8003 | 0 | N/A | 0 | 0
2022-04-30 04:30 | 2.8215 | 0 | N/A | 0 | 0
2022-04-30 05:00 | 2.8408 | 0 | N/A | 0 | 0
2022-04-30 05:30 | 2.9815 | 0 | N/A | 0 | 0
2022-04-30 06:00 | 3.1044 | 0 | N/A | 0 | 0
2022-04-30 06:30 | 3.4485 | 0 | N/A | 0 | 0
2022-04-30 07:00 | 3.7747 | 0 | N/A | 0 | 0
2022-04-30 07:30 | 3.834 | 0 | N/A | 0 | 0
2022-04-30 08:00 | 4.0206 | 0 | N/A | 0 | 0
2022-04-30 08:30 | 3.9064 | 0 | N/A | 0 | 0
2022-04-30 09:00 | 3.548 | 0 | N/A | 0 | 0
2022-04-30 09:30 | 3.0255 | 0 | N/A | 0 | 0
2022-04-30 10:00 | 3.0434 | 0 | N/A | 0 | 0
2022-04-30 10:30 | 2.9749 | 0 | N/A | 0 | 0
2022-04-30 11:00 | 3.1627 | 0 | N/A | 0 | 0
2022-04-30 11:30 | 2.6167 | 0 | N/A | 0 | 0
2022-04-30 12:00 | 1.7591 | 0 | N/A | 0 | 0
2022-04-30 12:30 | 2.6122 | 0 | N/A | 0 | 0
2022-04-30 13:00 | 2.5868 | 0 | N/A | 0 | 0
2022-04-30 13:30 | 3.4138 | 0 | N/A | 0 | 0
2022-04-30 14:00 | 3.4656 | 0 | N/A | 0 | 0
2022-04-30 14:30 | 3.6547 | 0 | N/A | 0 | 0
2022-04-30 15:00 | 3.8768 | 0 | N/A | 0 | 0
2022-04-30 15:30 | 3.3493 | 0 | N/A | 0 | 0
2022-04-30 16:00 | 4.2364 | 0 | N/A | 0 | 0
2022-04-30 16:30 | 4.5736 | 0 | N/A | 0 | 0
2022-04-30 17:00 | 4.6655 | 0 | N/A | 0 | 0
2022-04-30 17:30 | 5.7732 | 0 | N/A | 0 | 0
2022-04-30 18:00 | 6.6516 | 0 | N/A | 0 | 0
2022-04-30 18:30 | 6.9944 | 0 | N/A | 0 | 0
2022-04-30 19:00 | 6.8306 | 0 | N/A | 0 | 0
2022-04-30 19:30 | 6.585 | 0 | N/A | 0 | 0
2022-04-30 20:00 | 6.1617 | 0 | N/A | 0 | 0
2022-04-30 20:30 | 5.7452 | 0 | N/A | 0 | 0
2022-04-30 21:00 | 5.5097 | 0 | N/A | 0 | 0
2022-04-30 21:30 | 5.8407 | 0 | N/A | 0 | 0
2022-04-30 22:00 | 6.0335 | 0 | N/A | 0 | 0
2022-04-30 22:30 | 5.6592 | 0 | N/A | 0 | 0
2022-04-30 23:00 | 5.5775 | 0 | N/A | 0 | 0
2022-04-30 23:30 | 5.8494 | 0 | N/A | 0 | 0
2022-05-01 | 6.0907 | 0 | N/A | 0 | 0
2022-05-01 00:30 | 5.2554 | 0 | N/A | 0 | 0
2022-05-01 01:00 | 4.5083 | 0 | N/A | 0 | 0
2022-05-01 01:30 | 4.3215 | 0 | N/A | 0 | 0
2022-05-01 02:00 | 3.9236 | 0 | N/A | 0 | 0
2022-05-01 02:30 | 3.5442 | 0 | N/A | 0 | 0
2022-05-01 03:00 | 3.2621 | 0 | N/A | 0 | 0
2022-05-01 03:30 | 3.0831 | 0 | N/A | 0 | 0
2022-05-01 04:00 | 2.9438 | 0 | N/A | 0 | 0
2022-05-01 04:30 | 2.8878 | 0 | N/A | 0 | 0
2022-05-01 05:00 | 2.8881 | 0 | N/A | 0 | 0
2022-05-01 05:30 | 2.9134 | 0 | N/A | 0 | 0
2022-05-01 06:00 | 3.0411 | 0 | N/A | 0 | 0
2022-05-01 06:30 | 3.4102 | 0 | N/A | 0 | 0
2022-05-01 07:00 | 3.6211 | 0 | N/A | 0 | 0
2022-05-01 07:30 | 3.6211 | 0 | N/A | 0 | 0
2022-05-01 08:00 | 3.9691 | 0 | N/A | 0 | 0
2022-05-01 08:30 | 4.1573 | 0 | N/A | 0 | 0
2022-05-01 09:00 | 4.0456 | 0 | N/A | 0 | 0
2022-05-01 09:30 | 4.0085 | 0 | N/A | 0 | 0
2022-05-01 10:00 | 4.0924 | 0 | N/A | 0 | 0
2022-05-01 10:30 | 3.7504 | 0 | N/A | 0 | 0
2022-05-01 11:00 | 4.0076 | 0 | N/A | 0 | 0
2022-05-01 11:30 | 3.9394 | 0 | N/A | 0 | 0
2022-05-01 12:00 | 3.5498 | 0 | N/A | 0 | 0
2022-05-01 12:30 | 3.8412 | 0 | N/A | 0 | 0
2022-05-01 13:00 | 3.2646 | 0 | N/A | 0 | 0
2022-05-01 13:30 | 3.292 | 0 | N/A | 0 | 0
2022-05-01 14:00 | 3.8314 | 0 | N/A | 0 | 0
2022-05-01 14:30 | 3.6754 | 0 | N/A | 0 | 0
2022-05-01 15:00 | 3.5673 | 0 | N/A | 0 | 0
2022-05-01 15:30 | 2.9272 | 0 | N/A | 0 | 0
2022-05-01 16:00 | 3.107 | 0 | N/A | 0 | 0
2022-05-01 16:30 | 3.9889 | 0 | N/A | 0 | 0
2022-05-01 17:00 | 5.2671 | 0 | N/A | 0 | 0
2022-05-01 17:30 | 5.8712 | 0 | N/A | 0 | 0
2022-05-01 18:00 | 6.6917 | 0 | N/A | 0 | 0
2022-05-01 18:30 | 7.1714 | 0 | N/A | 0 | 0
2022-05-01 19:00 | 7.0397 | 0 | N/A | 0 | 0
2022-05-01 19:30 | 6.5486 | 0 | N/A | 0 | 0
2022-05-01 20:00 | 6.2452 | 0 | N/A | 0 | 0
2022-05-01 20:30 | 5.8519 | 0 | N/A | 0 | 0
2022-05-01 21:00 | 5.4438 | 0 | N/A | 0 | 0
2022-05-01 21:30 | 5.741 | 0 | N/A | 0 | 0
2022-05-01 22:00 | 5.7239 | 0 | N/A | 0 | 0
2022-05-01 22:30 | 5.2451 | 0 | N/A | 0 | 0
2022-05-01 23:00 | 5.2424 | 0 | N/A | 0 | 0
2022-05-01 23:30 | 5.4173 | 0 | N/A | 0 | 0
2022-05-02 | 5.6427 | 0 | N/A | 0 | 0
2022-05-02 00:30 | 4.8804 | 0 | N/A | 0 | 0
2022-05-02 01:00 | 4.1991 | 0 | N/A | 0 | 0
2022-05-02 01:30 | 3.9693 | 0 | N/A | 0 | 0
2022-05-02 02:00 | 3.7041 | 0 | N/A | 0 | 0
2022-05-02 02:30 | 3.241 | 0 | N/A | 0 | 0
2022-05-02 03:00 | 3.031 | 0 | N/A | 0 | 0
2022-05-02 03:30 | 2.9151 | 0 | N/A | 0 | 0
2022-05-02 04:00 | 2.782 | 0 | N/A | 0 | 0
2022-05-02 04:30 | 2.7908 | 0 | N/A | 0 | 0
2022-05-02 05:00 | 2.8871 | 0 | N/A | 0 | 0
2022-05-02 05:30 | 3.0599 | 0 | N/A | 0 | 0
2022-05-02 06:30 | 4.0874 | 0 | N/A | 0 | 0
2022-05-02 07:00 | 4.7218 | 0 | N/A | 0 | 0
2022-05-02 07:30 | 5.2984 | 0 | N/A | 0 | 0
2022-05-02 08:00 | 5.8336 | 0 | N/A | 0 | 0
2022-05-02 08:30 | 5.7415 | 0 | N/A | 0 | 0
2022-05-02 09:00 | 5.3192 | 0 | N/A | 0 | 0
2022-05-02 09:30 | 4.8087 | 0 | N/A | 0 | 0
2022-05-02 10:00 | 4.3981 | 0 | N/A | 0 | 0
2022-05-02 10:30 | 3.609 | 0 | N/A | 0 | 0
2022-05-02 11:00 | 2.8078 | 0 | N/A | 0 | 0
2022-05-02 11:30 | 2.2268 | 0 | N/A | 0 | 0
2022-05-02 12:00 | 1.9553 | 0 | N/A | 0 | 0
2022-05-02 12:30 | 2.4025 | 0 | N/A | 0 | 0
2022-05-02 13:00 | 2.602 | 0 | N/A | 0 | 0
2022-05-02 13:30 | 3.1694 | 0 | N/A | 0 | 0
2022-05-02 14:00 | 3.4285 | 0 | N/A | 0 | 0
2022-05-02 14:30 | 3.5374 | 0 | N/A | 0 | 0
2022-05-02 15:00 | 3.2913 | 0 | N/A | 0 | 0
2022-05-02 15:30 | 3.1041 | 0 | N/A | 0 | 0
2022-05-02 16:00 | 3.874 | 0 | N/A | 0 | 0
2022-05-02 16:30 | 4.4356 | 0 | N/A | 0 | 0
2022-05-02 17:00 | 4.8624 | 0 | N/A | 0 | 0
2022-05-02 17:30 | 5.868 | 0 | N/A | 0 | 0
2022-05-02 18:00 | 6.7172 | 0 | N/A | 0 | 0
2022-05-02 18:30 | 7.013 | 0 | N/A | 0 | 0
2022-05-02 19:00 | 6.9066 | 0 | N/A | 0 | 0
2022-05-02 19:30 | 6.4805 | 0 | N/A | 0 | 0
2022-05-02 20:00 | 6.1835 | 0 | N/A | 0 | 0
2022-05-02 20:30 | 5.7725 | 0 | N/A | 0 | 0
2022-05-02 21:00 | 5.5308 | 0 | N/A | 0 | 0
2022-05-02 21:30 | 5.7402 | 0 | N/A | 0 | 0
2022-05-02 22:00 | 5.767 | 0 | N/A | 0 | 0
2022-05-02 22:30 | 5.1488 | 0 | N/A | 0 | 0
2022-05-02 23:00 | 4.9589 | 0 | N/A | 0 | 0
2022-05-02 23:30 | 5.2639 | 0 | N/A | 0 | 0
2022-05-03 | 5.4894 | 0 | N/A | 0 | 0
2022-05-03 00:30 | 4.7213 | 0 | N/A | 0 | 0
2022-05-03 01:00 | 4.0522 | 0 | N/A | 0 | 0
2022-05-03 01:30 | 3.9556 | 0 | N/A | 0 | 0
2022-05-03 02:00 | 3.583 | 0 | N/A | 0 | 0
2022-05-03 02:30 | 3.1562 | 0 | N/A | 0 | 0
2022-05-03 03:00 | 2.979 | 0 | N/A | 0 | 0
2022-05-03 03:30 | 2.8911 | 0 | N/A | 0 | 0
2022-05-03 04:00 | 2.8108 | 0 | N/A | 0 | 0
2022-05-03 04:30 | 2.8016 | 0 | N/A | 0 | 0
2022-05-03 05:00 | 2.844 | 0 | N/A | 0 | 0
2022-05-03 05:30 | 3.0657 | 0 | N/A | 0 | 0
2022-05-03 06:00 | 3.4543 | 0 | N/A | 0 | 0
2022-05-03 06:30 | 4.2072 | 0 | N/A | 0 | 0
2022-05-03 07:00 | 4.7594 | 0 | N/A | 0 | 0
2022-05-03 07:30 | 5.0858 | 0 | N/A | 0 | 0
2022-05-03 08:00 | 5.4274 | 0 | N/A | 0 | 0
2022-05-03 08:30 | 5.0317 | 0 | N/A | 0 | 0
2022-05-03 09:00 | 4.8813 | 0 | N/A | 0 | 0
2022-05-03 09:30 | 4.2654 | 0 | N/A | 0 | 0
2022-05-03 10:00 | 3.3857 | 0 | N/A | 0 | 0
2022-05-03 10:30 | 2.3011 | 0 | N/A | 0 | 0
2022-05-03 11:00 | 1.4957 | 0 | N/A | 0 | 0
2022-05-03 11:30 | 1.3922 | 0 | N/A | 0 | 0
2022-05-03 12:00 | 2.669 | 0 | N/A | 0 | 0
2022-05-03 12:30 | 1.5413 | 0 | N/A | 0 | 0
2022-05-03 13:00 | 0.56887 | 0 | N/A | 0 | 0
2022-05-03 13:30 | 1.3322 | 0 | N/A | 0 | 0
2022-05-03 14:00 | 1.4324 | 0 | N/A | 0 | 0
2022-05-03 14:30 | 2.0366 | 0 | N/A | 0 | 0
2022-05-03 15:00 | 2.4035 | 0 | N/A | 0 | 0
2022-05-03 15:30 | 2.9355 | 0 | N/A | 0 | 0
2022-05-03 16:00 | 3.9301 | 0 | N/A | 0 | 0
2022-05-03 16:30 | 4.3133 | 0 | N/A | 0 | 0
2022-05-03 17:00 | 4.0581 | 0 | N/A | 0 | 0
2022-05-03 17:30 | 5.1463 | 0 | N/A | 0 | 0
2022-05-03 18:00 | 6.1701 | 0 | N/A | 0 | 0
2022-05-03 18:30 | 6.9096 | 0 | N/A | 0 | 0
2022-05-03 19:00 | 6.9544 | 0 | N/A | 0 | 0
2022-05-03 19:30 | 6.6436 | 0 | N/A | 0 | 0
2022-05-03 20:00 | 6.4154 | 0 | N/A | 0 | 0
2022-05-03 20:30 | 6.1368 | 0 | N/A | 0 | 0
2022-05-03 21:00 | 5.8353 | 0 | N/A | 0 | 0
2022-05-03 21:30 | 6.0436 | 0 | N/A | 0 | 0
2022-05-03 22:00 | 5.8883 | 0 | N/A | 0 | 0
2022-05-03 22:30 | 5.3639 | 0 | N/A | 0 | 0
2022-05-03 23:00 | 5.2418 | 0 | N/A | 0 | 0
2022-05-03 23:30 | 5.3792 | 0 | N/A | 0 | 0
2022-05-04 | 5.5887 | 0 | N/A | 0 | 0
2022-05-04 00:30 | 5.7496 | 0 | N/A | 0 | 0
2022-05-04 01:00 | 4.827 | 0 | N/A | 0 | 0
2022-05-04 01:30 | 3.7783 | 0 | N/A | 0 | 0
2022-05-04 02:00 | 4.0489 | 0 | N/A | 0 | 0
2022-05-04 02:30 | 2.9273 | 0 | N/A | 0 | 0
2022-05-04 03:00 | 2.7946 | 0 | N/A | 0 | 0
2022-05-04 03:30 | 2.7224 | 0 | N/A | 0 | 0
2022-05-04 04:00 | 2.6045 | 0 | N/A | 0 | 0
2022-05-04 04:30 | 2.7401 | 0 | N/A | 0 | 0
2022-05-04 05:00 | 2.7927 | 0 | N/A | 0 | 0
2022-05-04 05:30 | 2.9428 | 0 | N/A | 0 | 0
2022-05-04 06:00 | 3.301 | 0 | N/A | 0 | 0
2022-05-04 06:30 | 4.0351 | 0 | N/A | 0 | 0
2022-05-04 07:00 | 4.8292 | 0 | N/A | 0 | 0
2022-05-04 07:30 | 5.4852 | 0 | N/A | 0 | 0
2022-05-04 08:00 | 6.3426 | 0 | N/A | 0 | 0
2022-05-04 08:30 | 6.3346 | 0 | N/A | 0 | 0
2022-05-04 09:00 | 5.9527 | 0 | N/A | 0 | 0
2022-05-04 09:30 | 5.3179 | 0 | N/A | 0 | 0
2022-05-04 10:00 | 4.6079 | 0 | N/A | 0 | 0
2022-05-04 10:30 | 3.4919 | 0 | N/A | 0 | 0
2022-05-04 11:00 | 3.8262 | 0 | N/A | 0 | 0
2022-05-04 11:30 | 3.2849 | 0 | N/A | 0 | 0
2022-05-04 12:00 | 2.5165 | 0 | N/A | 0 | 0
2022-05-04 12:30 | 3.8378 | 0 | N/A | 0 | 0
2022-05-04 13:00 | 4.5074 | 0 | N/A | 0 | 0
2022-05-04 13:30 | 5.2384 | 0 | N/A | 0 | 0
2022-05-04 14:00 | 5.0127 | 0 | N/A | 0 | 0
2022-05-04 14:30 | 4.8848 | 0 | N/A | 0 | 0
2022-05-04 15:00 | 4.8962 | 0 | N/A | 0 | 0
2022-05-04 15:30 | 4.7272 | 0 | N/A | 0 | 0
2022-05-04 16:00 | 5.1963 | 0 | N/A | 0 | 0
2022-05-04 16:30 | 5.2526 | 0 | N/A | 0 | 0
2022-05-04 17:00 | 5.3141 | 0 | N/A | 0 | 0
2022-05-04 17:30 | 6.5175 | 0 | N/A | 0 | 0
2022-05-04 18:00 | 7.5364 | 0 | N/A | 0 | 0
2022-05-04 18:30 | 8.0469 | 0 | N/A | 0 | 0
2022-05-04 19:00 | 7.9939 | 0 | N/A | 0 | 0
2022-05-04 19:30 | 7.7478 | 0 | N/A | 0 | 0
2022-05-04 20:00 | 7.5933 | 0 | N/A | 0 | 0
2022-05-04 20:30 | 7.2583 | 0 | N/A | 0 | 0
2022-05-04 21:00 | 6.78 | 0 | N/A | 0 | 0
2022-05-04 21:30 | 6.9218 | 0 | N/A | 0 | 0
2022-05-04 22:00 | 6.7935 | 0 | N/A | 0 | 0
2022-05-04 22:30 | 6.1469 | 0 | N/A | 0 | 0
2022-05-04 23:00 | 5.925 | 0 | N/A | 0 | 0
2022-05-04 23:30 | 6.0307 | 0 | N/A | 0 | 0
2022-05-05 | 6.2901 | 0 | N/A | 0 | 0
2022-05-06 00:30 | 6.1008 | 0 | N/A | 0 | 0
2022-05-06 01:00 | 5.36 | 0 | N/A | 0 | 0
2022-05-06 01:30 | 5.2376 | 0 | N/A | 0 | 0
2022-05-06 02:00 | 4.8448 | 0 | N/A | 0 | 0
2022-05-06 02:30 | 4.3279 | 0 | N/A | 0 | 0
2022-05-06 03:00 | 4.1792 | 0 | N/A | 0 | 0
2022-05-06 03:30 | 4.0759 | 0 | N/A | 0 | 0
2022-05-06 04:00 | 3.9673 | 0 | N/A | 0 | 0
2022-05-06 04:30 | 3.9552 | 0 | N/A | 0 | 0
2022-05-06 05:00 | 4.1227 | 0 | N/A | 0 | 0
2022-05-06 05:30 | 4.3883 | 0 | N/A | 0 | 0
2022-05-06 06:00 | 4.8528 | 0 | N/A | 0 | 0
2022-05-06 06:30 | 6.0083 | 0 | N/A | 0 | 0
2022-05-06 07:00 | 6.9363 | 0 | N/A | 0 | 0
2022-05-06 07:30 | 7.4214 | 0 | N/A | 0 | 0
2022-05-06 08:00 | 7.8127 | 0 | N/A | 0 | 0
2022-05-06 08:30 | 7.3751 | 0 | N/A | 0 | 0
2022-05-06 09:00 | 5.9142 | 0 | N/A | 0 | 0
2022-05-06 09:30 | 4.2581 | 0 | N/A | 0 | 0
2022-05-06 10:00 | 3.4734 | 0 | N/A | 0 | 0
2022-05-06 10:30 | 2.6183 | 0 | N/A | 0 | 0
2022-05-06 11:00 | 2.6619 | 0 | N/A | 0 | 0
2022-05-06 11:30 | 2.1728 | 0 | N/A | 0 | 0
2022-05-06 12:00 | 2.732 | 0 | N/A | 0 | 0
2022-05-06 12:30 | 2.1858 | 0 | N/A | 0 | 0
2022-05-06 13:00 | 2.2194 | 0 | N/A | 0 | 0
2022-05-06 13:30 | 2.3666 | 0 | N/A | 0 | 0
2022-05-06 14:00 | 3.1661 | 0 | N/A | 0 | 0
2022-05-06 14:30 | 3.4488 | 0 | N/A | 0 | 0
2022-05-06 15:00 | 3.4891 | 0 | N/A | 0 | 0
2022-05-06 15:30 | 3.7052 | 0 | N/A | 0 | 0
2022-05-06 16:00 | 4.5169 | 0 | N/A | 0 | 0
2022-05-06 16:30 | 5.7065 | 0 | N/A | 0 | 0
2022-05-06 17:00 | 6.6 | 0 | N/A | 0 | 0
2022-05-06 17:30 | 7.364 | 0 | N/A | 0 | 0
2022-05-06 18:00 | 8.0173 | 0 | N/A | 0 | 0
2022-05-06 18:30 | 8.2964 | 0 | N/A | 0 | 0
2022-05-06 19:00 | 8.1359 | 0 | N/A | 0 | 0
2022-05-06 19:30 | 7.7947 | 0 | N/A | 0 | 0
2022-05-06 20:00 | 7.5852 | 0 | N/A | 0 | 0
2022-05-06 20:30 | 7.3238 | 0 | N/A | 0 | 0
2022-05-06 21:00 | 7.0883 | 0 | N/A | 0 | 0
2022-05-06 21:30 | 7.2934 | 0 | N/A | 0 | 0
2022-05-06 22:00 | 7.2773 | 0 | N/A | 0 | 0
2022-05-06 22:30 | 6.6291 | 0 | N/A | 0 | 0
2022-05-06 23:00 | 6.4436 | 0 | N/A | 0 | 0
2022-05-06 23:30 | 6.6148 | 0 | N/A | 0 | 0
2022-05-07 | 6.6699 | 0 | N/A | 0 | 0
2022-05-07 00:30 | 5.8483 | 0 | N/A | 0 | 0
2022-05-07 01:00 | 5.0946 | 0 | N/A | 0 | 0
2022-05-07 01:30 | 4.9257 | 0 | N/A | 0 | 0
2022-05-07 02:00 | 4.529 | 0 | N/A | 0 | 0
2022-05-07 02:30 | 4.0064 | 0 | N/A | 0 | 0
2022-05-07 03:00 | 3.7494 | 0 | N/A | 0 | 0
2022-05-07 03:30 | 3.6096 | 0 | N/A | 0 | 0
2022-05-07 04:00 | 3.4989 | 0 | N/A | 0 | 0
2022-05-07 04:30 | 3.4559 | 0 | N/A | 0 | 0
2022-05-07 05:00 | 3.4199 | 0 | N/A | 0 | 0
2022-05-07 05:30 | 3.5987 | 0 | N/A | 0 | 0
2022-05-07 06:00 | 3.7599 | 0 | N/A | 0 | 0
2022-05-07 06:30 | 4.1754 | 0 | N/A | 0 | 0
2022-05-07 07:00 | 4.5017 | 0 | N/A | 0 | 0
2022-05-07 07:30 | 4.6471 | 0 | N/A | 0 | 0
2022-05-07 08:00 | 5.2163 | 0 | N/A | 0 | 0
2022-05-07 08:30 | 5.4108 | 0 | N/A | 0 | 0
2022-05-07 09:00 | 5.7193 | 0 | N/A | 0 | 0
2022-05-07 09:30 | 5.8034 | 0 | N/A | 0 | 0
2022-05-07 10:00 | 5.6143 | 0 | N/A | 0 | 0
2022-05-07 10:30 | 5.4763 | 0 | N/A | 0 | 0
2022-05-07 11:00 | 5.4583 | 0 | N/A | 0 | 0
2022-05-07 11:30 | 5.151 | 0 | N/A | 0 | 0
2022-05-07 12:00 | 5.1566 | 0 | N/A | 0 | 0
2022-05-07 12:30 | 5.2968 | 0 | N/A | 0 | 0
2022-05-07 13:00 | 5.1587 | 0 | N/A | 0 | 0
2022-05-07 13:30 | 5.5098 | 0 | N/A | 0 | 0
2022-05-07 14:00 | 5.7075 | 0 | N/A | 0 | 0
2022-05-07 14:30 | 5.46 | 0 | N/A | 0 | 0
2022-05-07 15:00 | 5.4888 | 0 | N/A | 0 | 0
2022-05-07 15:30 | 5.6503 | 0 | N/A | 0 | 0
2022-05-07 16:00 | 5.8791 | 0 | N/A | 0 | 0
2022-05-07 16:30 | 6.0828 | 0 | N/A | 0 | 0
2022-05-07 17:00 | 6.5482 | 0 | N/A | 0 | 0
2022-05-07 17:30 | 7.1582 | 0 | N/A | 0 | 0
2022-05-07 18:00 | 7.9256 | 0 | N/A | 0 | 0
2022-05-07 18:30 | 8.1994 | 0 | N/A | 0 | 0
2022-05-07 19:00 | 7.7985 | 0 | N/A | 0 | 0
2022-05-07 19:30 | 7.4838 | 0 | N/A | 0 | 0
2022-05-07 20:00 | 6.9184 | 0 | N/A | 0 | 0
2022-05-07 20:30 | 6.5254 | 0 | N/A | 0 | 0
2022-05-07 21:00 | 6.2105 | 0 | N/A | 0 | 0
2022-05-07 21:30 | 6.4205 | 0 | N/A | 0 | 0
2022-05-07 22:00 | 6.5999 | 0 | N/A | 0 | 0
2022-05-07 22:30 | 6.2401 | 0 | N/A | 0 | 0
2022-05-07 23:00 | 6.1354 | 0 | N/A | 0 | 0
2022-05-07 23:30 | 6.2226 | 0 | N/A | 0 | 0
2022-05-08 | 6.4941 | 0 | N/A | 0 | 0
2022-05-08 00:30 | 5.7569 | 0 | N/A | 0 | 0
2022-05-08 01:00 | 5.0213 | 0 | N/A | 0 | 0
2022-05-08 01:30 | 4.8955 | 0 | N/A | 0 | 0
2022-05-08 02:00 | 4.4893 | 0 | N/A | 0 | 0
2022-05-08 02:30 | 4.0027 | 0 | N/A | 0 | 0
2022-05-08 03:00 | 3.6506 | 0 | N/A | 0 | 0
2022-05-08 03:30 | 3.4133 | 0 | N/A | 0 | 0
2022-05-08 04:00 | 3.3055 | 0 | N/A | 0 | 0
2022-05-08 04:30 | 3.2447 | 0 | N/A | 0 | 0
2022-05-08 05:00 | 3.2323 | 0 | N/A | 0 | 0
2022-05-08 05:30 | 3.3154 | 0 | N/A | 0 | 0
2022-05-08 06:00 | 3.4203 | 0 | N/A | 0 | 0
2022-05-08 06:30 | 3.765 | 0 | N/A | 0 | 0
2022-05-08 07:00 | 3.974 | 0 | N/A | 0 | 0
2022-05-08 07:30 | 4.2364 | 0 | N/A | 0 | 0
2022-05-08 08:00 | 4.587 | 0 | N/A | 0 | 0
2022-05-08 08:30 | 5.1376 | 0 | N/A | 0 | 0
2022-05-08 09:00 | 5.143 | 0 | N/A | 0 | 0
2022-05-08 09:30 | 4.5217 | 0 | N/A | 0 | 0
2022-05-08 10:00 | 4.3788 | 0 | N/A | 0 | 0
2022-05-08 10:30 | 3.976 | 0 | N/A | 0 | 0
2022-05-08 11:00 | 3.6846 | 0 | N/A | 0 | 0
2022-05-08 11:30 | 3.9688 | 0 | N/A | 0 | 0
2022-05-08 12:00 | 3.665 | 0 | N/A | 0 | 0
2022-05-08 12:30 | 3.365 | 0 | N/A | 0 | 0
2022-05-08 13:00 | 2.4108 | 0 | N/A | 0 | 0
2022-05-08 13:30 | 3.0516 | 0 | N/A | 0 | 0
2022-05-08 14:00 | 3.7749 | 0 | N/A | 0 | 0
2022-05-08 14:30 | 4.0045 | 0 | N/A | 0 | 0
2022-05-08 15:00 | 4.6964 | 0 | N/A | 0 | 0
2022-05-08 15:30 | 4.9662 | 0 | N/A | 0 | 0
2022-05-08 16:00 | 5.4071 | 0 | N/A | 0 | 0
2022-05-08 16:30 | 5.745 | 0 | N/A | 0 | 0
2022-05-08 17:00 | 6.32 | 0 | N/A | 0 | 0
2022-05-08 17:30 | 6.9942 | 0 | N/A | 0 | 0
2022-05-08 18:00 | 7.4457 | 0 | N/A | 0 | 0
2022-05-08 18:30 | 7.7204 | 0 | N/A | 0 | 0
2022-05-08 19:00 | 7.3758 | 0 | N/A | 0 | 0
2022-05-08 19:30 | 7.0105 | 0 | N/A | 0 | 0
2022-05-08 20:00 | 6.8031 | 0 | N/A | 0 | 0
2022-05-08 20:30 | 6.5365 | 0 | N/A | 0 | 0
2022-05-08 21:00 | 6.1368 | 0 | N/A | 0 | 0
2022-05-08 21:30 | 6.3149 | 0 | N/A | 0 | 0
2022-05-08 22:00 | 6.282 | 0 | N/A | 0 | 0
2022-05-08 22:30 | 5.8154 | 0 | N/A | 0 | 0
2022-05-08 23:00 | 5.7792 | 0 | N/A | 0 | 0
2022-05-08 23:30 | 5.856 | 0 | N/A | 0 | 0
2022-05-09 | 6.0461 | 0 | N/A | 0 | 0
2022-05-09 00:30 | 5.3934 | 0 | N/A | 0 | 0
2022-05-09 01:00 | 4.7276 | 0 | N/A | 0 | 0
2022-05-09 01:30 | 4.6584 | 0 | N/A | 0 | 0
2022-05-09 02:00 | 4.2876 | 0 | N/A | 0 | 0
2022-05-09 02:30 | 3.9455 | 0 | N/A | 0 | 0
2022-05-09 03:00 | 3.6621 | 0 | N/A | 0 | 0
2022-05-09 03:30 | 3.504 | 0 | N/A | 0 | 0
2022-05-09 04:00 | 3.4367 | 0 | N/A | 0 | 0
2022-05-09 04:30 | 3.5544 | 0 | N/A | 0 | 0
2022-05-09 05:00 | 3.6199 | 0 | N/A | 0 | 0
2022-05-09 05:30 | 3.9645 | 0 | N/A | 0 | 0
2022-05-09 06:00 | 4.4837 | 0 | N/A | 0 | 0
2022-05-09 06:30 | 5.3698 | 0 | N/A | 0 | 0
2022-05-09 07:00 | 6.2689 | 0 | N/A | 0 | 0
2022-05-09 07:30 | 7.1566 | 0 | N/A | 0 | 0
2022-05-09 08:00 | 7.5965 | 0 | N/A | 0 | 0
2022-05-09 08:30 | 7.1207 | 0 | N/A | 0 | 0
2022-05-09 09:00 | 6.2224 | 0 | N/A | 0 | 0
2022-05-09 09:30 | 5.0832 | 0 | N/A | 0 | 0
2022-05-09 10:00 | 3.9541 | 0 | N/A | 0 | 0
2022-05-09 10:30 | 3.0558 | 0 | N/A | 0 | 0
2022-05-09 11:00 | 2.2904 | 0 | N/A | 0 | 0
2022-05-09 11:30 | 2.102 | 0 | N/A | 0 | 0
2022-05-09 12:00 | 2.2194 | 0 | N/A | 0 | 0
2022-05-09 12:30 | 1.7409 | 0 | N/A | 0 | 0
2022-05-09 13:00 | 1.799 | 0 | N/A | 0 | 0
2022-05-09 13:30 | 1.7031 | 0 | N/A | 0 | 0
2022-05-09 14:00 | 2.7213 | 0 | N/A | 0 | 0
2022-05-09 14:30 | 2.2129 | 0 | N/A | 0 | 0
2022-05-09 15:00 | 2.621 | 0 | N/A | 0 | 0
2022-05-09 15:30 | 3.0236 | 0 | N/A | 0 | 0
2022-05-09 16:00 | 3.9673 | 0 | N/A | 0 | 0
2022-05-09 16:30 | 4.7151 | 0 | N/A | 0 | 0
2022-05-09 17:00 | 5.5787 | 0 | N/A | 0 | 0
2022-05-09 17:30 | 6.6407 | 0 | N/A | 0 | 0
2022-05-09 18:00 | 7.7569 | 0 | N/A | 0 | 0
2022-05-09 18:30 | 8.3183 | 0 | N/A | 0 | 0
2022-05-09 19:00 | 8.2444 | 0 | N/A | 0 | 0
2022-05-09 19:30 | 7.9343 | 0 | N/A | 0 | 0
2022-05-09 20:00 | 7.8011 | 0 | N/A | 0 | 0
2022-05-09 20:30 | 7.4572 | 0 | N/A | 0 | 0
2022-05-09 21:00 | 7.0213 | 0 | N/A | 0 | 0
2022-05-09 21:30 | 7.2313 | 0 | N/A | 0 | 0
2022-05-09 22:00 | 7.1716 | 0 | N/A | 0 | 0
2022-05-09 22:30 | 6.4972 | 0 | N/A | 0 | 0
2022-05-09 23:00 | 6.2447 | 0 | N/A | 0 | 0
2022-05-09 23:30 | 6.2407 | 0 | N/A | 0 | 0
2022-05-10 | 6.4484 | 0 | N/A | 0 | 0
2022-05-10 00:30 | 5.7311 | 0 | N/A | 0 | 0
2022-05-10 01:00 | 5.0911 | 0 | N/A | 0 | 0
2022-05-10 01:30 | 4.945 | 0 | N/A | 0 | 0
2022-05-10 02:00 | 4.6495 | 0 | N/A | 0 | 0
2022-05-10 02:30 | 4.1689 | 0 | N/A | 0 | 0
2022-05-10 03:00 | 3.9731 | 0 | N/A | 0 | 0
2022-05-10 03:30 | 3.777 | 0 | N/A | 0 | 0
2022-05-10 04:00 | 3.6749 | 0 | N/A | 0 | 0
2022-05-10 04:30 | 3.7473 | 0 | N/A | 0 | 0
2022-05-10 05:00 | 3.8802 | 0 | N/A | 0 | 0
2022-05-10 05:30 | 4.2253 | 0 | N/A | 0 | 0
2022-05-10 06:00 | 4.7648 | 0 | N/A | 0 | 0
2022-05-10 06:30 | 5.7776 | 0 | N/A | 0 | 0
2022-05-10 07:00 | 6.6423 | 0 | N/A | 0 | 0
2022-05-10 07:30 | 7.0839 | 0 | N/A | 0 | 0
2022-05-10 08:00 | 7.4866 | 0 | N/A | 0 | 0
2022-05-10 08:30 | 7.3827 | 0 | N/A | 0 | 0
2022-05-10 09:00 | 6.6195 | 0 | N/A | 0 | 0
2022-05-10 09:30 | 5.4936 | 0 | N/A | 0 | 0
2022-05-10 10:00 | 4.3989 | 0 | N/A | 0 | 0
2022-05-10 10:30 | 3.4234 | 0 | N/A | 0 | 0
2022-05-10 11:00 | 2.6762 | 0 | N/A | 0 | 0
2022-05-10 11:30 | 2.3761 | 0 | N/A | 0 | 0
2022-05-10 12:00 | 2.1005 | 0 | N/A | 0 | 0
2022-05-10 12:30 | 2.197 | 0 | N/A | 0 | 0
2022-05-10 13:00 | 2.5447 | 0 | N/A | 0 | 0
2022-05-10 13:30 | 2.3649 | 0 | N/A | 0 | 0
2022-05-10 14:00 | 1.6898 | 0 | N/A | 0 | 0
2022-05-10 14:30 | 1.9599 | 0 | N/A | 0 | 0
2022-05-10 15:00 | 2.0946 | 0 | N/A | 0 | 0
2022-05-10 15:30 | 2.3224 | 0 | N/A | 0 | 0
2022-05-10 16:00 | 3.3883 | 0 | N/A | 0 | 0
2022-05-10 16:30 | 3.82 | 0 | N/A | 0 | 0
2022-05-10 17:00 | 4.678 | 0 | N/A | 0 | 0
2022-05-10 17:30 | 6.0769 | 0 | N/A | 0 | 0
2022-05-10 18:00 | 7.1454 | 0 | N/A | 0 | 0
2022-05-10 18:30 | 7.5477 | 0 | N/A | 0 | 0
2022-05-10 19:00 | 7.3678 | 0 | N/A | 0 | 0
2022-05-10 19:30 | 7.057 | 0 | N/A | 0 | 0
2022-05-10 20:00 | 6.8824 | 0 | N/A | 0 | 0
2022-05-10 20:30 | 6.7599 | 0 | N/A | 0 | 0
2022-05-10 21:00 | 6.3307 | 0 | N/A | 0 | 0
2022-05-10 21:30 | 6.4541 | 0 | N/A | 0 | 0
2022-05-10 22:00 | 6.4649 | 0 | N/A | 0 | 0
2022-05-10 22:30 | 5.9081 | 0 | N/A | 0 | 0
2022-05-10 23:00 | 5.6322 | 0 | N/A | 0 | 0
2022-05-10 23:30 | 5.7098 | 0 | N/A | 0 | 0
2022-05-11 | 5.8899 | 0 | N/A | 0 | 0
2022-05-11 00:30 | 5.0821 | 0 | N/A | 0 | 0
2022-05-11 01:00 | 4.4272 | 0 | N/A | 0 | 0
2022-05-11 01:30 | 4.3178 | 0 | N/A | 0 | 0
2022-05-11 02:00 | 4.0376 | 0 | N/A | 0 | 0
2022-05-11 02:30 | 3.5697 | 0 | N/A | 0 | 0
2022-05-11 03:00 | 3.3266 | 0 | N/A | 0 | 0
2022-05-11 03:30 | 3.2058 | 0 | N/A | 0 | 0
2022-05-11 04:00 | 3.0857 | 0 | N/A | 0 | 0
2022-05-11 04:30 | 3.0745 | 0 | N/A | 0 | 0
2022-05-11 05:00 | 3.1767 | 0 | N/A | 0 | 0
2022-05-11 05:30 | 3.479 | 0 | N/A | 0 | 0
2022-05-11 06:00 | 3.9491 | 0 | N/A | 0 | 0
2022-05-11 06:30 | 4.6455 | 0 | N/A | 0 | 0
2022-05-11 07:00 | 5.424 | 0 | N/A | 0 | 0
2022-05-11 07:30 | 5.9228 | 0 | N/A | 0 | 0
2022-05-11 08:00 | 6.2211 | 0 | N/A | 0 | 0
2022-05-11 08:30 | 6.1373 | 0 | N/A | 0 | 0
2022-05-11 09:00 | 5.7816 | 0 | N/A | 0 | 0
2022-05-11 09:30 | 5.13 | 0 | N/A | 0 | 0
2022-05-11 10:00 | 4.2125 | 0 | N/A | 0 | 0
2022-05-11 10:30 | 4.0315 | 0 | N/A | 0 | 0
2022-05-11 11:00 | 3.442 | 0 | N/A | 0 | 0
2022-05-11 11:30 | 2.1553 | 0 | N/A | 0 | 0
2022-05-11 12:00 | 2.4534 | 0 | N/A | 0 | 0
2022-05-11 12:30 | 2.0345 | 0 | N/A | 0 | 0
2022-05-11 13:00 | 1.6422 | 0 | N/A | 0 | 0
2022-05-11 13:30 | 3.1327 | 0 | N/A | 0 | 0
2022-05-11 14:00 | 3.5741 | 0 | N/A | 0 | 0
2022-05-11 14:30 | 4.0352 | 0 | N/A | 0 | 0
2022-05-11 15:00 | 4.4006 | 0 | N/A | 0 | 0
2022-05-11 15:30 | 4.733 | 0 | N/A | 0 | 0
2022-05-11 16:00 | 4.9368 | 0 | N/A | 0 | 0
2022-05-11 16:30 | 5.0679 | 0 | N/A | 0 | 0
2022-05-11 17:00 | 5.5962 | 0 | N/A | 0 | 0
2022-05-11 17:30 | 6.2181 | 0 | N/A | 0 | 0
2022-05-11 18:00 | 6.9023 | 0 | N/A | 0 | 0
2022-05-11 18:30 | 7.1286 | 0 | N/A | 0 | 0
2022-05-11 19:00 | 6.9529 | 0 | N/A | 0 | 0
2022-05-11 19:30 | 6.6635 | 0 | N/A | 0 | 0
2022-05-11 20:00 | 6.5239 | 0 | N/A | 0 | 0
2022-05-11 20:30 | 6.1778 | 0 | N/A | 0 | 0
2022-05-11 21:00 | 5.8276 | 0 | N/A | 0 | 0
2022-05-11 21:30 | 6.0175 | 0 | N/A | 0 | 0
2022-05-11 22:00 | 5.9991 | 0 | N/A | 0 | 0
2022-05-11 22:30 | 5.5452 | 0 | N/A | 0 | 0
2022-05-11 23:00 | 5.4122 | 0 | N/A | 0 | 0
2022-05-11 23:30 | 5.4736 | 0 | N/A | 0 | 0
2022-05-12 | 5.5419 | 0 | N/A | 0 | 0
2022-05-12 00:30 | 4.762 | 0 | N/A | 0 | 0
2022-05-12 01:00 | 4.1201 | 0 | N/A | 0 | 0
2022-05-12 01:30 | 3.9444 | 0 | N/A | 0 | 0
2022-05-12 02:00 | 3.5975 | 0 | N/A | 0 | 0
2022-05-12 02:30 | 3.2448 | 0 | N/A | 0 | 0
2022-05-12 03:00 | 3.0678 | 0 | N/A | 0 | 0
2022-05-12 03:30 | 2.9685 | 0 | N/A | 0 | 0
2022-05-12 04:00 | 2.827 | 0 | N/A | 0 | 0
2022-05-12 04:30 | 2.8016 | 0 | N/A | 0 | 0
2022-05-12 05:00 | 2.8908 | 0 | N/A | 0 | 0
2022-05-12 05:30 | 3.2082 | 0 | N/A | 0 | 0
2022-05-12 06:00 | 3.5538 | 0 | N/A | 0 | 0
2022-05-12 06:30 | 4.2565 | 0 | N/A | 0 | 0
2022-05-12 07:00 | 5.0476 | 0 | N/A | 0 | 0
2022-05-12 07:30 | 5.5387 | 0 | N/A | 0 | 0
2022-05-12 08:00 | 5.7004 | 0 | N/A | 0 | 0
2022-05-12 08:30 | 5.2779 | 0 | N/A | 0 | 0
2022-05-12 09:00 | 4.7321 | 0 | N/A | 0 | 0
2022-05-12 09:30 | 4.209 | 0 | N/A | 0 | 0
2022-05-12 10:00 | 4.1936 | 0 | N/A | 0 | 0
2022-05-12 10:30 | 4.1418 | 0 | N/A | 0 | 0
2022-05-12 11:00 | 3.7593 | 0 | N/A | 0 | 0
2022-05-12 11:30 | 3.915 | 0 | N/A | 0 | 0
2022-05-12 12:00 | 3.5976 | 0 | N/A | 0 | 0
2022-05-12 12:30 | 3.0673 | 0 | N/A | 0 | 0
2022-05-12 13:00 | 3.6267 | 0 | N/A | 0 | 0
2022-05-12 13:30 | 4.1276 | 0 | N/A | 0 | 0
2022-05-12 14:00 | 3.476 | 0 | N/A | 0 | 0
2022-05-12 14:30 | 2.9546 | 0 | N/A | 0 | 0
2022-05-12 15:00 | 2.7812 | 0 | N/A | 0 | 0
2022-05-12 15:30 | 3.3826 | 0 | N/A | 0 | 0
2022-05-12 16:00 | 3.8127 | 0 | N/A | 0 | 0
2022-05-12 16:30 | 4.2418 | 0 | N/A | 0 | 0
2022-05-12 17:00 | 4.6657 | 0 | N/A | 0 | 0
2022-05-12 17:30 | 5.6054 | 0 | N/A | 0 | 0
2022-05-12 18:00 | 6.5573 | 0 | N/A | 0 | 0
2022-05-12 18:30 | 6.826 | 0 | N/A | 0 | 0
2022-05-12 19:00 | 6.8462 | 0 | N/A | 0 | 0
2022-05-12 19:30 | 6.546 | 0 | N/A | 0 | 0
2022-05-12 20:00 | 6.3513 | 0 | N/A | 0 | 0
2022-05-12 20:30 | 6.0976 | 0 | N/A | 0 | 0
2022-05-12 21:00 | 5.7121 | 0 | N/A | 0 | 0
2022-05-12 21:30 | 5.9261 | 0 | N/A | 0 | 0
2022-05-12 22:00 | 5.8987 | 0 | N/A | 0 | 0
2022-05-12 22:30 | 5.4181 | 0 | N/A | 0 | 0
2022-05-12 23:00 | 5.1899 | 0 | N/A | 0 | 0
2022-05-12 23:30 | 5.4295 | 0 | N/A | 0 | 0
2022-05-13 | 5.5633 | 0 | N/A | 0 | 0
2022-05-13 00:30 | 4.8974 | 0 | N/A | 0 | 0
2022-05-13 01:00 | 4.1327 | 0 | N/A | 0 | 0
2022-05-13 01:30 | 3.9551 | 0 | N/A | 0 | 0
2022-05-13 02:00 | 3.637 | 0 | N/A | 0 | 0
2022-05-13 02:30 | 3.1911 | 0 | N/A | 0 | 0
2022-05-13 03:00 | 3.0819 | 0 | N/A | 0 | 0
2022-05-13 03:30 | 2.9594 | 0 | N/A | 0 | 0
2022-05-13 04:00 | 2.8394 | 0 | N/A | 0 | 0
2022-05-13 04:30 | 2.8652 | 0 | N/A | 0 | 0
2022-05-13 05:00 | 2.9033 | 0 | N/A | 0 | 0
2022-05-13 05:30 | 3.2051 | 0 | N/A | 0 | 0
2022-05-13 06:00 | 3.5239 | 0 | N/A | 0 | 0
2022-05-13 06:30 | 4.192 | 0 | N/A | 0 | 0
2022-05-13 07:00 | 4.8484 | 0 | N/A | 0 | 0
2022-05-13 07:30 | 5.2522 | 0 | N/A | 0 | 0
2022-05-13 08:00 | 5.8893 | 0 | N/A | 0 | 0
2022-05-13 08:30 | 6.0075 | 0 | N/A | 0 | 0
2022-05-13 09:00 | 5.2114 | 0 | N/A | 0 | 0
2022-05-13 09:30 | 4.549 | 0 | N/A | 0 | 0
2022-05-13 10:00 | 4.0488 | 0 | N/A | 0 | 0
2022-05-13 10:30 | 4.2809 | 0 | N/A | 0 | 0
2022-05-13 11:00 | 4.3565 | 0 | N/A | 0 | 0
2022-05-13 11:30 | 4.915 | 0 | N/A | 0 | 0
2022-05-13 12:00 | 5.2252 | 0 | N/A | 0 | 0
2022-05-13 12:30 | 5.7541 | 0 | N/A | 0 | 0
2022-05-13 13:00 | 5.1152 | 0 | N/A | 0 | 0
2022-05-13 13:30 | 5.0183 | 0 | N/A | 0 | 0
2022-05-13 14:00 | 4.6957 | 0 | N/A | 0 | 0
2022-05-13 14:30 | 4.7636 | 0 | N/A | 0 | 0
2022-05-13 15:00 | 4.4059 | 0 | N/A | 0 | 0
2022-05-13 15:30 | 4.4848 | 0 | N/A | 0 | 0
2022-05-13 16:00 | 4.7528 | 0 | N/A | 0 | 0
2022-05-13 16:30 | 4.7776 | 0 | N/A | 0 | 0
2022-05-13 17:00 | 5.4601 | 0 | N/A | 0 | 0
2022-05-13 17:30 | 6.0405 | 0 | N/A | 0 | 0
2022-05-13 18:00 | 6.5948 | 0 | N/A | 0 | 0
2022-05-13 18:30 | 6.7045 | 0 | N/A | 0 | 0
2022-05-13 19:00 | 6.4386 | 0 | N/A | 0 | 0
2022-05-13 19:30 | 6.2582 | 0 | N/A | 0 | 0
2022-05-13 20:00 | 6.0845 | 0 | N/A | 0 | 0
2022-05-13 20:30 | 5.8553 | 0 | N/A | 0 | 0
2022-05-13 21:00 | 5.6173 | 0 | N/A | 0 | 0
2022-05-13 21:30 | 5.811 | 0 | N/A | 0 | 0
2022-05-13 22:00 | 5.83 | 0 | N/A | 0 | 0
2022-05-13 22:30 | 5.4296 | 0 | N/A | 0 | 0
2022-05-13 23:00 | 5.226 | 0 | N/A | 0 | 0
2022-05-13 23:30 | 5.273 | 0 | N/A | 0 | 0
2022-05-14 | 5.5714 | 0 | N/A | 0 | 0
2022-05-14 00:30 | 4.7251 | 0 | N/A | 0 | 0
2022-05-14 01:00 | 4.0216 | 0 | N/A | 0 | 0
2022-05-14 01:30 | 3.9349 | 0 | N/A | 0 | 0
2022-05-14 02:00 | 3.6052 | 0 | N/A | 0 | 0
2022-05-14 02:30 | 3.1107 | 0 | N/A | 0 | 0
2022-05-14 03:00 | 2.8968 | 0 | N/A | 0 | 0
2022-05-14 03:30 | 2.8177 | 0 | N/A | 0 | 0
2022-05-14 04:00 | 2.652 | 0 | N/A | 0 | 0
2022-05-14 04:30 | 2.6387 | 0 | N/A | 0 | 0
2022-05-14 05:00 | 2.5911 | 0 | N/A | 0 | 0
2022-05-14 05:30 | 2.742 | 0 | N/A | 0 | 0
2022-05-14 06:00 | 2.8743 | 0 | N/A | 0 | 0
2022-05-14 06:30 | 3.2788 | 0 | N/A | 0 | 0
2022-05-14 07:00 | 3.4269 | 0 | N/A | 0 | 0
2022-05-14 07:30 | 3.629 | 0 | N/A | 0 | 0
2022-05-14 08:00 | 3.9431 | 0 | N/A | 0 | 0
2022-05-14 08:30 | 4.5147 | 0 | N/A | 0 | 0
2022-05-14 09:00 | 4.8769 | 0 | N/A | 0 | 0
2022-05-14 09:30 | 5.0043 | 0 | N/A | 0 | 0
2022-05-14 10:00 | 5.2731 | 0 | N/A | 0 | 0
2022-05-14 10:30 | 5.5581 | 0 | N/A | 0 | 0
2022-05-14 11:00 | 5.4172 | 0 | N/A | 0 | 0
2022-05-14 11:30 | 5.3271 | 0 | N/A | 0 | 0
2022-05-14 12:00 | 4.9766 | 0 | N/A | 0 | 0
2022-05-14 12:30 | 4.4933 | 0 | N/A | 0 | 0
2022-05-14 13:00 | 4.4098 | 0 | N/A | 0 | 0
2022-05-14 13:30 | 4.1054 | 0 | N/A | 0 | 0
2022-05-14 14:00 | 4.2376 | 0 | N/A | 0 | 0
2022-05-14 14:30 | 4.3226 | 0 | N/A | 0 | 0
2022-05-14 15:00 | 4.2552 | 0 | N/A | 0 | 0
2022-05-14 15:30 | 4.1799 | 0 | N/A | 0 | 0
2022-05-14 16:00 | 4.4146 | 0 | N/A | 0 | 0
2022-05-14 16:30 | 5.3502 | 0 | N/A | 0 | 0
2022-05-14 17:00 | 5.6844 | 0 | N/A | 0 | 0
2022-05-14 17:30 | 6.2005 | 0 | N/A | 0 | 0
2022-05-14 18:00 | 6.7529 | 0 | N/A | 0 | 0
2022-05-14 18:30 | 6.8922 | 0 | N/A | 0 | 0
2022-05-14 19:00 | 6.6054 | 0 | N/A | 0 | 0
2022-05-14 19:30 | 6.2869 | 0 | N/A | 0 | 0
2022-05-14 20:00 | 5.9512 | 0 | N/A | 0 | 0
2022-05-14 20:30 | 5.6168 | 0 | N/A | 0 | 0
2022-05-14 21:00 | 5.3813 | 0 | N/A | 0 | 0
2022-05-14 21:30 | 5.6636 | 0 | N/A | 0 | 0
2022-05-14 22:00 | 5.7564 | 0 | N/A | 0 | 0
2022-05-14 22:30 | 5.4065 | 0 | N/A | 0 | 0
2022-05-14 23:00 | 5.3994 | 0 | N/A | 0 | 0
2022-05-14 23:30 | 5.5959 | 0 | N/A | 0 | 0
2022-05-15 | 5.7935 | 0 | N/A | 0 | 0
2022-05-15 00:30 | 5.0142 | 0 | N/A | 0 | 0
2022-05-15 01:00 | 4.2979 | 0 | N/A | 0 | 0
2022-05-15 01:30 | 4.1557 | 0 | N/A | 0 | 0
2022-05-15 02:00 | 3.7506 | 0 | N/A | 0 | 0
2022-05-15 02:30 | 3.276 | 0 | N/A | 0 | 0
2022-05-15 03:00 | 3.024 | 0 | N/A | 0 | 0
2022-05-15 03:30 | 2.9218 | 0 | N/A | 0 | 0
2022-05-15 04:00 | 2.82 | 0 | N/A | 0 | 0
2022-05-15 04:30 | 2.7701 | 0 | N/A | 0 | 0
2022-05-15 05:00 | 2.7595 | 0 | N/A | 0 | 0
2022-05-15 05:30 | 2.8484 | 0 | N/A | 0 | 0
2022-05-15 06:00 | 2.9013 | 0 | N/A | 0 | 0
2022-05-15 06:30 | 3.1816 | 0 | N/A | 0 | 0
2022-05-15 07:00 | 3.3802 | 0 | N/A | 0 | 0
2022-05-15 07:30 | 3.4058 | 0 | N/A | 0 | 0
2022-05-15 08:00 | 3.7099 | 0 | N/A | 0 | 0
2022-05-15 08:30 | 3.7791 | 0 | N/A | 0 | 0
2022-05-15 09:00 | 3.5833 | 0 | N/A | 0 | 0
2022-05-15 09:30 | 3.0551 | 0 | N/A | 0 | 0
2022-05-15 10:00 | 2.5206 | 0 | N/A | 0 | 0
2022-05-15 10:30 | 1.9673 | 0 | N/A | 0 | 0
2022-05-15 11:00 | 2.4471 | 0 | N/A | 0 | 0
2022-05-15 11:30 | 2.8574 | 0 | N/A | 0 | 0
2022-05-15 12:00 | 2.7428 | 0 | N/A | 0 | 0
2022-05-15 12:30 | 2.4407 | 0 | N/A | 0 | 0
2022-05-15 13:00 | 2.0369 | 0 | N/A | 0 | 0
2022-05-15 13:30 | 1.5448 | 0 | N/A | 0 | 0
2022-05-15 14:00 | 1.5495 | 0 | N/A | 0 | 0
2022-05-15 14:30 | 1.9984 | 0 | N/A | 0 | 0
2022-05-15 15:00 | 2.2653 | 0 | N/A | 0 | 0
2022-05-15 15:30 | 2.6828 | 0 | N/A | 0 | 0
2022-05-15 16:00 | 3.4834 | 0 | N/A | 0 | 0
2022-05-15 16:30 | 4.8636 | 0 | N/A | 0 | 0
2022-05-15 17:00 | 5.7766 | 0 | N/A | 0 | 0
2022-05-15 17:30 | 6.4937 | 0 | N/A | 0 | 0
2022-05-15 18:00 | 7.1588 | 0 | N/A | 0 | 0
2022-05-15 18:30 | 7.2546 | 0 | N/A | 0 | 0
2022-05-15 19:00 | 6.9795 | 0 | N/A | 0 | 0
2022-05-15 19:30 | 6.6447 | 0 | N/A | 0 | 0
2022-05-15 20:00 | 6.3031 | 0 | N/A | 0 | 0
2022-05-15 20:30 | 5.8446 | 0 | N/A | 0 | 0
2022-05-15 21:00 | 5.5442 | 0 | N/A | 0 | 0
2022-05-15 21:30 | 5.7394 | 0 | N/A | 0 | 0
2022-05-15 22:00 | 5.7996 | 0 | N/A | 0 | 0
2022-05-15 22:30 | 5.353 | 0 | N/A | 0 | 0
2022-05-15 23:00 | 5.2763 | 0 | N/A | 0 | 0
2022-05-15 23:30 | 5.5076 | 0 | N/A | 0 | 0
2022-05-16 | 5.7898 | 0 | N/A | 0 | 0
2022-05-16 00:30 | 5.0456 | 0 | N/A | 0 | 0
2022-05-16 01:00 | 4.3739 | 0 | N/A | 0 | 0
2022-05-16 01:30 | 4.2263 | 0 | N/A | 0 | 0
2022-05-16 02:00 | 3.9524 | 0 | N/A | 0 | 0
2022-05-16 02:30 | 3.5206 | 0 | N/A | 0 | 0
2022-05-16 03:00 | 3.2476 | 0 | N/A | 0 | 0
2022-05-16 03:30 | 3.0971 | 0 | N/A | 0 | 0
2022-05-16 04:00 | 3.0538 | 0 | N/A | 0 | 0
2022-05-16 04:30 | 3.0954 | 0 | N/A | 0 | 0
2022-05-16 05:00 | 3.1533 | 0 | N/A | 0 | 0
2022-05-16 05:30 | 3.4223 | 0 | N/A | 0 | 0
2022-05-16 06:00 | 3.8377 | 0 | N/A | 0 | 0
2022-05-16 06:30 | 4.6362 | 0 | N/A | 0 | 0
2022-05-16 07:00 | 5.2432 | 0 | N/A | 0 | 0
2022-05-16 07:30 | 5.8542 | 0 | N/A | 0 | 0
2022-05-16 08:00 | 6.5969 | 0 | N/A | 0 | 0
2022-05-16 08:30 | 6.5851 | 0 | N/A | 0 | 0
2022-05-16 09:00 | 6.5261 | 0 | N/A | 0 | 0
2022-05-16 09:30 | 6.1878 | 0 | N/A | 0 | 0
2022-05-16 10:00 | 6.0863 | 0 | N/A | 0 | 0
2022-05-16 10:30 | 6.1806 | 0 | N/A | 0 | 0
2022-05-16 11:00 | 5.8363 | 0 | N/A | 0 | 0
2022-05-16 11:30 | 5.6383 | 0 | N/A | 0 | 0
2022-05-16 12:00 | 5.1384 | 0 | N/A | 0 | 0
2022-05-16 12:30 | 5.0771 | 0 | N/A | 0 | 0
2022-05-16 13:00 | 5.3248 | 0 | N/A | 0 | 0
2022-05-16 13:30 | 4.585 | 0 | N/A | 0 | 0
2022-05-16 14:00 | 4.5955 | 0 | N/A | 0 | 0
2022-05-16 14:30 | 4.2449 | 0 | N/A | 0 | 0
2022-05-16 15:00 | 3.7679 | 0 | N/A | 0 | 0
2022-05-16 15:30 | 4.1234 | 0 | N/A | 0 | 0
2022-05-16 16:00 | 5.6158 | 0 | N/A | 0 | 0
2022-05-16 16:30 | 6.1145 | 0 | N/A | 0 | 0
2022-05-16 17:00 | 6.2167 | 0 | N/A | 0 | 0
2022-05-16 17:30 | 7.2803 | 0 | N/A | 0 | 0
2022-05-16 18:00 | 8.2986 | 0 | N/A | 0 | 0
2022-05-16 18:30 | 8.6963 | 0 | N/A | 0 | 0
2022-05-16 19:00 | 8.2922 | 0 | N/A | 0 | 0
2022-05-16 19:30 | 7.9827 | 0 | N/A | 0 | 0
2022-05-16 20:00 | 7.7227 | 0 | N/A | 0 | 0
2022-05-16 20:30 | 7.3601 | 0 | N/A | 0 | 0
2022-05-16 21:00 | 6.9009 | 0 | N/A | 0 | 0
2022-05-16 21:30 | 7.0415 | 0 | N/A | 0 | 0
2022-05-16 22:00 | 6.8917 | 0 | N/A | 0 | 0
2022-05-16 22:30 | 6.3494 | 0 | N/A | 0 | 0
2022-05-16 23:00 | 6.0614 | 0 | N/A | 0 | 0
2022-05-16 23:30 | 6.1688 | 0 | N/A | 0 | 0
2022-05-17 | 6.496 | 0 | N/A | 0 | 0
2022-05-18 00:30 | 5.5225 | 0 | N/A | 0 | 0
2022-05-18 01:00 | 4.8203 | 0 | N/A | 0 | 0
2022-05-18 01:30 | 4.6673 | 0 | N/A | 0 | 0
2022-05-18 02:00 | 4.2582 | 0 | N/A | 0 | 0
2022-05-18 02:30 | 3.8106 | 0 | N/A | 0 | 0
2022-05-18 03:00 | 3.5371 | 0 | N/A | 0 | 0
2022-05-18 03:30 | 3.3771 | 0 | N/A | 0 | 0
2022-05-18 04:00 | 3.3464 | 0 | N/A | 0 | 0
2022-05-18 04:30 | 3.3297 | 0 | N/A | 0 | 0
2022-05-18 05:00 | 3.4821 | 0 | N/A | 0 | 0
2022-05-18 05:30 | 3.7819 | 0 | N/A | 0 | 0
2022-05-18 06:00 | 4.3139 | 0 | N/A | 0 | 0
2022-05-18 06:30 | 5.2438 | 0 | N/A | 0 | 0
2022-05-18 07:00 | 6.0469 | 0 | N/A | 0 | 0
2022-05-18 07:30 | 6.5482 | 0 | N/A | 0 | 0
2022-05-18 08:00 | 7.2616 | 0 | N/A | 0 | 0
2022-05-18 08:30 | 7.1936 | 0 | N/A | 0 | 0
2022-05-18 09:00 | 6.2832 | 0 | N/A | 0 | 0
2022-05-18 09:30 | 5.5968 | 0 | N/A | 0 | 0
2022-05-18 10:00 | 4.7687 | 0 | N/A | 0 | 0
2022-05-18 10:30 | 4.1517 | 0 | N/A | 0 | 0
2022-05-18 11:00 | 5.3889 | 0 | N/A | 0 | 0
2022-05-18 11:30 | 3.7144 | 0 | N/A | 0 | 0
2022-05-18 12:00 | 2.9628 | 0 | N/A | 0 | 0
2022-05-18 12:30 | 3.9725 | 0 | N/A | 0 | 0
2022-05-18 13:00 | 4.0444 | 0 | N/A | 0 | 0
2022-05-18 13:30 | 5.1627 | 0 | N/A | 0 | 0
2022-05-18 14:00 | 5.858 | 0 | N/A | 0 | 0
2022-05-18 14:30 | 4.137 | 0 | N/A | 0 | 0
2022-05-18 15:00 | 4.497 | 0 | N/A | 0 | 0
2022-05-18 15:30 | 5.6208 | 0 | N/A | 0 | 0
2022-05-18 16:00 | 6.2233 | 0 | N/A | 0 | 0
2022-05-18 16:30 | 6.028 | 0 | N/A | 0 | 0
2022-05-18 17:00 | 6.8643 | 0 | N/A | 0 | 0
2022-05-18 17:30 | 7.6389 | 0 | N/A | 0 | 0
2022-05-18 18:00 | 8.5621 | 0 | N/A | 0 | 0
2022-05-18 18:30 | 8.9617 | 0 | N/A | 0 | 0
2022-05-18 19:00 | 8.709 | 0 | N/A | 0 | 0
2022-05-18 19:30 | 8.4582 | 0 | N/A | 0 | 0
2022-05-18 20:00 | 8.0136 | 0 | N/A | 0 | 0
2022-05-18 20:30 | 7.6992 | 0 | N/A | 0 | 0
2022-05-18 21:00 | 7.2953 | 0 | N/A | 0 | 0
2022-05-18 21:30 | 7.296 | 0 | N/A | 0 | 0
2022-05-18 22:00 | 7.1978 | 0 | N/A | 0 | 0
2022-05-18 22:30 | 6.6632 | 0 | N/A | 0 | 0
2022-05-18 23:00 | 6.4696 | 0 | N/A | 0 | 0
2022-05-18 23:30 | 6.4516 | 0 | N/A | 0 | 0
2022-05-19 | 6.76 | 0 | N/A | 0 | 0
2022-05-19 00:30 | 5.8977 | 0 | N/A | 0 | 0
2022-05-19 01:00 | 5.1221 | 0 | N/A | 0 | 0
2022-05-19 01:30 | 5.0845 | 0 | N/A | 0 | 0
2022-05-19 02:00 | 4.6649 | 0 | N/A | 0 | 0
2022-05-19 02:30 | 4.222 | 0 | N/A | 0 | 0
2022-05-19 03:00 | 4.0045 | 0 | N/A | 0 | 0
2022-05-19 03:30 | 3.8443 | 0 | N/A | 0 | 0
2022-05-19 04:00 | 3.7358 | 0 | N/A | 0 | 0
2022-05-19 04:30 | 3.7252 | 0 | N/A | 0 | 0
2022-05-19 05:00 | 3.8169 | 0 | N/A | 0 | 0
2022-05-19 05:30 | 4.2359 | 0 | N/A | 0 | 0
2022-05-19 06:00 | 4.7696 | 0 | N/A | 0 | 0
2022-05-19 06:30 | 5.5182 | 0 | N/A | 0 | 0
2022-05-19 07:00 | 6.6423 | 0 | N/A | 0 | 0
2022-05-19 07:30 | 6.9131 | 0 | N/A | 0 | 0
2022-05-19 08:00 | 7.6282 | 0 | N/A | 0 | 0
2022-05-19 08:30 | 7.8642 | 0 | N/A | 0 | 0
2022-05-19 09:00 | 6.9172 | 0 | N/A | 0 | 0
2022-05-19 09:30 | 5.5321 | 0 | N/A | 0 | 0
2022-05-19 10:00 | 4.5601 | 0 | N/A | 0 | 0
2022-05-19 10:30 | 4.6403 | 0 | N/A | 0 | 0
2022-05-19 11:00 | 4.8565 | 0 | N/A | 0 | 0
2022-05-19 11:30 | 4.9728 | 0 | N/A | 0 | 0
2022-05-19 12:00 | 4.6788 | 0 | N/A | 0 | 0
2022-05-19 12:30 | 4.7713 | 0 | N/A | 0 | 0
2022-05-19 13:00 | 4.745 | 0 | N/A | 0 | 0
2022-05-19 13:30 | 5.0961 | 0 | N/A | 0 | 0
2022-05-19 14:00 | 5.193 | 0 | N/A | 0 | 0
2022-05-19 14:30 | 5.4696 | 0 | N/A | 0 | 0
2022-05-19 15:00 | 5.4701 | 0 | N/A | 0 | 0
2022-05-19 15:30 | 5.4368 | 0 | N/A | 0 | 0
2022-05-19 16:00 | 5.9144 | 0 | N/A | 0 | 0
2022-05-19 16:30 | 6.0485 | 0 | N/A | 0 | 0
2022-05-19 17:00 | 6.6822 | 0 | N/A | 0 | 0
2022-05-19 17:30 | 7.572 | 0 | N/A | 0 | 0
2022-05-19 18:00 | 8.3304 | 0 | N/A | 0 | 0
2022-05-19 18:30 | 8.6659 | 0 | N/A | 0 | 0
2022-05-19 19:00 | 8.4346 | 0 | N/A | 0 | 0
2022-05-19 19:30 | 8.1307 | 0 | N/A | 0 | 0
2022-05-19 20:00 | 7.9113 | 0 | N/A | 0 | 0
2022-05-19 20:30 | 7.5033 | 0 | N/A | 0 | 0
2022-05-19 21:00 | 7.0268 | 0 | N/A | 0 | 0
2022-05-19 21:30 | 7.0087 | 0 | N/A | 0 | 0
2022-05-19 22:00 | 6.9071 | 0 | N/A | 0 | 0
2022-05-19 22:30 | 6.2919 | 0 | N/A | 0 | 0
2022-05-19 23:00 | 6.115 | 0 | N/A | 0 | 0
2022-05-19 23:30 | 6.1464 | 0 | N/A | 0 | 0
2022-05-20 | 6.3111 | 0 | N/A | 0 | 0
2022-05-20 00:30 | 5.6212 | 0 | N/A | 0 | 0
2022-05-20 01:00 | 4.9992 | 0 | N/A | 0 | 0
2022-05-20 01:30 | 4.7738 | 0 | N/A | 0 | 0
2022-05-20 02:00 | 4.5177 | 0 | N/A | 0 | 0
2022-05-20 02:30 | 3.9944 | 0 | N/A | 0 | 0
2022-05-20 03:00 | 3.7115 | 0 | N/A | 0 | 0
2022-05-20 03:30 | 3.5396 | 0 | N/A | 0 | 0
2022-05-20 04:00 | 3.459 | 0 | N/A | 0 | 0
2022-05-20 04:30 | 3.4121 | 0 | N/A | 0 | 0
2022-05-20 05:00 | 3.5274 | 0 | N/A | 0 | 0
2022-05-20 05:30 | 3.8744 | 0 | N/A | 0 | 0
2022-05-20 06:00 | 4.3472 | 0 | N/A | 0 | 0
2022-05-20 06:30 | 5.0247 | 0 | N/A | 0 | 0
2022-05-20 07:00 | 5.8963 | 0 | N/A | 0 | 0
2022-05-20 07:30 | 6.526 | 0 | N/A | 0 | 0
2022-05-20 08:00 | 7.0782 | 0 | N/A | 0 | 0
2022-05-20 08:30 | 7.164 | 0 | N/A | 0 | 0
2022-05-20 09:00 | 6.7774 | 0 | N/A | 0 | 0
2022-05-20 09:30 | 6.4815 | 0 | N/A | 0 | 0
2022-05-20 10:00 | 5.9769 | 0 | N/A | 0 | 0
2022-05-20 10:30 | 5.4667 | 0 | N/A | 0 | 0
2022-05-20 11:00 | 4.4262 | 0 | N/A | 0 | 0
2022-05-20 11:30 | 3.7078 | 0 | N/A | 0 | 0
2022-05-20 12:00 | 2.9361 | 0 | N/A | 0 | 0
2022-05-20 12:30 | 2.1647 | 0 | N/A | 0 | 0
2022-05-20 13:00 | 2.007 | 0 | N/A | 0 | 0
2022-05-20 13:30 | 2.0816 | 0 | N/A | 0 | 0
2022-05-20 14:00 | 2.4723 | 0 | N/A | 0 | 0
2022-05-20 14:30 | 3.4261 | 0 | N/A | 0 | 0
2022-05-20 15:00 | 3.0389 | 0 | N/A | 0 | 0
2022-05-20 15:30 | 3.4923 | 0 | N/A | 0 | 0
2022-05-20 16:00 | 3.7287 | 0 | N/A | 0 | 0
2022-05-20 16:30 | 4.3937 | 0 | N/A | 0 | 0
2022-05-20 17:00 | 5.4148 | 0 | N/A | 0 | 0
2022-05-20 17:30 | 6.5604 | 0 | N/A | 0 | 0
2022-05-20 18:00 | 7.5797 | 0 | N/A | 0 | 0
2022-05-20 18:30 | 7.9333 | 0 | N/A | 0 | 0
2022-05-20 19:00 | 7.8572 | 0 | N/A | 0 | 0
2022-05-20 19:30 | 7.7616 | 0 | N/A | 0 | 0
2022-05-20 20:00 | 7.4511 | 0 | N/A | 0 | 0
2022-05-20 20:30 | 7.2385 | 0 | N/A | 0 | 0
2022-05-20 21:00 | 6.9058 | 0 | N/A | 0 | 0
2022-05-20 21:30 | 7.087 | 0 | N/A | 0 | 0
2022-05-20 22:00 | 7.1388 | 0 | N/A | 0 | 0
2022-05-20 22:30 | 6.6555 | 0 | N/A | 0 | 0
2022-05-20 23:00 | 6.4791 | 0 | N/A | 0 | 0
2022-05-20 23:30 | 6.4526 | 0 | N/A | 0 | 0
2022-05-21 | 6.6177 | 0 | N/A | 0 | 0
2022-05-21 00:30 | 5.8707 | 0 | N/A | 0 | 0
2022-05-21 01:00 | 5.2301 | 0 | N/A | 0 | 0
2022-05-21 01:30 | 5.0299 | 0 | N/A | 0 | 0
2022-05-21 02:00 | 4.6301 | 0 | N/A | 0 | 0
2022-05-21 02:30 | 4.2422 | 0 | N/A | 0 | 0
2022-05-21 03:00 | 3.9645 | 0 | N/A | 0 | 0
2022-05-21 03:30 | 3.8381 | 0 | N/A | 0 | 0
2022-05-21 04:00 | 3.6958 | 0 | N/A | 0 | 0
2022-05-21 04:30 | 3.7368 | 0 | N/A | 0 | 0
2022-05-21 05:00 | 3.7684 | 0 | N/A | 0 | 0
2022-05-21 05:30 | 3.9676 | 0 | N/A | 0 | 0
2022-05-21 06:00 | 4.3197 | 0 | N/A | 0 | 0
2022-05-21 06:30 | 4.761 | 0 | N/A | 0 | 0
2022-05-21 07:00 | 5.1806 | 0 | N/A | 0 | 0
2022-05-21 07:30 | 5.2323 | 0 | N/A | 0 | 0
2022-05-21 08:00 | 5.788 | 0 | N/A | 0 | 0
2022-05-21 08:30 | 5.8798 | 0 | N/A | 0 | 0
2022-05-21 09:00 | 5.5838 | 0 | N/A | 0 | 0
2022-05-21 09:30 | 4.9613 | 0 | N/A | 0 | 0
2022-05-21 10:00 | 4.0168 | 0 | N/A | 0 | 0
2022-05-21 10:30 | 3.0993 | 0 | N/A | 0 | 0
2022-05-21 11:00 | 2.3199 | 0 | N/A | 0 | 0
2022-05-21 11:30 | 1.713 | 0 | N/A | 0 | 0
2022-05-21 12:00 | 1.2884 | 0 | N/A | 0 | 0
2022-05-21 12:30 | 1.0755 | 0 | N/A | 0 | 0
2022-05-21 13:00 | 0.96888 | 0 | N/A | 0 | 0
2022-05-21 13:30 | 1.0589 | 0 | N/A | 0 | 0
2022-05-21 14:00 | 1.1645 | 0 | N/A | 0 | 0
2022-05-21 14:30 | 1.4384 | 0 | N/A | 0 | 0
2022-05-21 15:00 | 2.0917 | 0 | N/A | 0 | 0
2022-05-21 15:30 | 2.5903 | 0 | N/A | 0 | 0
2022-05-21 16:00 | 3.2541 | 0 | N/A | 0 | 0
2022-05-21 16:30 | 3.9785 | 0 | N/A | 0 | 0
2022-05-21 17:00 | 5.0605 | 0 | N/A | 0 | 0
2022-05-21 17:30 | 6.1231 | 0 | N/A | 0 | 0
2022-05-21 18:00 | 7.0518 | 0 | N/A | 0 | 0
2022-05-21 18:30 | 7.4409 | 0 | N/A | 0 | 0
2022-05-21 19:00 | 7.3022 | 0 | N/A | 0 | 0
2022-05-21 19:30 | 6.8857 | 0 | N/A | 0 | 0
2022-05-21 20:00 | 6.6744 | 0 | N/A | 0 | 0
2022-05-21 20:30 | 6.4283 | 0 | N/A | 0 | 0
2022-05-21 21:00 | 6.1434 | 0 | N/A | 0 | 0
2022-05-21 21:30 | 6.4326 | 0 | N/A | 0 | 0
2022-05-21 22:00 | 6.7558 | 0 | N/A | 0 | 0
2022-05-21 22:30 | 6.4168 | 0 | N/A | 0 | 0
2022-05-21 23:00 | 6.413 | 0 | N/A | 0 | 0
2022-05-21 23:30 | 6.5134 | 0 | N/A | 0 | 0
2022-05-22 | 6.727 | 0 | N/A | 0 | 0
2022-05-22 00:30 | 6.0527 | 0 | N/A | 0 | 0
2022-05-22 01:00 | 5.2867 | 0 | N/A | 0 | 0
2022-05-22 01:30 | 5.0339 | 0 | N/A | 0 | 0
2022-05-22 02:00 | 4.6908 | 0 | N/A | 0 | 0
2022-05-22 02:30 | 4.2181 | 0 | N/A | 0 | 0
2022-05-22 03:00 | 3.8331 | 0 | N/A | 0 | 0
2022-05-22 03:30 | 3.6411 | 0 | N/A | 0 | 0
2022-05-22 04:00 | 3.4895 | 0 | N/A | 0 | 0
2022-05-22 04:30 | 3.4719 | 0 | N/A | 0 | 0
2022-05-22 05:00 | 3.4371 | 0 | N/A | 0 | 0
2022-05-22 05:30 | 3.5192 | 0 | N/A | 0 | 0
2022-05-22 06:00 | 3.6999 | 0 | N/A | 0 | 0
2022-05-22 06:30 | 4.0879 | 0 | N/A | 0 | 0
2022-05-22 07:00 | 4.3891 | 0 | N/A | 0 | 0
2022-05-22 07:30 | 4.4615 | 0 | N/A | 0 | 0
2022-05-22 08:00 | 4.8997 | 0 | N/A | 0 | 0
2022-05-22 08:30 | 5.0285 | 0 | N/A | 0 | 0
2022-05-22 09:00 | 4.8137 | 0 | N/A | 0 | 0
2022-05-22 09:30 | 4.2834 | 0 | N/A | 0 | 0
2022-05-22 10:00 | 3.5816 | 0 | N/A | 0 | 0
2022-05-22 10:30 | 2.8419 | 0 | N/A | 0 | 0
2022-05-22 11:00 | 2.1277 | 0 | N/A | 0 | 0
2022-05-22 11:30 | 1.6428 | 0 | N/A | 0 | 0
2022-05-22 12:00 | 1.3027 | 0 | N/A | 0 | 0
2022-05-22 12:30 | 1.0523 | 0 | N/A | 0 | 0
2022-05-22 13:00 | 0.95975 | 0 | N/A | 0 | 0
2022-05-22 13:30 | 1.0303 | 0 | N/A | 0 | 0
2022-05-22 14:00 | 1.0979 | 0 | N/A | 0 | 0
2022-05-22 14:30 | 1.3973 | 0 | N/A | 0 | 0
2022-05-22 15:00 | 1.8966 | 0 | N/A | 0 | 0
2022-05-22 15:30 | 2.6 | 0 | N/A | 0 | 0
2022-05-22 16:00 | 3.391 | 0 | N/A | 0 | 0
2022-05-22 16:30 | 4.4464 | 0 | N/A | 0 | 0
2022-05-22 17:00 | 5.7181 | 0 | N/A | 0 | 0
2022-05-22 17:30 | 7.0124 | 0 | N/A | 0 | 0
2022-05-22 18:00 | 8.2072 | 0 | N/A | 0 | 0
2022-05-22 18:30 | 8.4748 | 0 | N/A | 0 | 0
2022-05-22 19:00 | 8.4033 | 0 | N/A | 0 | 0
2022-05-22 19:30 | 7.9266 | 0 | N/A | 0 | 0
2022-05-22 20:00 | 7.5029 | 0 | N/A | 0 | 0
2022-05-22 20:30 | 7.0007 | 0 | N/A | 0 | 0
2022-05-22 21:00 | 6.733 | 0 | N/A | 0 | 0
2022-05-22 21:30 | 6.8377 | 0 | N/A | 0 | 0
2022-05-22 22:00 | 6.8125 | 0 | N/A | 0 | 0
2022-05-22 22:30 | 6.2872 | 0 | N/A | 0 | 0
2022-05-22 23:00 | 6.1668 | 0 | N/A | 0 | 0
2022-05-22 23:30 | 6.1705 | 0 | N/A | 0 | 0
2022-05-23 | 6.3635 | 0 | N/A | 0 | 0
2022-05-23 00:30 | 5.7944 | 0 | N/A | 0 | 0
2022-05-23 01:00 | 5.2494 | 0 | N/A | 0 | 0
2022-05-23 01:30 | 5.0863 | 0 | N/A | 0 | 0
2022-05-23 02:00 | 4.8785 | 0 | N/A | 0 | 0
2022-05-23 02:30 | 4.3874 | 0 | N/A | 0 | 0
2022-05-23 03:00 | 4.0432 | 0 | N/A | 0 | 0
2022-05-23 03:30 | 3.9161 | 0 | N/A | 0 | 0
2022-05-23 04:00 | 3.8644 | 0 | N/A | 0 | 0
2022-05-23 04:30 | 3.8654 | 0 | N/A | 0 | 0
2022-05-23 05:00 | 3.9045 | 0 | N/A | 0 | 0
2022-05-23 05:30 | 4.3617 | 0 | N/A | 0 | 0
2022-05-23 06:00 | 4.9379 | 0 | N/A | 0 | 0
2022-05-23 06:30 | 5.7672 | 0 | N/A | 0 | 0
2022-05-23 07:00 | 6.7302 | 0 | N/A | 0 | 0
2022-05-23 07:30 | 7.267 | 0 | N/A | 0 | 0
2022-05-23 08:00 | 8.2516 | 0 | N/A | 0 | 0
2022-05-23 08:30 | 8.1736 | 0 | N/A | 0 | 0
2022-05-23 09:00 | 7.2968 | 0 | N/A | 0 | 0
2022-05-23 09:30 | 6.4401 | 0 | N/A | 0 | 0
2022-05-23 10:00 | 5.1143 | 0 | N/A | 0 | 0
2022-05-23 10:30 | 3.8674 | 0 | N/A | 0 | 0
2022-05-23 11:00 | 3.4098 | 0 | N/A | 0 | 0
2022-05-23 11:30 | 2.7228 | 0 | N/A | 0 | 0
2022-05-23 12:00 | 2.3431 | 0 | N/A | 0 | 0
2022-05-23 12:30 | 1.8732 | 0 | N/A | 0 | 0
2022-05-23 13:00 | 1.6622 | 0 | N/A | 0 | 0
2022-05-23 13:30 | 1.8195 | 0 | N/A | 0 | 0
2022-05-23 14:00 | 1.8867 | 0 | N/A | 0 | 0
2022-05-23 14:30 | 2.0914 | 0 | N/A | 0 | 0
2022-05-23 15:00 | 2.7274 | 0 | N/A | 0 | 0
2022-05-23 15:30 | 3.0679 | 0 | N/A | 0 | 0
2022-05-23 16:00 | 3.3738 | 0 | N/A | 0 | 0
2022-05-23 16:30 | 4.2251 | 0 | N/A | 0 | 0
2022-05-23 17:00 | 5.2021 | 0 | N/A | 0 | 0
2022-05-23 17:30 | 6.5135 | 0 | N/A | 0 | 0
2022-05-23 18:00 | 7.6197 | 0 | N/A | 0 | 0
2022-05-23 18:30 | 8.1413 | 0 | N/A | 0 | 0
2022-05-23 19:00 | 7.9963 | 0 | N/A | 0 | 0
2022-05-23 19:30 | 7.6106 | 0 | N/A | 0 | 0
2022-05-23 20:00 | 7.3274 | 0 | N/A | 0 | 0
2022-05-23 20:30 | 6.9832 | 0 | N/A | 0 | 0
2022-05-23 21:00 | 6.6863 | 0 | N/A | 0 | 0
2022-05-23 21:30 | 6.8796 | 0 | N/A | 0 | 0
2022-05-23 22:00 | 6.8387 | 0 | N/A | 0 | 0
2022-05-23 22:30 | 6.2161 | 0 | N/A | 0 | 0
2022-05-23 23:00 | 6.0187 | 0 | N/A | 0 | 0
2022-05-23 23:30 | 6.0587 | 0 | N/A | 0 | 0
2022-05-24 | 6.3217 | 0 | N/A | 0 | 0
2022-05-24 00:30 | 5.6223 | 0 | N/A | 0 | 0
2022-05-24 01:00 | 5.0252 | 0 | N/A | 0 | 0
2022-05-24 01:30 | 4.9422 | 0 | N/A | 0 | 0
2022-05-24 02:00 | 4.5848 | 0 | N/A | 0 | 0
2022-05-24 02:30 | 4.0954 | 0 | N/A | 0 | 0
2022-05-24 03:00 | 3.8697 | 0 | N/A | 0 | 0
2022-05-24 03:30 | 3.7474 | 0 | N/A | 0 | 0
2022-05-24 04:00 | 3.6781 | 0 | N/A | 0 | 0
2022-05-24 04:30 | 3.7091 | 0 | N/A | 0 | 0
2022-05-24 05:00 | 3.8991 | 0 | N/A | 0 | 0
2022-05-24 05:30 | 4.2871 | 0 | N/A | 0 | 0
2022-05-24 06:00 | 4.8367 | 0 | N/A | 0 | 0
2022-05-24 06:30 | 5.8738 | 0 | N/A | 0 | 0
2022-05-24 07:00 | 6.8237 | 0 | N/A | 0 | 0
2022-05-24 07:30 | 7.2845 | 0 | N/A | 0 | 0
2022-05-24 08:00 | 7.9797 | 0 | N/A | 0 | 0
2022-05-24 08:30 | 7.8656 | 0 | N/A | 0 | 0
2022-05-24 09:00 | 7.0222 | 0 | N/A | 0 | 0
2022-05-24 09:30 | 5.909 | 0 | N/A | 0 | 0
2022-05-24 10:00 | 4.688 | 0 | N/A | 0 | 0
2022-05-24 10:30 | 3.6017 | 0 | N/A | 0 | 0
2022-05-24 11:00 | 2.4287 | 0 | N/A | 0 | 0
2022-05-24 11:30 | 1.8748 | 0 | N/A | 0 | 0
2022-05-24 12:00 | 1.6687 | 0 | N/A | 0 | 0
2022-05-24 12:30 | 1.5889 | 0 | N/A | 0 | 0
2022-05-24 13:00 | 1.279 | 0 | N/A | 0 | 0
2022-05-24 13:30 | 1.4641 | 0 | N/A | 0 | 0
2022-05-24 14:00 | 1.6226 | 0 | N/A | 0 | 0
2022-05-24 14:30 | 2.1086 | 0 | N/A | 0 | 0
2022-05-24 15:00 | 2.3233 | 0 | N/A | 0 | 0
2022-05-24 15:30 | 2.8733 | 0 | N/A | 0 | 0
2022-05-24 16:00 | 3.0242 | 0 | N/A | 0 | 0
2022-05-24 16:30 | 3.9708 | 0 | N/A | 0 | 0
2022-05-24 17:00 | 5.0822 | 0 | N/A | 0 | 0
2022-05-24 17:30 | 6.2931 | 0 | N/A | 0 | 0
2022-05-24 18:00 | 7.436 | 0 | N/A | 0 | 0
2022-05-24 18:30 | 7.8194 | 0 | N/A | 0 | 0
2022-05-24 19:00 | 7.7527 | 0 | N/A | 0 | 0
2022-05-24 19:30 | 7.5569 | 0 | N/A | 0 | 0
2022-05-24 20:00 | 7.3051 | 0 | N/A | 0 | 0
2022-05-24 20:30 | 7.0764 | 0 | N/A | 0 | 0
2022-05-24 21:00 | 6.5619 | 0 | N/A | 0 | 0
2022-05-24 21:30 | 6.6728 | 0 | N/A | 0 | 0
2022-05-24 22:00 | 6.7413 | 0 | N/A | 0 | 0
2022-05-24 22:30 | 6.1722 | 0 | N/A | 0 | 0
2022-05-24 23:00 | 5.958 | 0 | N/A | 0 | 0
2022-05-24 23:30 | 5.9885 | 0 | N/A | 0 | 0
2022-05-25 | 6.1375 | 0 | N/A | 0 | 0
2022-05-25 00:30 | 5.2513 | 0 | N/A | 0 | 0
2022-05-25 01:00 | 4.6042 | 0 | N/A | 0 | 0
2022-05-25 01:30 | 4.5347 | 0 | N/A | 0 | 0
2022-05-25 02:00 | 4.2083 | 0 | N/A | 0 | 0
2022-05-25 02:30 | 3.8105 | 0 | N/A | 0 | 0
2022-05-25 03:00 | 3.5533 | 0 | N/A | 0 | 0
2022-05-25 03:30 | 3.3519 | 0 | N/A | 0 | 0
2022-05-25 04:00 | 3.2133 | 0 | N/A | 0 | 0
2022-05-25 04:30 | 3.1941 | 0 | N/A | 0 | 0
2022-05-25 05:00 | 3.4118 | 0 | N/A | 0 | 0
2022-05-25 05:30 | 3.664 | 0 | N/A | 0 | 0
2022-05-25 06:00 | 4.2373 | 0 | N/A | 0 | 0
2022-05-25 06:30 | 5.1761 | 0 | N/A | 0 | 0
2022-05-25 07:00 | 6.0806 | 0 | N/A | 0 | 0
2022-05-25 07:30 | 6.4781 | 0 | N/A | 0 | 0
2022-05-25 08:00 | 6.9786 | 0 | N/A | 0 | 0
2022-05-25 08:30 | 6.9671 | 0 | N/A | 0 | 0
2022-05-25 09:00 | 5.9563 | 0 | N/A | 0 | 0
2022-05-25 09:30 | 5.4237 | 0 | N/A | 0 | 0
2022-05-25 10:00 | 4.6411 | 0 | N/A | 0 | 0
2022-05-25 10:30 | 3.8648 | 0 | N/A | 0 | 0
2022-05-25 11:00 | 2.5946 | 0 | N/A | 0 | 0
2022-05-25 11:30 | 2.1232 | 0 | N/A | 0 | 0
2022-05-25 12:00 | 2.0549 | 0 | N/A | 0 | 0
2022-05-25 12:30 | 1.8426 | 0 | N/A | 0 | 0
2022-05-25 13:00 | 2.7429 | 0 | N/A | 0 | 0
2022-05-25 13:30 | 3.9936 | 0 | N/A | 0 | 0
2022-05-25 14:00 | 4.4755 | 0 | N/A | 0 | 0
2022-05-25 14:30 | 3.772 | 0 | N/A | 0 | 0
2022-05-25 15:00 | 3.2886 | 0 | N/A | 0 | 0
2022-05-25 15:30 | 3.7731 | 0 | N/A | 0 | 0
2022-05-25 16:00 | 4.2242 | 0 | N/A | 0 | 0
2022-05-25 16:30 | 4.778 | 0 | N/A | 0 | 0
2022-05-25 17:00 | 5.4161 | 0 | N/A | 0 | 0
2022-05-25 17:30 | 6.3287 | 0 | N/A | 0 | 0
2022-05-25 18:00 | 7.2981 | 0 | N/A | 0 | 0
2022-05-25 18:30 | 7.7403 | 0 | N/A | 0 | 0
2022-05-25 19:00 | 7.459 | 0 | N/A | 0 | 0
2022-05-25 19:30 | 7.2878 | 0 | N/A | 0 | 0
2022-05-25 20:00 | 7.0048 | 0 | N/A | 0 | 0
2022-05-25 20:30 | 6.6848 | 0 | N/A | 0 | 0
2022-05-25 21:00 | 6.376 | 0 | N/A | 0 | 0
2022-05-25 21:30 | 6.4544 | 0 | N/A | 0 | 0
2022-05-25 22:00 | 6.3655 | 0 | N/A | 0 | 0
2022-05-25 22:30 | 5.8696 | 0 | N/A | 0 | 0
2022-05-25 23:00 | 5.6316 | 0 | N/A | 0 | 0
2022-05-25 23:30 | 5.6753 | 0 | N/A | 0 | 0
2022-05-26 | 5.8866 | 0 | N/A | 0 | 0
2022-05-26 00:30 | 5.2266 | 0 | N/A | 0 | 0
2022-05-26 01:00 | 4.4659 | 0 | N/A | 0 | 0
2022-05-26 01:30 | 4.2877 | 0 | N/A | 0 | 0
2022-05-26 02:00 | 3.9339 | 0 | N/A | 0 | 0
2022-05-26 02:30 | 3.5177 | 0 | N/A | 0 | 0
2022-05-26 03:00 | 3.2967 | 0 | N/A | 0 | 0
2022-05-26 03:30 | 3.0608 | 0 | N/A | 0 | 0
2022-05-26 04:00 | 2.9756 | 0 | N/A | 0 | 0
2022-05-26 04:30 | 2.9518 | 0 | N/A | 0 | 0
2022-05-26 05:00 | 3.0875 | 0 | N/A | 0 | 0
2022-05-26 05:30 | 3.3335 | 0 | N/A | 0 | 0
2022-05-26 06:00 | 3.7876 | 0 | N/A | 0 | 0
2022-05-26 06:30 | 4.5601 | 0 | N/A | 0 | 0
2022-05-26 07:00 | 5.2939 | 0 | N/A | 0 | 0
2022-05-26 07:30 | 6.0375 | 0 | N/A | 0 | 0
2022-05-26 08:00 | 6.6425 | 0 | N/A | 0 | 0
2022-05-26 08:30 | 6.6879 | 0 | N/A | 0 | 0
2022-05-26 09:00 | 6.4322 | 0 | N/A | 0 | 0
2022-05-26 09:30 | 6.2551 | 0 | N/A | 0 | 0
2022-05-26 10:00 | 5.8717 | 0 | N/A | 0 | 0
2022-05-26 10:30 | 5.3509 | 0 | N/A | 0 | 0
2022-05-26 11:00 | 5.6541 | 0 | N/A | 0 | 0
2022-05-26 11:30 | 5.1521 | 0 | N/A | 0 | 0
2022-05-26 12:00 | 4.0981 | 0 | N/A | 0 | 0
2022-05-26 12:30 | 4.245 | 0 | N/A | 0 | 0
2022-05-26 13:00 | 4.0027 | 0 | N/A | 0 | 0
2022-05-26 13:30 | 3.9382 | 0 | N/A | 0 | 0
2022-05-26 14:00 | 3.3473 | 0 | N/A | 0 | 0
2022-05-26 14:30 | 3.9927 | 0 | N/A | 0 | 0
2022-05-26 15:00 | 4.5948 | 0 | N/A | 0 | 0
2022-05-26 15:30 | 4.7376 | 0 | N/A | 0 | 0
2022-05-26 16:00 | 4.9386 | 0 | N/A | 0 | 0
2022-05-26 16:30 | 5.1165 | 0 | N/A | 0 | 0
2022-05-26 17:00 | 5.6528 | 0 | N/A | 0 | 0
2022-05-26 17:30 | 6.6408 | 0 | N/A | 0 | 0
2022-05-26 18:00 | 7.5175 | 0 | N/A | 0 | 0
2022-05-26 18:30 | 7.71 | 0 | N/A | 0 | 0
2022-05-26 19:00 | 7.478 | 0 | N/A | 0 | 0
2022-05-26 19:30 | 7.3016 | 0 | N/A | 0 | 0
2022-05-26 20:00 | 7.0624 | 0 | N/A | 0 | 0
2022-05-26 20:30 | 6.7304 | 0 | N/A | 0 | 0
2022-05-26 21:00 | 6.3415 | 0 | N/A | 0 | 0
2022-05-26 21:30 | 6.3758 | 0 | N/A | 0 | 0
2022-05-26 22:00 | 6.3589 | 0 | N/A | 0 | 0
2022-05-26 22:30 | 5.7238 | 0 | N/A | 0 | 0
2022-05-26 23:00 | 5.5067 | 0 | N/A | 0 | 0
2022-05-26 23:30 | 5.668 | 0 | N/A | 0 | 0
2022-05-27 | 5.8724 | 0 | N/A | 0 | 0
2022-05-28 00:30 | 5.8369 | 0 | N/A | 0 | 0
2022-05-28 01:00 | 5.0498 | 0 | N/A | 0 | 0
2022-05-28 01:30 | 4.9009 | 0 | N/A | 0 | 0
2022-05-28 02:00 | 4.4821 | 0 | N/A | 0 | 0
2022-05-28 02:30 | 3.9121 | 0 | N/A | 0 | 0
2022-05-28 03:00 | 3.6905 | 0 | N/A | 0 | 0
2022-05-28 03:30 | 3.5145 | 0 | N/A | 0 | 0
2022-05-28 04:00 | 3.418 | 0 | N/A | 0 | 0
2022-05-28 04:30 | 3.3885 | 0 | N/A | 0 | 0
2022-05-28 05:00 | 3.3737 | 0 | N/A | 0 | 0
2022-05-28 05:30 | 3.554 | 0 | N/A | 0 | 0
2022-05-28 06:00 | 3.6915 | 0 | N/A | 0 | 0
2022-05-28 06:30 | 4.1648 | 0 | N/A | 0 | 0
2022-05-28 07:00 | 4.4174 | 0 | N/A | 0 | 0
2022-05-28 07:30 | 4.6438 | 0 | N/A | 0 | 0
2022-05-28 08:00 | 5.1377 | 0 | N/A | 0 | 0
2022-05-28 08:30 | 5.5932 | 0 | N/A | 0 | 0
2022-05-28 09:00 | 5.4502 | 0 | N/A | 0 | 0
2022-05-28 09:30 | 4.6655 | 0 | N/A | 0 | 0
2022-05-28 10:00 | 3.7811 | 0 | N/A | 0 | 0
2022-05-28 10:30 | 2.944 | 0 | N/A | 0 | 0
2022-05-28 11:00 | 2.444 | 0 | N/A | 0 | 0
2022-05-28 11:30 | 2.2284 | 0 | N/A | 0 | 0
2022-05-28 12:00 | 2.9265 | 0 | N/A | 0 | 0
2022-05-28 12:30 | 2.9307 | 0 | N/A | 0 | 0
2022-05-28 13:00 | 2.0964 | 0 | N/A | 0 | 0
2022-05-28 13:30 | 1.8212 | 0 | N/A | 0 | 0
2022-05-28 14:00 | 2.7371 | 0 | N/A | 0 | 0
2022-05-28 14:30 | 3.2387 | 0 | N/A | 0 | 0
2022-05-28 15:00 | 3.5701 | 0 | N/A | 0 | 0
2022-05-28 15:30 | 4.0201 | 0 | N/A | 0 | 0
2022-05-28 16:00 | 4.5179 | 0 | N/A | 0 | 0
2022-05-28 16:30 | 4.9311 | 0 | N/A | 0 | 0
2022-05-28 17:00 | 5.8573 | 0 | N/A | 0 | 0
2022-05-28 17:30 | 6.7691 | 0 | N/A | 0 | 0
2022-05-28 18:00 | 7.6057 | 0 | N/A | 0 | 0
2022-05-28 18:30 | 7.8304 | 0 | N/A | 0 | 0
2022-05-28 19:00 | 7.6763 | 0 | N/A | 0 | 0
2022-05-28 19:30 | 7.4074 | 0 | N/A | 0 | 0
2022-05-28 20:00 | 7.1309 | 0 | N/A | 0 | 0
2022-05-28 20:30 | 6.9012 | 0 | N/A | 0 | 0
2022-05-28 21:00 | 6.5093 | 0 | N/A | 0 | 0
2022-05-28 21:30 | 6.7521 | 0 | N/A | 0 | 0
2022-05-28 22:00 | 6.9291 | 0 | N/A | 0 | 0
2022-05-28 22:30 | 6.5941 | 0 | N/A | 0 | 0
2022-05-28 23:00 | 6.5054 | 0 | N/A | 0 | 0
2022-05-28 23:30 | 6.5898 | 0 | N/A | 0 | 0
2022-05-29 | 6.801 | 0 | N/A | 0 | 0
2022-05-29 00:30 | 6.0493 | 0 | N/A | 0 | 0
2022-05-29 01:00 | 5.3886 | 0 | N/A | 0 | 0
2022-05-29 01:30 | 5.2466 | 0 | N/A | 0 | 0
2022-05-29 02:00 | 4.849 | 0 | N/A | 0 | 0
2022-05-29 02:30 | 4.3362 | 0 | N/A | 0 | 0
2022-05-29 03:00 | 4.0214 | 0 | N/A | 0 | 0
2022-05-29 03:30 | 3.8148 | 0 | N/A | 0 | 0
2022-05-29 04:00 | 3.5847 | 0 | N/A | 0 | 0
2022-05-29 04:30 | 3.4878 | 0 | N/A | 0 | 0
2022-05-29 05:00 | 3.3787 | 0 | N/A | 0 | 0
2022-05-29 05:30 | 3.5414 | 0 | N/A | 0 | 0
2022-05-29 06:00 | 3.7073 | 0 | N/A | 0 | 0
2022-05-29 06:30 | 3.9421 | 0 | N/A | 0 | 0
2022-05-29 07:00 | 4.2304 | 0 | N/A | 0 | 0
2022-05-29 07:30 | 4.3193 | 0 | N/A | 0 | 0
2022-05-29 08:00 | 4.7759 | 0 | N/A | 0 | 0
2022-05-29 08:30 | 5.3019 | 0 | N/A | 0 | 0
2022-05-29 09:00 | 5.7134 | 0 | N/A | 0 | 0
2022-05-29 09:30 | 5.895 | 0 | N/A | 0 | 0
2022-05-29 10:00 | 6.09 | 0 | N/A | 0 | 0
2022-05-29 10:30 | 6.2078 | 0 | N/A | 0 | 0
2022-05-29 11:00 | 6.0417 | 0 | N/A | 0 | 0
2022-05-29 11:30 | 5.628 | 0 | N/A | 0 | 0
2022-05-29 12:00 | 5.088 | 0 | N/A | 0 | 0
2022-05-29 12:30 | 3.8207 | 0 | N/A | 0 | 0
2022-05-29 13:00 | 3.5692 | 0 | N/A | 0 | 0
2022-05-29 13:30 | 4.2987 | 0 | N/A | 0 | 0
2022-05-29 14:00 | 4.1338 | 0 | N/A | 0 | 0
2022-05-29 14:30 | 4.1458 | 0 | N/A | 0 | 0
2022-05-29 15:00 | 4.6048 | 0 | N/A | 0 | 0
2022-05-29 15:30 | 5.3403 | 0 | N/A | 0 | 0
2022-05-29 16:00 | 5.8789 | 0 | N/A | 0 | 0
2022-05-29 16:30 | 6.3815 | 0 | N/A | 0 | 0
2022-05-29 17:00 | 7.2803 | 0 | N/A | 0 | 0
2022-05-29 17:30 | 7.9194 | 0 | N/A | 0 | 0
2022-05-29 18:00 | 8.68 | 0 | N/A | 0 | 0
2022-05-29 18:30 | 8.8333 | 0 | N/A | 0 | 0
2022-05-29 19:00 | 8.5072 | 0 | N/A | 0 | 0
2022-05-29 19:30 | 8.1096 | 0 | N/A | 0 | 0
2022-05-29 20:00 | 7.6226 | 0 | N/A | 0 | 0
2022-05-29 20:30 | 7.1677 | 0 | N/A | 0 | 0
2022-05-29 21:00 | 6.6286 | 0 | N/A | 0 | 0
2022-05-29 21:30 | 6.6409 | 0 | N/A | 0 | 0
2022-05-29 22:00 | 6.6467 | 0 | N/A | 0 | 0
2022-05-29 22:30 | 6.1184 | 0 | N/A | 0 | 0
2022-05-29 23:00 | 6.1221 | 0 | N/A | 0 | 0
2022-05-29 23:30 | 6.1541 | 0 | N/A | 0 | 0
2022-05-30 | 6.4578 | 0 | N/A | 0 | 0
2022-05-30 00:30 | 5.6534 | 0 | N/A | 0 | 0
2022-05-30 01:00 | 4.9453 | 0 | N/A | 0 | 0
2022-05-30 01:30 | 4.8912 | 0 | N/A | 0 | 0
2022-05-30 02:00 | 4.567 | 0 | N/A | 0 | 0
2022-05-30 02:30 | 4.1185 | 0 | N/A | 0 | 0
2022-05-30 03:00 | 3.8814 | 0 | N/A | 0 | 0
2022-05-30 03:30 | 3.6474 | 0 | N/A | 0 | 0
2022-05-30 04:00 | 3.479 | 0 | N/A | 0 | 0
2022-05-30 04:30 | 3.4733 | 0 | N/A | 0 | 0
2022-05-30 05:00 | 3.5379 | 0 | N/A | 0 | 0
2022-05-30 05:30 | 3.8163 | 0 | N/A | 0 | 0
2022-05-30 06:00 | 4.2147 | 0 | N/A | 0 | 0
2022-05-30 06:30 | 5.1557 | 0 | N/A | 0 | 0
2022-05-30 07:00 | 5.926 | 0 | N/A | 0 | 0
2022-05-30 07:30 | 6.7751 | 0 | N/A | 0 | 0
2022-05-30 08:00 | 7.5574 | 0 | N/A | 0 | 0
2022-05-30 08:30 | 7.7681 | 0 | N/A | 0 | 0
2022-05-30 09:00 | 7.9808 | 0 | N/A | 0 | 0
2022-05-30 09:30 | 7.8613 | 0 | N/A | 0 | 0
2022-05-30 10:00 | 7.8502 | 0 | N/A | 0 | 0
2022-05-30 10:30 | 7.7336 | 0 | N/A | 0 | 0
2022-05-30 11:00 | 7.6068 | 0 | N/A | 0 | 0
2022-05-30 11:30 | 7.434 | 0 | N/A | 0 | 0
2022-05-30 12:00 | 7.7468 | 0 | N/A | 0 | 0
2022-05-30 12:30 | 7.6507 | 0 | N/A | 0 | 0
2022-05-30 13:00 | 7.5508 | 0 | N/A | 0 | 0
2022-05-30 13:30 | 7.8767 | 0 | N/A | 0 | 0
2022-05-30 14:00 | 7.8502 | 0 | N/A | 0 | 0
2022-05-30 14:30 | 7.5876 | 0 | N/A | 0 | 0
2022-05-30 15:00 | 7.567 | 0 | N/A | 0 | 0
2022-05-30 15:30 | 7.3751 | 0 | N/A | 0 | 0
2022-05-30 16:00 | 7.1657 | 0 | N/A | 0 | 0
2022-05-30 16:30 | 7.0528 | 0 | N/A | 0 | 0
2022-05-30 17:00 | 7.5317 | 0 | N/A | 0 | 0
2022-05-30 17:30 | 8.6278 | 0 | N/A | 0 | 0
2022-05-30 18:00 | 9.6045 | 0 | N/A | 0 | 0
2022-05-30 18:30 | 9.7031 | 0 | N/A | 0 | 0
2022-05-30 19:00 | 9.3279 | 0 | N/A | 0 | 0
2022-05-30 19:30 | 8.8627 | 0 | N/A | 0 | 0
2022-05-30 20:00 | 8.5567 | 0 | N/A | 0 | 0
2022-05-30 20:30 | 8.0645 | 0 | N/A | 0 | 0
2022-05-30 21:00 | 7.6897 | 0 | N/A | 0 | 0
2022-05-30 21:30 | 7.7129 | 0 | N/A | 0 | 0
2022-05-30 22:00 | 7.5504 | 0 | N/A | 0 | 0
2022-05-30 22:30 | 6.8477 | 0 | N/A | 0 | 0
2022-05-30 23:00 | 6.5461 | 0 | N/A | 0 | 0
2022-05-30 23:30 | 6.5275 | 0 | N/A | 0 | 0
2022-05-31 | 6.7214 | 0 | N/A | 0 | 0
2022-05-31 00:30 | 6.0784 | 0 | N/A | 0 | 0
2022-05-31 01:00 | 5.3638 | 0 | N/A | 0 | 0
2022-05-31 01:30 | 5.2527 | 0 | N/A | 0 | 0
2022-05-31 02:00 | 4.8435 | 0 | N/A | 0 | 0
2022-05-31 02:30 | 4.3721 | 0 | N/A | 0 | 0
2022-05-31 03:00 | 4.1799 | 0 | N/A | 0 | 0
2022-05-31 03:30 | 3.9716 | 0 | N/A | 0 | 0
2022-05-31 04:00 | 3.8519 | 0 | N/A | 0 | 0
2022-05-31 04:30 | 3.8106 | 0 | N/A | 0 | 0
2022-05-31 05:00 | 3.9543 | 0 | N/A | 0 | 0
2022-05-31 05:30 | 4.3015 | 0 | N/A | 0 | 0
2022-05-31 06:00 | 4.9211 | 0 | N/A | 0 | 0
2022-05-31 06:30 | 6.0124 | 0 | N/A | 0 | 0
2022-05-31 07:00 | 6.9106 | 0 | N/A | 0 | 0
2022-05-31 07:30 | 7.491 | 0 | N/A | 0 | 0
2022-05-31 08:00 | 8.2964 | 0 | N/A | 0 | 0
2022-05-31 08:30 | 8.3321 | 0 | N/A | 0 | 0
2022-05-31 09:00 | 7.554 | 0 | N/A | 0 | 0
2022-05-31 09:30 | 8.3471 | 0 | N/A | 0 | 0
2022-05-31 10:00 | 8.0007 | 0 | N/A | 0 | 0
2022-05-31 10:30 | 7.2078 | 0 | N/A | 0 | 0
2022-05-31 11:00 | 7.4742 | 0 | N/A | 0 | 0
2022-05-31 11:30 | 7.5005 | 0 | N/A | 0 | 0
2022-05-31 12:00 | 6.7737 | 0 | N/A | 0 | 0
2022-05-31 12:30 | 6.8772 | 0 | N/A | 0 | 0
2022-05-31 13:00 | 6.4452 | 0 | N/A | 0 | 0
2022-05-31 13:30 | 8.0645 | 0 | N/A | 0 | 0
2022-05-31 14:00 | 8.56 | 0 | N/A | 0 | 0
2022-05-31 14:30 | 8.0767 | 0 | N/A | 0 | 0
2022-05-31 15:00 | 7.81 | 0 | N/A | 0 | 0
2022-05-31 15:30 | 7.7378 | 0 | N/A | 0 | 0
2022-05-31 16:00 | 8.3114 | 0 | N/A | 0 | 0
2022-05-31 16:30 | 7.9233 | 0 | N/A | 0 | 0
2022-05-31 17:00 | 9.0143 | 0 | N/A | 0 | 0
2022-05-31 17:30 | 9.888 | 0 | N/A | 0 | 0
2022-05-31 18:00 | 10.89 | 0 | N/A | 0 | 0
2022-05-31 18:30 | 11.0133 | 0 | N/A | 0 | 0
2022-05-31 19:00 | 10.83 | 0 | N/A | 0 | 0
2022-05-31 19:30 | 10.4236 | 0 | N/A | 0 | 0
2022-05-31 20:00 | 9.9796 | 0 | N/A | 0 | 0
2022-05-31 20:30 | 9.7232 | 0 | N/A | 0 | 0
2022-05-31 21:00 | 9.0784 | 0 | N/A | 0 | 0
2022-05-31 21:30 | 9.0169 | 0 | N/A | 0 | 0
2022-05-31 22:00 | 8.9397 | 0 | N/A | 0 | 0
2022-05-31 22:30 | 8.0161 | 0 | N/A | 0 | 0
2022-05-31 23:00 | 7.5988 | 0 | N/A | 0 | 0
2022-05-31 23:30 | 7.4693 | 0 | N/A | 0 | 0
2022-06-01 | 7.7596 | 0 | N/A | 0 | 0
2022-06-01 00:30 | 7.2444 | 0 | N/A | 0 | 0
2022-06-01 01:00 | 6.5582 | 0 | N/A | 0 | 0
2022-06-01 01:30 | 6.3388 | 0 | N/A | 0 | 0
2022-06-01 02:00 | 5.885 | 0 | N/A | 0 | 0
2022-06-01 02:30 | 5.3933 | 0 | N/A | 0 | 0
2022-06-01 03:00 | 5.0673 | 0 | N/A | 0 | 0
2022-06-01 03:30 | 4.8523 | 0 | N/A | 0 | 0
2022-06-01 04:00 | 4.7898 | 0 | N/A | 0 | 0
2022-06-01 04:30 | 4.7175 | 0 | N/A | 0 | 0
2022-06-01 05:00 | 4.858 | 0 | N/A | 0 | 0
2022-06-01 05:30 | 5.2606 | 0 | N/A | 0 | 0
2022-06-01 06:00 | 5.9685 | 0 | N/A | 0 | 0
2022-06-01 06:30 | 6.9424 | 0 | N/A | 0 | 0
2022-06-01 07:00 | 7.7081 | 0 | N/A | 0 | 0
2022-06-01 07:30 | 8.4 | 0 | N/A | 0 | 0
2022-06-01 08:00 | 9.2943 | 0 | N/A | 0 | 0
2022-06-01 08:30 | 9.4067 | 0 | N/A | 0 | 0
2022-06-01 09:00 | 9.17 | 0 | N/A | 0 | 0
2022-06-01 09:30 | 8.7967 | 0 | N/A | 0 | 0
2022-06-01 10:00 | 8.8602 | 0 | N/A | 0 | 0
2022-06-01 10:30 | 8.2133 | 0 | N/A | 0 | 0
2022-06-01 11:00 | 7.19 | 0 | N/A | 0 | 0
2022-06-01 11:30 | 6.8467 | 0 | N/A | 0 | 0
2022-06-01 12:00 | 6.9538 | 0 | N/A | 0 | 0
2022-06-01 12:30 | 6.8376 | 0 | N/A | 0 | 0
2022-06-01 13:00 | 6.0113 | 0 | N/A | 0 | 0
2022-06-01 13:30 | 7.0961 | 0 | N/A | 0 | 0
2022-06-01 14:00 | 6.9476 | 0 | N/A | 0 | 0
2022-06-01 14:30 | 6.4902 | 0 | N/A | 0 | 0
2022-06-01 15:00 | 7.0706 | 0 | N/A | 0 | 0
2022-06-01 15:30 | 6.8748 | 0 | N/A | 0 | 0
2022-06-01 16:00 | 7.6624 | 0 | N/A | 0 | 0
2022-06-01 16:30 | 7.2261 | 0 | N/A | 0 | 0
2022-06-01 17:00 | 7.9168 | 0 | N/A | 0 | 0
2022-06-01 17:30 | 8.8998 | 0 | N/A | 0 | 0
2022-06-01 18:00 | 9.8518 | 0 | N/A | 0 | 0
2022-06-01 18:30 | 10.1505 | 0 | N/A | 0 | 0
2022-06-01 19:00 | 9.9508 | 0 | N/A | 0 | 0
2022-06-01 19:30 | 9.5919 | 0 | N/A | 0 | 0
2022-06-01 20:00 | 9.4164 | 0 | N/A | 0 | 0
2022-06-01 20:30 | 8.9934 | 0 | N/A | 0 | 0
2022-06-01 21:00 | 8.6764 | 0 | N/A | 0 | 0
2022-06-01 21:30 | 8.5729 | 0 | N/A | 0 | 0
2022-06-01 22:00 | 8.5051 | 0 | N/A | 0 | 0
2022-06-01 22:30 | 7.9156 | 0 | N/A | 0 | 0
2022-06-01 23:00 | 7.6271 | 0 | N/A | 0 | 0
2022-06-01 23:30 | 7.5536 | 0 | N/A | 0 | 0
2022-06-02 | 7.7744 | 0 | N/A | 0 | 0
2022-06-02 00:30 | 7.1862 | 0 | N/A | 0 | 0
2022-06-02 01:00 | 6.5714 | 0 | N/A | 0 | 0
2022-06-02 01:30 | 6.4063 | 0 | N/A | 0 | 0
2022-06-02 02:00 | 6.1721 | 0 | N/A | 0 | 0
2022-06-02 02:30 | 5.6394 | 0 | N/A | 0 | 0
2022-06-02 03:00 | 5.266 | 0 | N/A | 0 | 0
2022-06-02 03:30 | 5.0498 | 0 | N/A | 0 | 0
2022-06-02 04:00 | 4.9222 | 0 | N/A | 0 | 0
2022-06-02 04:30 | 4.9407 | 0 | N/A | 0 | 0
2022-06-02 05:00 | 5.0888 | 0 | N/A | 0 | 0
2022-06-02 05:30 | 5.5282 | 0 | N/A | 0 | 0
2022-06-02 06:00 | 6.1392 | 0 | N/A | 0 | 0
2022-06-02 06:30 | 7.3075 | 0 | N/A | 0 | 0
2022-06-02 07:00 | 8.2524 | 0 | N/A | 0 | 0
2022-06-02 07:30 | 8.4082 | 0 | N/A | 0 | 0
2022-06-02 08:00 | 9.6601 | 0 | N/A | 0 | 0
2022-06-02 08:30 | 10.004 | 0 | N/A | 0 | 0
2022-06-02 09:00 | 9.4106 | 0 | N/A | 0 | 0
2022-06-02 09:30 | 8.3945 | 0 | N/A | 0 | 0
2022-06-02 10:00 | 7.6505 | 0 | N/A | 0 | 0
2022-06-02 10:30 | 6.4569 | 0 | N/A | 0 | 0
2022-06-02 11:00 | 5.8741 | 0 | N/A | 0 | 0
2022-06-02 11:30 | 5.3155 | 0 | N/A | 0 | 0
2022-06-02 12:00 | 4.9672 | 0 | N/A | 0 | 0
2022-06-02 12:30 | 5.6777 | 0 | N/A | 0 | 0
2022-06-02 13:00 | 6.1919 | 0 | N/A | 0 | 0
2022-06-02 13:30 | 6.314 | 0 | N/A | 0 | 0
2022-06-02 14:00 | 6.1535 | 0 | N/A | 0 | 0
2022-06-02 14:30 | 6.7729 | 0 | N/A | 0 | 0
2022-06-02 15:00 | 6.9672 | 0 | N/A | 0 | 0
2022-06-02 15:30 | 6.9733 | 0 | N/A | 0 | 0
2022-06-02 16:00 | 7.4879 | 0 | N/A | 0 | 0
2022-06-02 16:30 | 7.9409 | 0 | N/A | 0 | 0
2022-06-02 17:00 | 8.301 | 0 | N/A | 0 | 0
2022-06-02 17:30 | 9.2084 | 0 | N/A | 0 | 0
2022-06-02 18:00 | 9.9508 | 0 | N/A | 0 | 0
2022-06-02 18:30 | 10.1036 | 0 | N/A | 0 | 0
2022-06-02 19:00 | 9.7617 | 0 | N/A | 0 | 0
2022-06-02 19:30 | 9.5094 | 0 | N/A | 0 | 0
2022-06-02 20:00 | 9.277 | 0 | N/A | 0 | 0
2022-06-02 20:30 | 8.969 | 0 | N/A | 0 | 0
2022-06-02 21:00 | 8.537 | 0 | N/A | 0 | 0
2022-06-02 21:30 | 8.5936 | 0 | N/A | 0 | 0
2022-06-02 22:00 | 8.4249 | 0 | N/A | 0 | 0
2022-06-02 22:30 | 7.4536 | 0 | N/A | 0 | 0
2022-06-02 23:00 | 7.1337 | 0 | N/A | 0 | 0
2022-06-02 23:30 | 6.9503 | 0 | N/A | 0 | 0
2022-06-03 | 7.2722 | 0 | N/A | 0 | 0
2022-06-04 00:30 | 6.4582 | 0 | N/A | 0 | 0
2022-06-04 01:00 | 5.7062 | 0 | N/A | 0 | 0
2022-06-04 01:30 | 5.4012 | 0 | N/A | 0 | 0
2022-06-04 02:00 | 5.0476 | 0 | N/A | 0 | 0
2022-06-04 02:30 | 4.5628 | 0 | N/A | 0 | 0
2022-06-04 03:00 | 4.2948 | 0 | N/A | 0 | 0
2022-06-04 03:30 | 3.9939 | 0 | N/A | 0 | 0
2022-06-04 04:00 | 3.8792 | 0 | N/A | 0 | 0
2022-06-04 04:30 | 3.8317 | 0 | N/A | 0 | 0
2022-06-04 05:00 | 3.76 | 0 | N/A | 0 | 0
2022-06-04 05:30 | 3.9285 | 0 | N/A | 0 | 0
2022-06-04 06:00 | 4.1302 | 0 | N/A | 0 | 0
2022-06-04 06:30 | 4.5641 | 0 | N/A | 0 | 0
2022-06-04 07:00 | 4.9025 | 0 | N/A | 0 | 0
2022-06-04 07:30 | 5.0442 | 0 | N/A | 0 | 0
2022-06-04 08:00 | 5.6684 | 0 | N/A | 0 | 0
2022-06-04 08:30 | 6.2234 | 0 | N/A | 0 | 0
2022-06-04 09:00 | 6.4028 | 0 | N/A | 0 | 0
2022-06-04 09:30 | 6.3572 | 0 | N/A | 0 | 0
2022-06-04 10:00 | 5.9063 | 0 | N/A | 0 | 0
2022-06-04 10:30 | 5.6545 | 0 | N/A | 0 | 0
2022-06-04 11:00 | 5.4969 | 0 | N/A | 0 | 0
2022-06-04 11:30 | 5.5419 | 0 | N/A | 0 | 0
2022-06-04 12:00 | 5.9868 | 0 | N/A | 0 | 0
2022-06-04 12:30 | 5.7964 | 0 | N/A | 0 | 0
2022-06-04 13:00 | 5.6368 | 0 | N/A | 0 | 0
2022-06-04 13:30 | 6.1102 | 0 | N/A | 0 | 0
2022-06-04 14:00 | 6.0459 | 0 | N/A | 0 | 0
2022-06-04 14:30 | 5.8917 | 0 | N/A | 0 | 0
2022-06-04 15:00 | 6.0618 | 0 | N/A | 0 | 0
2022-06-04 15:30 | 6.479 | 0 | N/A | 0 | 0
2022-06-04 16:00 | 7.029 | 0 | N/A | 0 | 0
2022-06-04 16:30 | 7.3039 | 0 | N/A | 0 | 0
2022-06-04 17:00 | 7.8633 | 0 | N/A | 0 | 0
2022-06-04 17:30 | 8.2533 | 0 | N/A | 0 | 0
2022-06-04 18:00 | 8.7344 | 0 | N/A | 0 | 0
2022-06-04 18:30 | 8.5881 | 0 | N/A | 0 | 0
2022-06-04 19:00 | 8.2707 | 0 | N/A | 0 | 0
2022-06-04 19:30 | 7.7723 | 0 | N/A | 0 | 0
2022-06-04 20:00 | 7.442 | 0 | N/A | 0 | 0
2022-06-04 20:30 | 7.0383 | 0 | N/A | 0 | 0
2022-06-04 21:00 | 6.7699 | 0 | N/A | 0 | 0
2022-06-04 21:30 | 6.9961 | 0 | N/A | 0 | 0
2022-06-04 22:00 | 7.1109 | 0 | N/A | 0 | 0
2022-06-04 22:30 | 6.9211 | 0 | N/A | 0 | 0
2022-06-04 23:00 | 6.705 | 0 | N/A | 0 | 0
2022-06-04 23:30 | 6.7232 | 0 | N/A | 0 | 0
2022-06-05 | 7.0784 | 0 | N/A | 0 | 0
2022-06-05 00:30 | 6.3659 | 0 | N/A | 0 | 0
2022-06-05 01:00 | 5.6772 | 0 | N/A | 0 | 0
2022-06-05 01:30 | 5.4275 | 0 | N/A | 0 | 0
2022-06-05 02:00 | 5.0488 | 0 | N/A | 0 | 0
2022-06-05 02:30 | 4.5435 | 0 | N/A | 0 | 0
2022-06-05 03:00 | 4.1631 | 0 | N/A | 0 | 0
2022-06-05 03:30 | 4.0062 | 0 | N/A | 0 | 0
2022-06-05 04:00 | 3.7853 | 0 | N/A | 0 | 0
2022-06-05 04:30 | 3.7431 | 0 | N/A | 0 | 0
2022-06-05 05:00 | 3.7494 | 0 | N/A | 0 | 0
2022-06-05 05:30 | 3.9325 | 0 | N/A | 0 | 0
2022-06-05 06:00 | 3.9961 | 0 | N/A | 0 | 0
2022-06-05 06:30 | 4.1901 | 0 | N/A | 0 | 0
2022-06-05 07:00 | 4.3398 | 0 | N/A | 0 | 0
2022-06-05 07:30 | 4.547 | 0 | N/A | 0 | 0
2022-06-05 08:00 | 5.0879 | 0 | N/A | 0 | 0
2022-06-05 08:30 | 5.7134 | 0 | N/A | 0 | 0
2022-06-05 09:00 | 6.169 | 0 | N/A | 0 | 0
2022-06-05 09:30 | 6.1899 | 0 | N/A | 0 | 0
2022-06-05 10:00 | 6.6412 | 0 | N/A | 0 | 0
2022-06-05 10:30 | 6.9908 | 0 | N/A | 0 | 0
2022-06-05 11:00 | 6.7381 | 0 | N/A | 0 | 0
2022-06-05 11:30 | 6.8289 | 0 | N/A | 0 | 0
2022-06-05 12:00 | 6.7405 | 0 | N/A | 0 | 0
2022-06-05 12:30 | 6.9016 | 0 | N/A | 0 | 0
2022-06-05 13:00 | 6.2318 | 0 | N/A | 0 | 0
2022-06-05 13:30 | 6.3896 | 0 | N/A | 0 | 0
2022-06-05 14:00 | 6.6834 | 0 | N/A | 0 | 0
2022-06-05 14:30 | 7.404 | 0 | N/A | 0 | 0
2022-06-05 15:00 | 7.5724 | 0 | N/A | 0 | 0
2022-06-05 15:30 | 7.7069 | 0 | N/A | 0 | 0
2022-06-05 16:00 | 7.7369 | 0 | N/A | 0 | 0
2022-06-05 16:30 | 8.3422 | 0 | N/A | 0 | 0
2022-06-05 17:00 | 8.969 | 0 | N/A | 0 | 0
2022-06-05 17:30 | 9.571 | 0 | N/A | 0 | 0
2022-06-05 18:00 | 10.0155 | 0 | N/A | 0 | 0
2022-06-05 18:30 | 9.825 | 0 | N/A | 0 | 0
2022-06-05 19:00 | 9.5299 | 0 | N/A | 0 | 0
2022-06-05 19:30 | 8.941 | 0 | N/A | 0 | 0
2022-06-05 20:00 | 8.5135 | 0 | N/A | 0 | 0
2022-06-05 20:30 | 8.1054 | 0 | N/A | 0 | 0
2022-06-05 21:00 | 7.5757 | 0 | N/A | 0 | 0
2022-06-05 21:30 | 7.663 | 0 | N/A | 0 | 0
2022-06-05 22:00 | 7.7053 | 0 | N/A | 0 | 0
2022-06-05 22:30 | 7.153 | 0 | N/A | 0 | 0
2022-06-05 23:00 | 6.8753 | 0 | N/A | 0 | 0
2022-06-05 23:30 | 6.792 | 0 | N/A | 0 | 0
2022-06-06 | 7.0924 | 0 | N/A | 0 | 0
2022-06-06 00:30 | 6.5888 | 0 | N/A | 0 | 0
2022-06-06 01:00 | 5.9485 | 0 | N/A | 0 | 0
2022-06-06 01:30 | 5.8582 | 0 | N/A | 0 | 0
2022-06-06 02:00 | 5.5657 | 0 | N/A | 0 | 0
2022-06-06 02:30 | 5.0972 | 0 | N/A | 0 | 0
2022-06-06 03:00 | 4.7013 | 0 | N/A | 0 | 0
2022-06-06 03:30 | 4.4918 | 0 | N/A | 0 | 0
2022-06-06 04:00 | 4.2602 | 0 | N/A | 0 | 0
2022-06-06 04:30 | 4.2124 | 0 | N/A | 0 | 0
2022-06-06 05:00 | 4.2765 | 0 | N/A | 0 | 0
2022-06-06 05:30 | 4.6465 | 0 | N/A | 0 | 0
2022-06-06 06:00 | 5.135 | 0 | N/A | 0 | 0
2022-06-06 06:30 | 6.1448 | 0 | N/A | 0 | 0
2022-06-06 07:00 | 6.8943 | 0 | N/A | 0 | 0
2022-06-06 07:30 | 7.4844 | 0 | N/A | 0 | 0
2022-06-06 08:00 | 8.473 | 0 | N/A | 0 | 0
2022-06-06 08:30 | 8.7907 | 0 | N/A | 0 | 0
2022-06-06 09:00 | 8.3107 | 0 | N/A | 0 | 0
2022-06-06 09:30 | 8.047 | 0 | N/A | 0 | 0
2022-06-06 10:00 | 7.2301 | 0 | N/A | 0 | 0
2022-06-06 10:30 | 6.6547 | 0 | N/A | 0 | 0
2022-06-06 11:00 | 5.7406 | 0 | N/A | 0 | 0
2022-06-06 11:30 | 6.0573 | 0 | N/A | 0 | 0
2022-06-06 12:00 | 6.3668 | 0 | N/A | 0 | 0
2022-06-06 12:30 | 5.4939 | 0 | N/A | 0 | 0
2022-06-06 13:00 | 5.2213 | 0 | N/A | 0 | 0
2022-06-06 13:30 | 4.908 | 0 | N/A | 0 | 0
2022-06-06 14:00 | 6.6719 | 0 | N/A | 0 | 0
2022-06-06 14:30 | 6.8107 | 0 | N/A | 0 | 0
2022-06-06 15:00 | 6.5875 | 0 | N/A | 0 | 0
2022-06-06 15:30 | 6.273 | 0 | N/A | 0 | 0
2022-06-06 16:00 | 6.1522 | 0 | N/A | 0 | 0
2022-06-06 16:30 | 7.3375 | 0 | N/A | 0 | 0
2022-06-06 17:00 | 8.4896 | 0 | N/A | 0 | 0
2022-06-06 17:30 | 9.5125 | 0 | N/A | 0 | 0
2022-06-06 18:00 | 10.4136 | 0 | N/A | 0 | 0
2022-06-06 18:30 | 10.5333 | 0 | N/A | 0 | 0
2022-06-06 19:00 | 10.1304 | 0 | N/A | 0 | 0
2022-06-06 19:30 | 9.6355 | 0 | N/A | 0 | 0
2022-06-06 20:00 | 9.2453 | 0 | N/A | 0 | 0
2022-06-06 20:30 | 8.9594 | 0 | N/A | 0 | 0
2022-06-06 21:00 | 8.4977 | 0 | N/A | 0 | 0
2022-06-06 21:30 | 8.4123 | 0 | N/A | 0 | 0
2022-06-06 22:00 | 8.297 | 0 | N/A | 0 | 0
2022-06-06 22:30 | 7.5305 | 0 | N/A | 0 | 0
2022-06-06 23:00 | 7.0349 | 0 | N/A | 0 | 0
2022-06-06 23:30 | 7.0118 | 0 | N/A | 0 | 0
2022-06-07 | 7.2329 | 0 | N/A | 0 | 0
2022-06-07 00:30 | 6.7379 | 0 | N/A | 0 | 0
2022-06-07 01:00 | 6.1294 | 0 | N/A | 0 | 0
2022-06-07 01:30 | 5.9546 | 0 | N/A | 0 | 0
2022-06-07 02:00 | 5.5208 | 0 | N/A | 0 | 0
2022-06-07 02:30 | 5.0495 | 0 | N/A | 0 | 0
2022-06-07 03:00 | 4.716 | 0 | N/A | 0 | 0
2022-06-07 03:30 | 4.5241 | 0 | N/A | 0 | 0
2022-06-07 04:00 | 4.3584 | 0 | N/A | 0 | 0
2022-06-07 04:30 | 4.3061 | 0 | N/A | 0 | 0
2022-06-07 05:00 | 4.4684 | 0 | N/A | 0 | 0
2022-06-07 05:30 | 4.969 | 0 | N/A | 0 | 0
2022-06-07 06:00 | 5.4099 | 0 | N/A | 0 | 0
2022-06-07 06:30 | 6.4118 | 0 | N/A | 0 | 0
2022-06-07 07:00 | 7.2119 | 0 | N/A | 0 | 0
2022-06-07 07:30 | 7.7034 | 0 | N/A | 0 | 0
2022-06-07 08:00 | 8.5499 | 0 | N/A | 0 | 0
2022-06-07 08:30 | 8.7056 | 0 | N/A | 0 | 0
2022-06-07 09:00 | 8.6445 | 0 | N/A | 0 | 0
2022-06-07 09:30 | 8.3074 | 0 | N/A | 0 | 0
2022-06-07 10:00 | 7.0905 | 0 | N/A | 0 | 0
2022-06-07 10:30 | 6.7791 | 0 | N/A | 0 | 0
2022-06-07 11:00 | 5.4671 | 0 | N/A | 0 | 0
2022-06-07 11:30 | 5.2997 | 0 | N/A | 0 | 0
2022-06-07 12:00 | 5.0529 | 0 | N/A | 0 | 0
2022-06-07 12:30 | 5.2466 | 0 | N/A | 0 | 0
2022-06-07 13:00 | 4.9282 | 0 | N/A | 0 | 0
2022-06-07 13:30 | 5.0057 | 0 | N/A | 0 | 0
2022-06-07 14:00 | 4.7105 | 0 | N/A | 0 | 0
2022-06-07 14:30 | 5.9061 | 0 | N/A | 0 | 0
2022-06-07 15:00 | 6.0609 | 0 | N/A | 0 | 0
2022-06-07 15:30 | 6.4071 | 0 | N/A | 0 | 0
2022-06-07 16:00 | 6.7529 | 0 | N/A | 0 | 0
2022-06-07 16:30 | 7.5636 | 0 | N/A | 0 | 0
2022-06-07 17:00 | 8.2494 | 0 | N/A | 0 | 0
2022-06-07 17:30 | 9.16 | 0 | N/A | 0 | 0
2022-06-07 18:00 | 10.0188 | 0 | N/A | 0 | 0
2022-06-07 18:30 | 10.1649 | 0 | N/A | 0 | 0
2022-06-07 19:00 | 9.8656 | 0 | N/A | 0 | 0
2022-06-07 19:30 | 9.4991 | 0 | N/A | 0 | 0
2022-06-07 20:00 | 9.2674 | 0 | N/A | 0 | 0
2022-06-07 20:30 | 8.8047 | 0 | N/A | 0 | 0
2022-06-07 21:00 | 8.308 | 0 | N/A | 0 | 0
2022-06-07 21:30 | 8.2351 | 0 | N/A | 0 | 0
2022-06-07 22:00 | 8.1191 | 0 | N/A | 0 | 0
2022-06-07 22:30 | 7.3747 | 0 | N/A | 0 | 0
2022-06-07 23:00 | 7.0055 | 0 | N/A | 0 | 0
2022-06-07 23:30 | 6.8908 | 0 | N/A | 0 | 0
2022-06-08 | 7.1957 | 0 | N/A | 0 | 0
2022-06-08 00:30 | 6.5007 | 0 | N/A | 0 | 0
2022-06-08 01:00 | 5.9135 | 0 | N/A | 0 | 0
2022-06-08 01:30 | 5.6915 | 0 | N/A | 0 | 0
2022-06-08 02:00 | 5.3788 | 0 | N/A | 0 | 0
2022-06-08 02:30 | 4.9512 | 0 | N/A | 0 | 0
2022-06-08 03:00 | 4.5928 | 0 | N/A | 0 | 0
2022-06-08 03:30 | 4.3882 | 0 | N/A | 0 | 0
2022-06-08 04:00 | 4.2106 | 0 | N/A | 0 | 0
2022-06-08 04:30 | 4.2202 | 0 | N/A | 0 | 0
2022-06-08 05:00 | 4.3395 | 0 | N/A | 0 | 0
2022-06-08 05:30 | 4.6613 | 0 | N/A | 0 | 0
2022-06-08 06:00 | 5.1258 | 0 | N/A | 0 | 0
2022-06-08 06:30 | 6.1311 | 0 | N/A | 0 | 0
2022-06-08 07:00 | 7.0229 | 0 | N/A | 0 | 0
2022-06-08 07:30 | 7.6233 | 0 | N/A | 0 | 0
2022-06-08 08:00 | 8.4125 | 0 | N/A | 0 | 0
2022-06-08 08:30 | 8.7308 | 0 | N/A | 0 | 0
2022-06-08 09:00 | 8.727 | 0 | N/A | 0 | 0
2022-06-08 09:30 | 8.5001 | 0 | N/A | 0 | 0
2022-06-08 10:00 | 8.0834 | 0 | N/A | 0 | 0
2022-06-08 10:30 | 7.4135 | 0 | N/A | 0 | 0
2022-06-08 11:00 | 7.3633 | 0 | N/A | 0 | 0
2022-06-08 11:30 | 7.3967 | 0 | N/A | 0 | 0
2022-06-08 12:00 | 6.7974 | 0 | N/A | 0 | 0
2022-06-08 12:30 | 6.7213 | 0 | N/A | 0 | 0
2022-06-08 13:00 | 6.225 | 0 | N/A | 0 | 0
2022-06-08 13:30 | 6.5646 | 0 | N/A | 0 | 0
2022-06-08 14:00 | 6.7402 | 0 | N/A | 0 | 0
2022-06-08 14:30 | 6.3528 | 0 | N/A | 0 | 0
2022-06-08 15:00 | 5.8351 | 0 | N/A | 0 | 0
2022-06-08 15:30 | 6.2868 | 0 | N/A | 0 | 0
2022-06-08 16:00 | 6.9262 | 0 | N/A | 0 | 0
2022-06-08 16:30 | 7.4168 | 0 | N/A | 0 | 0
2022-06-08 17:00 | 8.0081 | 0 | N/A | 0 | 0
2022-06-08 17:30 | 8.8906 | 0 | N/A | 0 | 0
2022-06-08 18:00 | 9.7803 | 0 | N/A | 0 | 0
2022-06-08 18:30 | 10.0101 | 0 | N/A | 0 | 0
2022-06-08 19:00 | 9.6839 | 0 | N/A | 0 | 0
2022-06-08 19:30 | 9.2253 | 0 | N/A | 0 | 0
2022-06-08 20:00 | 8.9601 | 0 | N/A | 0 | 0
2022-06-08 20:30 | 8.4956 | 0 | N/A | 0 | 0
2022-06-08 21:00 | 7.9564 | 0 | N/A | 0 | 0
2022-06-08 21:30 | 7.9583 | 0 | N/A | 0 | 0
2022-06-08 22:00 | 7.908 | 0 | N/A | 0 | 0
2022-06-08 22:30 | 7.1494 | 0 | N/A | 0 | 0
2022-06-08 23:00 | 6.7943 | 0 | N/A | 0 | 0
2022-06-08 23:30 | 6.9051 | 0 | N/A | 0 | 0
2022-06-09 | 7.0696 | 0 | N/A | 0 | 0
2022-06-09 00:30 | 6.4696 | 0 | N/A | 0 | 0
2022-06-09 01:00 | 5.7892 | 0 | N/A | 0 | 0
2022-06-09 01:30 | 5.6266 | 0 | N/A | 0 | 0
2022-06-09 02:00 | 5.1939 | 0 | N/A | 0 | 0
2022-06-09 02:30 | 4.6479 | 0 | N/A | 0 | 0
2022-06-09 03:00 | 4.2976 | 0 | N/A | 0 | 0
2022-06-09 03:30 | 4.0673 | 0 | N/A | 0 | 0
2022-06-09 04:00 | 3.9005 | 0 | N/A | 0 | 0
2022-06-09 04:30 | 3.9577 | 0 | N/A | 0 | 0
2022-06-09 05:00 | 4.0348 | 0 | N/A | 0 | 0
2022-06-09 05:30 | 4.4069 | 0 | N/A | 0 | 0
2022-06-09 06:00 | 4.8704 | 0 | N/A | 0 | 0
2022-06-09 06:30 | 5.8855 | 0 | N/A | 0 | 0
2022-06-09 07:00 | 6.8524 | 0 | N/A | 0 | 0
2022-06-09 07:30 | 7.5757 | 0 | N/A | 0 | 0
2022-06-09 08:00 | 8.2742 | 0 | N/A | 0 | 0
2022-06-09 08:30 | 8.5605 | 0 | N/A | 0 | 0
2022-06-09 09:00 | 8.3303 | 0 | N/A | 0 | 0
2022-06-09 09:30 | 8.1333 | 0 | N/A | 0 | 0
2022-06-09 10:00 | 7.8202 | 0 | N/A | 0 | 0
2022-06-09 10:30 | 7.4868 | 0 | N/A | 0 | 0
2022-06-09 11:00 | 7.4036 | 0 | N/A | 0 | 0
2022-06-09 11:30 | 6.9641 | 0 | N/A | 0 | 0
2022-06-09 12:00 | 6.5935 | 0 | N/A | 0 | 0
2022-06-09 12:30 | 6.5545 | 0 | N/A | 0 | 0
2022-06-09 13:00 | 6.1809 | 0 | N/A | 0 | 0
2022-06-09 13:30 | 5.5729 | 0 | N/A | 0 | 0
2022-06-09 14:00 | 5.9159 | 0 | N/A | 0 | 0
2022-06-09 14:30 | 6.1063 | 0 | N/A | 0 | 0
2022-06-09 15:00 | 6.6235 | 0 | N/A | 0 | 0
2022-06-09 15:30 | 6.467 | 0 | N/A | 0 | 0
2022-06-09 16:00 | 6.5347 | 0 | N/A | 0 | 0
2022-06-09 16:30 | 7.0074 | 0 | N/A | 0 | 0
2022-06-09 17:00 | 7.8876 | 0 | N/A | 0 | 0
2022-06-09 17:30 | 8.8071 | 0 | N/A | 0 | 0
2022-06-09 18:00 | 9.5302 | 0 | N/A | 0 | 0
2022-06-09 18:30 | 9.6351 | 0 | N/A | 0 | 0
2022-06-09 19:00 | 9.4186 | 0 | N/A | 0 | 0
2022-06-09 19:30 | 9.1822 | 0 | N/A | 0 | 0
2022-06-09 20:00 | 8.7315 | 0 | N/A | 0 | 0
2022-06-09 20:30 | 8.308 | 0 | N/A | 0 | 0
2022-06-09 21:00 | 7.9733 | 0 | N/A | 0 | 0
2022-06-09 21:30 | 7.7441 | 0 | N/A | 0 | 0
2022-06-09 22:00 | 7.5666 | 0 | N/A | 0 | 0
2022-06-09 22:30 | 7.0233 | 0 | N/A | 0 | 0
2022-06-09 23:00 | 6.6489 | 0 | N/A | 0 | 0
2022-06-09 23:30 | 6.587 | 0 | N/A | 0 | 0
2022-06-10 | 6.918 | 0 | N/A | 0 | 0
2022-06-10 00:30 | 6.2434 | 0 | N/A | 0 | 0
2022-06-10 01:00 | 5.5682 | 0 | N/A | 0 | 0
2022-06-10 01:30 | 5.4443 | 0 | N/A | 0 | 0
2022-06-10 02:00 | 5.0774 | 0 | N/A | 0 | 0
2022-06-10 02:30 | 4.5742 | 0 | N/A | 0 | 0
2022-06-10 03:00 | 4.2333 | 0 | N/A | 0 | 0
2022-06-10 03:30 | 4.0121 | 0 | N/A | 0 | 0
2022-06-10 04:00 | 3.8613 | 0 | N/A | 0 | 0
2022-06-10 04:30 | 3.7905 | 0 | N/A | 0 | 0
2022-06-10 05:00 | 4.0088 | 0 | N/A | 0 | 0
2022-06-10 05:30 | 4.3787 | 0 | N/A | 0 | 0
2022-06-10 06:00 | 4.7843 | 0 | N/A | 0 | 0
2022-06-10 06:30 | 5.5419 | 0 | N/A | 0 | 0
2022-06-10 07:00 | 6.4084 | 0 | N/A | 0 | 0
2022-06-10 07:30 | 6.8464 | 0 | N/A | 0 | 0
2022-06-10 08:00 | 7.5391 | 0 | N/A | 0 | 0
2022-06-10 08:30 | 8.1303 | 0 | N/A | 0 | 0
2022-06-10 09:00 | 8.1067 | 0 | N/A | 0 | 0
2022-06-10 09:30 | 7.8633 | 0 | N/A | 0 | 0
2022-06-10 10:00 | 7.6406 | 0 | N/A | 0 | 0
2022-06-10 10:30 | 7.2612 | 0 | N/A | 0 | 0
2022-06-10 11:00 | 6.8521 | 0 | N/A | 0 | 0
2022-06-10 11:30 | 6.4445 | 0 | N/A | 0 | 0
2022-06-10 12:00 | 6.2979 | 0 | N/A | 0 | 0
2022-06-10 12:30 | 6.3901 | 0 | N/A | 0 | 0
2022-06-10 13:00 | 6.1825 | 0 | N/A | 0 | 0
2022-06-10 13:30 | 5.748 | 0 | N/A | 0 | 0
2022-06-10 14:00 | 5.6556 | 0 | N/A | 0 | 0
2022-06-10 14:30 | 5.752 | 0 | N/A | 0 | 0
2022-06-10 15:00 | 5.1893 | 0 | N/A | 0 | 0
2022-06-10 15:30 | 5.2167 | 0 | N/A | 0 | 0
2022-06-10 16:00 | 6.0652 | 0 | N/A | 0 | 0
2022-06-10 16:30 | 6.9566 | 0 | N/A | 0 | 0
2022-06-10 17:00 | 7.4605 | 0 | N/A | 0 | 0
2022-06-10 17:30 | 8.1428 | 0 | N/A | 0 | 0
2022-06-10 18:00 | 8.7701 | 0 | N/A | 0 | 0
2022-06-10 18:30 | 8.826 | 0 | N/A | 0 | 0
2022-06-10 19:00 | 8.6221 | 0 | N/A | 0 | 0
2022-06-10 19:30 | 8.2798 | 0 | N/A | 0 | 0
2022-06-10 20:00 | 8.0918 | 0 | N/A | 0 | 0
2022-06-10 20:30 | 7.7961 | 0 | N/A | 0 | 0
2022-06-10 21:00 | 7.5333 | 0 | N/A | 0 | 0
2022-06-10 21:30 | 7.5805 | 0 | N/A | 0 | 0
2022-06-10 22:00 | 7.6955 | 0 | N/A | 0 | 0
2022-06-10 22:30 | 7.0907 | 0 | N/A | 0 | 0
2022-06-10 23:00 | 6.9637 | 0 | N/A | 0 | 0
2022-06-10 23:30 | 6.9604 | 0 | N/A | 0 | 0
2022-06-11 | 7.1448 | 0 | N/A | 0 | 0
2022-06-11 00:30 | 6.5087 | 0 | N/A | 0 | 0
2022-06-11 01:00 | 5.6525 | 0 | N/A | 0 | 0
2022-06-11 01:30 | 5.4687 | 0 | N/A | 0 | 0
2022-06-11 02:00 | 5.0613 | 0 | N/A | 0 | 0
2022-06-11 02:30 | 4.5257 | 0 | N/A | 0 | 0
2022-06-11 03:00 | 4.242 | 0 | N/A | 0 | 0
2022-06-11 03:30 | 4.108 | 0 | N/A | 0 | 0
2022-06-11 04:00 | 3.9386 | 0 | N/A | 0 | 0
2022-06-11 04:30 | 3.853 | 0 | N/A | 0 | 0
2022-06-11 05:00 | 3.8634 | 0 | N/A | 0 | 0
2022-06-11 05:30 | 3.989 | 0 | N/A | 0 | 0
2022-06-11 06:00 | 4.1719 | 0 | N/A | 0 | 0
2022-06-11 06:30 | 4.6062 | 0 | N/A | 0 | 0
2022-06-11 07:00 | 4.7929 | 0 | N/A | 0 | 0
2022-06-11 07:30 | 4.9324 | 0 | N/A | 0 | 0
2022-06-11 08:00 | 5.4802 | 0 | N/A | 0 | 0
2022-06-11 08:30 | 6.1905 | 0 | N/A | 0 | 0
2022-06-11 09:00 | 6.4775 | 0 | N/A | 0 | 0
2022-06-11 09:30 | 6.3475 | 0 | N/A | 0 | 0
2022-06-11 10:00 | 6.6171 | 0 | N/A | 0 | 0
2022-06-11 10:30 | 6.2151 | 0 | N/A | 0 | 0
2022-06-11 11:00 | 6.2827 | 0 | N/A | 0 | 0
2022-06-11 11:30 | 6.0191 | 0 | N/A | 0 | 0
2022-06-11 12:00 | 6.1346 | 0 | N/A | 0 | 0
2022-06-11 12:30 | 6.1059 | 0 | N/A | 0 | 0
2022-06-11 13:00 | 5.9325 | 0 | N/A | 0 | 0
2022-06-11 13:30 | 5.8954 | 0 | N/A | 0 | 0
2022-06-11 14:00 | 6.26 | 0 | N/A | 0 | 0
2022-06-11 14:30 | 6.2747 | 0 | N/A | 0 | 0
2022-06-11 15:00 | 6.4034 | 0 | N/A | 0 | 0
2022-06-11 15:30 | 6.8158 | 0 | N/A | 0 | 0
2022-06-11 16:00 | 6.9946 | 0 | N/A | 0 | 0
2022-06-11 16:30 | 7.2322 | 0 | N/A | 0 | 0
2022-06-11 17:00 | 7.81 | 0 | N/A | 0 | 0
2022-06-11 17:30 | 8.3469 | 0 | N/A | 0 | 0
2022-06-11 18:00 | 8.7346 | 0 | N/A | 0 | 0
2022-06-11 18:30 | 8.6989 | 0 | N/A | 0 | 0
2022-06-11 19:00 | 8.3117 | 0 | N/A | 0 | 0
2022-06-11 19:30 | 7.9317 | 0 | N/A | 0 | 0
2022-06-11 20:00 | 7.5936 | 0 | N/A | 0 | 0
2022-06-11 20:30 | 7.2163 | 0 | N/A | 0 | 0
2022-06-11 21:00 | 7.0404 | 0 | N/A | 0 | 0
2022-06-11 21:30 | 7.3084 | 0 | N/A | 0 | 0
2022-06-11 22:00 | 7.3718 | 0 | N/A | 0 | 0
2022-06-11 22:30 | 7.0106 | 0 | N/A | 0 | 0
2022-06-11 23:00 | 6.9293 | 0 | N/A | 0 | 0
2022-06-11 23:30 | 6.8537 | 0 | N/A | 0 | 0
2022-06-12 | 7.145 | 0 | N/A | 0 | 0
2022-06-12 00:30 | 6.5252 | 0 | N/A | 0 | 0
2022-06-12 01:00 | 5.7394 | 0 | N/A | 0 | 0
2022-06-12 01:30 | 5.5156 | 0 | N/A | 0 | 0
2022-06-12 02:00 | 5.2043 | 0 | N/A | 0 | 0
2022-06-12 02:30 | 4.7013 | 0 | N/A | 0 | 0
2022-06-12 03:00 | 4.3393 | 0 | N/A | 0 | 0
2022-06-12 03:30 | 4.0941 | 0 | N/A | 0 | 0
2022-06-12 04:00 | 4.0175 | 0 | N/A | 0 | 0
2022-06-12 04:30 | 3.9067 | 0 | N/A | 0 | 0
2022-06-12 05:00 | 3.8458 | 0 | N/A | 0 | 0
2022-06-12 05:30 | 3.9054 | 0 | N/A | 0 | 0
2022-06-12 06:00 | 3.9891 | 0 | N/A | 0 | 0
2022-06-12 06:30 | 4.1567 | 0 | N/A | 0 | 0
2022-06-12 07:00 | 4.3544 | 0 | N/A | 0 | 0
2022-06-12 07:30 | 4.4433 | 0 | N/A | 0 | 0
2022-06-12 08:00 | 4.9199 | 0 | N/A | 0 | 0
2022-06-12 08:30 | 5.7311 | 0 | N/A | 0 | 0
2022-06-12 09:00 | 6.1675 | 0 | N/A | 0 | 0
2022-06-12 09:30 | 6.3852 | 0 | N/A | 0 | 0
2022-06-12 10:00 | 6.3876 | 0 | N/A | 0 | 0
2022-06-12 10:30 | 6.3604 | 0 | N/A | 0 | 0
2022-06-12 11:00 | 5.9089 | 0 | N/A | 0 | 0
2022-06-12 11:30 | 5.9441 | 0 | N/A | 0 | 0
2022-06-12 12:00 | 5.7263 | 0 | N/A | 0 | 0
2022-06-12 12:30 | 5.408 | 0 | N/A | 0 | 0
2022-06-12 13:00 | 5.2614 | 0 | N/A | 0 | 0
2022-06-12 13:30 | 4.8603 | 0 | N/A | 0 | 0
2022-06-12 14:00 | 4.773 | 0 | N/A | 0 | 0
2022-06-12 14:30 | 5.6965 | 0 | N/A | 0 | 0
2022-06-12 15:00 | 5.1672 | 0 | N/A | 0 | 0
2022-06-12 15:30 | 4.9622 | 0 | N/A | 0 | 0
2022-06-12 16:00 | 6.1628 | 0 | N/A | 0 | 0
2022-06-12 16:30 | 6.5921 | 0 | N/A | 0 | 0
2022-06-12 17:00 | 7.3459 | 0 | N/A | 0 | 0
2022-06-12 17:30 | 8.2295 | 0 | N/A | 0 | 0
2022-06-12 18:00 | 8.7542 | 0 | N/A | 0 | 0
2022-06-12 18:30 | 8.7381 | 0 | N/A | 0 | 0
2022-06-12 19:00 | 8.3047 | 0 | N/A | 0 | 0
2022-06-12 19:30 | 7.9054 | 0 | N/A | 0 | 0
2022-06-12 20:00 | 7.4979 | 0 | N/A | 0 | 0
2022-06-12 20:30 | 7.1899 | 0 | N/A | 0 | 0
2022-06-12 21:00 | 6.908 | 0 | N/A | 0 | 0
2022-06-12 21:30 | 7.0887 | 0 | N/A | 0 | 0
2022-06-12 22:00 | 7.1457 | 0 | N/A | 0 | 0
2022-06-12 22:30 | 6.7708 | 0 | N/A | 0 | 0
2022-06-12 23:00 | 6.6761 | 0 | N/A | 0 | 0
2022-06-12 23:30 | 6.7716 | 0 | N/A | 0 | 0
2022-06-13 | 6.9245 | 0 | N/A | 0 | 0
2022-06-13 00:30 | 6.1921 | 0 | N/A | 0 | 0
2022-06-13 01:00 | 5.4935 | 0 | N/A | 0 | 0
2022-06-13 01:30 | 5.2725 | 0 | N/A | 0 | 0
2022-06-13 02:00 | 4.9955 | 0 | N/A | 0 | 0
2022-06-13 02:30 | 4.4943 | 0 | N/A | 0 | 0
2022-06-13 03:00 | 4.1589 | 0 | N/A | 0 | 0
2022-06-13 03:30 | 3.8614 | 0 | N/A | 0 | 0
2022-06-13 04:00 | 3.8074 | 0 | N/A | 0 | 0
2022-06-13 04:30 | 3.6823 | 0 | N/A | 0 | 0
2022-06-13 05:00 | 3.6905 | 0 | N/A | 0 | 0
2022-06-13 05:30 | 3.7938 | 0 | N/A | 0 | 0
2022-06-13 06:00 | 3.9648 | 0 | N/A | 0 | 0
2022-06-13 06:30 | 4.3474 | 0 | N/A | 0 | 0
2022-06-13 07:00 | 4.5015 | 0 | N/A | 0 | 0
2022-06-13 07:30 | 4.4793 | 0 | N/A | 0 | 0
2022-06-13 08:00 | 5.0422 | 0 | N/A | 0 | 0
2022-06-13 08:30 | 5.5002 | 0 | N/A | 0 | 0
2022-06-13 09:00 | 5.7116 | 0 | N/A | 0 | 0
2022-06-13 09:30 | 5.8086 | 0 | N/A | 0 | 0
2022-06-13 10:00 | 5.9217 | 0 | N/A | 0 | 0
2022-06-13 10:30 | 5.6356 | 0 | N/A | 0 | 0
2022-06-13 11:00 | 5.0338 | 0 | N/A | 0 | 0
2022-06-13 11:30 | 4.8357 | 0 | N/A | 0 | 0
2022-06-13 12:00 | 4.8307 | 0 | N/A | 0 | 0
2022-06-13 12:30 | 4.7217 | 0 | N/A | 0 | 0
2022-06-13 13:00 | 4.7851 | 0 | N/A | 0 | 0
2022-06-13 13:30 | 5.0795 | 0 | N/A | 0 | 0
2022-06-13 14:00 | 5.2184 | 0 | N/A | 0 | 0
2022-06-13 14:30 | 5.1981 | 0 | N/A | 0 | 0
2022-06-13 15:00 | 5.506 | 0 | N/A | 0 | 0
2022-06-13 15:30 | 5.8884 | 0 | N/A | 0 | 0
2022-06-13 16:00 | 6.2129 | 0 | N/A | 0 | 0
2022-06-13 16:30 | 6.6761 | 0 | N/A | 0 | 0
2022-06-13 17:00 | 7.4553 | 0 | N/A | 0 | 0
2022-06-13 17:30 | 8.2044 | 0 | N/A | 0 | 0
2022-06-13 18:00 | 8.9305 | 0 | N/A | 0 | 0
2022-06-13 18:30 | 8.9961 | 0 | N/A | 0 | 0
2022-06-13 19:00 | 8.6575 | 0 | N/A | 0 | 0
2022-06-13 19:30 | 8.1624 | 0 | N/A | 0 | 0
2022-06-13 20:00 | 7.8324 | 0 | N/A | 0 | 0
2022-06-13 20:30 | 7.4366 | 0 | N/A | 0 | 0
2022-06-13 21:00 | 7.0389 | 0 | N/A | 0 | 0
2022-06-13 21:30 | 7.0629 | 0 | N/A | 0 | 0
2022-06-13 22:00 | 6.959 | 0 | N/A | 0 | 0
2022-06-13 22:30 | 6.2671 | 0 | N/A | 0 | 0
2022-06-13 23:00 | 6.1063 | 0 | N/A | 0 | 0
2022-06-13 23:30 | 6.211 | 0 | N/A | 0 | 0
2022-06-14 | 6.5162 | 0 | N/A | 0 | 0
2022-06-14 00:30 | 5.889 | 0 | N/A | 0 | 0
2022-06-14 01:00 | 5.3403 | 0 | N/A | 0 | 0
2022-06-14 01:30 | 5.3151 | 0 | N/A | 0 | 0
2022-06-14 02:00 | 4.9692 | 0 | N/A | 0 | 0
2022-06-14 02:30 | 4.4406 | 0 | N/A | 0 | 0
2022-06-14 03:00 | 4.1161 | 0 | N/A | 0 | 0
2022-06-14 03:30 | 3.8845 | 0 | N/A | 0 | 0
2022-06-14 04:00 | 3.7168 | 0 | N/A | 0 | 0
2022-06-14 04:30 | 3.6538 | 0 | N/A | 0 | 0
2022-06-14 05:00 | 3.8708 | 0 | N/A | 0 | 0
2022-06-14 05:30 | 4.173 | 0 | N/A | 0 | 0
2022-06-14 06:00 | 4.6564 | 0 | N/A | 0 | 0
2022-06-14 06:30 | 5.3708 | 0 | N/A | 0 | 0
2022-06-14 07:00 | 6.2598 | 0 | N/A | 0 | 0
2022-06-14 07:30 | 6.9059 | 0 | N/A | 0 | 0
2022-06-14 08:00 | 7.6164 | 0 | N/A | 0 | 0
2022-06-14 08:30 | 7.9096 | 0 | N/A | 0 | 0
2022-06-14 09:00 | 7.7317 | 0 | N/A | 0 | 0
2022-06-14 09:30 | 7.4162 | 0 | N/A | 0 | 0
2022-06-14 10:00 | 7.0622 | 0 | N/A | 0 | 0
2022-06-14 10:30 | 6.613 | 0 | N/A | 0 | 0
2022-06-14 11:00 | 6.5931 | 0 | N/A | 0 | 0
2022-06-14 11:30 | 6.5258 | 0 | N/A | 0 | 0
2022-06-14 12:00 | 5.8803 | 0 | N/A | 0 | 0
2022-06-14 12:30 | 5.5535 | 0 | N/A | 0 | 0
2022-06-14 13:00 | 5.1676 | 0 | N/A | 0 | 0
2022-06-14 13:30 | 4.3464 | 0 | N/A | 0 | 0
2022-06-14 14:00 | 4.402 | 0 | N/A | 0 | 0
2022-06-14 14:30 | 4.7457 | 0 | N/A | 0 | 0
2022-06-14 15:00 | 5.1975 | 0 | N/A | 0 | 0
2022-06-14 15:30 | 5.376 | 0 | N/A | 0 | 0
2022-06-14 16:00 | 6.5337 | 0 | N/A | 0 | 0
2022-06-14 16:30 | 6.9978 | 0 | N/A | 0 | 0
2022-06-14 17:00 | 7.7825 | 0 | N/A | 0 | 0
2022-06-14 17:30 | 8.9168 | 0 | N/A | 0 | 0
2022-06-14 18:00 | 9.8181 | 0 | N/A | 0 | 0
2022-06-14 18:30 | 10.0934 | 0 | N/A | 0 | 0
2022-06-14 19:00 | 9.8404 | 0 | N/A | 0 | 0
2022-06-14 19:30 | 9.5043 | 0 | N/A | 0 | 0
2022-06-14 20:00 | 9.0865 | 0 | N/A | 0 | 0
2022-06-14 20:30 | 8.7961 | 0 | N/A | 0 | 0
2022-06-14 21:00 | 8.2039 | 0 | N/A | 0 | 0
2022-06-14 21:30 | 8.2119 | 0 | N/A | 0 | 0
2022-06-14 22:00 | 7.9396 | 0 | N/A | 0 | 0
2022-06-14 22:30 | 7.1619 | 0 | N/A | 0 | 0
2022-06-14 23:00 | 6.8434 | 0 | N/A | 0 | 0
2022-06-14 23:30 | 6.8257 | 0 | N/A | 0 | 0
2022-06-15 | 6.9935 | 0 | N/A | 0 | 0
2022-06-15 00:30 | 6.3979 | 0 | N/A | 0 | 0
2022-06-15 01:00 | 5.7475 | 0 | N/A | 0 | 0
2022-06-15 01:30 | 5.4932 | 0 | N/A | 0 | 0
2022-06-15 02:00 | 5.1111 | 0 | N/A | 0 | 0
2022-06-15 02:30 | 4.5936 | 0 | N/A | 0 | 0
2022-06-15 03:00 | 4.3208 | 0 | N/A | 0 | 0
2022-06-15 03:30 | 4.1214 | 0 | N/A | 0 | 0
2022-06-15 04:00 | 3.9759 | 0 | N/A | 0 | 0
2022-06-15 04:30 | 3.9868 | 0 | N/A | 0 | 0
2022-06-15 05:00 | 4.2134 | 0 | N/A | 0 | 0
2022-06-15 05:30 | 4.5453 | 0 | N/A | 0 | 0
2022-06-15 06:00 | 4.9814 | 0 | N/A | 0 | 0
2022-06-15 06:30 | 5.9025 | 0 | N/A | 0 | 0
2022-06-15 07:00 | 6.8017 | 0 | N/A | 0 | 0
2022-06-15 07:30 | 7.3309 | 0 | N/A | 0 | 0
2022-06-15 08:00 | 7.9186 | 0 | N/A | 0 | 0
2022-06-15 08:30 | 8.0912 | 0 | N/A | 0 | 0
2022-06-15 09:00 | 8.25 | 0 | N/A | 0 | 0
2022-06-15 09:30 | 8.0534 | 0 | N/A | 0 | 0
2022-06-15 10:00 | 7.5405 | 0 | N/A | 0 | 0
2022-06-15 10:30 | 7.1168 | 0 | N/A | 0 | 0
2022-06-15 11:00 | 6.984 | 0 | N/A | 0 | 0
2022-06-15 11:30 | 6.7273 | 0 | N/A | 0 | 0
2022-06-15 12:00 | 7.2838 | 0 | N/A | 0 | 0
2022-06-15 12:30 | 6.8605 | 0 | N/A | 0 | 0
2022-06-15 13:00 | 7.1607 | 0 | N/A | 0 | 0
2022-06-15 13:30 | 7.1637 | 0 | N/A | 0 | 0
2022-06-15 14:00 | 6.9872 | 0 | N/A | 0 | 0
2022-06-15 14:30 | 7.296 | 0 | N/A | 0 | 0
2022-06-15 15:00 | 7.4089 | 0 | N/A | 0 | 0
2022-06-15 15:30 | 7.536 | 0 | N/A | 0 | 0
2022-06-15 16:00 | 7.6911 | 0 | N/A | 0 | 0
2022-06-15 16:30 | 7.9988 | 0 | N/A | 0 | 0
2022-06-15 17:00 | 8.3987 | 0 | N/A | 0 | 0
2022-06-15 17:30 | 8.9561 | 0 | N/A | 0 | 0
2022-06-15 18:00 | 9.6907 | 0 | N/A | 0 | 0
2022-06-15 18:30 | 9.604 | 0 | N/A | 0 | 0
2022-06-15 19:00 | 9.3312 | 0 | N/A | 0 | 0
2022-06-15 19:30 | 8.9195 | 0 | N/A | 0 | 0
2022-06-15 20:00 | 8.5956 | 0 | N/A | 0 | 0
2022-06-15 20:30 | 8.1074 | 0 | N/A | 0 | 0
2022-06-15 21:00 | 7.5403 | 0 | N/A | 0 | 0
2022-06-15 21:30 | 7.5234 | 0 | N/A | 0 | 0
2022-06-15 22:00 | 7.4387 | 0 | N/A | 0 | 0
2022-06-15 22:30 | 6.6666 | 0 | N/A | 0 | 0
2022-06-15 23:00 | 6.3895 | 0 | N/A | 0 | 0
2022-06-15 23:30 | 6.4375 | 0 | N/A | 0 | 0
2022-06-16 | 6.6801 | 0 | N/A | 0 | 0
2022-06-16 00:30 | 5.9822 | 0 | N/A | 0 | 0
2022-06-16 01:00 | 5.2546 | 0 | N/A | 0 | 0
2022-06-16 01:30 | 5.0718 | 0 | N/A | 0 | 0
2022-06-16 02:00 | 4.7171 | 0 | N/A | 0 | 0
2022-06-16 02:30 | 4.2266 | 0 | N/A | 0 | 0
2022-06-16 03:00 | 3.8782 | 0 | N/A | 0 | 0
2022-06-16 03:30 | 3.7305 | 0 | N/A | 0 | 0
2022-06-16 04:00 | 3.6433 | 0 | N/A | 0 | 0
2022-06-16 04:30 | 3.6229 | 0 | N/A | 0 | 0
2022-06-16 05:00 | 3.6789 | 0 | N/A | 0 | 0
2022-06-16 05:30 | 4.0691 | 0 | N/A | 0 | 0
2022-06-16 06:00 | 4.5617 | 0 | N/A | 0 | 0
2022-06-16 06:30 | 5.3619 | 0 | N/A | 0 | 0
2022-06-16 07:00 | 5.8793 | 0 | N/A | 0 | 0
2022-06-16 07:30 | 6.5091 | 0 | N/A | 0 | 0
2022-06-16 08:00 | 7.1046 | 0 | N/A | 0 | 0
2022-06-16 08:30 | 7.6848 | 0 | N/A | 0 | 0
2022-06-16 09:00 | 7.5343 | 0 | N/A | 0 | 0
2022-06-16 09:30 | 7.043 | 0 | N/A | 0 | 0
2022-06-16 10:00 | 6.3334 | 0 | N/A | 0 | 0
2022-06-16 10:30 | 5.9691 | 0 | N/A | 0 | 0
2022-06-16 11:00 | 5.4163 | 0 | N/A | 0 | 0
2022-06-16 11:30 | 5.3213 | 0 | N/A | 0 | 0
2022-06-16 12:00 | 4.7588 | 0 | N/A | 0 | 0
2022-06-16 12:30 | 3.9652 | 0 | N/A | 0 | 0
2022-06-16 13:00 | 3.3413 | 0 | N/A | 0 | 0
2022-06-16 13:30 | 3.859 | 0 | N/A | 0 | 0
2022-06-16 14:00 | 4.3106 | 0 | N/A | 0 | 0
2022-06-16 14:30 | 4.9094 | 0 | N/A | 0 | 0
2022-06-16 15:00 | 4.4727 | 0 | N/A | 0 | 0
2022-06-16 15:30 | 5.0003 | 0 | N/A | 0 | 0
2022-06-16 16:00 | 5.2753 | 0 | N/A | 0 | 0
2022-06-16 16:30 | 6.19 | 0 | N/A | 0 | 0
2022-06-16 17:00 | 6.7716 | 0 | N/A | 0 | 0
2022-06-16 17:30 | 7.6934 | 0 | N/A | 0 | 0
2022-06-16 18:00 | 8.5072 | 0 | N/A | 0 | 0
2022-06-16 18:30 | 8.6619 | 0 | N/A | 0 | 0
2022-06-16 19:00 | 8.4867 | 0 | N/A | 0 | 0
2022-06-16 19:30 | 8.1517 | 0 | N/A | 0 | 0
2022-06-16 20:00 | 7.9185 | 0 | N/A | 0 | 0
2022-06-16 20:30 | 7.6472 | 0 | N/A | 0 | 0
2022-06-16 21:00 | 7.2977 | 0 | N/A | 0 | 0
2022-06-16 21:30 | 7.3296 | 0 | N/A | 0 | 0
2022-06-16 22:00 | 7.1271 | 0 | N/A | 0 | 0
2022-06-16 22:30 | 6.4108 | 0 | N/A | 0 | 0
2022-06-16 23:00 | 6.2419 | 0 | N/A | 0 | 0
2022-06-16 23:30 | 6.2499 | 0 | N/A | 0 | 0
2022-06-17 | 6.463 | 0 | N/A | 0 | 0
2022-06-17 00:30 | 5.8027 | 0 | N/A | 0 | 0
2022-06-17 01:00 | 5.086 | 0 | N/A | 0 | 0
2022-06-17 01:30 | 4.9522 | 0 | N/A | 0 | 0
2022-06-17 02:00 | 4.554 | 0 | N/A | 0 | 0
2022-06-17 02:30 | 4.1108 | 0 | N/A | 0 | 0
2022-06-17 03:00 | 3.767 | 0 | N/A | 0 | 0
2022-06-17 03:30 | 3.643 | 0 | N/A | 0 | 0
2022-06-17 04:00 | 3.5235 | 0 | N/A | 0 | 0
2022-06-17 04:30 | 3.4645 | 0 | N/A | 0 | 0
2022-06-17 05:00 | 3.5682 | 0 | N/A | 0 | 0
2022-06-17 05:30 | 3.9784 | 0 | N/A | 0 | 0
2022-06-17 06:00 | 4.3964 | 0 | N/A | 0 | 0
2022-06-17 06:30 | 5.2295 | 0 | N/A | 0 | 0
2022-06-17 07:00 | 5.7763 | 0 | N/A | 0 | 0
2022-06-17 07:30 | 6.2645 | 0 | N/A | 0 | 0
2022-06-17 08:00 | 6.8179 | 0 | N/A | 0 | 0
2022-06-17 08:30 | 7.0402 | 0 | N/A | 0 | 0
2022-06-17 09:00 | 6.9494 | 0 | N/A | 0 | 0
2022-06-17 09:30 | 6.6403 | 0 | N/A | 0 | 0
2022-06-17 10:00 | 6.398 | 0 | N/A | 0 | 0
2022-06-17 10:30 | 6.0083 | 0 | N/A | 0 | 0
2022-06-17 11:00 | 5.7178 | 0 | N/A | 0 | 0
2022-06-17 11:30 | 5.1662 | 0 | N/A | 0 | 0
2022-06-17 12:00 | 4.8949 | 0 | N/A | 0 | 0
2022-06-17 12:30 | 3.674 | 0 | N/A | 0 | 0
2022-06-17 13:00 | 4.3711 | 0 | N/A | 0 | 0
2022-06-17 13:30 | 4.4219 | 0 | N/A | 0 | 0
2022-06-17 14:00 | 4.7361 | 0 | N/A | 0 | 0
2022-06-17 14:30 | 4.949 | 0 | N/A | 0 | 0
2022-06-17 15:00 | 3.7796 | 0 | N/A | 0 | 0
2022-06-17 15:30 | 3.8316 | 0 | N/A | 0 | 0
2022-06-17 16:00 | 4.1543 | 0 | N/A | 0 | 0
2022-06-17 16:30 | 4.8882 | 0 | N/A | 0 | 0
2022-06-17 17:00 | 5.8492 | 0 | N/A | 0 | 0
2022-06-17 17:30 | 6.9288 | 0 | N/A | 0 | 0
2022-06-17 18:00 | 7.6854 | 0 | N/A | 0 | 0
2022-06-17 18:30 | 8.0953 | 0 | N/A | 0 | 0
2022-06-17 19:00 | 8.0628 | 0 | N/A | 0 | 0
2022-06-17 19:30 | 7.8784 | 0 | N/A | 0 | 0
2022-06-17 20:00 | 7.7381 | 0 | N/A | 0 | 0
2022-06-17 20:30 | 7.5089 | 0 | N/A | 0 | 0
2022-06-17 21:00 | 7.2161 | 0 | N/A | 0 | 0
2022-06-17 21:30 | 7.4711 | 0 | N/A | 0 | 0
2022-06-17 22:00 | 7.4946 | 0 | N/A | 0 | 0
2022-06-17 22:30 | 6.9158 | 0 | N/A | 0 | 0
2022-06-17 23:00 | 6.6829 | 0 | N/A | 0 | 0
2022-06-17 23:30 | 6.7313 | 0 | N/A | 0 | 0
2022-06-18 | 7.0184 | 0 | N/A | 0 | 0
2022-06-18 00:30 | 6.2034 | 0 | N/A | 0 | 0
2022-06-18 01:00 | 5.4627 | 0 | N/A | 0 | 0
2022-06-18 01:30 | 5.2652 | 0 | N/A | 0 | 0
2022-06-18 02:00 | 4.8485 | 0 | N/A | 0 | 0
2022-06-18 02:30 | 4.4781 | 0 | N/A | 0 | 0
2022-06-18 03:00 | 4.12 | 0 | N/A | 0 | 0
2022-06-18 03:30 | 3.9832 | 0 | N/A | 0 | 0
2022-06-18 04:00 | 3.7663 | 0 | N/A | 0 | 0
2022-06-18 04:30 | 3.7969 | 0 | N/A | 0 | 0
2022-06-18 05:00 | 3.7705 | 0 | N/A | 0 | 0
2022-06-18 05:30 | 3.8696 | 0 | N/A | 0 | 0
2022-06-18 06:00 | 3.9963 | 0 | N/A | 0 | 0
2022-06-18 06:30 | 4.5772 | 0 | N/A | 0 | 0
2022-06-18 07:00 | 4.8487 | 0 | N/A | 0 | 0
2022-06-18 07:30 | 4.8957 | 0 | N/A | 0 | 0
2022-06-18 08:00 | 5.489 | 0 | N/A | 0 | 0
2022-06-18 08:30 | 6.0993 | 0 | N/A | 0 | 0
2022-06-18 09:00 | 6.1407 | 0 | N/A | 0 | 0
2022-06-18 09:30 | 5.7606 | 0 | N/A | 0 | 0
2022-06-18 10:00 | 5.0379 | 0 | N/A | 0 | 0
2022-06-18 10:30 | 4.21 | 0 | N/A | 0 | 0
2022-06-18 11:00 | 3.237 | 0 | N/A | 0 | 0
2022-06-18 11:30 | 2.5796 | 0 | N/A | 0 | 0
2022-06-18 12:00 | 2.1671 | 0 | N/A | 0 | 0
2022-06-18 12:30 | 2.0663 | 0 | N/A | 0 | 0
2022-06-18 13:00 | 2.9402 | 0 | N/A | 0 | 0
2022-06-18 13:30 | 3.5238 | 0 | N/A | 0 | 0
2022-06-18 14:00 | 3.8054 | 0 | N/A | 0 | 0
2022-06-18 14:30 | 3.4656 | 0 | N/A | 0 | 0
2022-06-18 15:00 | 3.3202 | 0 | N/A | 0 | 0
2022-06-18 15:30 | 3.3904 | 0 | N/A | 0 | 0
2022-06-18 16:00 | 4.1073 | 0 | N/A | 0 | 0
2022-06-18 16:30 | 5.2397 | 0 | N/A | 0 | 0
2022-06-18 17:00 | 6.062 | 0 | N/A | 0 | 0
2022-06-18 17:30 | 6.8426 | 0 | N/A | 0 | 0
2022-06-18 18:00 | 7.7806 | 0 | N/A | 0 | 0
2022-06-18 18:30 | 7.9168 | 0 | N/A | 0 | 0
2022-06-18 19:00 | 7.6382 | 0 | N/A | 0 | 0
2022-06-18 19:30 | 7.3698 | 0 | N/A | 0 | 0
2022-06-18 20:00 | 7.143 | 0 | N/A | 0 | 0
2022-06-18 20:30 | 6.826 | 0 | N/A | 0 | 0
2022-06-18 21:00 | 6.5346 | 0 | N/A | 0 | 0
2022-06-18 21:30 | 6.8356 | 0 | N/A | 0 | 0
2022-06-18 22:00 | 7.0707 | 0 | N/A | 0 | 0
2022-06-18 22:30 | 6.6414 | 0 | N/A | 0 | 0
2022-06-18 23:00 | 6.6049 | 0 | N/A | 0 | 0
2022-06-18 23:30 | 6.7551 | 0 | N/A | 0 | 0
2022-06-19 | 7.1568 | 0 | N/A | 0 | 0
2022-06-19 00:30 | 6.4206 | 0 | N/A | 0 | 0
2022-06-19 01:00 | 5.6176 | 0 | N/A | 0 | 0
2022-06-19 01:30 | 5.5248 | 0 | N/A | 0 | 0
2022-06-19 02:00 | 5.1961 | 0 | N/A | 0 | 0
2022-06-19 02:30 | 4.6971 | 0 | N/A | 0 | 0
2022-06-19 03:00 | 4.3781 | 0 | N/A | 0 | 0
2022-06-19 03:30 | 4.2651 | 0 | N/A | 0 | 0
2022-06-19 04:00 | 4.1616 | 0 | N/A | 0 | 0
2022-06-19 04:30 | 4.0383 | 0 | N/A | 0 | 0
2022-06-19 05:00 | 4.0596 | 0 | N/A | 0 | 0
2022-06-19 05:30 | 4.2011 | 0 | N/A | 0 | 0
2022-06-19 06:00 | 4.3182 | 0 | N/A | 0 | 0
2022-06-19 06:30 | 4.6319 | 0 | N/A | 0 | 0
2022-06-19 07:00 | 4.8502 | 0 | N/A | 0 | 0
2022-06-19 07:30 | 4.8404 | 0 | N/A | 0 | 0
2022-06-19 08:00 | 5.3364 | 0 | N/A | 0 | 0
2022-06-19 08:30 | 5.8633 | 0 | N/A | 0 | 0
2022-06-19 09:00 | 5.8426 | 0 | N/A | 0 | 0
2022-06-19 09:30 | 5.4514 | 0 | N/A | 0 | 0
2022-06-19 10:00 | 4.9847 | 0 | N/A | 0 | 0
2022-06-19 10:30 | 4.8333 | 0 | N/A | 0 | 0
2022-06-19 11:00 | 4.7518 | 0 | N/A | 0 | 0
2022-06-19 11:30 | 5.1344 | 0 | N/A | 0 | 0
2022-06-19 12:00 | 5.0028 | 0 | N/A | 0 | 0
2022-06-19 12:30 | 4.7811 | 0 | N/A | 0 | 0
2022-06-19 13:00 | 4.253 | 0 | N/A | 0 | 0
2022-06-19 13:30 | 5.2252 | 0 | N/A | 0 | 0
2022-06-19 14:00 | 5.6498 | 0 | N/A | 0 | 0
2022-06-19 14:30 | 5.9494 | 0 | N/A | 0 | 0
2022-06-19 15:00 | 6.1884 | 0 | N/A | 0 | 0
2022-06-19 15:30 | 6.3774 | 0 | N/A | 0 | 0
2022-06-19 16:00 | 6.8925 | 0 | N/A | 0 | 0
2022-06-19 16:30 | 7.394 | 0 | N/A | 0 | 0
2022-06-19 17:00 | 8.1472 | 0 | N/A | 0 | 0
2022-06-19 17:30 | 8.979 | 0 | N/A | 0 | 0
2022-06-19 18:00 | 9.6126 | 0 | N/A | 0 | 0
2022-06-19 18:30 | 9.6024 | 0 | N/A | 0 | 0
2022-06-19 19:00 | 9.1412 | 0 | N/A | 0 | 0
2022-06-19 19:30 | 8.7257 | 0 | N/A | 0 | 0
2022-06-19 20:00 | 8.242 | 0 | N/A | 0 | 0
2022-06-19 20:30 | 7.7039 | 0 | N/A | 0 | 0
2022-06-19 21:00 | 7.3017 | 0 | N/A | 0 | 0
2022-06-19 21:30 | 7.3289 | 0 | N/A | 0 | 0
2022-06-19 22:00 | 7.2313 | 0 | N/A | 0 | 0
2022-06-19 22:30 | 6.7604 | 0 | N/A | 0 | 0
2022-06-19 23:00 | 6.5735 | 0 | N/A | 0 | 0
2022-06-19 23:30 | 6.4799 | 0 | N/A | 0 | 0
2022-06-20 | 6.7377 | 0 | N/A | 0 | 0
2022-06-20 00:30 | 6.1208 | 0 | N/A | 0 | 0
2022-06-20 01:00 | 5.3828 | 0 | N/A | 0 | 0
2022-06-20 01:30 | 5.2873 | 0 | N/A | 0 | 0
2022-06-20 02:00 | 5.0764 | 0 | N/A | 0 | 0
2022-06-20 02:30 | 4.5322 | 0 | N/A | 0 | 0
2022-06-20 03:00 | 4.2219 | 0 | N/A | 0 | 0
2022-06-20 03:30 | 3.9399 | 0 | N/A | 0 | 0
2022-06-20 04:00 | 3.8321 | 0 | N/A | 0 | 0
2022-06-20 04:30 | 3.6515 | 0 | N/A | 0 | 0
2022-06-20 05:00 | 3.7011 | 0 | N/A | 0 | 0
2022-06-20 05:30 | 4.0883 | 0 | N/A | 0 | 0
2022-06-20 06:00 | 4.5396 | 0 | N/A | 0 | 0
2022-06-20 06:30 | 5.4523 | 0 | N/A | 0 | 0
2022-06-20 07:00 | 6.036 | 0 | N/A | 0 | 0
2022-06-20 07:30 | 6.4528 | 0 | N/A | 0 | 0
2022-06-20 08:00 | 7.0772 | 0 | N/A | 0 | 0
2022-06-20 08:30 | 7.158 | 0 | N/A | 0 | 0
2022-06-20 09:00 | 2.4569 | 0 | N/A | 0 | 0
2022-06-20 09:30 | 5.3736 | 0 | N/A | 0 | 0
2022-06-20 10:00 | 5.1507 | 0 | N/A | 0 | 0
2022-06-20 10:30 | 4.4591 | 0 | N/A | 0 | 0
2022-06-20 11:00 | 3.8724 | 0 | N/A | 0 | 0
2022-06-20 11:30 | 3.4383 | 0 | N/A | 0 | 0
2022-06-20 12:00 | 3.0843 | 0 | N/A | 0 | 0
2022-06-20 12:30 | 3.0558 | 0 | N/A | 0 | 0
2022-06-20 13:00 | 3.1368 | 0 | N/A | 0 | 0
2022-06-20 13:30 | 3.2552 | 0 | N/A | 0 | 0
2022-06-20 14:00 | 4.1832 | 0 | N/A | 0 | 0
2022-06-20 14:30 | 4.4456 | 0 | N/A | 0 | 0
2022-06-20 15:00 | 6.2636 | 0 | N/A | 0 | 0
2022-06-20 15:30 | 5.885 | 0 | N/A | 0 | 0
2022-06-20 16:00 | 5.8366 | 0 | N/A | 0 | 0
2022-06-20 16:30 | 6.4911 | 0 | N/A | 0 | 0
2022-06-20 17:00 | 6.8441 | 0 | N/A | 0 | 0
2022-06-20 17:30 | 7.8541 | 0 | N/A | 0 | 0
2022-06-20 18:00 | 8.6462 | 0 | N/A | 0 | 0
2022-06-20 18:30 | 8.8748 | 0 | N/A | 0 | 0
2022-06-20 19:00 | 8.3957 | 0 | N/A | 0 | 0
2022-06-20 19:30 | 7.8805 | 0 | N/A | 0 | 0
2022-06-20 20:00 | 7.5977 | 0 | N/A | 0 | 0
2022-06-20 20:30 | 7.161 | 0 | N/A | 0 | 0
2022-06-20 21:00 | 6.712 | 0 | N/A | 0 | 0
2022-06-20 21:30 | 6.96 | 0 | N/A | 0 | 0
2022-06-20 22:00 | 6.7662 | 0 | N/A | 0 | 0
2022-06-20 22:30 | 6.1034 | 0 | N/A | 0 | 0
2022-06-20 23:00 | 5.8707 | 0 | N/A | 0 | 0
2022-06-20 23:30 | 5.8927 | 0 | N/A | 0 | 0
2022-06-21 | 6.1036 | 0 | N/A | 0 | 0
2022-06-21 00:30 | 5.4617 | 0 | N/A | 0 | 0
2022-06-21 01:00 | 4.8135 | 0 | N/A | 0 | 0
2022-06-21 01:30 | 4.5914 | 0 | N/A | 0 | 0
2022-06-21 02:00 | 4.2028 | 0 | N/A | 0 | 0
2022-06-21 02:30 | 3.6978 | 0 | N/A | 0 | 0
2022-06-21 03:00 | 3.5194 | 0 | N/A | 0 | 0
2022-06-21 03:30 | 3.4719 | 0 | N/A | 0 | 0
2022-06-21 04:00 | 3.2943 | 0 | N/A | 0 | 0
2022-06-21 04:30 | 3.28 | 0 | N/A | 0 | 0
2022-06-21 05:00 | 3.4215 | 0 | N/A | 0 | 0
2022-06-21 05:30 | 3.8543 | 0 | N/A | 0 | 0
2022-06-21 06:00 | 4.2108 | 0 | N/A | 0 | 0
2022-06-21 06:30 | 5.106 | 0 | N/A | 0 | 0
2022-06-21 07:00 | 5.8438 | 0 | N/A | 0 | 0
2022-06-21 07:30 | 6.7593 | 0 | N/A | 0 | 0
2022-06-21 08:00 | 7.5899 | 0 | N/A | 0 | 0
2022-06-21 08:30 | 7.6645 | 0 | N/A | 0 | 0
2022-06-21 09:00 | 6.905 | 0 | N/A | 0 | 0
2022-06-21 09:30 | 6.093 | 0 | N/A | 0 | 0
2022-06-21 10:00 | 5.7998 | 0 | N/A | 0 | 0
2022-06-21 10:30 | 4.8082 | 0 | N/A | 0 | 0
2022-06-21 11:00 | 4.2375 | 0 | N/A | 0 | 0
2022-06-21 11:30 | 4.2922 | 0 | N/A | 0 | 0
2022-06-21 12:00 | 3.9055 | 0 | N/A | 0 | 0
2022-06-21 12:30 | 3.8424 | 0 | N/A | 0 | 0
2022-06-21 13:00 | 3.29 | 0 | N/A | 0 | 0
2022-06-21 13:30 | 3.4755 | 0 | N/A | 0 | 0
2022-06-21 14:00 | 3.0926 | 0 | N/A | 0 | 0
2022-06-21 14:30 | 3.3974 | 0 | N/A | 0 | 0
2022-06-21 15:00 | 4.688 | 0 | N/A | 0 | 0
2022-06-21 15:30 | 4.9756 | 0 | N/A | 0 | 0
2022-06-21 16:00 | 4.8837 | 0 | N/A | 0 | 0
2022-06-21 16:30 | 5.257 | 0 | N/A | 0 | 0
2022-06-21 17:00 | 6.3846 | 0 | N/A | 0 | 0
2022-06-21 17:30 | 7.3988 | 0 | N/A | 0 | 0
2022-06-21 18:00 | 8.3777 | 0 | N/A | 0 | 0
2022-06-21 18:30 | 8.9018 | 0 | N/A | 0 | 0
2022-06-21 19:00 | 8.7655 | 0 | N/A | 0 | 0
2022-06-21 19:30 | 8.6449 | 0 | N/A | 0 | 0
2022-06-21 20:00 | 8.2236 | 0 | N/A | 0 | 0
2022-06-21 20:30 | 7.9442 | 0 | N/A | 0 | 0
2022-06-21 21:00 | 7.5843 | 0 | N/A | 0 | 0
2022-06-21 21:30 | 7.5541 | 0 | N/A | 0 | 0
2022-06-21 22:00 | 7.4893 | 0 | N/A | 0 | 0
2022-06-21 22:30 | 6.6958 | 0 | N/A | 0 | 0
2022-06-21 23:00 | 6.3479 | 0 | N/A | 0 | 0
2022-06-21 23:30 | 6.3623 | 0 | N/A | 0 | 0
2022-06-22 | 6.6058 | 0 | N/A | 0 | 0
2022-06-22 00:30 | 5.807 | 0 | N/A | 0 | 0
2022-06-22 01:00 | 5.0765 | 0 | N/A | 0 | 0
2022-06-22 01:30 | 5.0104 | 0 | N/A | 0 | 0
2022-06-22 02:00 | 4.6138 | 0 | N/A | 0 | 0
2022-06-22 02:30 | 4.1593 | 0 | N/A | 0 | 0
2022-06-22 03:00 | 3.8941 | 0 | N/A | 0 | 0
2022-06-22 03:30 | 3.7357 | 0 | N/A | 0 | 0
2022-06-22 04:00 | 3.5991 | 0 | N/A | 0 | 0
2022-06-22 04:30 | 3.5365 | 0 | N/A | 0 | 0
2022-06-22 05:00 | 3.6536 | 0 | N/A | 0 | 0
2022-06-22 05:30 | 4.0564 | 0 | N/A | 0 | 0
2022-06-22 06:00 | 4.4765 | 0 | N/A | 0 | 0
2022-06-22 06:30 | 5.1941 | 0 | N/A | 0 | 0
2022-06-22 07:00 | 5.9322 | 0 | N/A | 0 | 0
2022-06-22 07:30 | 6.7243 | 0 | N/A | 0 | 0
2022-06-22 08:00 | 7.3869 | 0 | N/A | 0 | 0
2022-06-22 08:30 | 7.7222 | 0 | N/A | 0 | 0
2022-06-22 09:00 | 7.5028 | 0 | N/A | 0 | 0
2022-06-22 09:30 | 7.1173 | 0 | N/A | 0 | 0
2022-06-22 10:00 | 6.706 | 0 | N/A | 0 | 0
2022-06-22 10:30 | 6.0571 | 0 | N/A | 0 | 0
2022-06-22 11:00 | 5.6153 | 0 | N/A | 0 | 0
2022-06-22 11:30 | 5.7078 | 0 | N/A | 0 | 0
2022-06-22 12:00 | 5.4384 | 0 | N/A | 0 | 0
2022-06-22 12:30 | 5.229 | 0 | N/A | 0 | 0
2022-06-22 13:00 | 5.0945 | 0 | N/A | 0 | 0
2022-06-22 13:30 | 5.2716 | 0 | N/A | 0 | 0
2022-06-22 14:00 | 4.8317 | 0 | N/A | 0 | 0
2022-06-22 14:30 | 4.9687 | 0 | N/A | 0 | 0
2022-06-22 15:00 | 5.5176 | 0 | N/A | 0 | 0
2022-06-22 15:30 | 5.1998 | 0 | N/A | 0 | 0
2022-06-22 16:00 | 5.1757 | 0 | N/A | 0 | 0
2022-06-22 16:30 | 5.8107 | 0 | N/A | 0 | 0
2022-06-22 17:00 | 6.4667 | 0 | N/A | 0 | 0
2022-06-22 17:30 | 7.2294 | 0 | N/A | 0 | 0
2022-06-22 18:00 | 8.1126 | 0 | N/A | 0 | 0
2022-06-22 18:30 | 8.3539 | 0 | N/A | 0 | 0
2022-06-22 19:00 | 8.0016 | 0 | N/A | 0 | 0
2022-06-22 19:30 | 7.7767 | 0 | N/A | 0 | 0
2022-06-22 20:00 | 7.4836 | 0 | N/A | 0 | 0
2022-06-22 20:30 | 7.2601 | 0 | N/A | 0 | 0
2022-06-22 21:00 | 6.7583 | 0 | N/A | 0 | 0
2022-06-22 21:30 | 6.8273 | 0 | N/A | 0 | 0
2022-06-22 22:00 | 6.7081 | 0 | N/A | 0 | 0
2022-06-22 22:30 | 6.0308 | 0 | N/A | 0 | 0
2022-06-22 23:00 | 5.7564 | 0 | N/A | 0 | 0
2022-06-22 23:30 | 5.8546 | 0 | N/A | 0 | 0
2022-06-23 | 6.1173 | 0 | N/A | 0 | 0
2022-06-23 00:30 | 5.4422 | 0 | N/A | 0 | 0
2022-06-23 01:00 | 4.7509 | 0 | N/A | 0 | 0
2022-06-23 01:30 | 4.5912 | 0 | N/A | 0 | 0
2022-06-23 02:00 | 4.2263 | 0 | N/A | 0 | 0
2022-06-23 02:30 | 3.721 | 0 | N/A | 0 | 0
2022-06-23 03:00 | 3.4926 | 0 | N/A | 0 | 0
2022-06-23 03:30 | 3.3502 | 0 | N/A | 0 | 0
2022-06-23 04:00 | 3.2497 | 0 | N/A | 0 | 0
2022-06-23 04:30 | 3.2509 | 0 | N/A | 0 | 0
2022-06-23 05:00 | 3.4254 | 0 | N/A | 0 | 0
2022-06-23 05:30 | 3.8442 | 0 | N/A | 0 | 0
2022-06-23 06:00 | 4.2328 | 0 | N/A | 0 | 0
2022-06-23 06:30 | 5.0294 | 0 | N/A | 0 | 0
2022-06-23 07:00 | 5.9479 | 0 | N/A | 0 | 0
2022-06-23 07:30 | 6.6258 | 0 | N/A | 0 | 0
2022-06-23 08:00 | 7.09 | 0 | N/A | 0 | 0
2022-06-23 08:30 | 7.1884 | 0 | N/A | 0 | 0
2022-06-23 09:00 | 7.0493 | 0 | N/A | 0 | 0
2022-06-23 09:30 | 6.3135 | 0 | N/A | 0 | 0
2022-06-23 10:00 | 5.9553 | 0 | N/A | 0 | 0
2022-06-23 10:30 | 5.4596 | 0 | N/A | 0 | 0
2022-06-23 11:00 | 4.4748 | 0 | N/A | 0 | 0
2022-06-23 11:30 | 3.8302 | 0 | N/A | 0 | 0
2022-06-23 12:00 | 3.7643 | 0 | N/A | 0 | 0
2022-06-23 12:30 | 4.4143 | 0 | N/A | 0 | 0
2022-06-23 13:00 | 4.3278 | 0 | N/A | 0 | 0
2022-06-23 13:30 | 4.5645 | 0 | N/A | 0 | 0
2022-06-23 14:00 | 4.4217 | 0 | N/A | 0 | 0
2022-06-23 14:30 | 4.5718 | 0 | N/A | 0 | 0
2022-06-23 15:00 | 4.6297 | 0 | N/A | 0 | 0
2022-06-23 15:30 | 4.6028 | 0 | N/A | 0 | 0
2022-06-23 16:00 | 5.2007 | 0 | N/A | 0 | 0
2022-06-23 16:30 | 5.821 | 0 | N/A | 0 | 0
2022-06-23 17:00 | 6.4274 | 0 | N/A | 0 | 0
2022-06-23 17:30 | 7.2247 | 0 | N/A | 0 | 0
2022-06-23 18:00 | 8.1112 | 0 | N/A | 0 | 0
2022-06-23 18:30 | 8.3214 | 0 | N/A | 0 | 0
2022-06-23 19:00 | 8.1671 | 0 | N/A | 0 | 0
2022-06-23 19:30 | 7.897 | 0 | N/A | 0 | 0
2022-06-23 20:00 | 7.6435 | 0 | N/A | 0 | 0
2022-06-23 20:30 | 7.2507 | 0 | N/A | 0 | 0
2022-06-23 21:00 | 6.974 | 0 | N/A | 0 | 0
2022-06-23 21:30 | 6.9557 | 0 | N/A | 0 | 0
2022-06-23 22:00 | 6.9057 | 0 | N/A | 0 | 0
2022-06-23 22:30 | 6.2735 | 0 | N/A | 0 | 0
2022-06-23 23:00 | 5.9397 | 0 | N/A | 0 | 0
2022-06-23 23:30 | 5.9464 | 0 | N/A | 0 | 0
2022-06-24 | 6.263 | 0 | N/A | 0 | 0
2022-06-24 00:30 | 5.6012 | 0 | N/A | 0 | 0
2022-06-24 01:00 | 4.8777 | 0 | N/A | 0 | 0
2022-06-24 01:30 | 4.6349 | 0 | N/A | 0 | 0
2022-06-24 02:00 | 4.3485 | 0 | N/A | 0 | 0
2022-06-24 02:30 | 3.8633 | 0 | N/A | 0 | 0
2022-06-24 03:00 | 3.6191 | 0 | N/A | 0 | 0
2022-06-24 03:30 | 3.4602 | 0 | N/A | 0 | 0
2022-06-24 04:00 | 3.2385 | 0 | N/A | 0 | 0
2022-06-24 04:30 | 3.2713 | 0 | N/A | 0 | 0
2022-06-24 05:00 | 3.3744 | 0 | N/A | 0 | 0
2022-06-24 05:30 | 3.7779 | 0 | N/A | 0 | 0
2022-06-24 06:00 | 4.0628 | 0 | N/A | 0 | 0
2022-06-24 06:30 | 4.9239 | 0 | N/A | 0 | 0
2022-06-24 07:00 | 5.6953 | 0 | N/A | 0 | 0
2022-06-24 07:30 | 6.2514 | 0 | N/A | 0 | 0
2022-06-24 08:00 | 6.9537 | 0 | N/A | 0 | 0
2022-06-24 08:30 | 7.3261 | 0 | N/A | 0 | 0
2022-06-24 09:00 | 6.8191 | 0 | N/A | 0 | 0
2022-06-24 09:30 | 6.4889 | 0 | N/A | 0 | 0
2022-06-24 10:00 | 5.7611 | 0 | N/A | 0 | 0
2022-06-24 10:30 | 5.6162 | 0 | N/A | 0 | 0
2022-06-24 11:00 | 4.57 | 0 | N/A | 0 | 0
2022-06-24 11:30 | 4.4273 | 0 | N/A | 0 | 0
2022-06-24 12:00 | 4.7149 | 0 | N/A | 0 | 0
2022-06-24 12:30 | 5.0713 | 0 | N/A | 0 | 0
2022-06-24 13:00 | 4.5311 | 0 | N/A | 0 | 0
2022-06-24 13:30 | 4.3288 | 0 | N/A | 0 | 0
2022-06-24 14:00 | 3.7457 | 0 | N/A | 0 | 0
2022-06-24 14:30 | 3.8409 | 0 | N/A | 0 | 0
2022-06-24 15:00 | 3.8957 | 0 | N/A | 0 | 0
2022-06-24 15:30 | 4.5068 | 0 | N/A | 0 | 0
2022-06-24 16:00 | 4.6963 | 0 | N/A | 0 | 0
2022-06-24 16:30 | 5.0686 | 0 | N/A | 0 | 0
2022-06-24 17:00 | 6.0587 | 0 | N/A | 0 | 0
2022-06-24 17:30 | 6.9996 | 0 | N/A | 0 | 0
2022-06-24 18:00 | 7.7159 | 0 | N/A | 0 | 0
2022-06-24 18:30 | 7.9727 | 0 | N/A | 0 | 0
2022-06-24 19:00 | 7.9175 | 0 | N/A | 0 | 0
2022-06-24 19:30 | 7.6098 | 0 | N/A | 0 | 0
2022-06-24 20:00 | 7.4636 | 0 | N/A | 0 | 0
2022-06-24 20:30 | 7.2215 | 0 | N/A | 0 | 0
2022-06-24 21:00 | 6.9073 | 0 | N/A | 0 | 0
2022-06-24 21:30 | 7.0691 | 0 | N/A | 0 | 0
2022-06-24 22:00 | 7.0372 | 0 | N/A | 0 | 0
2022-06-24 22:30 | 6.4409 | 0 | N/A | 0 | 0
2022-06-24 23:00 | 6.1667 | 0 | N/A | 0 | 0
2022-06-24 23:30 | 6.3925 | 0 | N/A | 0 | 0
2022-06-25 | 6.5997 | 0 | N/A | 0 | 0
2022-06-25 00:30 | 5.8784 | 0 | N/A | 0 | 0
2022-06-25 01:00 | 5.0722 | 0 | N/A | 0 | 0
2022-06-25 01:30 | 4.9637 | 0 | N/A | 0 | 0
2022-06-25 02:00 | 4.6197 | 0 | N/A | 0 | 0
2022-06-25 02:30 | 4.1736 | 0 | N/A | 0 | 0
2022-06-25 03:00 | 3.9373 | 0 | N/A | 0 | 0
2022-06-25 03:30 | 3.8063 | 0 | N/A | 0 | 0
2022-06-25 04:00 | 3.6811 | 0 | N/A | 0 | 0
2022-06-25 04:30 | 3.5616 | 0 | N/A | 0 | 0
2022-06-25 05:00 | 3.6432 | 0 | N/A | 0 | 0
2022-06-25 05:30 | 3.7548 | 0 | N/A | 0 | 0
2022-06-25 06:00 | 3.9195 | 0 | N/A | 0 | 0
2022-06-25 06:30 | 4.3865 | 0 | N/A | 0 | 0
2022-06-25 07:00 | 4.6276 | 0 | N/A | 0 | 0
2022-06-25 07:30 | 4.6774 | 0 | N/A | 0 | 0
2022-06-25 08:00 | 5.2333 | 0 | N/A | 0 | 0
2022-06-25 08:30 | 5.9021 | 0 | N/A | 0 | 0
2022-06-25 09:00 | 5.7626 | 0 | N/A | 0 | 0
2022-06-25 09:30 | 5.982 | 0 | N/A | 0 | 0
2022-06-25 10:00 | 5.2289 | 0 | N/A | 0 | 0
2022-06-25 10:30 | 5.0238 | 0 | N/A | 0 | 0
2022-06-25 11:00 | 3.5204 | 0 | N/A | 0 | 0
2022-06-25 11:30 | 3.4706 | 0 | N/A | 0 | 0
2022-06-25 12:00 | 4.2026 | 0 | N/A | 0 | 0
2022-06-25 12:30 | 4.0689 | 0 | N/A | 0 | 0
2022-06-25 13:00 | 3.6439 | 0 | N/A | 0 | 0
2022-06-25 13:30 | 3.6008 | 0 | N/A | 0 | 0
2022-06-25 14:00 | 4.4404 | 0 | N/A | 0 | 0
2022-06-25 14:30 | 4.3593 | 0 | N/A | 0 | 0
2022-06-25 15:00 | 3.6673 | 0 | N/A | 0 | 0
2022-06-25 15:30 | 3.8439 | 0 | N/A | 0 | 0
2022-06-25 16:00 | 4.9745 | 0 | N/A | 0 | 0
2022-06-25 16:30 | 5.6561 | 0 | N/A | 0 | 0
2022-06-25 17:00 | 6.5346 | 0 | N/A | 0 | 0
2022-06-25 17:30 | 7.2963 | 0 | N/A | 0 | 0
2022-06-25 18:00 | 8.0397 | 0 | N/A | 0 | 0
2022-06-25 18:30 | 8.0331 | 0 | N/A | 0 | 0
2022-06-25 19:00 | 7.815 | 0 | N/A | 0 | 0
2022-06-25 19:30 | 7.2836 | 0 | N/A | 0 | 0
2022-06-25 20:00 | 6.9399 | 0 | N/A | 0 | 0
2022-06-25 20:30 | 6.5872 | 0 | N/A | 0 | 0
2022-06-25 21:00 | 6.3126 | 0 | N/A | 0 | 0
2022-06-25 21:30 | 6.4639 | 0 | N/A | 0 | 0
2022-06-25 22:00 | 6.638 | 0 | N/A | 0 | 0
2022-06-25 22:30 | 6.2443 | 0 | N/A | 0 | 0
2022-06-25 23:00 | 6.1315 | 0 | N/A | 0 | 0
2022-06-25 23:30 | 6.3287 | 0 | N/A | 0 | 0
2022-06-26 | 6.6096 | 0 | N/A | 0 | 0
2022-06-26 00:30 | 5.9288 | 0 | N/A | 0 | 0
2022-06-26 01:00 | 5.1145 | 0 | N/A | 0 | 0
2022-06-26 01:30 | 5.0092 | 0 | N/A | 0 | 0
2022-06-26 02:00 | 4.6508 | 0 | N/A | 0 | 0
2022-06-26 02:30 | 4.1551 | 0 | N/A | 0 | 0
2022-06-26 03:00 | 3.8519 | 0 | N/A | 0 | 0
2022-06-26 03:30 | 3.5908 | 0 | N/A | 0 | 0
2022-06-26 04:00 | 3.498 | 0 | N/A | 0 | 0
2022-06-26 04:30 | 3.4301 | 0 | N/A | 0 | 0
2022-06-26 05:00 | 3.4633 | 0 | N/A | 0 | 0
2022-06-26 05:30 | 3.5621 | 0 | N/A | 0 | 0
2022-06-26 06:00 | 3.7106 | 0 | N/A | 0 | 0
2022-06-26 06:30 | 3.895 | 0 | N/A | 0 | 0
2022-06-26 07:00 | 4.0691 | 0 | N/A | 0 | 0
2022-06-26 07:30 | 4.187 | 0 | N/A | 0 | 0
2022-06-26 08:00 | 4.6488 | 0 | N/A | 0 | 0
2022-06-26 08:30 | 5.2074 | 0 | N/A | 0 | 0
2022-06-26 09:00 | 5.3684 | 0 | N/A | 0 | 0
2022-06-26 09:30 | 5.3765 | 0 | N/A | 0 | 0
2022-06-26 10:00 | 5.1393 | 0 | N/A | 0 | 0
2022-06-26 10:30 | 5.6008 | 0 | N/A | 0 | 0
2022-06-26 11:00 | 6.2138 | 0 | N/A | 0 | 0
2022-06-26 11:30 | 5.7565 | 0 | N/A | 0 | 0
2022-06-26 12:00 | 4.9462 | 0 | N/A | 0 | 0
2022-06-26 12:30 | 4.8762 | 0 | N/A | 0 | 0
2022-06-26 13:00 | 5.6548 | 0 | N/A | 0 | 0
2022-06-26 13:30 | 5.2049 | 0 | N/A | 0 | 0
2022-06-26 14:00 | 4.4185 | 0 | N/A | 0 | 0
2022-06-26 14:30 | 4.8415 | 0 | N/A | 0 | 0
2022-06-26 15:00 | 5.3086 | 0 | N/A | 0 | 0
2022-06-26 15:30 | 5.1196 | 0 | N/A | 0 | 0
2022-06-26 16:00 | 5.5584 | 0 | N/A | 0 | 0
2022-06-26 16:30 | 6.7223 | 0 | N/A | 0 | 0
2022-06-26 17:00 | 7.3512 | 0 | N/A | 0 | 0
2022-06-26 17:30 | 8.228 | 0 | N/A | 0 | 0
2022-06-26 18:00 | 9.0289 | 0 | N/A | 0 | 0
2022-06-26 18:30 | 9.1635 | 0 | N/A | 0 | 0
2022-06-26 19:00 | 8.8198 | 0 | N/A | 0 | 0
2022-06-26 19:30 | 8.3509 | 0 | N/A | 0 | 0
2022-06-26 20:00 | 7.9892 | 0 | N/A | 0 | 0
2022-06-26 20:30 | 7.5885 | 0 | N/A | 0 | 0
2022-06-26 21:00 | 7.2569 | 0 | N/A | 0 | 0
2022-06-26 21:30 | 7.3823 | 0 | N/A | 0 | 0
2022-06-26 22:00 | 7.2885 | 0 | N/A | 0 | 0
2022-06-26 22:30 | 6.8237 | 0 | N/A | 0 | 0
2022-06-26 23:00 | 6.7101 | 0 | N/A | 0 | 0
2022-06-26 23:30 | 6.703 | 0 | N/A | 0 | 0
2022-06-27 | 7.0118 | 0 | N/A | 0 | 0
2022-06-27 00:30 | 6.3905 | 0 | N/A | 0 | 0
2022-06-27 01:00 | 5.7099 | 0 | N/A | 0 | 0
2022-06-27 01:30 | 5.5135 | 0 | N/A | 0 | 0
2022-06-27 02:00 | 5.2785 | 0 | N/A | 0 | 0
2022-06-27 02:30 | 4.8079 | 0 | N/A | 0 | 0
2022-06-27 03:00 | 4.5277 | 0 | N/A | 0 | 0
2022-06-27 03:30 | 4.3635 | 0 | N/A | 0 | 0
2022-06-27 04:00 | 4.2701 | 0 | N/A | 0 | 0
2022-06-27 04:30 | 4.1761 | 0 | N/A | 0 | 0
2022-06-27 05:00 | 4.3949 | 0 | N/A | 0 | 0
2022-06-27 05:30 | 4.8217 | 0 | N/A | 0 | 0
2022-06-27 06:00 | 5.2162 | 0 | N/A | 0 | 0
2022-06-27 06:30 | 6.078 | 0 | N/A | 0 | 0
2022-06-27 07:00 | 6.7935 | 0 | N/A | 0 | 0
2022-06-27 07:30 | 7.3908 | 0 | N/A | 0 | 0
2022-06-27 08:00 | 8.094 | 0 | N/A | 0 | 0
2022-06-27 08:30 | 8.119 | 0 | N/A | 0 | 0
2022-06-27 09:00 | 8.4934 | 0 | N/A | 0 | 0
2022-06-27 09:30 | 7.7868 | 0 | N/A | 0 | 0
2022-06-27 10:00 | 7.2337 | 0 | N/A | 0 | 0
2022-06-27 10:30 | 7.0018 | 0 | N/A | 0 | 0
2022-06-27 11:00 | 6.2454 | 0 | N/A | 0 | 0
2022-06-27 11:30 | 5.4156 | 0 | N/A | 0 | 0
2022-06-27 12:00 | 5.6186 | 0 | N/A | 0 | 0
2022-06-27 12:30 | 5.5288 | 0 | N/A | 0 | 0
2022-06-27 13:00 | 5.7507 | 0 | N/A | 0 | 0
2022-06-27 13:30 | 6.2376 | 0 | N/A | 0 | 0
2022-06-27 14:00 | 6.3328 | 0 | N/A | 0 | 0
2022-06-27 14:30 | 6.2627 | 0 | N/A | 0 | 0
2022-06-27 15:00 | 6.5187 | 0 | N/A | 0 | 0
2022-06-27 15:30 | 6.9072 | 0 | N/A | 0 | 0
2022-06-27 16:00 | 7.5851 | 0 | N/A | 0 | 0
2022-06-27 16:30 | 7.7066 | 0 | N/A | 0 | 0
2022-06-27 17:00 | 7.948 | 0 | N/A | 0 | 0
2022-06-27 17:30 | 8.6423 | 0 | N/A | 0 | 0
2022-06-27 18:00 | 9.4138 | 0 | N/A | 0 | 0
2022-06-27 18:30 | 9.6156 | 0 | N/A | 0 | 0
2022-06-27 19:00 | 9.2762 | 0 | N/A | 0 | 0
2022-06-27 19:30 | 9.0778 | 0 | N/A | 0 | 0
2022-06-27 20:00 | 8.7051 | 0 | N/A | 0 | 0
2022-06-27 20:30 | 8.2955 | 0 | N/A | 0 | 0
2022-06-27 21:00 | 7.8978 | 0 | N/A | 0 | 0
2022-06-27 21:30 | 8.0863 | 0 | N/A | 0 | 0
2022-06-27 22:00 | 7.9992 | 0 | N/A | 0 | 0
2022-06-27 22:30 | 7.1692 | 0 | N/A | 0 | 0
2022-06-27 23:00 | 6.8707 | 0 | N/A | 0 | 0
2022-06-27 23:30 | 7.0857 | 0 | N/A | 0 | 0
2022-06-28 | 7.2379 | 0 | N/A | 0 | 0
2022-06-28 00:30 | 6.6421 | 0 | N/A | 0 | 0
2022-06-28 01:00 | 5.7894 | 0 | N/A | 0 | 0
2022-06-28 01:30 | 5.6526 | 0 | N/A | 0 | 0
2022-06-28 02:00 | 5.428 | 0 | N/A | 0 | 0
2022-06-28 02:30 | 4.8709 | 0 | N/A | 0 | 0
2022-06-28 03:00 | 4.6555 | 0 | N/A | 0 | 0
2022-06-28 03:30 | 4.5125 | 0 | N/A | 0 | 0
2022-06-28 04:00 | 4.3713 | 0 | N/A | 0 | 0
2022-06-28 04:30 | 4.2752 | 0 | N/A | 0 | 0
2022-06-28 05:00 | 4.3841 | 0 | N/A | 0 | 0
2022-06-28 05:30 | 4.9673 | 0 | N/A | 0 | 0
2022-06-28 06:00 | 5.4117 | 0 | N/A | 0 | 0
2022-06-28 06:30 | 6.297 | 0 | N/A | 0 | 0
2022-06-28 07:00 | 7.0189 | 0 | N/A | 0 | 0
2022-06-28 07:30 | 7.6553 | 0 | N/A | 0 | 0
2022-06-28 08:00 | 8.2405 | 0 | N/A | 0 | 0
2022-06-28 08:30 | 8.7608 | 0 | N/A | 0 | 0
2022-06-28 09:00 | 9.1569 | 0 | N/A | 0 | 0
2022-06-28 09:30 | 9.3504 | 0 | N/A | 0 | 0
2022-06-28 10:00 | 9.1504 | 0 | N/A | 0 | 0
2022-06-28 10:30 | 8.5177 | 0 | N/A | 0 | 0
2022-06-28 11:00 | 7.4113 | 0 | N/A | 0 | 0
2022-06-28 11:30 | 7.2535 | 0 | N/A | 0 | 0
2022-06-28 12:00 | 6.997 | 0 | N/A | 0 | 0
2022-06-28 12:30 | 6.5382 | 0 | N/A | 0 | 0
2022-06-28 13:00 | 4.9935 | 0 | N/A | 0 | 0
2022-06-28 13:30 | 4.4867 | 0 | N/A | 0 | 0
2022-06-28 14:00 | 4.5235 | 0 | N/A | 0 | 0
2022-06-28 14:30 | 4.3738 | 0 | N/A | 0 | 0
2022-06-28 15:00 | 4.6459 | 0 | N/A | 0 | 0
2022-06-28 15:30 | 5.2339 | 0 | N/A | 0 | 0
2022-06-28 16:00 | 5.432 | 0 | N/A | 0 | 0
2022-06-28 16:30 | 5.804 | 0 | N/A | 0 | 0
2022-06-28 17:00 | 6.9192 | 0 | N/A | 0 | 0
2022-06-28 17:30 | 8.2144 | 0 | N/A | 0 | 0
2022-06-28 18:00 | 9.3484 | 0 | N/A | 0 | 0
2022-06-28 18:30 | 9.7857 | 0 | N/A | 0 | 0
2022-06-28 19:00 | 9.6497 | 0 | N/A | 0 | 0
2022-06-28 19:30 | 9.3073 | 0 | N/A | 0 | 0
2022-06-28 20:00 | 8.9453 | 0 | N/A | 0 | 0
2022-06-28 20:30 | 8.5536 | 0 | N/A | 0 | 0
2022-06-28 21:00 | 8.1543 | 0 | N/A | 0 | 0
2022-06-28 21:30 | 8.2271 | 0 | N/A | 0 | 0
2022-06-28 22:00 | 8.1618 | 0 | N/A | 0 | 0
2022-06-28 22:30 | 7.5024 | 0 | N/A | 0 | 0
2022-06-28 23:00 | 7.0638 | 0 | N/A | 0 | 0
2022-06-28 23:30 | 7.0065 | 0 | N/A | 0 | 0
2022-06-29 | 7.1696 | 0 | N/A | 0 | 0
2022-06-29 00:30 | 6.6178 | 0 | N/A | 0 | 0
2022-06-29 01:00 | 5.8923 | 0 | N/A | 0 | 0
2022-06-29 01:30 | 5.7804 | 0 | N/A | 0 | 0
2022-06-29 02:00 | 5.3771 | 0 | N/A | 0 | 0
2022-06-29 02:30 | 4.9624 | 0 | N/A | 0 | 0
2022-06-29 03:00 | 4.626 | 0 | N/A | 0 | 0
2022-06-29 03:30 | 4.4297 | 0 | N/A | 0 | 0
2022-06-29 04:00 | 4.3406 | 0 | N/A | 0 | 0
2022-06-29 04:30 | 4.2663 | 0 | N/A | 0 | 0
2022-06-29 05:00 | 4.4363 | 0 | N/A | 0 | 0
2022-06-29 05:30 | 4.9171 | 0 | N/A | 0 | 0
2022-06-29 06:00 | 5.3839 | 0 | N/A | 0 | 0
2022-06-29 06:30 | 6.0929 | 0 | N/A | 0 | 0
2022-06-29 07:00 | 6.7433 | 0 | N/A | 0 | 0
2022-06-29 07:30 | 7.116 | 0 | N/A | 0 | 0
2022-06-29 08:00 | 8.0172 | 0 | N/A | 0 | 0
2022-06-29 08:30 | 8.7904 | 0 | N/A | 0 | 0
2022-06-29 09:00 | 8.71 | 0 | N/A | 0 | 0
2022-06-29 09:30 | 8.8 | 0 | N/A | 0 | 0
2022-06-29 10:00 | 7.98 | 0 | N/A | 0 | 0
2022-06-29 10:30 | 7.96 | 0 | N/A | 0 | 0
2022-06-29 11:00 | 7.75 | 0 | N/A | 0 | 0
2022-06-29 11:30 | 7.5033 | 0 | N/A | 0 | 0
2022-06-29 12:00 | 7.2439 | 0 | N/A | 0 | 0
2022-06-29 12:30 | 7.4297 | 0 | N/A | 0 | 0
2022-06-29 13:00 | 7.494 | 0 | N/A | 0 | 0
2022-06-29 13:30 | 7.234 | 0 | N/A | 0 | 0
2022-06-29 14:00 | 7.0744 | 0 | N/A | 0 | 0
2022-06-29 14:30 | 7.4171 | 0 | N/A | 0 | 0
2022-06-29 15:00 | 7.3947 | 0 | N/A | 0 | 0
2022-06-29 15:30 | 7.3184 | 0 | N/A | 0 | 0
2022-06-29 16:00 | 7.6962 | 0 | N/A | 0 | 0
2022-06-29 16:30 | 7.9622 | 0 | N/A | 0 | 0
2022-06-29 17:00 | 8.4248 | 0 | N/A | 0 | 0
2022-06-29 17:30 | 9.1875 | 0 | N/A | 0 | 0
2022-06-29 18:00 | 9.9686 | 0 | N/A | 0 | 0
2022-06-29 18:30 | 10.0279 | 0 | N/A | 0 | 0
2022-06-29 19:00 | 9.8277 | 0 | N/A | 0 | 0
2022-06-29 19:30 | 9.5181 | 0 | N/A | 0 | 0
2022-06-29 20:00 | 9.2324 | 0 | N/A | 0 | 0
2022-06-29 20:30 | 8.8549 | 0 | N/A | 0 | 0
2022-06-29 21:00 | 8.5174 | 0 | N/A | 0 | 0
2022-06-29 21:30 | 8.4918 | 0 | N/A | 0 | 0
2022-06-29 22:00 | 8.4519 | 0 | N/A | 0 | 0
2022-06-29 22:30 | 7.5159 | 0 | N/A | 0 | 0
2022-06-29 23:00 | 7.2087 | 0 | N/A | 0 | 0
2022-06-29 23:30 | 7.2769 | 0 | N/A | 0 | 0
2022-06-30 | 7.4531 | 0 | N/A | 0 | 0
2022-06-30 00:30 | 6.9073 | 0 | N/A | 0 | 0
2022-06-30 01:00 | 6.1447 | 0 | N/A | 0 | 0
2022-06-30 01:30 | 5.9047 | 0 | N/A | 0 | 0
2022-06-30 02:00 | 5.5436 | 0 | N/A | 0 | 0
2022-06-30 02:30 | 5.0062 | 0 | N/A | 0 | 0
2022-06-30 03:00 | 4.7418 | 0 | N/A | 0 | 0
2022-06-30 03:30 | 4.566 | 0 | N/A | 0 | 0
2022-06-30 04:00 | 4.3613 | 0 | N/A | 0 | 0
2022-06-30 04:30 | 4.3118 | 0 | N/A | 0 | 0
2022-06-30 05:00 | 4.3887 | 0 | N/A | 0 | 0
2022-06-30 05:30 | 4.8534 | 0 | N/A | 0 | 0
2022-06-30 06:00 | 5.2683 | 0 | N/A | 0 | 0
2022-06-30 06:30 | 6.0775 | 0 | N/A | 0 | 0
2022-06-30 07:00 | 6.6198 | 0 | N/A | 0 | 0
2022-06-30 07:30 | 7.1494 | 0 | N/A | 0 | 0
2022-06-30 08:00 | 7.8109 | 0 | N/A | 0 | 0
2022-06-30 08:30 | 8.3853 | 0 | N/A | 0 | 0
2022-06-30 09:00 | 8.2538 | 0 | N/A | 0 | 0
2022-06-30 09:30 | 8.2938 | 0 | N/A | 0 | 0
2022-06-30 10:00 | 7.8774 | 0 | N/A | 0 | 0
2022-06-30 10:30 | 6.3784 | 0 | N/A | 0 | 0
2022-06-30 11:00 | 5.2073 | 0 | N/A | 0 | 0
2022-06-30 11:30 | 4.139 | 0 | N/A | 0 | 0
2022-06-30 12:00 | 3.7382 | 0 | N/A | 0 | 0
2022-06-30 12:30 | 2.9506 | 0 | N/A | 0 | 0
2022-06-30 13:00 | 2.7649 | 0 | N/A | 0 | 0
2022-06-30 13:30 | 3.1759 | 0 | N/A | 0 | 0
2022-06-30 14:00 | 3.2706 | 0 | N/A | 0 | 0
2022-06-30 14:30 | 3.5402 | 0 | N/A | 0 | 0
2022-06-30 15:00 | 3.9688 | 0 | N/A | 0 | 0
2022-06-30 15:30 | 4.2586 | 0 | N/A | 0 | 0
2022-06-30 16:00 | 4.7437 | 0 | N/A | 0 | 0
2022-06-30 16:30 | 5.6998 | 0 | N/A | 0 | 0
2022-06-30 17:00 | 6.1957 | 0 | N/A | 0 | 0
2022-06-30 17:30 | 7.4883 | 0 | N/A | 0 | 0
2022-06-30 18:00 | 8.5299 | 0 | N/A | 0 | 0
2022-06-30 18:30 | 8.9028 | 0 | N/A | 0 | 0
2022-06-30 19:00 | 8.995 | 0 | N/A | 0 | 0
2022-06-30 19:30 | 8.7061 | 0 | N/A | 0 | 0
2022-06-30 20:00 | 8.4331 | 0 | N/A | 0 | 0
2022-06-30 20:30 | 8.072 | 0 | N/A | 0 | 0
2022-06-30 21:00 | 7.6591 | 0 | N/A | 0 | 0
2022-06-30 21:30 | 7.6327 | 0 | N/A | 0 | 0
2022-06-30 22:00 | 7.567 | 0 | N/A | 0 | 0
2022-06-30 22:30 | 6.822 | 0 | N/A | 0 | 0
2022-06-30 23:00 | 6.4931 | 0 | N/A | 0 | 0
2022-06-30 23:30 | 6.488 | 0 | N/A | 0 | 0
2022-07-01 | 6.7164 | 0 | N/A | 0 | 0
2022-07-02 00:30 | 6.6094 | 0 | N/A | 0 | 0
2022-07-02 01:00 | 5.911 | 0 | N/A | 0 | 0
2022-07-02 01:30 | 5.7025 | 0 | N/A | 0 | 0
2022-07-02 02:00 | 5.3032 | 0 | N/A | 0 | 0
2022-07-02 02:30 | 4.7319 | 0 | N/A | 0 | 0
2022-07-02 03:00 | 4.3928 | 0 | N/A | 0 | 0
2022-07-02 03:30 | 4.1889 | 0 | N/A | 0 | 0
2022-07-02 04:00 | 4.0645 | 0 | N/A | 0 | 0
2022-07-02 04:30 | 3.9871 | 0 | N/A | 0 | 0
2022-07-02 05:00 | 4.0202 | 0 | N/A | 0 | 0
2022-07-02 05:30 | 4.1785 | 0 | N/A | 0 | 0
2022-07-02 06:00 | 4.3558 | 0 | N/A | 0 | 0
2022-07-02 06:30 | 4.7634 | 0 | N/A | 0 | 0
2022-07-02 07:00 | 4.9512 | 0 | N/A | 0 | 0
2022-07-02 07:30 | 4.9389 | 0 | N/A | 0 | 0
2022-07-02 08:00 | 5.5625 | 0 | N/A | 0 | 0
2022-07-02 08:30 | 6.5673 | 0 | N/A | 0 | 0
2022-07-02 09:00 | 6.8659 | 0 | N/A | 0 | 0
2022-07-02 09:30 | 6.7508 | 0 | N/A | 0 | 0
2022-07-02 10:00 | 6.3281 | 0 | N/A | 0 | 0
2022-07-02 10:30 | 5.7231 | 0 | N/A | 0 | 0
2022-07-02 11:00 | 4.9257 | 0 | N/A | 0 | 0
2022-07-02 11:30 | 4.5623 | 0 | N/A | 0 | 0
2022-07-02 12:00 | 4.2267 | 0 | N/A | 0 | 0
2022-07-02 12:30 | 4.0022 | 0 | N/A | 0 | 0
2022-07-02 13:00 | 3.9686 | 0 | N/A | 0 | 0
2022-07-02 13:30 | 4.1962 | 0 | N/A | 0 | 0
2022-07-02 14:00 | 4.5264 | 0 | N/A | 0 | 0
2022-07-02 14:30 | 4.5601 | 0 | N/A | 0 | 0
2022-07-02 15:00 | 4.6561 | 0 | N/A | 0 | 0
2022-07-02 15:30 | 5.4862 | 0 | N/A | 0 | 0
2022-07-02 16:00 | 5.4729 | 0 | N/A | 0 | 0
2022-07-02 16:30 | 6.166 | 0 | N/A | 0 | 0
2022-07-02 17:00 | 7.0031 | 0 | N/A | 0 | 0
2022-07-02 17:30 | 7.8488 | 0 | N/A | 0 | 0
2022-07-02 18:00 | 8.3771 | 0 | N/A | 0 | 0
2022-07-02 18:30 | 8.6651 | 0 | N/A | 0 | 0
2022-07-02 19:00 | 8.4736 | 0 | N/A | 0 | 0
2022-07-02 19:30 | 8.1524 | 0 | N/A | 0 | 0
2022-07-02 20:00 | 7.9248 | 0 | N/A | 0 | 0
2022-07-02 20:30 | 7.5454 | 0 | N/A | 0 | 0
2022-07-02 21:00 | 7.2363 | 0 | N/A | 0 | 0
2022-07-02 21:30 | 7.5094 | 0 | N/A | 0 | 0
2022-07-02 22:00 | 7.5954 | 0 | N/A | 0 | 0
2022-07-02 22:30 | 7.1242 | 0 | N/A | 0 | 0
2022-07-02 23:00 | 6.9518 | 0 | N/A | 0 | 0
2022-07-02 23:30 | 6.9945 | 0 | N/A | 0 | 0
2022-07-03 | 7.2689 | 0 | N/A | 0 | 0
2022-07-03 00:30 | 6.6455 | 0 | N/A | 0 | 0
2022-07-03 01:00 | 5.8595 | 0 | N/A | 0 | 0
2022-07-03 01:30 | 5.6273 | 0 | N/A | 0 | 0
2022-07-03 02:00 | 5.2678 | 0 | N/A | 0 | 0
2022-07-03 02:30 | 4.7024 | 0 | N/A | 0 | 0
2022-07-03 03:00 | 4.3552 | 0 | N/A | 0 | 0
2022-07-03 03:30 | 4.1665 | 0 | N/A | 0 | 0
2022-07-03 04:00 | 4.0623 | 0 | N/A | 0 | 0
2022-07-03 04:30 | 4.0104 | 0 | N/A | 0 | 0
2022-07-03 05:00 | 3.9307 | 0 | N/A | 0 | 0
2022-07-03 05:30 | 3.9497 | 0 | N/A | 0 | 0
2022-07-03 06:00 | 4.0625 | 0 | N/A | 0 | 0
2022-07-03 06:30 | 4.3739 | 0 | N/A | 0 | 0
2022-07-03 07:00 | 4.5653 | 0 | N/A | 0 | 0
2022-07-03 07:30 | 4.5954 | 0 | N/A | 0 | 0
2022-07-03 08:00 | 5.0958 | 0 | N/A | 0 | 0
2022-07-03 08:30 | 5.7546 | 0 | N/A | 0 | 0
2022-07-03 09:00 | 6.1364 | 0 | N/A | 0 | 0
2022-07-03 09:30 | 6.1919 | 0 | N/A | 0 | 0
2022-07-03 10:00 | 6.3638 | 0 | N/A | 0 | 0
2022-07-03 10:30 | 6.3355 | 0 | N/A | 0 | 0
2022-07-03 11:00 | 5.9392 | 0 | N/A | 0 | 0
2022-07-03 11:30 | 5.78 | 0 | N/A | 0 | 0
2022-07-03 12:00 | 5.9578 | 0 | N/A | 0 | 0
2022-07-03 12:30 | 5.9053 | 0 | N/A | 0 | 0
2022-07-03 13:00 | 5.4222 | 0 | N/A | 0 | 0
2022-07-03 13:30 | 5.3401 | 0 | N/A | 0 | 0
2022-07-03 14:00 | 5.4866 | 0 | N/A | 0 | 0
2022-07-03 14:30 | 5.3907 | 0 | N/A | 0 | 0
2022-07-03 15:00 | 5.046 | 0 | N/A | 0 | 0
2022-07-03 15:30 | 5.1423 | 0 | N/A | 0 | 0
2022-07-03 16:00 | 6.3556 | 0 | N/A | 0 | 0
2022-07-03 16:30 | 7.148 | 0 | N/A | 0 | 0
2022-07-03 17:00 | 7.9514 | 0 | N/A | 0 | 0
2022-07-03 17:30 | 8.7206 | 0 | N/A | 0 | 0
2022-07-03 18:00 | 9.5685 | 0 | N/A | 0 | 0
2022-07-03 18:30 | 9.5554 | 0 | N/A | 0 | 0
2022-07-03 19:00 | 9.0512 | 0 | N/A | 0 | 0
2022-07-03 19:30 | 8.6099 | 0 | N/A | 0 | 0
2022-07-03 20:00 | 8.23 | 0 | N/A | 0 | 0
2022-07-03 20:30 | 7.7408 | 0 | N/A | 0 | 0
2022-07-03 21:00 | 7.3349 | 0 | N/A | 0 | 0
2022-07-03 21:30 | 7.4532 | 0 | N/A | 0 | 0
2022-07-03 22:00 | 7.4762 | 0 | N/A | 0 | 0
2022-07-03 22:30 | 7.0168 | 0 | N/A | 0 | 0
2022-07-03 23:00 | 6.8583 | 0 | N/A | 0 | 0
2022-07-03 23:30 | 6.6809 | 0 | N/A | 0 | 0
2022-07-04 | 7.0146 | 0 | N/A | 0 | 0
2022-07-04 00:30 | 6.4277 | 0 | N/A | 0 | 0
2022-07-04 01:00 | 5.8079 | 0 | N/A | 0 | 0
2022-07-04 01:30 | 5.6444 | 0 | N/A | 0 | 0
2022-07-04 02:00 | 5.3586 | 0 | N/A | 0 | 0
2022-07-04 02:30 | 4.8597 | 0 | N/A | 0 | 0
2022-07-04 03:00 | 4.4499 | 0 | N/A | 0 | 0
2022-07-04 03:30 | 4.2231 | 0 | N/A | 0 | 0
2022-07-04 04:00 | 4.1155 | 0 | N/A | 0 | 0
2022-07-04 04:30 | 4.0697 | 0 | N/A | 0 | 0
2022-07-04 05:00 | 4.0808 | 0 | N/A | 0 | 0
2022-07-04 05:30 | 4.6382 | 0 | N/A | 0 | 0
2022-07-04 06:00 | 4.9547 | 0 | N/A | 0 | 0
2022-07-04 06:30 | 5.6581 | 0 | N/A | 0 | 0
2022-07-04 07:00 | 6.2059 | 0 | N/A | 0 | 0
2022-07-04 07:30 | 6.6694 | 0 | N/A | 0 | 0
2022-07-04 08:00 | 7.4874 | 0 | N/A | 0 | 0
2022-07-04 08:30 | 7.7811 | 0 | N/A | 0 | 0
2022-07-04 09:00 | 7.4505 | 0 | N/A | 0 | 0
2022-07-04 09:30 | 6.8571 | 0 | N/A | 0 | 0
2022-07-04 10:00 | 5.8188 | 0 | N/A | 0 | 0
2022-07-04 10:30 | 5.1674 | 0 | N/A | 0 | 0
2022-07-04 11:00 | 4.9513 | 0 | N/A | 0 | 0
2022-07-04 11:30 | 4.5333 | 0 | N/A | 0 | 0
2022-07-04 12:00 | 4.4139 | 0 | N/A | 0 | 0
2022-07-04 12:30 | 4.2187 | 0 | N/A | 0 | 0
2022-07-04 13:00 | 4.2555 | 0 | N/A | 0 | 0
2022-07-04 13:30 | 4.7722 | 0 | N/A | 0 | 0
2022-07-04 14:00 | 4.3599 | 0 | N/A | 0 | 0
2022-07-04 14:30 | 4.359 | 0 | N/A | 0 | 0
2022-07-04 15:00 | 5.0429 | 0 | N/A | 0 | 0
2022-07-04 15:30 | 5.845 | 0 | N/A | 0 | 0
2022-07-04 16:00 | 5.8797 | 0 | N/A | 0 | 0
2022-07-04 16:30 | 6.1195 | 0 | N/A | 0 | 0
2022-07-04 17:00 | 6.9494 | 0 | N/A | 0 | 0
2022-07-04 17:30 | 7.8989 | 0 | N/A | 0 | 0
2022-07-04 18:00 | 8.9803 | 0 | N/A | 0 | 0
2022-07-04 18:30 | 9.1415 | 0 | N/A | 0 | 0
2022-07-04 19:00 | 8.8562 | 0 | N/A | 0 | 0
2022-07-04 19:30 | 8.5887 | 0 | N/A | 0 | 0
2022-07-04 20:00 | 8.247 | 0 | N/A | 0 | 0
2022-07-04 20:30 | 7.7536 | 0 | N/A | 0 | 0
2022-07-04 21:00 | 7.4066 | 0 | N/A | 0 | 0
2022-07-04 21:30 | 7.4614 | 0 | N/A | 0 | 0
2022-07-04 22:00 | 7.4668 | 0 | N/A | 0 | 0
2022-07-04 22:30 | 6.8327 | 0 | N/A | 0 | 0
2022-07-04 23:00 | 6.5542 | 0 | N/A | 0 | 0
2022-07-04 23:30 | 6.5104 | 0 | N/A | 0 | 0
2022-07-05 | 6.7038 | 0 | N/A | 0 | 0
2022-07-05 00:30 | 6.0962 | 0 | N/A | 0 | 0
2022-07-05 01:00 | 5.4873 | 0 | N/A | 0 | 0
2022-07-05 01:30 | 5.3397 | 0 | N/A | 0 | 0
2022-07-05 02:00 | 4.9909 | 0 | N/A | 0 | 0
2022-07-05 02:30 | 4.4432 | 0 | N/A | 0 | 0
2022-07-05 03:00 | 4.0645 | 0 | N/A | 0 | 0
2022-07-05 03:30 | 3.895 | 0 | N/A | 0 | 0
2022-07-05 04:00 | 3.8033 | 0 | N/A | 0 | 0
2022-07-05 04:30 | 3.7521 | 0 | N/A | 0 | 0
2022-07-05 05:00 | 3.8576 | 0 | N/A | 0 | 0
2022-07-05 05:30 | 4.3693 | 0 | N/A | 0 | 0
2022-07-05 06:00 | 4.7389 | 0 | N/A | 0 | 0
2022-07-05 06:30 | 5.3781 | 0 | N/A | 0 | 0
2022-07-05 07:00 | 5.7858 | 0 | N/A | 0 | 0
2022-07-05 07:30 | 5.8962 | 0 | N/A | 0 | 0
2022-07-05 08:00 | 6.5482 | 0 | N/A | 0 | 0
2022-07-05 08:30 | 7.4603 | 0 | N/A | 0 | 0
2022-07-05 09:00 | 7.5275 | 0 | N/A | 0 | 0
2022-07-05 09:30 | 6.9236 | 0 | N/A | 0 | 0
2022-07-05 10:00 | 6.1785 | 0 | N/A | 0 | 0
2022-07-05 10:30 | 5.8405 | 0 | N/A | 0 | 0
2022-07-05 11:00 | 5.3989 | 0 | N/A | 0 | 0
2022-07-05 11:30 | 5.217 | 0 | N/A | 0 | 0
2022-07-05 12:00 | 4.688 | 0 | N/A | 0 | 0
2022-07-05 12:30 | 4.7077 | 0 | N/A | 0 | 0
2022-07-05 13:00 | 4.0017 | 0 | N/A | 0 | 0
2022-07-05 13:30 | 3.5908 | 0 | N/A | 0 | 0
2022-07-05 14:00 | 3.9193 | 0 | N/A | 0 | 0
2022-07-05 14:30 | 4.4293 | 0 | N/A | 0 | 0
2022-07-05 15:00 | 3.9883 | 0 | N/A | 0 | 0
2022-07-05 15:30 | 4.338 | 0 | N/A | 0 | 0
2022-07-05 16:00 | 4.9111 | 0 | N/A | 0 | 0
2022-07-05 16:30 | 5.4872 | 0 | N/A | 0 | 0
2022-07-05 17:00 | 6.3677 | 0 | N/A | 0 | 0
2022-07-05 17:30 | 7.4066 | 0 | N/A | 0 | 0
2022-07-05 18:00 | 8.3686 | 0 | N/A | 0 | 0
2022-07-05 18:30 | 8.8874 | 0 | N/A | 0 | 0
2022-07-05 19:00 | 8.7681 | 0 | N/A | 0 | 0
2022-07-05 19:30 | 8.5762 | 0 | N/A | 0 | 0
2022-07-05 20:00 | 8.4072 | 0 | N/A | 0 | 0
2022-07-05 20:30 | 8.0939 | 0 | N/A | 0 | 0
2022-07-05 21:00 | 7.6489 | 0 | N/A | 0 | 0
2022-07-05 21:30 | 7.8313 | 0 | N/A | 0 | 0
2022-07-05 22:00 | 7.7249 | 0 | N/A | 0 | 0
2022-07-05 22:30 | 7.1388 | 0 | N/A | 0 | 0
2022-07-05 23:00 | 6.9038 | 0 | N/A | 0 | 0
2022-07-05 23:30 | 6.8769 | 0 | N/A | 0 | 0
2022-07-06 | 7.3032 | 0 | N/A | 0 | 0
2022-07-07 00:30 | 6.5217 | 0 | N/A | 0 | 0
2022-07-07 01:00 | 5.8801 | 0 | N/A | 0 | 0
2022-07-07 01:30 | 5.6832 | 0 | N/A | 0 | 0
2022-07-07 02:00 | 5.3246 | 0 | N/A | 0 | 0
2022-07-07 02:30 | 4.8602 | 0 | N/A | 0 | 0
2022-07-07 03:00 | 4.3823 | 0 | N/A | 0 | 0
2022-07-07 03:30 | 4.2113 | 0 | N/A | 0 | 0
2022-07-07 04:00 | 4.0731 | 0 | N/A | 0 | 0
2022-07-07 04:30 | 3.9798 | 0 | N/A | 0 | 0
2022-07-07 05:00 | 4.1506 | 0 | N/A | 0 | 0
2022-07-07 05:30 | 4.5285 | 0 | N/A | 0 | 0
2022-07-07 06:00 | 5.0311 | 0 | N/A | 0 | 0
2022-07-07 06:30 | 5.8737 | 0 | N/A | 0 | 0
2022-07-07 07:00 | 6.5931 | 0 | N/A | 0 | 0
2022-07-07 07:30 | 6.9694 | 0 | N/A | 0 | 0
2022-07-07 08:00 | 7.558 | 0 | N/A | 0 | 0
2022-07-07 08:30 | 8.3843 | 0 | N/A | 0 | 0
2022-07-07 09:00 | 8.4957 | 0 | N/A | 0 | 0
2022-07-07 09:30 | 7.8854 | 0 | N/A | 0 | 0
2022-07-07 10:00 | 7.1642 | 0 | N/A | 0 | 0
2022-07-07 10:30 | 6.0162 | 0 | N/A | 0 | 0
2022-07-07 11:00 | 5.117 | 0 | N/A | 0 | 0
2022-07-07 11:30 | 4.834 | 0 | N/A | 0 | 0
2022-07-07 12:00 | 4.9138 | 0 | N/A | 0 | 0
2022-07-07 12:30 | 4.8106 | 0 | N/A | 0 | 0
2022-07-07 13:00 | 5.1157 | 0 | N/A | 0 | 0
2022-07-07 13:30 | 5.0088 | 0 | N/A | 0 | 0
2022-07-07 14:00 | 5.2854 | 0 | N/A | 0 | 0
2022-07-07 14:30 | 4.2507 | 0 | N/A | 0 | 0
2022-07-07 15:00 | 4.6783 | 0 | N/A | 0 | 0
2022-07-07 15:30 | 5.8172 | 0 | N/A | 0 | 0
2022-07-07 16:00 | 5.31 | 0 | N/A | 0 | 0
2022-07-07 16:30 | 6.1948 | 0 | N/A | 0 | 0
2022-07-07 17:00 | 7.4097 | 0 | N/A | 0 | 0
2022-07-07 17:30 | 8.1637 | 0 | N/A | 0 | 0
2022-07-07 18:00 | 8.8441 | 0 | N/A | 0 | 0
2022-07-07 18:30 | 9.1789 | 0 | N/A | 0 | 0
2022-07-07 19:00 | 9.1032 | 0 | N/A | 0 | 0
2022-07-07 19:30 | 8.8581 | 0 | N/A | 0 | 0
2022-07-07 20:00 | 8.5199 | 0 | N/A | 0 | 0
2022-07-07 20:30 | 8.1487 | 0 | N/A | 0 | 0
2022-07-07 21:00 | 7.8393 | 0 | N/A | 0 | 0
2022-07-07 21:30 | 7.8374 | 0 | N/A | 0 | 0
2022-07-07 22:00 | 7.7443 | 0 | N/A | 0 | 0
2022-07-07 22:30 | 7.0792 | 0 | N/A | 0 | 0
2022-07-07 23:00 | 6.8073 | 0 | N/A | 0 | 0
2022-07-07 23:30 | 6.9082 | 0 | N/A | 0 | 0
2022-07-08 | 6.947 | 0 | N/A | 0 | 0
2022-07-08 00:30 | 6.2595 | 0 | N/A | 0 | 0
2022-07-08 01:00 | 5.6012 | 0 | N/A | 0 | 0
2022-07-08 01:30 | 5.4174 | 0 | N/A | 0 | 0
2022-07-08 02:00 | 5.0881 | 0 | N/A | 0 | 0
2022-07-08 02:30 | 4.5815 | 0 | N/A | 0 | 0
2022-07-08 03:00 | 4.2911 | 0 | N/A | 0 | 0
2022-07-08 03:30 | 4.1602 | 0 | N/A | 0 | 0
2022-07-08 04:00 | 3.9882 | 0 | N/A | 0 | 0
2022-07-08 04:30 | 3.9711 | 0 | N/A | 0 | 0
2022-07-08 05:00 | 4.0315 | 0 | N/A | 0 | 0
2022-07-08 05:30 | 4.4102 | 0 | N/A | 0 | 0
2022-07-08 06:00 | 4.7864 | 0 | N/A | 0 | 0
2022-07-08 06:30 | 5.6862 | 0 | N/A | 0 | 0
2022-07-08 07:00 | 6.0699 | 0 | N/A | 0 | 0
2022-07-08 07:30 | 6.4698 | 0 | N/A | 0 | 0
2022-07-08 08:00 | 7.2314 | 0 | N/A | 0 | 0
2022-07-08 08:30 | 7.9846 | 0 | N/A | 0 | 0
2022-07-08 09:00 | 8.0971 | 0 | N/A | 0 | 0
2022-07-08 09:30 | 8.0013 | 0 | N/A | 0 | 0
2022-07-08 10:00 | 7.3352 | 0 | N/A | 0 | 0
2022-07-08 10:30 | 6.9065 | 0 | N/A | 0 | 0
2022-07-08 11:00 | 7.2118 | 0 | N/A | 0 | 0
2022-07-08 11:30 | 6.994 | 0 | N/A | 0 | 0
2022-07-08 12:00 | 7.0124 | 0 | N/A | 0 | 0
2022-07-08 12:30 | 6.3504 | 0 | N/A | 0 | 0
2022-07-08 13:00 | 4.2069 | 0 | N/A | 0 | 0
2022-07-08 13:30 | 5.1089 | 0 | N/A | 0 | 0
2022-07-08 14:00 | 5.683 | 0 | N/A | 0 | 0
2022-07-08 14:30 | 5.2911 | 0 | N/A | 0 | 0
2022-07-08 15:00 | 6.4235 | 0 | N/A | 0 | 0
2022-07-08 15:30 | 6.0596 | 0 | N/A | 0 | 0
2022-07-08 16:00 | 6.5823 | 0 | N/A | 0 | 0
2022-07-08 16:30 | 7.0725 | 0 | N/A | 0 | 0
2022-07-08 17:00 | 7.7036 | 0 | N/A | 0 | 0
2022-07-08 17:30 | 8.2552 | 0 | N/A | 0 | 0
2022-07-08 18:00 | 8.8786 | 0 | N/A | 0 | 0
2022-07-08 18:30 | 9.1395 | 0 | N/A | 0 | 0
2022-07-08 19:00 | 9.0528 | 0 | N/A | 0 | 0
2022-07-08 19:30 | 8.6732 | 0 | N/A | 0 | 0
2022-07-08 20:00 | 8.4401 | 0 | N/A | 0 | 0
2022-07-08 20:30 | 8.0346 | 0 | N/A | 0 | 0
2022-07-08 21:00 | 7.6785 | 0 | N/A | 0 | 0
2022-07-08 21:30 | 7.7676 | 0 | N/A | 0 | 0
2022-07-08 22:00 | 7.9033 | 0 | N/A | 0 | 0
2022-07-08 22:30 | 7.249 | 0 | N/A | 0 | 0
2022-07-08 23:00 | 7.1979 | 0 | N/A | 0 | 0
2022-07-08 23:30 | 7.067 | 0 | N/A | 0 | 0
2022-07-09 | 7.254 | 0 | N/A | 0 | 0
2022-07-09 00:30 | 6.6102 | 0 | N/A | 0 | 0
2022-07-09 01:00 | 5.9384 | 0 | N/A | 0 | 0
2022-07-09 01:30 | 5.709 | 0 | N/A | 0 | 0
2022-07-09 02:00 | 5.3477 | 0 | N/A | 0 | 0
2022-07-09 02:30 | 4.885 | 0 | N/A | 0 | 0
2022-07-09 03:00 | 4.4809 | 0 | N/A | 0 | 0
2022-07-09 03:30 | 4.3145 | 0 | N/A | 0 | 0
2022-07-09 04:00 | 4.1008 | 0 | N/A | 0 | 0
2022-07-09 04:30 | 3.9899 | 0 | N/A | 0 | 0
2022-07-09 05:00 | 3.9899 | 0 | N/A | 0 | 0
2022-07-09 05:30 | 4.1341 | 0 | N/A | 0 | 0
2022-07-09 06:00 | 4.3257 | 0 | N/A | 0 | 0
2022-07-09 06:30 | 4.7998 | 0 | N/A | 0 | 0
2022-07-09 07:00 | 5.0662 | 0 | N/A | 0 | 0
2022-07-09 07:30 | 5.0984 | 0 | N/A | 0 | 0
2022-07-09 08:00 | 5.7178 | 0 | N/A | 0 | 0
2022-07-09 08:30 | 6.5069 | 0 | N/A | 0 | 0
2022-07-09 09:00 | 6.6104 | 0 | N/A | 0 | 0
2022-07-09 09:30 | 7.1259 | 0 | N/A | 0 | 0
2022-07-09 10:00 | 6.8261 | 0 | N/A | 0 | 0
2022-07-09 10:30 | 5.6104 | 0 | N/A | 0 | 0
2022-07-09 11:00 | 5.1078 | 0 | N/A | 0 | 0
2022-07-09 11:30 | 4.4586 | 0 | N/A | 0 | 0
2022-07-09 12:00 | 4.2862 | 0 | N/A | 0 | 0
2022-07-09 12:30 | 4.0579 | 0 | N/A | 0 | 0
2022-07-09 13:00 | 3.6768 | 0 | N/A | 0 | 0
2022-07-09 13:30 | 4.3773 | 0 | N/A | 0 | 0
2022-07-09 14:00 | 4.3663 | 0 | N/A | 0 | 0
2022-07-09 14:30 | 4.0143 | 0 | N/A | 0 | 0
2022-07-09 15:00 | 4.3631 | 0 | N/A | 0 | 0
2022-07-09 15:30 | 4.6567 | 0 | N/A | 0 | 0
2022-07-09 16:00 | 5.267 | 0 | N/A | 0 | 0
2022-07-09 16:30 | 5.5456 | 0 | N/A | 0 | 0
2022-07-09 17:00 | 6.9429 | 0 | N/A | 0 | 0
2022-07-09 17:30 | 7.6087 | 0 | N/A | 0 | 0
2022-07-09 18:00 | 8.2776 | 0 | N/A | 0 | 0
2022-07-09 18:30 | 8.6555 | 0 | N/A | 0 | 0
2022-07-09 19:00 | 8.4228 | 0 | N/A | 0 | 0
2022-07-09 19:30 | 8.059 | 0 | N/A | 0 | 0
2022-07-09 20:00 | 7.6904 | 0 | N/A | 0 | 0
2022-07-09 20:30 | 7.379 | 0 | N/A | 0 | 0
2022-07-09 21:00 | 7.1968 | 0 | N/A | 0 | 0
2022-07-09 21:30 | 7.4545 | 0 | N/A | 0 | 0
2022-07-09 22:00 | 7.49 | 0 | N/A | 0 | 0
2022-07-09 22:30 | 7.1855 | 0 | N/A | 0 | 0
2022-07-09 23:00 | 7.1102 | 0 | N/A | 0 | 0
2022-07-09 23:30 | 7.1767 | 0 | N/A | 0 | 0
2022-07-10 | 7.3942 | 0 | N/A | 0 | 0
2022-07-10 00:30 | 6.7449 | 0 | N/A | 0 | 0
2022-07-10 01:00 | 6.1189 | 0 | N/A | 0 | 0
2022-07-10 01:30 | 5.88 | 0 | N/A | 0 | 0
2022-07-10 02:00 | 5.5841 | 0 | N/A | 0 | 0
2022-07-10 02:30 | 4.9882 | 0 | N/A | 0 | 0
2022-07-10 03:00 | 4.6427 | 0 | N/A | 0 | 0
2022-07-10 03:30 | 4.4864 | 0 | N/A | 0 | 0
2022-07-10 04:00 | 4.3639 | 0 | N/A | 0 | 0
2022-07-10 04:30 | 4.1803 | 0 | N/A | 0 | 0
2022-07-10 05:00 | 4.0836 | 0 | N/A | 0 | 0
2022-07-10 05:30 | 4.1659 | 0 | N/A | 0 | 0
2022-07-10 06:00 | 4.325 | 0 | N/A | 0 | 0
2022-07-10 06:30 | 4.5845 | 0 | N/A | 0 | 0
2022-07-10 07:00 | 4.7361 | 0 | N/A | 0 | 0
2022-07-10 07:30 | 4.7602 | 0 | N/A | 0 | 0
2022-07-10 08:00 | 5.3668 | 0 | N/A | 0 | 0
2022-07-10 08:30 | 5.7949 | 0 | N/A | 0 | 0
2022-07-10 09:00 | 5.5501 | 0 | N/A | 0 | 0
2022-07-10 09:30 | 5.1407 | 0 | N/A | 0 | 0
2022-07-10 10:00 | 4.5441 | 0 | N/A | 0 | 0
2022-07-10 10:30 | 3.9227 | 0 | N/A | 0 | 0
2022-07-10 11:00 | 3.0769 | 0 | N/A | 0 | 0
2022-07-10 11:30 | 2.3958 | 0 | N/A | 0 | 0
2022-07-10 12:00 | 2.0011 | 0 | N/A | 0 | 0
2022-07-10 12:30 | 1.793 | 0 | N/A | 0 | 0
2022-07-10 13:00 | 1.462 | 0 | N/A | 0 | 0
2022-07-10 13:30 | 1.4637 | 0 | N/A | 0 | 0
2022-07-10 14:00 | 1.6244 | 0 | N/A | 0 | 0
2022-07-10 14:30 | 1.8747 | 0 | N/A | 0 | 0
2022-07-10 15:00 | 2.3859 | 0 | N/A | 0 | 0
2022-07-10 15:30 | 3.0205 | 0 | N/A | 0 | 0
2022-07-10 16:00 | 3.7812 | 0 | N/A | 0 | 0
2022-07-10 16:30 | 4.8278 | 0 | N/A | 0 | 0
2022-07-10 17:00 | 6.0103 | 0 | N/A | 0 | 0
2022-07-10 17:30 | 7.3536 | 0 | N/A | 0 | 0
2022-07-10 18:00 | 8.4342 | 0 | N/A | 0 | 0
2022-07-10 18:30 | 8.8486 | 0 | N/A | 0 | 0
2022-07-10 19:00 | 8.8294 | 0 | N/A | 0 | 0
2022-07-10 19:30 | 8.3608 | 0 | N/A | 0 | 0
2022-07-10 20:00 | 7.9455 | 0 | N/A | 0 | 0
2022-07-10 20:30 | 7.5374 | 0 | N/A | 0 | 0
2022-07-10 21:00 | 7.0897 | 0 | N/A | 0 | 0
2022-07-10 21:30 | 7.1316 | 0 | N/A | 0 | 0
2022-07-10 22:00 | 7.1275 | 0 | N/A | 0 | 0
2022-07-10 22:30 | 6.8518 | 0 | N/A | 0 | 0
2022-07-10 23:00 | 6.7351 | 0 | N/A | 0 | 0
2022-07-10 23:30 | 6.6972 | 0 | N/A | 0 | 0
2022-07-11 | 6.9836 | 0 | N/A | 0 | 0
2022-07-11 00:30 | 6.4533 | 0 | N/A | 0 | 0
2022-07-11 01:00 | 5.6698 | 0 | N/A | 0 | 0
2022-07-11 01:30 | 5.571 | 0 | N/A | 0 | 0
2022-07-11 02:00 | 5.2766 | 0 | N/A | 0 | 0
2022-07-11 02:30 | 4.816 | 0 | N/A | 0 | 0
2022-07-11 03:00 | 4.4722 | 0 | N/A | 0 | 0
2022-07-11 03:30 | 4.282 | 0 | N/A | 0 | 0
2022-07-11 04:00 | 4.0895 | 0 | N/A | 0 | 0
2022-07-11 04:30 | 3.9971 | 0 | N/A | 0 | 0
2022-07-11 05:00 | 4.0973 | 0 | N/A | 0 | 0
2022-07-11 05:30 | 4.4121 | 0 | N/A | 0 | 0
2022-07-11 06:00 | 4.9447 | 0 | N/A | 0 | 0
2022-07-11 06:30 | 5.8231 | 0 | N/A | 0 | 0
2022-07-11 07:00 | 6.5626 | 0 | N/A | 0 | 0
2022-07-11 07:30 | 6.9993 | 0 | N/A | 0 | 0
2022-07-11 08:00 | 8.0322 | 0 | N/A | 0 | 0
2022-07-11 08:30 | 8.4471 | 0 | N/A | 0 | 0
2022-07-11 09:00 | 8.187 | 0 | N/A | 0 | 0
2022-07-11 09:30 | 7.9203 | 0 | N/A | 0 | 0
2022-07-11 10:00 | 7.6734 | 0 | N/A | 0 | 0
2022-07-11 10:30 | 7.7143 | 0 | N/A | 0 | 0
2022-07-11 11:00 | 6.8599 | 0 | N/A | 0 | 0
2022-07-11 11:30 | 7.0202 | 0 | N/A | 0 | 0
2022-07-11 12:00 | 6.9555 | 0 | N/A | 0 | 0
2022-07-11 12:30 | 7.1005 | 0 | N/A | 0 | 0
2022-07-11 13:00 | 7.0642 | 0 | N/A | 0 | 0
2022-07-11 13:30 | 6.9803 | 0 | N/A | 0 | 0
2022-07-11 14:00 | 7.1237 | 0 | N/A | 0 | 0
2022-07-11 14:30 | 7.8509 | 0 | N/A | 0 | 0
2022-07-11 15:00 | 7.2667 | 0 | N/A | 0 | 0
2022-07-11 15:30 | 6.6712 | 0 | N/A | 0 | 0
2022-07-11 16:00 | 7.087 | 0 | N/A | 0 | 0
2022-07-11 16:30 | 7.4596 | 0 | N/A | 0 | 0
2022-07-11 17:00 | 8.0562 | 0 | N/A | 0 | 0
2022-07-11 17:30 | 8.972 | 0 | N/A | 0 | 0
2022-07-11 18:00 | 9.6027 | 0 | N/A | 0 | 0
2022-07-11 18:30 | 9.9142 | 0 | N/A | 0 | 0
2022-07-11 19:00 | 9.6219 | 0 | N/A | 0 | 0
2022-07-11 19:30 | 9.2435 | 0 | N/A | 0 | 0
2022-07-11 20:00 | 8.7939 | 0 | N/A | 0 | 0
2022-07-11 20:30 | 8.2834 | 0 | N/A | 0 | 0
2022-07-11 21:00 | 7.9381 | 0 | N/A | 0 | 0
2022-07-11 21:30 | 7.8831 | 0 | N/A | 0 | 0
2022-07-11 22:00 | 7.6419 | 0 | N/A | 0 | 0
2022-07-11 22:30 | 6.8745 | 0 | N/A | 0 | 0
2022-07-11 23:00 | 6.662 | 0 | N/A | 0 | 0
2022-07-11 23:30 | 6.5253 | 0 | N/A | 0 | 0
2022-07-12 | 6.6938 | 0 | N/A | 0 | 0
2022-07-12 00:30 | 6.1529 | 0 | N/A | 0 | 0
2022-07-12 01:00 | 5.5705 | 0 | N/A | 0 | 0
2022-07-12 01:30 | 5.437 | 0 | N/A | 0 | 0
2022-07-12 02:00 | 5.0664 | 0 | N/A | 0 | 0
2022-07-12 02:30 | 4.6067 | 0 | N/A | 0 | 0
2022-07-12 03:00 | 4.2633 | 0 | N/A | 0 | 0
2022-07-12 03:30 | 4.0878 | 0 | N/A | 0 | 0
2022-07-12 04:00 | 3.8855 | 0 | N/A | 0 | 0
2022-07-12 04:30 | 3.8485 | 0 | N/A | 0 | 0
2022-07-12 05:00 | 3.9796 | 0 | N/A | 0 | 0
2022-07-12 05:30 | 4.4377 | 0 | N/A | 0 | 0
2022-07-12 06:00 | 4.9267 | 0 | N/A | 0 | 0
2022-07-12 06:30 | 5.7452 | 0 | N/A | 0 | 0
2022-07-12 07:00 | 6.5619 | 0 | N/A | 0 | 0
2022-07-12 07:30 | 7.1402 | 0 | N/A | 0 | 0
2022-07-12 08:00 | 7.7976 | 0 | N/A | 0 | 0
2022-07-12 08:30 | 7.7392 | 0 | N/A | 0 | 0
2022-07-12 09:00 | 7.9277 | 0 | N/A | 0 | 0
2022-07-12 09:30 | 7.9002 | 0 | N/A | 0 | 0
2022-07-12 10:00 | 7.1577 | 0 | N/A | 0 | 0
2022-07-12 10:30 | 6.5075 | 0 | N/A | 0 | 0
2022-07-12 11:00 | 5.7251 | 0 | N/A | 0 | 0
2022-07-12 11:30 | 5.8423 | 0 | N/A | 0 | 0
2022-07-12 12:00 | 5.6555 | 0 | N/A | 0 | 0
2022-07-12 12:30 | 5.8679 | 0 | N/A | 0 | 0
2022-07-12 13:00 | 5.7941 | 0 | N/A | 0 | 0
2022-07-12 13:30 | 6.0562 | 0 | N/A | 0 | 0
2022-07-12 14:00 | 6.0664 | 0 | N/A | 0 | 0
2022-07-12 14:30 | 5.2654 | 0 | N/A | 0 | 0
2022-07-12 15:00 | 5.9648 | 0 | N/A | 0 | 0
2022-07-12 15:30 | 5.9924 | 0 | N/A | 0 | 0
2022-07-12 16:00 | 6.2938 | 0 | N/A | 0 | 0
2022-07-12 16:30 | 6.8101 | 0 | N/A | 0 | 0
2022-07-12 17:00 | 7.526 | 0 | N/A | 0 | 0
2022-07-12 17:30 | 8.4985 | 0 | N/A | 0 | 0
2022-07-12 18:00 | 9.2479 | 0 | N/A | 0 | 0
2022-07-12 18:30 | 9.658 | 0 | N/A | 0 | 0
2022-07-12 19:00 | 9.2692 | 0 | N/A | 0 | 0
2022-07-12 19:30 | 9.076 | 0 | N/A | 0 | 0
2022-07-12 20:00 | 8.8435 | 0 | N/A | 0 | 0
2022-07-12 20:30 | 8.6023 | 0 | N/A | 0 | 0
2022-07-12 21:00 | 8.0519 | 0 | N/A | 0 | 0
2022-07-12 21:30 | 8.1058 | 0 | N/A | 0 | 0
2022-07-12 22:00 | 8.0519 | 0 | N/A | 0 | 0
2022-07-12 22:30 | 7.4144 | 0 | N/A | 0 | 0
2022-07-12 23:00 | 7.1341 | 0 | N/A | 0 | 0
2022-07-12 23:30 | 6.9348 | 0 | N/A | 0 | 0
2022-07-13 | 7.2026 | 0 | N/A | 0 | 0
2022-07-15 00:30 | 6.2999 | 0 | N/A | 0 | 0
2022-07-15 01:00 | 5.6246 | 0 | N/A | 0 | 0
2022-07-15 01:30 | 5.4634 | 0 | N/A | 0 | 0
2022-07-15 02:00 | 5.159 | 0 | N/A | 0 | 0
2022-07-15 02:30 | 4.6622 | 0 | N/A | 0 | 0
2022-07-15 03:00 | 4.4056 | 0 | N/A | 0 | 0
2022-07-15 03:30 | 4.2368 | 0 | N/A | 0 | 0
2022-07-15 04:00 | 4.0566 | 0 | N/A | 0 | 0
2022-07-15 04:30 | 4.0266 | 0 | N/A | 0 | 0
2022-07-15 05:00 | 4.1508 | 0 | N/A | 0 | 0
2022-07-15 05:30 | 4.4863 | 0 | N/A | 0 | 0
2022-07-15 06:00 | 4.9008 | 0 | N/A | 0 | 0
2022-07-15 06:30 | 5.7712 | 0 | N/A | 0 | 0
2022-07-15 07:00 | 6.548 | 0 | N/A | 0 | 0
2022-07-15 07:30 | 6.7799 | 0 | N/A | 0 | 0
2022-07-15 08:00 | 7.3326 | 0 | N/A | 0 | 0
2022-07-15 08:30 | 7.8318 | 0 | N/A | 0 | 0
2022-07-15 09:00 | 7.5068 | 0 | N/A | 0 | 0
2022-07-15 09:30 | 7.1484 | 0 | N/A | 0 | 0
2022-07-15 10:00 | 6.4661 | 0 | N/A | 0 | 0
2022-07-15 10:30 | 5.0408 | 0 | N/A | 0 | 0
2022-07-15 11:00 | 3.8934 | 0 | N/A | 0 | 0
2022-07-15 11:30 | 3.7303 | 0 | N/A | 0 | 0
2022-07-15 12:00 | 3.3669 | 0 | N/A | 0 | 0
2022-07-15 12:30 | 3.0074 | 0 | N/A | 0 | 0
2022-07-15 13:00 | 2.8119 | 0 | N/A | 0 | 0
2022-07-15 13:30 | 3.3309 | 0 | N/A | 0 | 0
2022-07-15 14:00 | 3.85 | 0 | N/A | 0 | 0
2022-07-15 14:30 | 3.9592 | 0 | N/A | 0 | 0
2022-07-15 15:00 | 4.8722 | 0 | N/A | 0 | 0
2022-07-15 15:30 | 5.3068 | 0 | N/A | 0 | 0
2022-07-15 16:00 | 5.5872 | 0 | N/A | 0 | 0
2022-07-15 16:30 | 5.944 | 0 | N/A | 0 | 0
2022-07-15 17:00 | 6.6661 | 0 | N/A | 0 | 0
2022-07-15 17:30 | 7.5193 | 0 | N/A | 0 | 0
2022-07-15 18:00 | 8.2732 | 0 | N/A | 0 | 0
2022-07-15 18:30 | 8.5844 | 0 | N/A | 0 | 0
2022-07-15 19:00 | 8.476 | 0 | N/A | 0 | 0
2022-07-15 19:30 | 8.1948 | 0 | N/A | 0 | 0
2022-07-15 20:00 | 7.9855 | 0 | N/A | 0 | 0
2022-07-15 20:30 | 7.6799 | 0 | N/A | 0 | 0
2022-07-15 21:00 | 7.445 | 0 | N/A | 0 | 0
2022-07-15 21:30 | 7.604 | 0 | N/A | 0 | 0
2022-07-15 22:00 | 7.5223 | 0 | N/A | 0 | 0
2022-07-15 22:30 | 6.9543 | 0 | N/A | 0 | 0
2022-07-15 23:00 | 6.794 | 0 | N/A | 0 | 0
2022-07-15 23:30 | 6.7775 | 0 | N/A | 0 | 0
2022-07-16 | 6.966 | 0 | N/A | 0 | 0
2022-07-16 00:30 | 6.3513 | 0 | N/A | 0 | 0
2022-07-16 01:00 | 5.6547 | 0 | N/A | 0 | 0
2022-07-16 01:30 | 5.4463 | 0 | N/A | 0 | 0
2022-07-16 02:00 | 5.0567 | 0 | N/A | 0 | 0
2022-07-16 02:30 | 4.6292 | 0 | N/A | 0 | 0
2022-07-16 03:00 | 4.3681 | 0 | N/A | 0 | 0
2022-07-16 03:30 | 4.1562 | 0 | N/A | 0 | 0
2022-07-16 04:00 | 3.9753 | 0 | N/A | 0 | 0
2022-07-16 04:30 | 3.9403 | 0 | N/A | 0 | 0
2022-07-16 05:00 | 3.9753 | 0 | N/A | 0 | 0
2022-07-16 05:30 | 4.2165 | 0 | N/A | 0 | 0
2022-07-16 06:00 | 4.3091 | 0 | N/A | 0 | 0
2022-07-16 06:30 | 4.7833 | 0 | N/A | 0 | 0
2022-07-16 07:00 | 5.1422 | 0 | N/A | 0 | 0
2022-07-16 07:30 | 5.1406 | 0 | N/A | 0 | 0
2022-07-16 08:00 | 5.7696 | 0 | N/A | 0 | 0
2022-07-16 08:30 | 6.6697 | 0 | N/A | 0 | 0
2022-07-16 09:00 | 7.3314 | 0 | N/A | 0 | 0
2022-07-16 09:30 | 7.9154 | 0 | N/A | 0 | 0
2022-07-16 10:00 | 7.7156 | 0 | N/A | 0 | 0
2022-07-16 10:30 | 5.8592 | 0 | N/A | 0 | 0
2022-07-16 11:00 | 3.9779 | 0 | N/A | 0 | 0
2022-07-16 11:30 | 3.3357 | 0 | N/A | 0 | 0
2022-07-16 12:00 | 2.7664 | 0 | N/A | 0 | 0
2022-07-16 12:30 | 2.7129 | 0 | N/A | 0 | 0
2022-07-16 13:00 | 3.0435 | 0 | N/A | 0 | 0
2022-07-16 13:30 | 3.23 | 0 | N/A | 0 | 0
2022-07-16 14:00 | 3.6998 | 0 | N/A | 0 | 0
2022-07-16 14:30 | 4.2512 | 0 | N/A | 0 | 0
2022-07-16 15:00 | 4.8882 | 0 | N/A | 0 | 0
2022-07-16 15:30 | 5.6885 | 0 | N/A | 0 | 0
2022-07-16 16:00 | 6.344 | 0 | N/A | 0 | 0
2022-07-16 16:30 | 6.7463 | 0 | N/A | 0 | 0
2022-07-16 17:00 | 7.3898 | 0 | N/A | 0 | 0
2022-07-16 17:30 | 8.1219 | 0 | N/A | 0 | 0
2022-07-16 18:00 | 8.6567 | 0 | N/A | 0 | 0
2022-07-16 18:30 | 8.7265 | 0 | N/A | 0 | 0
2022-07-16 19:00 | 8.5969 | 0 | N/A | 0 | 0
2022-07-16 19:30 | 8.2142 | 0 | N/A | 0 | 0
2022-07-16 20:00 | 7.8605 | 0 | N/A | 0 | 0
2022-07-16 20:30 | 7.5333 | 0 | N/A | 0 | 0
2022-07-16 21:00 | 7.147 | 0 | N/A | 0 | 0
2022-07-16 21:30 | 7.3573 | 0 | N/A | 0 | 0
2022-07-16 22:00 | 7.4496 | 0 | N/A | 0 | 0
2022-07-16 22:30 | 7.1186 | 0 | N/A | 0 | 0
2022-07-16 23:00 | 6.9093 | 0 | N/A | 0 | 0
2022-07-16 23:30 | 6.8556 | 0 | N/A | 0 | 0
2022-07-17 | 7.0868 | 0 | N/A | 0 | 0
2022-07-17 00:30 | 6.3895 | 0 | N/A | 0 | 0
2022-07-17 01:00 | 5.7386 | 0 | N/A | 0 | 0
2022-07-17 01:30 | 5.4374 | 0 | N/A | 0 | 0
2022-07-17 02:00 | 5.0739 | 0 | N/A | 0 | 0
2022-07-17 02:30 | 4.5873 | 0 | N/A | 0 | 0
2022-07-17 03:00 | 4.3027 | 0 | N/A | 0 | 0
2022-07-17 03:30 | 4.0751 | 0 | N/A | 0 | 0
2022-07-17 04:00 | 3.8992 | 0 | N/A | 0 | 0
2022-07-17 04:30 | 3.8065 | 0 | N/A | 0 | 0
2022-07-17 05:00 | 3.7004 | 0 | N/A | 0 | 0
2022-07-17 05:30 | 3.7526 | 0 | N/A | 0 | 0
2022-07-17 06:00 | 3.8316 | 0 | N/A | 0 | 0
2022-07-17 06:30 | 4.0528 | 0 | N/A | 0 | 0
2022-07-17 07:00 | 4.2276 | 0 | N/A | 0 | 0
2022-07-17 07:30 | 4.3831 | 0 | N/A | 0 | 0
2022-07-17 08:00 | 4.7384 | 0 | N/A | 0 | 0
2022-07-17 08:30 | 5.3337 | 0 | N/A | 0 | 0
2022-07-17 09:00 | 5.62 | 0 | N/A | 0 | 0
2022-07-17 09:30 | 5.532 | 0 | N/A | 0 | 0
2022-07-17 10:00 | 5.501 | 0 | N/A | 0 | 0
2022-07-17 10:30 | 5.6342 | 0 | N/A | 0 | 0
2022-07-17 11:00 | 5.6078 | 0 | N/A | 0 | 0
2022-07-17 11:30 | 4.584 | 0 | N/A | 0 | 0
2022-07-17 12:00 | 4.281 | 0 | N/A | 0 | 0
2022-07-17 12:30 | 4.8674 | 0 | N/A | 0 | 0
2022-07-17 13:00 | 4.256 | 0 | N/A | 0 | 0
2022-07-17 13:30 | 4.8575 | 0 | N/A | 0 | 0
2022-07-17 14:00 | 5.5424 | 0 | N/A | 0 | 0
2022-07-17 14:30 | 6.4999 | 0 | N/A | 0 | 0
2022-07-17 15:00 | 7.1759 | 0 | N/A | 0 | 0
2022-07-17 15:30 | 6.8887 | 0 | N/A | 0 | 0
2022-07-17 16:00 | 6.043 | 0 | N/A | 0 | 0
2022-07-17 16:30 | 6.9841 | 0 | N/A | 0 | 0
2022-07-17 17:00 | 7.5199 | 0 | N/A | 0 | 0
2022-07-17 17:30 | 8.5049 | 0 | N/A | 0 | 0
2022-07-17 18:00 | 9.3278 | 0 | N/A | 0 | 0
2022-07-17 18:30 | 9.4401 | 0 | N/A | 0 | 0
2022-07-17 19:00 | 9.2147 | 0 | N/A | 0 | 0
2022-07-17 19:30 | 8.8344 | 0 | N/A | 0 | 0
2022-07-17 20:00 | 8.4589 | 0 | N/A | 0 | 0
2022-07-17 20:30 | 8.0145 | 0 | N/A | 0 | 0
2022-07-17 21:00 | 7.6609 | 0 | N/A | 0 | 0
2022-07-17 21:30 | 7.7882 | 0 | N/A | 0 | 0
2022-07-17 22:00 | 7.6868 | 0 | N/A | 0 | 0
2022-07-17 22:30 | 7.0882 | 0 | N/A | 0 | 0
2022-07-17 23:00 | 6.8651 | 0 | N/A | 0 | 0
2022-07-17 23:30 | 6.834 | 0 | N/A | 0 | 0
2022-07-18 | 7.1717 | 0 | N/A | 0 | 0
2022-07-18 00:30 | 6.6066 | 0 | N/A | 0 | 0
2022-07-18 01:00 | 5.8794 | 0 | N/A | 0 | 0
2022-07-18 01:30 | 5.7823 | 0 | N/A | 0 | 0
2022-07-18 02:00 | 5.4953 | 0 | N/A | 0 | 0
2022-07-18 02:30 | 5.0013 | 0 | N/A | 0 | 0
2022-07-18 03:00 | 4.604 | 0 | N/A | 0 | 0
2022-07-18 03:30 | 4.4217 | 0 | N/A | 0 | 0
2022-07-18 04:00 | 4.2974 | 0 | N/A | 0 | 0
2022-07-18 04:30 | 4.2008 | 0 | N/A | 0 | 0
2022-07-18 05:00 | 4.2866 | 0 | N/A | 0 | 0
2022-07-18 05:30 | 4.6731 | 0 | N/A | 0 | 0
2022-07-18 06:00 | 5.1629 | 0 | N/A | 0 | 0
2022-07-18 06:30 | 6.0954 | 0 | N/A | 0 | 0
2022-07-18 07:00 | 6.7791 | 0 | N/A | 0 | 0
2022-07-18 07:30 | 7.326 | 0 | N/A | 0 | 0
2022-07-18 08:00 | 8.2658 | 0 | N/A | 0 | 0
2022-07-18 08:30 | 8.6218 | 0 | N/A | 0 | 0
2022-07-18 09:00 | 8.4019 | 0 | N/A | 0 | 0
2022-07-18 09:30 | 8.2258 | 0 | N/A | 0 | 0
2022-07-18 10:00 | 7.6247 | 0 | N/A | 0 | 0
2022-07-18 10:30 | 6.8917 | 0 | N/A | 0 | 0
2022-07-18 11:00 | 5.8264 | 0 | N/A | 0 | 0
2022-07-18 11:30 | 6.0239 | 0 | N/A | 0 | 0
2022-07-18 12:00 | 5.3127 | 0 | N/A | 0 | 0
2022-07-18 12:30 | 5.0725 | 0 | N/A | 0 | 0
2022-07-18 13:00 | 4.9275 | 0 | N/A | 0 | 0
2022-07-18 13:30 | 3.6781 | 0 | N/A | 0 | 0
2022-07-18 14:00 | 5.0618 | 0 | N/A | 0 | 0
2022-07-18 14:30 | 5.2824 | 0 | N/A | 0 | 0
2022-07-18 15:00 | 5.8552 | 0 | N/A | 0 | 0
2022-07-18 15:30 | 5.0682 | 0 | N/A | 0 | 0
2022-07-18 16:00 | 5.0473 | 0 | N/A | 0 | 0
2022-07-18 16:30 | 6.542 | 0 | N/A | 0 | 0
2022-07-18 17:00 | 7.4639 | 0 | N/A | 0 | 0
2022-07-18 17:30 | 8.4967 | 0 | N/A | 0 | 0
2022-07-18 18:00 | 9.5724 | 0 | N/A | 0 | 0
2022-07-18 18:30 | 10.2016 | 0 | N/A | 0 | 0
2022-07-18 19:00 | 10.0848 | 0 | N/A | 0 | 0
2022-07-18 19:30 | 9.5509 | 0 | N/A | 0 | 0
2022-07-18 20:00 | 9.2554 | 0 | N/A | 0 | 0
2022-07-18 20:30 | 8.8152 | 0 | N/A | 0 | 0
2022-07-18 21:00 | 8.2846 | 0 | N/A | 0 | 0
2022-07-18 21:30 | 8.3068 | 0 | N/A | 0 | 0
2022-07-18 22:00 | 8.2615 | 0 | N/A | 0 | 0
2022-07-18 22:30 | 7.4513 | 0 | N/A | 0 | 0
2022-07-18 23:00 | 7.0168 | 0 | N/A | 0 | 0
2022-07-18 23:30 | 6.7773 | 0 | N/A | 0 | 0
2022-07-19 | 7.1965 | 0 | N/A | 0 | 0
2022-07-19 00:30 | 6.6397 | 0 | N/A | 0 | 0
2022-07-19 01:00 | 6.0309 | 0 | N/A | 0 | 0
2022-07-19 01:30 | 5.9417 | 0 | N/A | 0 | 0
2022-07-19 02:00 | 5.6194 | 0 | N/A | 0 | 0
2022-07-19 02:30 | 5.1532 | 0 | N/A | 0 | 0
2022-07-19 03:00 | 4.7982 | 0 | N/A | 0 | 0
2022-07-19 03:30 | 4.5414 | 0 | N/A | 0 | 0
2022-07-19 04:00 | 4.4216 | 0 | N/A | 0 | 0
2022-07-19 04:30 | 4.3285 | 0 | N/A | 0 | 0
2022-07-19 05:00 | 4.4816 | 0 | N/A | 0 | 0
2022-07-19 05:30 | 4.7945 | 0 | N/A | 0 | 0
2022-07-19 06:00 | 5.3408 | 0 | N/A | 0 | 0
2022-07-19 06:30 | 6.1738 | 0 | N/A | 0 | 0
2022-07-19 07:00 | 6.9503 | 0 | N/A | 0 | 0
2022-07-19 07:30 | 7.4759 | 0 | N/A | 0 | 0
2022-07-19 08:00 | 8.3337 | 0 | N/A | 0 | 0
2022-07-19 08:30 | 8.0314 | 0 | N/A | 0 | 0
2022-07-19 09:00 | 7.1703 | 0 | N/A | 0 | 0
2022-07-19 09:30 | 6.2537 | 0 | N/A | 0 | 0
2022-07-19 10:00 | 5.2489 | 0 | N/A | 0 | 0
2022-07-19 10:30 | 4.7215 | 0 | N/A | 0 | 0
2022-07-19 11:00 | 3.9302 | 0 | N/A | 0 | 0
2022-07-19 11:30 | 3.2065 | 0 | N/A | 0 | 0
2022-07-19 12:00 | 2.7201 | 0 | N/A | 0 | 0
2022-07-19 12:30 | 2.5054 | 0 | N/A | 0 | 0
2022-07-19 13:00 | 2.1561 | 0 | N/A | 0 | 0
2022-07-19 13:30 | 2.2459 | 0 | N/A | 0 | 0
2022-07-19 14:00 | 2.2643 | 0 | N/A | 0 | 0
2022-07-19 14:30 | 2.4858 | 0 | N/A | 0 | 0
2022-07-19 15:00 | 3.034 | 0 | N/A | 0 | 0
2022-07-19 15:30 | 3.6721 | 0 | N/A | 0 | 0
2022-07-19 16:00 | 4.3723 | 0 | N/A | 0 | 0
2022-07-19 16:30 | 5.3194 | 0 | N/A | 0 | 0
2022-07-19 17:00 | 6.5983 | 0 | N/A | 0 | 0
2022-07-19 17:30 | 8.128 | 0 | N/A | 0 | 0
2022-07-19 18:00 | 9.3842 | 0 | N/A | 0 | 0
2022-07-19 18:30 | 10.0787 | 0 | N/A | 0 | 0
2022-07-19 19:00 | 10.0686 | 0 | N/A | 0 | 0
2022-07-19 19:30 | 9.7388 | 0 | N/A | 0 | 0
2022-07-19 20:00 | 9.5126 | 0 | N/A | 0 | 0
2022-07-19 20:30 | 9.2082 | 0 | N/A | 0 | 0
2022-07-19 21:00 | 8.7531 | 0 | N/A | 0 | 0
2022-07-19 21:30 | 8.7868 | 0 | N/A | 0 | 0
2022-07-19 22:00 | 8.6996 | 0 | N/A | 0 | 0
2022-07-19 22:30 | 7.8845 | 0 | N/A | 0 | 0
2022-07-19 23:00 | 7.4641 | 0 | N/A | 0 | 0
2022-07-19 23:30 | 7.4122 | 0 | N/A | 0 | 0
2022-07-20 | 7.5517 | 0 | N/A | 0 | 0
2022-07-20 00:30 | 6.9636 | 0 | N/A | 0 | 0
2022-07-20 01:00 | 6.3498 | 0 | N/A | 0 | 0
2022-07-20 01:30 | 6.3311 | 0 | N/A | 0 | 0
2022-07-20 02:00 | 6.0034 | 0 | N/A | 0 | 0
2022-07-20 02:30 | 5.6603 | 0 | N/A | 0 | 0
2022-07-20 03:00 | 5.4253 | 0 | N/A | 0 | 0
2022-07-20 03:30 | 5.1901 | 0 | N/A | 0 | 0
2022-07-20 04:00 | 5.0688 | 0 | N/A | 0 | 0
2022-07-20 04:30 | 5.0416 | 0 | N/A | 0 | 0
2022-07-20 05:00 | 5.2932 | 0 | N/A | 0 | 0
2022-07-20 05:30 | 5.6837 | 0 | N/A | 0 | 0
2022-07-20 06:00 | 6.2522 | 0 | N/A | 0 | 0
2022-07-20 06:30 | 7.2708 | 0 | N/A | 0 | 0
2022-07-20 07:00 | 8.2778 | 0 | N/A | 0 | 0
2022-07-20 07:30 | 8.8277 | 0 | N/A | 0 | 0
2022-07-20 08:00 | 9.5773 | 0 | N/A | 0 | 0
2022-07-20 08:30 | 9.4434 | 0 | N/A | 0 | 0
2022-07-20 09:00 | 8.5972 | 0 | N/A | 0 | 0
2022-07-20 09:30 | 7.8218 | 0 | N/A | 0 | 0
2022-07-20 10:00 | 6.5903 | 0 | N/A | 0 | 0
2022-07-20 10:30 | 5.5746 | 0 | N/A | 0 | 0
2022-07-20 11:00 | 4.4076 | 0 | N/A | 0 | 0
2022-07-20 11:30 | 3.5313 | 0 | N/A | 0 | 0
2022-07-20 12:00 | 3.1907 | 0 | N/A | 0 | 0
2022-07-20 12:30 | 2.7554 | 0 | N/A | 0 | 0
2022-07-20 13:00 | 2.3169 | 0 | N/A | 0 | 0
2022-07-20 13:30 | 2.4291 | 0 | N/A | 0 | 0
2022-07-20 14:00 | 2.5668 | 0 | N/A | 0 | 0
2022-07-20 14:30 | 2.651 | 0 | N/A | 0 | 0
2022-07-20 15:00 | 3.153 | 0 | N/A | 0 | 0
2022-07-20 15:30 | 3.6535 | 0 | N/A | 0 | 0
2022-07-20 16:00 | 4.3126 | 0 | N/A | 0 | 0
2022-07-20 16:30 | 5.051 | 0 | N/A | 0 | 0
2022-07-20 17:00 | 6.201 | 0 | N/A | 0 | 0
2022-07-20 17:30 | 7.6124 | 0 | N/A | 0 | 0
2022-07-20 18:00 | 8.9325 | 0 | N/A | 0 | 0
2022-07-20 18:30 | 9.6383 | 0 | N/A | 0 | 0
2022-07-20 19:00 | 9.5654 | 0 | N/A | 0 | 0
2022-07-20 19:30 | 9.4214 | 0 | N/A | 0 | 0
2022-07-20 20:00 | 9.1651 | 0 | N/A | 0 | 0
2022-07-20 20:30 | 9.0377 | 0 | N/A | 0 | 0
2022-07-20 21:00 | 8.6393 | 0 | N/A | 0 | 0
2022-07-20 21:30 | 8.575 | 0 | N/A | 0 | 0
2022-07-20 22:00 | 8.4216 | 0 | N/A | 0 | 0
2022-07-20 22:30 | 7.7309 | 0 | N/A | 0 | 0
2022-07-20 23:00 | 7.4423 | 0 | N/A | 0 | 0
2022-07-20 23:30 | 7.3239 | 0 | N/A | 0 | 0
2022-07-21 | 7.6068 | 0 | N/A | 0 | 0
2022-07-23 00:30 | 5.8546 | 0 | N/A | 0 | 0
2022-07-23 01:00 | 5.0489 | 0 | N/A | 0 | 0
2022-07-23 01:30 | 4.9238 | 0 | N/A | 0 | 0
2022-07-23 02:00 | 4.5967 | 0 | N/A | 0 | 0
2022-07-23 02:30 | 4.1551 | 0 | N/A | 0 | 0
2022-07-23 03:00 | 3.8127 | 0 | N/A | 0 | 0
2022-07-23 03:30 | 3.6656 | 0 | N/A | 0 | 0
2022-07-23 04:00 | 3.5274 | 0 | N/A | 0 | 0
2022-07-23 04:30 | 3.3941 | 0 | N/A | 0 | 0
2022-07-23 05:00 | 3.4138 | 0 | N/A | 0 | 0
2022-07-23 05:30 | 3.5943 | 0 | N/A | 0 | 0
2022-07-23 06:00 | 3.8137 | 0 | N/A | 0 | 0
2022-07-23 06:30 | 4.1753 | 0 | N/A | 0 | 0
2022-07-23 07:00 | 4.38 | 0 | N/A | 0 | 0
2022-07-23 07:30 | 4.5495 | 0 | N/A | 0 | 0
2022-07-23 08:00 | 5.1337 | 0 | N/A | 0 | 0
2022-07-23 08:30 | 5.7309 | 0 | N/A | 0 | 0
2022-07-23 09:00 | 6.0189 | 0 | N/A | 0 | 0
2022-07-23 10:00 | 6.3544 | 0 | N/A | 0 | 0
2022-07-23 10:30 | 6.0573 | 0 | N/A | 0 | 0
2022-07-23 11:00 | 5.7601 | 0 | N/A | 0 | 0
2022-07-23 11:30 | 5.5861 | 0 | N/A | 0 | 0
2022-07-23 12:00 | 5.5857 | 0 | N/A | 0 | 0
2022-07-23 12:30 | 5.1875 | 0 | N/A | 0 | 0
2022-07-23 13:00 | 5.2076 | 0 | N/A | 0 | 0
2022-07-23 13:30 | 5.1921 | 0 | N/A | 0 | 0
2022-07-23 14:00 | 4.6366 | 0 | N/A | 0 | 0
2022-07-23 14:30 | 5.4942 | 0 | N/A | 0 | 0
2022-07-23 15:00 | 5.8807 | 0 | N/A | 0 | 0
2022-07-23 15:30 | 5.665 | 0 | N/A | 0 | 0
2022-07-23 16:00 | 6.2673 | 0 | N/A | 0 | 0
2022-07-23 16:30 | 6.7262 | 0 | N/A | 0 | 0
2022-07-23 17:00 | 6.987 | 0 | N/A | 0 | 0
2022-07-23 17:30 | 7.6036 | 0 | N/A | 0 | 0
2022-07-23 18:00 | 8.0153 | 0 | N/A | 0 | 0
2022-07-23 18:30 | 8.1507 | 0 | N/A | 0 | 0
2022-07-23 19:00 | 7.9657 | 0 | N/A | 0 | 0
2022-07-23 19:30 | 7.6012 | 0 | N/A | 0 | 0
2022-07-23 20:00 | 7.2654 | 0 | N/A | 0 | 0
2022-07-23 20:30 | 6.8747 | 0 | N/A | 0 | 0
2022-07-23 21:00 | 6.4421 | 0 | N/A | 0 | 0
2022-07-23 21:30 | 6.7188 | 0 | N/A | 0 | 0
2022-07-23 22:00 | 6.8051 | 0 | N/A | 0 | 0
2022-07-23 22:30 | 6.4922 | 0 | N/A | 0 | 0
2022-07-23 23:00 | 6.3711 | 0 | N/A | 0 | 0
2022-07-23 23:30 | 6.3672 | 0 | N/A | 0 | 0
2022-07-24 | 6.6728 | 0 | N/A | 0 | 0
2022-07-24 00:30 | 6.0324 | 0 | N/A | 0 | 0
2022-07-24 01:00 | 5.2427 | 0 | N/A | 0 | 0
2022-07-24 01:30 | 5.0788 | 0 | N/A | 0 | 0
2022-07-24 02:00 | 4.7198 | 0 | N/A | 0 | 0
2022-07-24 02:30 | 4.2487 | 0 | N/A | 0 | 0
2022-07-24 03:00 | 3.9468 | 0 | N/A | 0 | 0
2022-07-24 03:30 | 3.7823 | 0 | N/A | 0 | 0
2022-07-24 04:00 | 3.649 | 0 | N/A | 0 | 0
2022-07-24 04:30 | 3.4943 | 0 | N/A | 0 | 0
2022-07-24 05:00 | 3.4565 | 0 | N/A | 0 | 0
2022-07-24 05:30 | 3.4691 | 0 | N/A | 0 | 0
2022-07-24 06:00 | 3.6062 | 0 | N/A | 0 | 0
2022-07-24 06:30 | 3.8254 | 0 | N/A | 0 | 0
2022-07-24 07:00 | 4.1659 | 0 | N/A | 0 | 0
2022-07-24 07:30 | 4.2151 | 0 | N/A | 0 | 0
2022-07-24 08:00 | 4.6665 | 0 | N/A | 0 | 0
2022-07-24 08:30 | 5.0846 | 0 | N/A | 0 | 0
2022-07-24 09:00 | 5.27 | 0 | N/A | 0 | 0
2022-07-24 09:30 | 5.2466 | 0 | N/A | 0 | 0
2022-07-24 10:00 | 4.9759 | 0 | N/A | 0 | 0
2022-07-24 10:30 | 4.4149 | 0 | N/A | 0 | 0
2022-07-24 11:00 | 4.6907 | 0 | N/A | 0 | 0
2022-07-24 11:30 | 4.5192 | 0 | N/A | 0 | 0
2022-07-24 12:00 | 4.6839 | 0 | N/A | 0 | 0
2022-07-24 12:30 | 4.5796 | 0 | N/A | 0 | 0
2022-07-24 13:00 | 4.3061 | 0 | N/A | 0 | 0
2022-07-24 13:30 | 4.0986 | 0 | N/A | 0 | 0
2022-07-24 14:00 | 3.8366 | 0 | N/A | 0 | 0
2022-07-24 14:30 | 3.4861 | 0 | N/A | 0 | 0
2022-07-24 15:00 | 3.2066 | 0 | N/A | 0 | 0
2022-07-24 15:30 | 3.6541 | 0 | N/A | 0 | 0
2022-07-24 16:00 | 3.8659 | 0 | N/A | 0 | 0
2022-07-24 16:30 | 4.4915 | 0 | N/A | 0 | 0
2022-07-24 17:00 | 5.7676 | 0 | N/A | 0 | 0
2022-07-24 17:30 | 6.7106 | 0 | N/A | 0 | 0
2022-07-24 18:00 | 7.5925 | 0 | N/A | 0 | 0
2022-07-24 18:30 | 8.1698 | 0 | N/A | 0 | 0
2022-07-24 19:00 | 8.0161 | 0 | N/A | 0 | 0
2022-07-24 19:30 | 7.7266 | 0 | N/A | 0 | 0
2022-07-24 20:00 | 7.4104 | 0 | N/A | 0 | 0
2022-07-24 20:30 | 6.9944 | 0 | N/A | 0 | 0
2022-07-24 21:00 | 6.5503 | 0 | N/A | 0 | 0
2022-07-24 21:30 | 6.7574 | 0 | N/A | 0 | 0
2022-07-24 22:00 | 6.6835 | 0 | N/A | 0 | 0
2022-07-24 22:30 | 6.0841 | 0 | N/A | 0 | 0
2022-07-24 23:00 | 6.0888 | 0 | N/A | 0 | 0
2022-07-24 23:30 | 6.1272 | 0 | N/A | 0 | 0
2022-07-25 | 6.3629 | 0 | N/A | 0 | 0
2022-07-27 00:30 | 6.3959 | 0 | N/A | 0 | 0
2022-07-27 01:00 | 5.6627 | 0 | N/A | 0 | 0
2022-07-27 01:30 | 5.507 | 0 | N/A | 0 | 0
2022-07-27 02:00 | 5.1131 | 0 | N/A | 0 | 0
2022-07-27 02:30 | 4.6965 | 0 | N/A | 0 | 0
2022-07-27 03:00 | 4.3736 | 0 | N/A | 0 | 0
2022-07-27 03:30 | 4.1396 | 0 | N/A | 0 | 0
2022-07-27 04:00 | 4.0266 | 0 | N/A | 0 | 0
2022-07-27 04:30 | 3.9182 | 0 | N/A | 0 | 0
2022-07-27 05:00 | 4.0856 | 0 | N/A | 0 | 0
2022-07-27 05:30 | 4.4588 | 0 | N/A | 0 | 0
2022-07-27 06:00 | 4.8241 | 0 | N/A | 0 | 0
2022-07-27 06:30 | 5.5187 | 0 | N/A | 0 | 0
2022-07-27 07:00 | 6.1242 | 0 | N/A | 0 | 0
2022-07-27 07:30 | 6.7208 | 0 | N/A | 0 | 0
2022-07-27 08:00 | 7.5916 | 0 | N/A | 0 | 0
2022-07-27 08:30 | 7.651 | 0 | N/A | 0 | 0
2022-07-27 09:00 | 7.3052 | 0 | N/A | 0 | 0
2022-07-27 09:30 | 7.0423 | 0 | N/A | 0 | 0
2022-07-27 10:00 | 6.9378 | 0 | N/A | 0 | 0
2022-07-27 10:30 | 6.8468 | 0 | N/A | 0 | 0
2022-07-27 11:00 | 6.3686 | 0 | N/A | 0 | 0
2022-07-27 11:30 | 5.9419 | 0 | N/A | 0 | 0
2022-07-27 12:00 | 5.6359 | 0 | N/A | 0 | 0
2022-07-27 12:30 | 4.8797 | 0 | N/A | 0 | 0
2022-07-27 13:00 | 4.353 | 0 | N/A | 0 | 0
2022-07-27 13:30 | 3.9881 | 0 | N/A | 0 | 0
2022-07-27 14:00 | 4.9411 | 0 | N/A | 0 | 0
2022-07-27 14:30 | 5.3311 | 0 | N/A | 0 | 0
2022-07-27 15:00 | 5.0156 | 0 | N/A | 0 | 0
2022-07-27 15:30 | 4.6458 | 0 | N/A | 0 | 0
2022-07-27 16:00 | 6.0472 | 0 | N/A | 0 | 0
2022-07-27 16:30 | 6.315 | 0 | N/A | 0 | 0
2022-07-27 17:00 | 6.6917 | 0 | N/A | 0 | 0
2022-07-27 17:30 | 7.4035 | 0 | N/A | 0 | 0
2022-07-27 18:00 | 8.5347 | 0 | N/A | 0 | 0
2022-07-27 18:30 | 8.8706 | 0 | N/A | 0 | 0
2022-07-27 19:00 | 8.7902 | 0 | N/A | 0 | 0
2022-07-27 19:30 | 8.5507 | 0 | N/A | 0 | 0
2022-07-27 20:00 | 8.2532 | 0 | N/A | 0 | 0
2022-07-27 20:30 | 7.7768 | 0 | N/A | 0 | 0
2022-07-27 21:00 | 7.4424 | 0 | N/A | 0 | 0
2022-07-27 21:30 | 7.4804 | 0 | N/A | 0 | 0
2022-07-27 22:00 | 7.3958 | 0 | N/A | 0 | 0
2022-07-27 22:30 | 6.7229 | 0 | N/A | 0 | 0
2022-07-27 23:00 | 6.373 | 0 | N/A | 0 | 0
2022-07-27 23:30 | 6.4667 | 0 | N/A | 0 | 0
2022-07-28 | 6.7078 | 0 | N/A | 0 | 0
2022-07-28 00:30 | 6.063 | 0 | N/A | 0 | 0
2022-07-28 01:00 | 5.3972 | 0 | N/A | 0 | 0
2022-07-28 01:30 | 5.205 | 0 | N/A | 0 | 0
2022-07-28 02:00 | 4.9509 | 0 | N/A | 0 | 0
2022-07-28 02:30 | 4.4194 | 0 | N/A | 0 | 0
2022-07-28 03:00 | 4.1168 | 0 | N/A | 0 | 0
2022-07-28 03:30 | 3.9724 | 0 | N/A | 0 | 0
2022-07-28 04:00 | 3.8422 | 0 | N/A | 0 | 0
2022-07-28 04:30 | 3.8148 | 0 | N/A | 0 | 0
2022-07-28 05:00 | 3.9554 | 0 | N/A | 0 | 0
2022-07-28 05:30 | 4.352 | 0 | N/A | 0 | 0
2022-07-28 06:00 | 4.8507 | 0 | N/A | 0 | 0
2022-07-28 06:30 | 5.6758 | 0 | N/A | 0 | 0
2022-07-28 07:00 | 6.4179 | 0 | N/A | 0 | 0
2022-07-28 07:30 | 6.7738 | 0 | N/A | 0 | 0
2022-07-28 08:00 | 7.269 | 0 | N/A | 0 | 0
2022-07-28 08:30 | 7.0459 | 0 | N/A | 0 | 0
2022-07-28 09:00 | 6.1534 | 0 | N/A | 0 | 0
2022-07-28 09:30 | 5.7755 | 0 | N/A | 0 | 0
2022-07-28 10:00 | 4.7921 | 0 | N/A | 0 | 0
2022-07-28 10:30 | 4.3959 | 0 | N/A | 0 | 0
2022-07-28 11:00 | 3.9297 | 0 | N/A | 0 | 0
2022-07-28 11:30 | 4.4441 | 0 | N/A | 0 | 0
2022-07-28 12:00 | 4.0648 | 0 | N/A | 0 | 0
2022-07-28 12:30 | 3.9848 | 0 | N/A | 0 | 0
2022-07-28 13:00 | 4.2954 | 0 | N/A | 0 | 0
2022-07-28 13:30 | 6.2747 | 0 | N/A | 0 | 0
2022-07-28 14:00 | 5.9994 | 0 | N/A | 0 | 0
2022-07-28 14:30 | 5.8484 | 0 | N/A | 0 | 0
2022-07-28 15:00 | 5.4958 | 0 | N/A | 0 | 0
2022-07-28 15:30 | 5.2735 | 0 | N/A | 0 | 0
2022-07-28 16:00 | 6.2847 | 0 | N/A | 0 | 0
2022-07-28 16:30 | 6.5763 | 0 | N/A | 0 | 0
2022-07-28 17:00 | 7.2011 | 0 | N/A | 0 | 0
2022-07-28 17:30 | 7.9292 | 0 | N/A | 0 | 0
2022-07-28 18:00 | 9.0504 | 0 | N/A | 0 | 0
2022-07-28 18:30 | 9.4769 | 0 | N/A | 0 | 0
2022-07-28 19:00 | 9.4836 | 0 | N/A | 0 | 0
2022-07-28 19:30 | 9.2376 | 0 | N/A | 0 | 0
2022-07-28 20:00 | 9.0273 | 0 | N/A | 0 | 0
2022-07-28 20:30 | 8.6971 | 0 | N/A | 0 | 0
2022-07-28 21:00 | 8.1704 | 0 | N/A | 0 | 0
2022-07-28 21:30 | 8.2287 | 0 | N/A | 0 | 0
2022-07-28 22:00 | 8.0264 | 0 | N/A | 0 | 0
2022-07-28 22:30 | 7.223 | 0 | N/A | 0 | 0
2022-07-28 23:00 | 6.8992 | 0 | N/A | 0 | 0
2022-07-28 23:30 | 7.0046 | 0 | N/A | 0 | 0
2022-07-29 | 7.3239 | 0 | N/A | 0 | 0
2022-07-29 00:30 | 6.7732 | 0 | N/A | 0 | 0
2022-07-29 01:00 | 6.1262 | 0 | N/A | 0 | 0
2022-07-29 01:30 | 5.9503 | 0 | N/A | 0 | 0
2022-07-29 02:00 | 5.5698 | 0 | N/A | 0 | 0
2022-07-29 02:30 | 5.0935 | 0 | N/A | 0 | 0
2022-07-29 03:00 | 4.8176 | 0 | N/A | 0 | 0
2022-07-29 03:30 | 4.6673 | 0 | N/A | 0 | 0
2022-07-29 04:00 | 4.5984 | 0 | N/A | 0 | 0
2022-07-29 04:30 | 4.6298 | 0 | N/A | 0 | 0
2022-07-29 05:00 | 4.8071 | 0 | N/A | 0 | 0
2022-07-29 05:30 | 5.2241 | 0 | N/A | 0 | 0
2022-07-29 06:00 | 5.6639 | 0 | N/A | 0 | 0
2022-07-29 06:30 | 6.4149 | 0 | N/A | 0 | 0
2022-07-29 07:00 | 7.0529 | 0 | N/A | 0 | 0
2022-07-29 07:30 | 7.4392 | 0 | N/A | 0 | 0
2022-07-29 08:00 | 8.2093 | 0 | N/A | 0 | 0
2022-07-29 08:30 | 8.275 | 0 | N/A | 0 | 0
2022-07-29 09:00 | 7.4633 | 0 | N/A | 0 | 0
2022-07-29 09:30 | 7.186 | 0 | N/A | 0 | 0
2022-07-29 10:00 | 6.0338 | 0 | N/A | 0 | 0
2022-07-29 10:30 | 4.6886 | 0 | N/A | 0 | 0
2022-07-29 11:00 | 3.6248 | 0 | N/A | 0 | 0
2022-07-29 11:30 | 2.9674 | 0 | N/A | 0 | 0
2022-07-29 12:00 | 3.241 | 0 | N/A | 0 | 0
2022-07-29 12:30 | 3.6223 | 0 | N/A | 0 | 0
2022-07-29 13:00 | 3.1896 | 0 | N/A | 0 | 0
2022-07-29 13:30 | 3.6897 | 0 | N/A | 0 | 0
2022-07-29 14:00 | 3.2861 | 0 | N/A | 0 | 0
2022-07-29 14:30 | 4.0776 | 0 | N/A | 0 | 0
2022-07-29 15:00 | 3.6667 | 0 | N/A | 0 | 0
2022-07-29 15:30 | 3.9997 | 0 | N/A | 0 | 0
2022-07-29 16:00 | 4.4838 | 0 | N/A | 0 | 0
2022-07-29 16:30 | 4.8621 | 0 | N/A | 0 | 0
2022-07-29 17:00 | 6.0098 | 0 | N/A | 0 | 0
2022-07-29 17:30 | 7.1652 | 0 | N/A | 0 | 0
2022-07-29 18:00 | 8.249 | 0 | N/A | 0 | 0
2022-07-29 18:30 | 8.9279 | 0 | N/A | 0 | 0
2022-07-29 19:00 | 8.9718 | 0 | N/A | 0 | 0
2022-07-29 19:30 | 8.9246 | 0 | N/A | 0 | 0
2022-07-29 20:00 | 8.8912 | 0 | N/A | 0 | 0
2022-07-29 20:30 | 8.6635 | 0 | N/A | 0 | 0
2022-07-29 21:00 | 8.3912 | 0 | N/A | 0 | 0
2022-07-29 21:30 | 8.6935 | 0 | N/A | 0 | 0
2022-07-29 22:00 | 8.7513 | 0 | N/A | 0 | 0
2022-07-29 22:30 | 8.0177 | 0 | N/A | 0 | 0
2022-07-29 23:00 | 7.7383 | 0 | N/A | 0 | 0
2022-07-29 23:30 | 7.7682 | 0 | N/A | 0 | 0
2022-07-30 | 7.8528 | 0 | N/A | 0 | 0
2022-07-30 00:30 | 7.173 | 0 | N/A | 0 | 0
2022-07-30 01:00 | 6.5699 | 0 | N/A | 0 | 0
2022-07-30 01:30 | 6.448 | 0 | N/A | 0 | 0
2022-07-30 02:00 | 6.09 | 0 | N/A | 0 | 0
2022-07-30 02:30 | 5.5455 | 0 | N/A | 0 | 0
2022-07-30 03:00 | 5.2895 | 0 | N/A | 0 | 0
2022-07-30 03:30 | 5.0867 | 0 | N/A | 0 | 0
2022-07-30 04:00 | 4.9557 | 0 | N/A | 0 | 0
2022-07-30 04:30 | 4.8677 | 0 | N/A | 0 | 0
2022-07-30 05:00 | 4.9257 | 0 | N/A | 0 | 0
2022-07-30 05:30 | 5.0776 | 0 | N/A | 0 | 0
2022-07-30 06:00 | 5.2729 | 0 | N/A | 0 | 0
2022-07-30 06:30 | 5.7157 | 0 | N/A | 0 | 0
2022-07-30 07:00 | 6.1178 | 0 | N/A | 0 | 0
2022-07-30 07:30 | 6.2101 | 0 | N/A | 0 | 0
2022-07-30 08:00 | 6.9811 | 0 | N/A | 0 | 0
2022-07-30 08:30 | 7.2568 | 0 | N/A | 0 | 0
2022-07-30 09:00 | 6.9833 | 0 | N/A | 0 | 0
2022-07-30 09:30 | 6.5273 | 0 | N/A | 0 | 0
2022-07-30 10:00 | 5.5351 | 0 | N/A | 0 | 0
2022-07-30 10:30 | 4.5727 | 0 | N/A | 0 | 0
2022-07-30 11:00 | 3.7967 | 0 | N/A | 0 | 0
2022-07-30 11:30 | 3.0718 | 0 | N/A | 0 | 0
2022-07-30 12:00 | 2.6208 | 0 | N/A | 0 | 0
2022-07-30 12:30 | 2.2811 | 0 | N/A | 0 | 0
2022-07-30 13:00 | 1.9929 | 0 | N/A | 0 | 0
2022-07-30 13:30 | 1.9213 | 0 | N/A | 0 | 0
2022-07-30 14:00 | 1.9961 | 0 | N/A | 0 | 0
2022-07-30 14:30 | 2.19 | 0 | N/A | 0 | 0
2022-07-30 15:00 | 2.8178 | 0 | N/A | 0 | 0
2022-07-30 15:30 | 3.5756 | 0 | N/A | 0 | 0
2022-07-30 16:00 | 4.2306 | 0 | N/A | 0 | 0
2022-07-30 16:30 | 5.4681 | 0 | N/A | 0 | 0
2022-07-30 17:00 | 6.8151 | 0 | N/A | 0 | 0
2022-07-30 17:30 | 8.1445 | 0 | N/A | 0 | 0
2022-07-30 18:00 | 8.9405 | 0 | N/A | 0 | 0
2022-07-30 18:30 | 9.2845 | 0 | N/A | 0 | 0
2022-07-30 19:00 | 9.1303 | 0 | N/A | 0 | 0
2022-07-30 19:30 | 8.6594 | 0 | N/A | 0 | 0
2022-07-30 20:00 | 8.3344 | 0 | N/A | 0 | 0
2022-07-30 20:30 | 7.9848 | 0 | N/A | 0 | 0
2022-07-30 21:00 | 7.6519 | 0 | N/A | 0 | 0
2022-07-30 21:30 | 7.7931 | 0 | N/A | 0 | 0
2022-07-30 22:00 | 7.9384 | 0 | N/A | 0 | 0
2022-07-30 22:30 | 7.6053 | 0 | N/A | 0 | 0
2022-07-30 23:00 | 7.2016 | 0 | N/A | 0 | 0
2022-07-30 23:30 | 7.2461 | 0 | N/A | 0 | 0
2022-07-31 | 7.4252 | 0 | N/A | 0 | 0
2022-07-31 00:30 | 6.8543 | 0 | N/A | 0 | 0
2022-07-31 01:00 | 6.1732 | 0 | N/A | 0 | 0
2022-07-31 01:30 | 5.9677 | 0 | N/A | 0 | 0
2022-07-31 02:00 | 5.4904 | 0 | N/A | 0 | 0
2022-07-31 02:30 | 4.9219 | 0 | N/A | 0 | 0
2022-07-31 03:00 | 4.6291 | 0 | N/A | 0 | 0
2022-07-31 03:30 | 4.4281 | 0 | N/A | 0 | 0
2022-07-31 04:00 | 4.2301 | 0 | N/A | 0 | 0
2022-07-31 04:30 | 4.0933 | 0 | N/A | 0 | 0
2022-07-31 05:00 | 4.0404 | 0 | N/A | 0 | 0
2022-07-31 05:30 | 4.1444 | 0 | N/A | 0 | 0
2022-07-31 06:00 | 4.2844 | 0 | N/A | 0 | 0
2022-07-31 06:30 | 4.537 | 0 | N/A | 0 | 0
2022-07-31 07:00 | 4.8668 | 0 | N/A | 0 | 0
2022-07-31 07:30 | 4.9311 | 0 | N/A | 0 | 0
2022-07-31 08:00 | 5.423 | 0 | N/A | 0 | 0
2022-07-31 08:30 | 5.9716 | 0 | N/A | 0 | 0
2022-07-31 09:00 | 5.9681 | 0 | N/A | 0 | 0
2022-07-31 09:30 | 5.1167 | 0 | N/A | 0 | 0
2022-07-31 10:00 | 4.7627 | 0 | N/A | 0 | 0
2022-07-31 10:30 | 3.7439 | 0 | N/A | 0 | 0
2022-07-31 11:00 | 2.9218 | 0 | N/A | 0 | 0
2022-07-31 11:30 | 3.6049 | 0 | N/A | 0 | 0
2022-07-31 12:00 | 4.6441 | 0 | N/A | 0 | 0
2022-07-31 12:30 | 5.0303 | 0 | N/A | 0 | 0
2022-07-31 13:00 | 5.1127 | 0 | N/A | 0 | 0
2022-07-31 13:30 | 4.9244 | 0 | N/A | 0 | 0
2022-07-31 14:00 | 4.6148 | 0 | N/A | 0 | 0
2022-07-31 14:30 | 4.7737 | 0 | N/A | 0 | 0
2022-07-31 15:00 | 5.9239 | 0 | N/A | 0 | 0
2022-07-31 15:30 | 6.7801 | 0 | N/A | 0 | 0
2022-07-31 16:00 | 7.3903 | 0 | N/A | 0 | 0
2022-07-31 16:30 | 7.5398 | 0 | N/A | 0 | 0
2022-07-31 17:00 | 8.1743 | 0 | N/A | 0 | 0
2022-07-31 17:30 | 8.8833 | 0 | N/A | 0 | 0
2022-07-31 18:00 | 9.4289 | 0 | N/A | 0 | 0
2022-07-31 18:30 | 9.5495 | 0 | N/A | 0 | 0
2022-07-31 19:00 | 9.2781 | 0 | N/A | 0 | 0
2022-07-31 19:30 | 8.7889 | 0 | N/A | 0 | 0
2022-07-31 20:00 | 8.3749 | 0 | N/A | 0 | 0
2022-07-31 20:30 | 7.9911 | 0 | N/A | 0 | 0
2022-07-31 21:00 | 7.5504 | 0 | N/A | 0 | 0
2022-07-31 21:30 | 7.5429 | 0 | N/A | 0 | 0
2022-07-31 22:00 | 7.5275 | 0 | N/A | 0 | 0
2022-07-31 22:30 | 6.8802 | 0 | N/A | 0 | 0
2022-07-31 23:00 | 6.7501 | 0 | N/A | 0 | 0
2022-07-31 23:30 | 6.6323 | 0 | N/A | 0 | 0
2022-08-01 | 6.8698 | 0 | N/A | 0 | 0
2022-08-02 00:30 | 6.1962 | 0 | N/A | 0 | 0
2022-08-02 01:00 | 5.4965 | 0 | N/A | 0 | 0
2022-08-02 01:30 | 5.2742 | 0 | N/A | 0 | 0
2022-08-02 02:00 | 4.9721 | 0 | N/A | 0 | 0
2022-08-02 02:30 | 4.5581 | 0 | N/A | 0 | 0
2022-08-02 03:00 | 4.1753 | 0 | N/A | 0 | 0
2022-08-02 03:30 | 4.0203 | 0 | N/A | 0 | 0
2022-08-02 04:00 | 3.8829 | 0 | N/A | 0 | 0
2022-08-02 04:30 | 3.8722 | 0 | N/A | 0 | 0
2022-08-02 05:00 | 3.9888 | 0 | N/A | 0 | 0
2022-08-02 05:30 | 4.4166 | 0 | N/A | 0 | 0
2022-08-02 06:00 | 4.9089 | 0 | N/A | 0 | 0
2022-08-02 06:30 | 5.742 | 0 | N/A | 0 | 0
2022-08-02 07:00 | 6.4717 | 0 | N/A | 0 | 0
2022-08-02 07:30 | 7.145 | 0 | N/A | 0 | 0
2022-08-02 08:00 | 8.1283 | 0 | N/A | 0 | 0
2022-08-02 08:30 | 7.9888 | 0 | N/A | 0 | 0
2022-08-02 09:00 | 7.5705 | 0 | N/A | 0 | 0
2022-08-02 09:30 | 6.7989 | 0 | N/A | 0 | 0
2022-08-02 10:00 | 5.8978 | 0 | N/A | 0 | 0
2022-08-02 10:30 | 5.1375 | 0 | N/A | 0 | 0
2022-08-02 11:00 | 4.477 | 0 | N/A | 0 | 0
2022-08-02 11:30 | 4.2357 | 0 | N/A | 0 | 0
2022-08-02 12:00 | 3.0028 | 0 | N/A | 0 | 0
2022-08-02 12:30 | 2.5471 | 0 | N/A | 0 | 0
2022-08-02 13:00 | 2.2049 | 0 | N/A | 0 | 0
2022-08-02 13:30 | 2.821 | 0 | N/A | 0 | 0
2022-08-02 14:00 | 4.6257 | 0 | N/A | 0 | 0
2022-08-02 14:30 | 3.5374 | 0 | N/A | 0 | 0
2022-08-02 15:00 | 3.9502 | 0 | N/A | 0 | 0
2022-08-02 15:30 | 4.6087 | 0 | N/A | 0 | 0
2022-08-02 16:00 | 5.8619 | 0 | N/A | 0 | 0
2022-08-02 16:30 | 6.35 | 0 | N/A | 0 | 0
2022-08-02 17:00 | 6.675 | 0 | N/A | 0 | 0
2022-08-02 17:30 | 7.6144 | 0 | N/A | 0 | 0
2022-08-02 18:00 | 8.6075 | 0 | N/A | 0 | 0
2022-08-02 18:30 | 9.1251 | 0 | N/A | 0 | 0
2022-08-02 19:00 | 8.8909 | 0 | N/A | 0 | 0
2022-08-02 19:30 | 8.4283 | 0 | N/A | 0 | 0
2022-08-02 20:00 | 8.2457 | 0 | N/A | 0 | 0
2022-08-02 20:30 | 7.841 | 0 | N/A | 0 | 0
2022-08-02 21:00 | 7.4279 | 0 | N/A | 0 | 0
2022-08-02 21:30 | 7.5126 | 0 | N/A | 0 | 0
2022-08-02 22:00 | 7.3962 | 0 | N/A | 0 | 0
2022-08-02 22:30 | 6.6439 | 0 | N/A | 0 | 0
2022-08-02 23:00 | 6.3748 | 0 | N/A | 0 | 0
2022-08-02 23:30 | 6.4069 | 0 | N/A | 0 | 0
2022-08-03 | 6.718 | 0 | N/A | 0 | 0
2022-08-06 00:30 | 6.5098 | 0 | N/A | 0 | 0
2022-08-06 01:00 | 5.74 | 0 | N/A | 0 | 0
2022-08-06 01:30 | 5.5776 | 0 | N/A | 0 | 0
2022-08-06 02:00 | 5.1695 | 0 | N/A | 0 | 0
2022-08-06 02:30 | 4.6878 | 0 | N/A | 0 | 0
2022-08-06 03:00 | 4.4281 | 0 | N/A | 0 | 0
2022-08-06 03:30 | 4.3118 | 0 | N/A | 0 | 0
2022-08-06 04:00 | 4.105 | 0 | N/A | 0 | 0
2022-08-06 04:30 | 4.0144 | 0 | N/A | 0 | 0
2022-08-06 05:00 | 4.04 | 0 | N/A | 0 | 0
2022-08-06 05:30 | 4.1714 | 0 | N/A | 0 | 0
2022-08-06 06:00 | 4.3269 | 0 | N/A | 0 | 0
2022-08-06 06:30 | 4.7189 | 0 | N/A | 0 | 0
2022-08-06 07:00 | 4.8995 | 0 | N/A | 0 | 0
2022-08-06 07:30 | 5.037 | 0 | N/A | 0 | 0
2022-08-06 08:00 | 5.682 | 0 | N/A | 0 | 0
2022-08-06 08:30 | 6.1815 | 0 | N/A | 0 | 0
2022-08-06 09:00 | 6.3258 | 0 | N/A | 0 | 0
2022-08-06 09:30 | 6.3248 | 0 | N/A | 0 | 0
2022-08-06 10:00 | 6.1017 | 0 | N/A | 0 | 0
2022-08-06 10:30 | 6.0294 | 0 | N/A | 0 | 0
2022-08-06 11:00 | 5.7057 | 0 | N/A | 0 | 0
2022-08-06 11:30 | 5.62 | 0 | N/A | 0 | 0
2022-08-06 12:00 | 5.2241 | 0 | N/A | 0 | 0
2022-08-06 12:30 | 4.9945 | 0 | N/A | 0 | 0
2022-08-06 13:00 | 4.5593 | 0 | N/A | 0 | 0
2022-08-06 13:30 | 5.0718 | 0 | N/A | 0 | 0
2022-08-06 14:00 | 5.0079 | 0 | N/A | 0 | 0
2022-08-06 14:30 | 4.0455 | 0 | N/A | 0 | 0
2022-08-06 15:00 | 3.7557 | 0 | N/A | 0 | 0
2022-08-06 15:30 | 3.5439 | 0 | N/A | 0 | 0
2022-08-06 16:00 | 4.2131 | 0 | N/A | 0 | 0
2022-08-06 16:30 | 5.0265 | 0 | N/A | 0 | 0
2022-08-06 17:00 | 6.0483 | 0 | N/A | 0 | 0
2022-08-06 17:30 | 7.0636 | 0 | N/A | 0 | 0
2022-08-06 18:00 | 7.8404 | 0 | N/A | 0 | 0
2022-08-06 18:30 | 8.226 | 0 | N/A | 0 | 0
2022-08-06 19:00 | 8.2119 | 0 | N/A | 0 | 0
2022-08-06 19:30 | 7.8938 | 0 | N/A | 0 | 0
2022-08-06 20:00 | 7.6285 | 0 | N/A | 0 | 0
2022-08-06 20:30 | 7.1643 | 0 | N/A | 0 | 0
2022-08-06 21:00 | 6.8018 | 0 | N/A | 0 | 0
2022-08-06 21:30 | 7.0146 | 0 | N/A | 0 | 0
2022-08-06 22:00 | 7.1932 | 0 | N/A | 0 | 0
2022-08-06 22:30 | 6.8113 | 0 | N/A | 0 | 0
2022-08-06 23:00 | 6.7769 | 0 | N/A | 0 | 0
2022-08-06 23:30 | 6.9292 | 0 | N/A | 0 | 0
2022-08-07 | 7.1894 | 0 | N/A | 0 | 0
2022-08-07 00:30 | 6.482 | 0 | N/A | 0 | 0
2022-08-07 01:00 | 5.7431 | 0 | N/A | 0 | 0
2022-08-07 01:30 | 5.4337 | 0 | N/A | 0 | 0
2022-08-07 02:00 | 5.0822 | 0 | N/A | 0 | 0
2022-08-07 02:30 | 4.6678 | 0 | N/A | 0 | 0
2022-08-07 03:00 | 4.2921 | 0 | N/A | 0 | 0
2022-08-07 03:30 | 4.1426 | 0 | N/A | 0 | 0
2022-08-07 04:00 | 4.0378 | 0 | N/A | 0 | 0
2022-08-07 04:30 | 3.859 | 0 | N/A | 0 | 0
2022-08-07 05:00 | 3.855 | 0 | N/A | 0 | 0
2022-08-07 05:30 | 3.9295 | 0 | N/A | 0 | 0
2022-08-07 06:00 | 4.0639 | 0 | N/A | 0 | 0
2022-08-07 06:30 | 4.266 | 0 | N/A | 0 | 0
2022-08-07 07:00 | 4.4696 | 0 | N/A | 0 | 0
2022-08-07 07:30 | 4.644 | 0 | N/A | 0 | 0
2022-08-07 08:00 | 5.0129 | 0 | N/A | 0 | 0
2022-08-07 08:30 | 5.2699 | 0 | N/A | 0 | 0
2022-08-07 09:00 | 4.811 | 0 | N/A | 0 | 0
2022-08-07 09:30 | 4.2936 | 0 | N/A | 0 | 0
2022-08-07 10:00 | 3.6408 | 0 | N/A | 0 | 0
2022-08-07 10:30 | 3.5395 | 0 | N/A | 0 | 0
2022-08-07 11:00 | 3.1848 | 0 | N/A | 0 | 0
2022-08-07 11:30 | 2.6869 | 0 | N/A | 0 | 0
2022-08-07 12:00 | 3.7302 | 0 | N/A | 0 | 0
2022-08-07 12:30 | 3.8499 | 0 | N/A | 0 | 0
2022-08-07 13:00 | 4.0035 | 0 | N/A | 0 | 0
2022-08-07 13:30 | 4.3327 | 0 | N/A | 0 | 0
2022-08-07 14:00 | 4.7479 | 0 | N/A | 0 | 0
2022-08-07 14:30 | 5.0199 | 0 | N/A | 0 | 0
2022-08-07 15:00 | 5.3967 | 0 | N/A | 0 | 0
2022-08-07 15:30 | 5.5687 | 0 | N/A | 0 | 0
2022-08-07 16:00 | 5.6461 | 0 | N/A | 0 | 0
2022-08-07 16:30 | 6.0309 | 0 | N/A | 0 | 0
2022-08-07 17:00 | 6.7195 | 0 | N/A | 0 | 0
2022-08-07 17:30 | 7.4883 | 0 | N/A | 0 | 0
2022-08-07 18:00 | 8.3572 | 0 | N/A | 0 | 0
2022-08-07 18:30 | 9.013 | 0 | N/A | 0 | 0
2022-08-07 19:00 | 9.0069 | 0 | N/A | 0 | 0
2022-08-07 19:30 | 8.7003 | 0 | N/A | 0 | 0
2022-08-07 20:00 | 8.2878 | 0 | N/A | 0 | 0
2022-08-07 20:30 | 7.863 | 0 | N/A | 0 | 0
2022-08-07 21:00 | 7.6292 | 0 | N/A | 0 | 0
2022-08-07 21:30 | 7.7251 | 0 | N/A | 0 | 0
2022-08-07 22:00 | 7.6464 | 0 | N/A | 0 | 0
2022-08-07 22:30 | 7.106 | 0 | N/A | 0 | 0
2022-08-07 23:00 | 7.0069 | 0 | N/A | 0 | 0
2022-08-07 23:30 | 6.8985 | 0 | N/A | 0 | 0
2022-08-08 | 7.2545 | 0 | N/A | 0 | 0
2022-08-08 00:30 | 6.7864 | 0 | N/A | 0 | 0
2022-08-08 01:00 | 6.1476 | 0 | N/A | 0 | 0
2022-08-08 01:30 | 5.9994 | 0 | N/A | 0 | 0
2022-08-08 02:00 | 5.8001 | 0 | N/A | 0 | 0
2022-08-08 02:30 | 5.3237 | 0 | N/A | 0 | 0
2022-08-08 03:00 | 5.0609 | 0 | N/A | 0 | 0
2022-08-08 03:30 | 4.8484 | 0 | N/A | 0 | 0
2022-08-08 04:00 | 4.68 | 0 | N/A | 0 | 0
2022-08-08 04:30 | 4.6566 | 0 | N/A | 0 | 0
2022-08-08 05:00 | 4.838 | 0 | N/A | 0 | 0
2022-08-08 05:30 | 5.1986 | 0 | N/A | 0 | 0
2022-08-08 06:00 | 5.7851 | 0 | N/A | 0 | 0
2022-08-08 06:30 | 6.7156 | 0 | N/A | 0 | 0
2022-08-08 07:00 | 7.6793 | 0 | N/A | 0 | 0
2022-08-08 07:30 | 8.5728 | 0 | N/A | 0 | 0
2022-08-08 08:00 | 9.4202 | 0 | N/A | 0 | 0
2022-08-08 08:30 | 8.9867 | 0 | N/A | 0 | 0
2022-08-08 09:00 | 8.05 | 0 | N/A | 0 | 0
2022-08-08 09:30 | 7.11 | 0 | N/A | 0 | 0
2022-08-08 10:00 | 6.0304 | 0 | N/A | 0 | 0
2022-08-08 10:30 | 4.8132 | 0 | N/A | 0 | 0
2022-08-08 11:00 | 4.2422 | 0 | N/A | 0 | 0
2022-08-08 11:30 | 4.1853 | 0 | N/A | 0 | 0
2022-08-08 12:00 | 3.5704 | 0 | N/A | 0 | 0
2022-08-08 12:30 | 3.6253 | 0 | N/A | 0 | 0
2022-08-08 13:00 | 2.7549 | 0 | N/A | 0 | 0
2022-08-08 13:30 | 2.7981 | 0 | N/A | 0 | 0
2022-08-08 14:00 | 2.48 | 0 | N/A | 0 | 0
2022-08-08 14:30 | 2.6889 | 0 | N/A | 0 | 0
2022-08-08 15:00 | 3.4102 | 0 | N/A | 0 | 0
2022-08-08 15:30 | 3.6365 | 0 | N/A | 0 | 0
2022-08-08 16:00 | 4.3673 | 0 | N/A | 0 | 0
2022-08-08 16:30 | 5.1717 | 0 | N/A | 0 | 0
2022-08-08 17:00 | 5.4939 | 0 | N/A | 0 | 0
2022-08-08 17:30 | 6.933 | 0 | N/A | 0 | 0
2022-08-08 18:00 | 8.5062 | 0 | N/A | 0 | 0
2022-08-08 18:30 | 9.3434 | 0 | N/A | 0 | 0
2022-08-08 19:00 | 9.4475 | 0 | N/A | 0 | 0
2022-08-08 19:30 | 9.165 | 0 | N/A | 0 | 0
2022-08-08 20:00 | 9.0006 | 0 | N/A | 0 | 0
2022-08-08 20:30 | 8.7976 | 0 | N/A | 0 | 0
2022-08-08 21:00 | 8.5227 | 0 | N/A | 0 | 0
2022-08-08 21:30 | 8.6001 | 0 | N/A | 0 | 0
2022-08-08 22:00 | 8.5743 | 0 | N/A | 0 | 0
2022-08-08 22:30 | 7.7981 | 0 | N/A | 0 | 0
2022-08-08 23:00 | 7.4582 | 0 | N/A | 0 | 0
2022-08-08 23:30 | 7.3877 | 0 | N/A | 0 | 0
2022-08-09 | 7.7207 | 0 | N/A | 0 | 0
2022-08-09 00:30 | 7.1017 | 0 | N/A | 0 | 0
2022-08-09 01:00 | 6.4265 | 0 | N/A | 0 | 0
2022-08-09 01:30 | 6.3519 | 0 | N/A | 0 | 0
2022-08-09 02:00 | 6.0609 | 0 | N/A | 0 | 0
2022-08-09 02:30 | 5.5762 | 0 | N/A | 0 | 0
2022-08-09 03:00 | 5.3848 | 0 | N/A | 0 | 0
2022-08-09 03:30 | 5.1908 | 0 | N/A | 0 | 0
2022-08-09 04:00 | 4.9978 | 0 | N/A | 0 | 0
2022-08-09 04:30 | 5.018 | 0 | N/A | 0 | 0
2022-08-09 05:00 | 5.2811 | 0 | N/A | 0 | 0
2022-08-09 05:30 | 5.836 | 0 | N/A | 0 | 0
2022-08-09 06:00 | 6.3836 | 0 | N/A | 0 | 0
2022-08-09 06:30 | 7.4339 | 0 | N/A | 0 | 0
2022-08-09 07:00 | 8.2916 | 0 | N/A | 0 | 0
2022-08-09 07:30 | 8.6725 | 0 | N/A | 0 | 0
2022-08-09 08:00 | 9.1706 | 0 | N/A | 0 | 0
2022-08-09 08:30 | 8.7467 | 0 | N/A | 0 | 0
2022-08-09 09:00 | 8.1267 | 0 | N/A | 0 | 0
2022-08-09 09:30 | 7.1838 | 0 | N/A | 0 | 0
2022-08-09 10:00 | 6.0419 | 0 | N/A | 0 | 0
2022-08-09 10:30 | 4.8861 | 0 | N/A | 0 | 0
2022-08-09 11:00 | 4.0182 | 0 | N/A | 0 | 0
2022-08-09 11:30 | 3.3796 | 0 | N/A | 0 | 0
2022-08-09 12:00 | 2.879 | 0 | N/A | 0 | 0
2022-08-09 12:30 | 3.0786 | 0 | N/A | 0 | 0
2022-08-09 13:00 | 3.1019 | 0 | N/A | 0 | 0
2022-08-09 13:30 | 2.7823 | 0 | N/A | 0 | 0
2022-08-09 14:00 | 3.0673 | 0 | N/A | 0 | 0
2022-08-09 14:30 | 2.9622 | 0 | N/A | 0 | 0
2022-08-09 15:00 | 3.3975 | 0 | N/A | 0 | 0
2022-08-09 15:30 | 3.5209 | 0 | N/A | 0 | 0
2022-08-09 16:00 | 4.4799 | 0 | N/A | 0 | 0
2022-08-09 16:30 | 4.222 | 0 | N/A | 0 | 0
2022-08-09 17:00 | 5.4165 | 0 | N/A | 0 | 0
2022-08-09 17:30 | 6.9027 | 0 | N/A | 0 | 0
2022-08-09 18:00 | 8.3998 | 0 | N/A | 0 | 0
2022-08-09 18:30 | 9.3693 | 0 | N/A | 0 | 0
2022-08-09 19:00 | 9.5158 | 0 | N/A | 0 | 0
2022-08-09 19:30 | 9.2503 | 0 | N/A | 0 | 0
2022-08-09 20:00 | 9.1081 | 0 | N/A | 0 | 0
2022-08-09 20:30 | 8.8567 | 0 | N/A | 0 | 0
2022-08-09 21:00 | 8.4469 | 0 | N/A | 0 | 0
2022-08-09 21:30 | 8.4692 | 0 | N/A | 0 | 0
2022-08-09 22:00 | 8.338 | 0 | N/A | 0 | 0
2022-08-09 22:30 | 7.4397 | 0 | N/A | 0 | 0
2022-08-09 23:00 | 7.0128 | 0 | N/A | 0 | 0
2022-08-09 23:30 | 7.0678 | 0 | N/A | 0 | 0
2022-08-10 | 7.2778 | 0 | N/A | 0 | 0
2022-08-10 00:30 | 6.7258 | 0 | N/A | 0 | 0
2022-08-10 01:00 | 6.1222 | 0 | N/A | 0 | 0
2022-08-10 01:30 | 5.9912 | 0 | N/A | 0 | 0
2022-08-10 02:00 | 5.7046 | 0 | N/A | 0 | 0
2022-08-10 02:30 | 5.3232 | 0 | N/A | 0 | 0
2022-08-10 03:00 | 4.9607 | 0 | N/A | 0 | 0
2022-08-10 03:30 | 4.8152 | 0 | N/A | 0 | 0
2022-08-10 04:00 | 4.7465 | 0 | N/A | 0 | 0
2022-08-10 04:30 | 4.7222 | 0 | N/A | 0 | 0
2022-08-10 05:00 | 4.9247 | 0 | N/A | 0 | 0
2022-08-10 05:30 | 5.4436 | 0 | N/A | 0 | 0
2022-08-10 06:00 | 5.8921 | 0 | N/A | 0 | 0
2022-08-10 06:30 | 6.8416 | 0 | N/A | 0 | 0
2022-08-10 07:00 | 7.7512 | 0 | N/A | 0 | 0
2022-08-10 07:30 | 8.6697 | 0 | N/A | 0 | 0
2022-08-10 08:00 | 9.2605 | 0 | N/A | 0 | 0
2022-08-10 08:30 | 9.2368 | 0 | N/A | 0 | 0
2022-08-10 09:00 | 8.9504 | 0 | N/A | 0 | 0
2022-08-10 09:30 | 8.7569 | 0 | N/A | 0 | 0
2022-08-10 10:00 | 8.464 | 0 | N/A | 0 | 0
2022-08-10 10:30 | 8.0124 | 0 | N/A | 0 | 0
2022-08-10 11:00 | 7.4631 | 0 | N/A | 0 | 0
2022-08-10 11:30 | 6.0887 | 0 | N/A | 0 | 0
2022-08-10 12:00 | 4.9479 | 0 | N/A | 0 | 0
2022-08-10 12:30 | 5.1841 | 0 | N/A | 0 | 0
2022-08-10 13:00 | 5.279 | 0 | N/A | 0 | 0
2022-08-10 13:30 | 5.3649 | 0 | N/A | 0 | 0
2022-08-10 14:00 | 5.2456 | 0 | N/A | 0 | 0
2022-08-10 14:30 | 5.0369 | 0 | N/A | 0 | 0
2022-08-10 15:00 | 5.4386 | 0 | N/A | 0 | 0
2022-08-10 15:30 | 6.114 | 0 | N/A | 0 | 0
2022-08-10 16:00 | 6.9003 | 0 | N/A | 0 | 0
2022-08-10 16:30 | 6.6442 | 0 | N/A | 0 | 0
2022-08-10 17:00 | 7.2196 | 0 | N/A | 0 | 0
2022-08-10 17:30 | 8.2158 | 0 | N/A | 0 | 0
2022-08-10 18:00 | 9.1886 | 0 | N/A | 0 | 0
2022-08-10 18:30 | 9.6341 | 0 | N/A | 0 | 0
2022-08-10 19:00 | 9.4611 | 0 | N/A | 0 | 0
2022-08-10 19:30 | 9.0988 | 0 | N/A | 0 | 0
2022-08-10 20:00 | 8.9027 | 0 | N/A | 0 | 0
2022-08-10 20:30 | 8.4505 | 0 | N/A | 0 | 0
2022-08-10 21:00 | 7.8916 | 0 | N/A | 0 | 0
2022-08-10 21:30 | 7.9261 | 0 | N/A | 0 | 0
2022-08-10 22:00 | 7.8382 | 0 | N/A | 0 | 0
2022-08-10 22:30 | 7.037 | 0 | N/A | 0 | 0
2022-08-10 23:00 | 6.7144 | 0 | N/A | 0 | 0
2022-08-10 23:30 | 6.7595 | 0 | N/A | 0 | 0
2022-08-11 | 6.8434 | 0 | N/A | 0 | 0
2022-08-12 00:30 | 6.0954 | 0 | N/A | 0 | 0
2022-08-12 01:00 | 5.3854 | 0 | N/A | 0 | 0
2022-08-12 01:30 | 5.2501 | 0 | N/A | 0 | 0
2022-08-12 02:00 | 4.8484 | 0 | N/A | 0 | 0
2022-08-12 02:30 | 4.3278 | 0 | N/A | 0 | 0
2022-08-12 03:00 | 4.0954 | 0 | N/A | 0 | 0
2022-08-12 03:30 | 3.9931 | 0 | N/A | 0 | 0
2022-08-12 04:00 | 3.8398 | 0 | N/A | 0 | 0
2022-08-12 04:30 | 3.774 | 0 | N/A | 0 | 0
2022-08-12 05:00 | 3.9202 | 0 | N/A | 0 | 0
2022-08-12 05:30 | 4.3507 | 0 | N/A | 0 | 0
2022-08-12 06:00 | 4.7501 | 0 | N/A | 0 | 0
2022-08-12 06:30 | 5.4149 | 0 | N/A | 0 | 0
2022-08-12 07:00 | 5.9593 | 0 | N/A | 0 | 0
2022-08-12 07:30 | 6.8416 | 0 | N/A | 0 | 0
2022-08-12 08:00 | 7.371 | 0 | N/A | 0 | 0
2022-08-12 08:30 | 7.4597 | 0 | N/A | 0 | 0
2022-08-12 09:00 | 6.9905 | 0 | N/A | 0 | 0
2022-08-12 09:30 | 7.1905 | 0 | N/A | 0 | 0
2022-08-12 10:00 | 6.9697 | 0 | N/A | 0 | 0
2022-08-12 10:30 | 6.3842 | 0 | N/A | 0 | 0
2022-08-12 11:00 | 6.0047 | 0 | N/A | 0 | 0
2022-08-12 11:30 | 5.4368 | 0 | N/A | 0 | 0
2022-08-12 12:00 | 4.3663 | 0 | N/A | 0 | 0
2022-08-12 12:30 | 3.9582 | 0 | N/A | 0 | 0
2022-08-12 13:00 | 5.3523 | 0 | N/A | 0 | 0
2022-08-12 13:30 | 4.5093 | 0 | N/A | 0 | 0
2022-08-12 14:00 | 4.7845 | 0 | N/A | 0 | 0
2022-08-12 14:30 | 4.9894 | 0 | N/A | 0 | 0
2022-08-12 15:00 | 5.309 | 0 | N/A | 0 | 0
2022-08-12 15:30 | 5.6744 | 0 | N/A | 0 | 0
2022-08-12 16:00 | 5.7357 | 0 | N/A | 0 | 0
2022-08-12 16:30 | 6.4021 | 0 | N/A | 0 | 0
2022-08-12 17:00 | 7.026 | 0 | N/A | 0 | 0
2022-08-12 17:30 | 7.6047 | 0 | N/A | 0 | 0
2022-08-12 18:00 | 8.1565 | 0 | N/A | 0 | 0
2022-08-12 18:30 | 8.5091 | 0 | N/A | 0 | 0
2022-08-12 19:00 | 8.3674 | 0 | N/A | 0 | 0
2022-08-12 19:30 | 8.1693 | 0 | N/A | 0 | 0
2022-08-12 20:00 | 7.9717 | 0 | N/A | 0 | 0
2022-08-12 20:30 | 7.8118 | 0 | N/A | 0 | 0
2022-08-12 21:00 | 7.3947 | 0 | N/A | 0 | 0
2022-08-12 21:30 | 7.4888 | 0 | N/A | 0 | 0
2022-08-12 22:00 | 7.6279 | 0 | N/A | 0 | 0
2022-08-12 22:30 | 7.1011 | 0 | N/A | 0 | 0
2022-08-12 23:00 | 6.7727 | 0 | N/A | 0 | 0
2022-08-12 23:30 | 6.7802 | 0 | N/A | 0 | 0
2022-08-13 | 6.975 | 0 | N/A | 0 | 0
2022-08-13 00:30 | 6.3335 | 0 | N/A | 0 | 0
2022-08-13 01:00 | 5.5887 | 0 | N/A | 0 | 0
2022-08-13 01:30 | 5.3863 | 0 | N/A | 0 | 0
2022-08-13 02:00 | 5.1433 | 0 | N/A | 0 | 0
2022-08-13 02:30 | 4.623 | 0 | N/A | 0 | 0
2022-08-13 03:00 | 4.2985 | 0 | N/A | 0 | 0
2022-08-13 03:30 | 4.0572 | 0 | N/A | 0 | 0
2022-08-13 04:00 | 3.9487 | 0 | N/A | 0 | 0
2022-08-13 04:30 | 3.8154 | 0 | N/A | 0 | 0
2022-08-13 05:00 | 3.8119 | 0 | N/A | 0 | 0
2022-08-13 05:30 | 3.9762 | 0 | N/A | 0 | 0
2022-08-13 06:00 | 4.1768 | 0 | N/A | 0 | 0
2022-08-13 06:30 | 4.5914 | 0 | N/A | 0 | 0
2022-08-13 07:00 | 4.8687 | 0 | N/A | 0 | 0
2022-08-13 07:30 | 4.8831 | 0 | N/A | 0 | 0
2022-08-13 08:00 | 5.3402 | 0 | N/A | 0 | 0
2022-08-13 08:30 | 5.7118 | 0 | N/A | 0 | 0
2022-08-13 09:00 | 5.7313 | 0 | N/A | 0 | 0
2022-08-13 09:30 | 5.3869 | 0 | N/A | 0 | 0
2022-08-13 10:00 | 4.6213 | 0 | N/A | 0 | 0
2022-08-13 10:30 | 4.1612 | 0 | N/A | 0 | 0
2022-08-13 11:00 | 3.78 | 0 | N/A | 0 | 0
2022-08-13 11:30 | 3.1043 | 0 | N/A | 0 | 0
2022-08-13 12:00 | 3.6766 | 0 | N/A | 0 | 0
2022-08-13 12:30 | 4.0067 | 0 | N/A | 0 | 0
2022-08-13 13:00 | 4.0336 | 0 | N/A | 0 | 0
2022-08-13 13:30 | 4.0884 | 0 | N/A | 0 | 0
2022-08-13 14:00 | 2.5875 | 0 | N/A | 0 | 0
2022-08-13 14:30 | 3.1887 | 0 | N/A | 0 | 0
2022-08-13 15:00 | 3.7317 | 0 | N/A | 0 | 0
2022-08-13 15:30 | 4.2931 | 0 | N/A | 0 | 0
2022-08-13 16:00 | 3.5842 | 0 | N/A | 0 | 0
2022-08-13 16:30 | 4.098 | 0 | N/A | 0 | 0
2022-08-13 17:00 | 5.866 | 0 | N/A | 0 | 0
2022-08-13 17:30 | 7.0247 | 0 | N/A | 0 | 0
2022-08-13 18:00 | 7.6739 | 0 | N/A | 0 | 0
2022-08-13 18:30 | 7.9726 | 0 | N/A | 0 | 0
2022-08-13 19:00 | 7.7867 | 0 | N/A | 0 | 0
2022-08-13 19:30 | 7.4877 | 0 | N/A | 0 | 0
2022-08-13 20:00 | 7.2691 | 0 | N/A | 0 | 0
2022-08-13 20:30 | 6.9978 | 0 | N/A | 0 | 0
2022-08-13 21:00 | 6.7577 | 0 | N/A | 0 | 0
2022-08-13 21:30 | 6.9034 | 0 | N/A | 0 | 0
2022-08-13 22:00 | 7.0518 | 0 | N/A | 0 | 0
2022-08-13 22:30 | 6.83 | 0 | N/A | 0 | 0
2022-08-13 23:00 | 6.8165 | 0 | N/A | 0 | 0
2022-08-13 23:30 | 6.7279 | 0 | N/A | 0 | 0
2022-08-14 | 6.81 | 0 | N/A | 0 | 0
2022-08-14 00:30 | 6.2488 | 0 | N/A | 0 | 0
2022-08-14 01:00 | 5.5125 | 0 | N/A | 0 | 0
2022-08-14 01:30 | 5.2892 | 0 | N/A | 0 | 0
2022-08-14 02:00 | 4.8753 | 0 | N/A | 0 | 0
2022-08-14 02:30 | 4.4918 | 0 | N/A | 0 | 0
2022-08-14 03:00 | 4.1974 | 0 | N/A | 0 | 0
2022-08-14 03:30 | 4.049 | 0 | N/A | 0 | 0
2022-08-14 04:00 | 3.8707 | 0 | N/A | 0 | 0
2022-08-14 04:30 | 3.7945 | 0 | N/A | 0 | 0
2022-08-14 05:00 | 3.7905 | 0 | N/A | 0 | 0
2022-08-14 05:30 | 3.8269 | 0 | N/A | 0 | 0
2022-08-14 06:00 | 3.9423 | 0 | N/A | 0 | 0
2022-08-14 06:30 | 4.2033 | 0 | N/A | 0 | 0
2022-08-14 07:00 | 4.4932 | 0 | N/A | 0 | 0
2022-08-14 07:30 | 4.5678 | 0 | N/A | 0 | 0
2022-08-14 08:00 | 4.9089 | 0 | N/A | 0 | 0
2022-08-14 08:30 | 5.3616 | 0 | N/A | 0 | 0
2022-08-14 09:00 | 5.6449 | 0 | N/A | 0 | 0
2022-08-14 09:30 | 6.1255 | 0 | N/A | 0 | 0
2022-08-14 10:00 | 5.8728 | 0 | N/A | 0 | 0
2022-08-14 10:30 | 6.2401 | 0 | N/A | 0 | 0
2022-08-14 11:00 | 6.1036 | 0 | N/A | 0 | 0
2022-08-14 11:30 | 5.9722 | 0 | N/A | 0 | 0
2022-08-14 12:00 | 5.1394 | 0 | N/A | 0 | 0
2022-08-14 12:30 | 4.7611 | 0 | N/A | 0 | 0
2022-08-14 13:00 | 4.0945 | 0 | N/A | 0 | 0
2022-08-14 13:30 | 4.5289 | 0 | N/A | 0 | 0
2022-08-14 14:00 | 5.319 | 0 | N/A | 0 | 0
2022-08-14 14:30 | 3.8369 | 0 | N/A | 0 | 0
2022-08-14 15:00 | 2.9834 | 0 | N/A | 0 | 0
2022-08-14 15:30 | 4.5896 | 0 | N/A | 0 | 0
2022-08-14 16:00 | 4.2591 | 0 | N/A | 0 | 0
2022-08-14 16:30 | 4.4499 | 0 | N/A | 0 | 0
2022-08-14 17:00 | 5.7622 | 0 | N/A | 0 | 0
2022-08-14 17:30 | 7.4888 | 0 | N/A | 0 | 0
2022-08-14 18:00 | 8.4279 | 0 | N/A | 0 | 0
2022-08-14 18:30 | 8.7965 | 0 | N/A | 0 | 0
2022-08-14 19:00 | 8.6404 | 0 | N/A | 0 | 0
2022-08-14 19:30 | 8.2321 | 0 | N/A | 0 | 0
2022-08-14 20:00 | 7.9242 | 0 | N/A | 0 | 0
2022-08-14 20:30 | 7.357 | 0 | N/A | 0 | 0
2022-08-14 21:00 | 7.0732 | 0 | N/A | 0 | 0
2022-08-14 21:30 | 7.0406 | 0 | N/A | 0 | 0
2022-08-14 22:00 | 6.984 | 0 | N/A | 0 | 0
2022-08-14 22:30 | 6.5691 | 0 | N/A | 0 | 0
2022-08-14 23:00 | 6.395 | 0 | N/A | 0 | 0
2022-08-14 23:30 | 6.4113 | 0 | N/A | 0 | 0
2022-08-15 | 6.6851 | 0 | N/A | 0 | 0
2022-08-15 00:30 | 6.1546 | 0 | N/A | 0 | 0
2022-08-15 01:00 | 5.4608 | 0 | N/A | 0 | 0
2022-08-15 01:30 | 5.3998 | 0 | N/A | 0 | 0
2022-08-15 02:00 | 5.1292 | 0 | N/A | 0 | 0
2022-08-15 02:30 | 4.6324 | 0 | N/A | 0 | 0
2022-08-15 03:00 | 4.3048 | 0 | N/A | 0 | 0
2022-08-15 03:30 | 4.1292 | 0 | N/A | 0 | 0
2022-08-15 04:00 | 3.9796 | 0 | N/A | 0 | 0
2022-08-15 04:30 | 3.8854 | 0 | N/A | 0 | 0
2022-08-15 05:00 | 3.9614 | 0 | N/A | 0 | 0
2022-08-15 05:30 | 4.4815 | 0 | N/A | 0 | 0
2022-08-15 06:00 | 4.8936 | 0 | N/A | 0 | 0
2022-08-15 06:30 | 5.5972 | 0 | N/A | 0 | 0
2022-08-15 07:00 | 6.4002 | 0 | N/A | 0 | 0
2022-08-15 07:30 | 6.4774 | 0 | N/A | 0 | 0
2022-08-15 08:00 | 7.2982 | 0 | N/A | 0 | 0
2022-08-15 08:30 | 7.3852 | 0 | N/A | 0 | 0
2022-08-15 09:00 | 7.3353 | 0 | N/A | 0 | 0
2022-08-15 09:30 | 7.0436 | 0 | N/A | 0 | 0
2022-08-15 10:00 | 6.8606 | 0 | N/A | 0 | 0
2022-08-15 10:30 | 6.265 | 0 | N/A | 0 | 0
2022-08-15 11:00 | 6.0186 | 0 | N/A | 0 | 0
2022-08-15 11:30 | 5.1664 | 0 | N/A | 0 | 0
2022-08-15 12:00 | 4.7185 | 0 | N/A | 0 | 0
2022-08-15 12:30 | 4.5008 | 0 | N/A | 0 | 0
2022-08-15 13:00 | 3.8142 | 0 | N/A | 0 | 0
2022-08-15 13:30 | 5.3852 | 0 | N/A | 0 | 0
2022-08-15 14:00 | 4.246 | 0 | N/A | 0 | 0
2022-08-15 14:30 | 5.329 | 0 | N/A | 0 | 0
2022-08-15 15:00 | 4.561 | 0 | N/A | 0 | 0
2022-08-15 15:30 | 5.614 | 0 | N/A | 0 | 0
2022-08-15 16:00 | 5.9652 | 0 | N/A | 0 | 0
2022-08-15 16:30 | 6.7477 | 0 | N/A | 0 | 0
2022-08-15 17:00 | 6.6884 | 0 | N/A | 0 | 0
2022-08-15 17:30 | 7.5317 | 0 | N/A | 0 | 0
2022-08-15 18:00 | 8.7011 | 0 | N/A | 0 | 0
2022-08-15 18:30 | 9.3418 | 0 | N/A | 0 | 0
2022-08-15 19:00 | 9.3354 | 0 | N/A | 0 | 0
2022-08-15 19:30 | 8.9837 | 0 | N/A | 0 | 0
2022-08-15 20:00 | 8.6194 | 0 | N/A | 0 | 0
2022-08-15 20:30 | 8.29 | 0 | N/A | 0 | 0
2022-08-15 21:00 | 7.8916 | 0 | N/A | 0 | 0
2022-08-15 21:30 | 7.8124 | 0 | N/A | 0 | 0
2022-08-15 22:00 | 7.714 | 0 | N/A | 0 | 0
2022-08-15 22:30 | 6.9626 | 0 | N/A | 0 | 0
2022-08-15 23:00 | 6.7399 | 0 | N/A | 0 | 0
2022-08-15 23:30 | 6.5466 | 0 | N/A | 0 | 0
2022-08-16 | 6.8261 | 0 | N/A | 0 | 0
2022-08-16 00:30 | 6.2702 | 0 | N/A | 0 | 0
2022-08-16 01:00 | 5.6155 | 0 | N/A | 0 | 0
2022-08-16 01:30 | 5.49 | 0 | N/A | 0 | 0
2022-08-16 02:00 | 5.1594 | 0 | N/A | 0 | 0
2022-08-16 02:30 | 4.5578 | 0 | N/A | 0 | 0
2022-08-16 03:00 | 4.2451 | 0 | N/A | 0 | 0
2022-08-16 03:30 | 4.0729 | 0 | N/A | 0 | 0
2022-08-16 04:00 | 3.9761 | 0 | N/A | 0 | 0
2022-08-16 04:30 | 3.9529 | 0 | N/A | 0 | 0
2022-08-16 05:00 | 4.0585 | 0 | N/A | 0 | 0
2022-08-16 05:30 | 4.4959 | 0 | N/A | 0 | 0
2022-08-16 06:00 | 4.9342 | 0 | N/A | 0 | 0
2022-08-16 06:30 | 5.6317 | 0 | N/A | 0 | 0
2022-08-16 07:00 | 6.3037 | 0 | N/A | 0 | 0
2022-08-16 07:30 | 7.0027 | 0 | N/A | 0 | 0
2022-08-16 08:00 | 7.7509 | 0 | N/A | 0 | 0
2022-08-16 08:30 | 7.6049 | 0 | N/A | 0 | 0
2022-08-16 09:00 | 7.4752 | 0 | N/A | 0 | 0
2022-08-16 09:30 | 7.2094 | 0 | N/A | 0 | 0
2022-08-16 10:00 | 7.2165 | 0 | N/A | 0 | 0
2022-08-16 10:30 | 5.4868 | 0 | N/A | 0 | 0
2022-08-16 11:00 | 4.7865 | 0 | N/A | 0 | 0
2022-08-16 11:30 | 4.5598 | 0 | N/A | 0 | 0
2022-08-16 12:00 | 4.4856 | 0 | N/A | 0 | 0
2022-08-16 12:30 | 5.1995 | 0 | N/A | 0 | 0
2022-08-16 13:00 | 4.1418 | 0 | N/A | 0 | 0
2022-08-16 13:30 | 5.2164 | 0 | N/A | 0 | 0
2022-08-16 14:00 | 5.2018 | 0 | N/A | 0 | 0
2022-08-16 14:30 | 5.5045 | 0 | N/A | 0 | 0
2022-08-16 15:00 | 5.7691 | 0 | N/A | 0 | 0
2022-08-16 15:30 | 5.9927 | 0 | N/A | 0 | 0
2022-08-16 16:00 | 6.3832 | 0 | N/A | 0 | 0
2022-08-16 16:30 | 6.652 | 0 | N/A | 0 | 0
2022-08-16 17:00 | 7.2344 | 0 | N/A | 0 | 0
2022-08-16 17:30 | 8.0309 | 0 | N/A | 0 | 0
2022-08-16 18:00 | 8.8025 | 0 | N/A | 0 | 0
2022-08-16 18:30 | 9.2897 | 0 | N/A | 0 | 0
2022-08-16 19:00 | 9.093 | 0 | N/A | 0 | 0
2022-08-16 19:30 | 8.7574 | 0 | N/A | 0 | 0
2022-08-16 20:00 | 8.5011 | 0 | N/A | 0 | 0
2022-08-16 20:30 | 8.0424 | 0 | N/A | 0 | 0
2022-08-16 21:00 | 7.7155 | 0 | N/A | 0 | 0
2022-08-16 21:30 | 7.6963 | 0 | N/A | 0 | 0
2022-08-16 22:00 | 7.6034 | 0 | N/A | 0 | 0
2022-08-16 22:30 | 6.9406 | 0 | N/A | 0 | 0
2022-08-16 23:00 | 6.5598 | 0 | N/A | 0 | 0
2022-08-16 23:30 | 6.4412 | 0 | N/A | 0 | 0
2022-08-17 | 6.6987 | 0 | N/A | 0 | 0
2022-08-18 00:30 | 5.999 | 0 | N/A | 0 | 0
2022-08-18 01:00 | 5.3468 | 0 | N/A | 0 | 0
2022-08-18 01:30 | 5.1565 | 0 | N/A | 0 | 0
2022-08-18 02:00 | 4.8871 | 0 | N/A | 0 | 0
2022-08-18 02:30 | 4.4704 | 0 | N/A | 0 | 0
2022-08-18 03:00 | 4.1611 | 0 | N/A | 0 | 0
2022-08-18 03:30 | 3.9922 | 0 | N/A | 0 | 0
2022-08-18 04:00 | 3.9023 | 0 | N/A | 0 | 0
2022-08-18 04:30 | 3.7644 | 0 | N/A | 0 | 0
2022-08-18 05:00 | 3.8654 | 0 | N/A | 0 | 0
2022-08-18 05:30 | 4.3675 | 0 | N/A | 0 | 0
2022-08-18 06:00 | 4.7113 | 0 | N/A | 0 | 0
2022-08-18 06:30 | 5.3592 | 0 | N/A | 0 | 0
2022-08-18 07:00 | 6.1236 | 0 | N/A | 0 | 0
2022-08-18 07:30 | 7.2759 | 0 | N/A | 0 | 0
2022-08-18 08:00 | 8.0772 | 0 | N/A | 0 | 0
2022-08-18 08:30 | 8.1957 | 0 | N/A | 0 | 0
2022-08-18 09:00 | 8.2718 | 0 | N/A | 0 | 0
2022-08-18 09:30 | 8.1394 | 0 | N/A | 0 | 0
2022-08-18 10:00 | 7.4737 | 0 | N/A | 0 | 0
2022-08-18 10:30 | 6.8819 | 0 | N/A | 0 | 0
2022-08-18 11:00 | 6.4031 | 0 | N/A | 0 | 0
2022-08-18 11:30 | 6.0609 | 0 | N/A | 0 | 0
2022-08-18 12:00 | 6.2578 | 0 | N/A | 0 | 0
2022-08-18 12:30 | 6.3737 | 0 | N/A | 0 | 0
2022-08-18 13:00 | 5.3552 | 0 | N/A | 0 | 0
2022-08-18 13:30 | 5.344 | 0 | N/A | 0 | 0
2022-08-18 14:00 | 5.7475 | 0 | N/A | 0 | 0
2022-08-18 14:30 | 5.0499 | 0 | N/A | 0 | 0
2022-08-18 15:00 | 5.367 | 0 | N/A | 0 | 0
2022-08-18 15:30 | 5.3947 | 0 | N/A | 0 | 0
2022-08-18 16:00 | 6.2225 | 0 | N/A | 0 | 0
2022-08-18 16:30 | 6.4759 | 0 | N/A | 0 | 0
2022-08-18 17:00 | 6.8632 | 0 | N/A | 0 | 0
2022-08-18 17:30 | 7.5415 | 0 | N/A | 0 | 0
2022-08-18 18:00 | 8.4518 | 0 | N/A | 0 | 0
2022-08-18 18:30 | 8.9097 | 0 | N/A | 0 | 0
2022-08-18 19:00 | 8.7741 | 0 | N/A | 0 | 0
2022-08-18 19:30 | 8.4729 | 0 | N/A | 0 | 0
2022-08-18 20:00 | 8.1985 | 0 | N/A | 0 | 0
2022-08-18 20:30 | 7.9021 | 0 | N/A | 0 | 0
2022-08-18 21:00 | 7.3693 | 0 | N/A | 0 | 0
2022-08-18 21:30 | 7.4931 | 0 | N/A | 0 | 0
2022-08-18 22:00 | 7.3021 | 0 | N/A | 0 | 0
2022-08-18 22:30 | 6.5992 | 0 | N/A | 0 | 0
2022-08-18 23:00 | 6.378 | 0 | N/A | 0 | 0
2022-08-18 23:30 | 6.4949 | 0 | N/A | 0 | 0
2022-08-19 | 6.6579 | 0 | N/A | 0 | 0
2022-08-19 00:30 | 6.0477 | 0 | N/A | 0 | 0
2022-08-19 01:00 | 5.3599 | 0 | N/A | 0 | 0
2022-08-19 01:30 | 5.3235 | 0 | N/A | 0 | 0
2022-08-19 02:00 | 4.9975 | 0 | N/A | 0 | 0
2022-08-19 02:30 | 4.5318 | 0 | N/A | 0 | 0
2022-08-19 03:00 | 4.3416 | 0 | N/A | 0 | 0
2022-08-19 03:30 | 4.2036 | 0 | N/A | 0 | 0
2022-08-19 04:00 | 4.1918 | 0 | N/A | 0 | 0
2022-08-19 04:30 | 4.1778 | 0 | N/A | 0 | 0
2022-08-19 05:00 | 4.3305 | 0 | N/A | 0 | 0
2022-08-19 05:30 | 4.8631 | 0 | N/A | 0 | 0
2022-08-19 06:00 | 5.3523 | 0 | N/A | 0 | 0
2022-08-19 06:30 | 6.1966 | 0 | N/A | 0 | 0
2022-08-19 07:00 | 6.9414 | 0 | N/A | 0 | 0
2022-08-19 07:30 | 7.4074 | 0 | N/A | 0 | 0
2022-08-19 08:00 | 7.3067 | 0 | N/A | 0 | 0
2022-08-19 08:30 | 6.9323 | 0 | N/A | 0 | 0
2022-08-19 09:00 | 5.9991 | 0 | N/A | 0 | 0
2022-08-19 09:30 | 4.8747 | 0 | N/A | 0 | 0
2022-08-19 10:00 | 3.91 | 0 | N/A | 0 | 0
2022-08-19 10:30 | 3.0726 | 0 | N/A | 0 | 0
2022-08-19 11:00 | 2.3809 | 0 | N/A | 0 | 0
2022-08-19 11:30 | 2.4742 | 0 | N/A | 0 | 0
2022-08-19 12:00 | 2.089 | 0 | N/A | 0 | 0
2022-08-19 12:30 | 1.3178 | 0 | N/A | 0 | 0
2022-08-19 13:00 | 1.9042 | 0 | N/A | 0 | 0
2022-08-19 13:30 | 1.3709 | 0 | N/A | 0 | 0
2022-08-19 14:00 | 1.5616 | 0 | N/A | 0 | 0
2022-08-19 14:30 | 2.1229 | 0 | N/A | 0 | 0
2022-08-19 15:00 | 3.0562 | 0 | N/A | 0 | 0
2022-08-19 15:30 | 3.3393 | 0 | N/A | 0 | 0
2022-08-19 16:00 | 4.1798 | 0 | N/A | 0 | 0
2022-08-19 16:30 | 5.2615 | 0 | N/A | 0 | 0
2022-08-19 17:00 | 6.1273 | 0 | N/A | 0 | 0
2022-08-19 17:30 | 6.9778 | 0 | N/A | 0 | 0
2022-08-19 18:00 | 7.8536 | 0 | N/A | 0 | 0
2022-08-19 18:30 | 8.4803 | 0 | N/A | 0 | 0
2022-08-19 19:00 | 8.4926 | 0 | N/A | 0 | 0
2022-08-19 19:30 | 8.3155 | 0 | N/A | 0 | 0
2022-08-19 20:00 | 8.0482 | 0 | N/A | 0 | 0
2022-08-19 20:30 | 7.7253 | 0 | N/A | 0 | 0
2022-08-19 21:00 | 7.4564 | 0 | N/A | 0 | 0
2022-08-19 21:30 | 7.6073 | 0 | N/A | 0 | 0
2022-08-19 22:00 | 7.6427 | 0 | N/A | 0 | 0
2022-08-19 22:30 | 7.0113 | 0 | N/A | 0 | 0
2022-08-19 23:00 | 6.7656 | 0 | N/A | 0 | 0
2022-08-19 23:30 | 6.7434 | 0 | N/A | 0 | 0
2022-08-20 | 6.7286 | 0 | N/A | 0 | 0
2022-08-20 00:30 | 6.0285 | 0 | N/A | 0 | 0
2022-08-20 01:00 | 5.3065 | 0 | N/A | 0 | 0
2022-08-20 01:30 | 5.0956 | 0 | N/A | 0 | 0
2022-08-20 02:00 | 4.7933 | 0 | N/A | 0 | 0
2022-08-20 02:30 | 4.429 | 0 | N/A | 0 | 0
2022-08-20 03:00 | 4.1164 | 0 | N/A | 0 | 0
2022-08-20 03:30 | 3.8928 | 0 | N/A | 0 | 0
2022-08-20 04:00 | 3.7298 | 0 | N/A | 0 | 0
2022-08-20 04:30 | 3.6931 | 0 | N/A | 0 | 0
2022-08-20 05:00 | 3.7143 | 0 | N/A | 0 | 0
2022-08-20 05:30 | 3.8992 | 0 | N/A | 0 | 0
2022-08-20 06:00 | 4.0486 | 0 | N/A | 0 | 0
2022-08-20 06:30 | 4.4529 | 0 | N/A | 0 | 0
2022-08-20 07:00 | 4.8346 | 0 | N/A | 0 | 0
2022-08-20 07:30 | 4.9713 | 0 | N/A | 0 | 0
2022-08-20 08:00 | 5.4181 | 0 | N/A | 0 | 0
2022-08-20 08:30 | 5.7691 | 0 | N/A | 0 | 0
2022-08-20 09:00 | 5.705 | 0 | N/A | 0 | 0
2022-08-20 09:30 | 5.1369 | 0 | N/A | 0 | 0
2022-08-20 10:00 | 4.9271 | 0 | N/A | 0 | 0
2022-08-20 10:30 | 4.2685 | 0 | N/A | 0 | 0
2022-08-20 11:00 | 4.2721 | 0 | N/A | 0 | 0
2022-08-20 11:30 | 4.0682 | 0 | N/A | 0 | 0
2022-08-20 12:00 | 3.02 | 0 | N/A | 0 | 0
2022-08-20 12:30 | 2.8331 | 0 | N/A | 0 | 0
2022-08-20 13:00 | 2.1314 | 0 | N/A | 0 | 0
2022-08-20 13:30 | 2.2344 | 0 | N/A | 0 | 0
2022-08-20 14:00 | 2.4121 | 0 | N/A | 0 | 0
2022-08-20 14:30 | 2.5905 | 0 | N/A | 0 | 0
2022-08-20 15:00 | 2.9424 | 0 | N/A | 0 | 0
2022-08-20 15:30 | 3.8074 | 0 | N/A | 0 | 0
2022-08-20 16:00 | 4.3644 | 0 | N/A | 0 | 0
2022-08-20 16:30 | 5.5197 | 0 | N/A | 0 | 0
2022-08-20 17:00 | 6.1859 | 0 | N/A | 0 | 0
2022-08-20 17:30 | 6.8683 | 0 | N/A | 0 | 0
2022-08-20 18:00 | 7.7998 | 0 | N/A | 0 | 0
2022-08-20 18:30 | 8.2346 | 0 | N/A | 0 | 0
2022-08-20 19:00 | 8.1306 | 0 | N/A | 0 | 0
2022-08-20 19:30 | 7.8404 | 0 | N/A | 0 | 0
2022-08-20 20:00 | 7.5753 | 0 | N/A | 0 | 0
2022-08-20 20:30 | 7.3379 | 0 | N/A | 0 | 0
2022-08-20 21:00 | 7.0081 | 0 | N/A | 0 | 0
2022-08-20 21:30 | 7.1034 | 0 | N/A | 0 | 0
2022-08-20 22:00 | 7.2944 | 0 | N/A | 0 | 0
2022-08-20 22:30 | 6.9271 | 0 | N/A | 0 | 0
2022-08-20 23:00 | 6.8439 | 0 | N/A | 0 | 0
2022-08-20 23:30 | 6.9118 | 0 | N/A | 0 | 0
2022-08-21 | 7.1128 | 0 | N/A | 0 | 0
2022-08-21 00:30 | 6.535 | 0 | N/A | 0 | 0
2022-08-21 01:00 | 5.9155 | 0 | N/A | 0 | 0
2022-08-21 01:30 | 5.8058 | 0 | N/A | 0 | 0
2022-08-21 02:00 | 5.4187 | 0 | N/A | 0 | 0
2022-08-21 02:30 | 4.8954 | 0 | N/A | 0 | 0
2022-08-21 03:00 | 4.875 | 0 | N/A | 0 | 0
2022-08-21 03:30 | 5.116 | 0 | N/A | 0 | 0
2022-08-21 04:00 | 4.8014 | 0 | N/A | 0 | 0
2022-08-21 04:30 | 4.1386 | 0 | N/A | 0 | 0
2022-08-21 05:00 | 4.2883 | 0 | N/A | 0 | 0
2022-08-21 05:30 | 4.4455 | 0 | N/A | 0 | 0
2022-08-21 06:00 | 4.6452 | 0 | N/A | 0 | 0
2022-08-21 06:30 | 4.8831 | 0 | N/A | 0 | 0
2022-08-21 07:00 | 5.2147 | 0 | N/A | 0 | 0
2022-08-21 07:30 | 5.2213 | 0 | N/A | 0 | 0
2022-08-21 08:00 | 5.5359 | 0 | N/A | 0 | 0
2022-08-21 08:30 | 5.2844 | 0 | N/A | 0 | 0
2022-08-21 09:00 | 4.9979 | 0 | N/A | 0 | 0
2022-08-21 09:30 | 4.9599 | 0 | N/A | 0 | 0
2022-08-21 10:00 | 3.9299 | 0 | N/A | 0 | 0
2022-08-21 10:30 | 3.3302 | 0 | N/A | 0 | 0
2022-08-21 11:00 | 2.8452 | 0 | N/A | 0 | 0
2022-08-21 11:30 | 2.3108 | 0 | N/A | 0 | 0
2022-08-21 12:00 | 1.7041 | 0 | N/A | 0 | 0
2022-08-21 12:30 | 1.7996 | 0 | N/A | 0 | 0
2022-08-21 13:00 | 1.7318 | 0 | N/A | 0 | 0
2022-08-21 13:30 | 2.2074 | 0 | N/A | 0 | 0
2022-08-21 14:00 | 2.2534 | 0 | N/A | 0 | 0
2022-08-21 14:30 | 2.6292 | 0 | N/A | 0 | 0
2022-08-21 15:00 | 2.1976 | 0 | N/A | 0 | 0
2022-08-21 15:30 | 2.9515 | 0 | N/A | 0 | 0
2022-08-21 16:00 | 3.4823 | 0 | N/A | 0 | 0
2022-08-21 16:30 | 4.3211 | 0 | N/A | 0 | 0
2022-08-21 17:00 | 5.2953 | 0 | N/A | 0 | 0
2022-08-21 17:30 | 6.5106 | 0 | N/A | 0 | 0
2022-08-21 18:00 | 8.3735 | 0 | N/A | 0 | 0
2022-08-21 18:30 | 9.0907 | 0 | N/A | 0 | 0
2022-08-21 19:00 | 9.3886 | 0 | N/A | 0 | 0
2022-08-21 19:30 | 9.1724 | 0 | N/A | 0 | 0
2022-08-21 20:00 | 8.8639 | 0 | N/A | 0 | 0
2022-08-21 20:30 | 8.2442 | 0 | N/A | 0 | 0
2022-08-21 21:00 | 7.2293 | 0 | N/A | 0 | 0
2022-08-21 21:30 | 7.3871 | 0 | N/A | 0 | 0
2022-08-21 22:00 | 7.1305 | 0 | N/A | 0 | 0
2022-08-21 22:30 | 6.6276 | 0 | N/A | 0 | 0
2022-08-21 23:00 | 6.4115 | 0 | N/A | 0 | 0
2022-08-21 23:30 | 6.3049 | 0 | N/A | 0 | 0
2022-08-22 | 6.6528 | 0 | N/A | 0 | 0
2022-08-22 00:30 | 6.1414 | 0 | N/A | 0 | 0
2022-08-22 01:00 | 5.4222 | 0 | N/A | 0 | 0
2022-08-22 01:30 | 5.3182 | 0 | N/A | 0 | 0
2022-08-22 02:00 | 5.0934 | 0 | N/A | 0 | 0
2022-08-22 02:30 | 4.712 | 0 | N/A | 0 | 0
2022-08-22 03:00 | 4.3708 | 0 | N/A | 0 | 0
2022-08-22 03:30 | 4.0924 | 0 | N/A | 0 | 0
2022-08-22 04:00 | 3.9055 | 0 | N/A | 0 | 0
2022-08-22 04:30 | 3.8401 | 0 | N/A | 0 | 0
2022-08-22 05:00 | 4.0309 | 0 | N/A | 0 | 0
2022-08-22 05:30 | 4.3635 | 0 | N/A | 0 | 0
2022-08-22 06:00 | 4.8795 | 0 | N/A | 0 | 0
2022-08-22 06:30 | 5.6658 | 0 | N/A | 0 | 0
2022-08-22 07:00 | 6.3989 | 0 | N/A | 0 | 0
2022-08-22 07:30 | 6.8773 | 0 | N/A | 0 | 0
2022-08-22 08:00 | 7.1226 | 0 | N/A | 0 | 0
2022-08-22 08:30 | 6.3123 | 0 | N/A | 0 | 0
2022-08-22 09:00 | 5.7708 | 0 | N/A | 0 | 0
2022-08-22 09:30 | 5.5611 | 0 | N/A | 0 | 0
2022-08-22 10:00 | 4.2542 | 0 | N/A | 0 | 0
2022-08-22 10:30 | 3.6044 | 0 | N/A | 0 | 0
2022-08-22 11:00 | 3.8583 | 0 | N/A | 0 | 0
2022-08-22 11:30 | 3.5313 | 0 | N/A | 0 | 0
2022-08-22 12:00 | 3.5161 | 0 | N/A | 0 | 0
2022-08-22 12:30 | 3.6439 | 0 | N/A | 0 | 0
2022-08-22 13:00 | 3.57 | 0 | N/A | 0 | 0
2022-08-22 13:30 | 3.5703 | 0 | N/A | 0 | 0
2022-08-22 14:00 | 3.9694 | 0 | N/A | 0 | 0
2022-08-22 14:30 | 4.8207 | 0 | N/A | 0 | 0
2022-08-22 15:00 | 6.6766 | 0 | N/A | 0 | 0
2022-08-22 15:30 | 6.6364 | 0 | N/A | 0 | 0
2022-08-22 16:00 | 6.8825 | 0 | N/A | 0 | 0
2022-08-22 16:30 | 7.1854 | 0 | N/A | 0 | 0
2022-08-22 17:00 | 7.6922 | 0 | N/A | 0 | 0
2022-08-22 17:30 | 8.5128 | 0 | N/A | 0 | 0
2022-08-22 18:00 | 9.2258 | 0 | N/A | 0 | 0
2022-08-22 18:30 | 9.5164 | 0 | N/A | 0 | 0
2022-08-22 19:00 | 9.4417 | 0 | N/A | 0 | 0
2022-08-22 19:30 | 9.0382 | 0 | N/A | 0 | 0
2022-08-22 20:00 | 8.7302 | 0 | N/A | 0 | 0
2022-08-22 20:30 | 8.2828 | 0 | N/A | 0 | 0
2022-08-22 21:00 | 7.8371 | 0 | N/A | 0 | 0
2022-08-22 21:30 | 7.8109 | 0 | N/A | 0 | 0
2022-08-22 22:00 | 7.7855 | 0 | N/A | 0 | 0
2022-08-22 22:30 | 7.0712 | 0 | N/A | 0 | 0
2022-08-22 23:00 | 6.6569 | 0 | N/A | 0 | 0
2022-08-22 23:30 | 6.6649 | 0 | N/A | 0 | 0
2022-08-23 | 6.9353 | 0 | N/A | 0 | 0
2022-08-23 00:30 | 6.4061 | 0 | N/A | 0 | 0
2022-08-23 01:00 | 5.8328 | 0 | N/A | 0 | 0
2022-08-23 01:30 | 5.7234 | 0 | N/A | 0 | 0
2022-08-23 02:00 | 5.3968 | 0 | N/A | 0 | 0
2022-08-23 02:30 | 4.9894 | 0 | N/A | 0 | 0
2022-08-23 03:00 | 4.7375 | 0 | N/A | 0 | 0
2022-08-23 03:30 | 4.6442 | 0 | N/A | 0 | 0
2022-08-23 04:00 | 4.5186 | 0 | N/A | 0 | 0
2022-08-23 04:30 | 4.4427 | 0 | N/A | 0 | 0
2022-08-23 05:00 | 4.6705 | 0 | N/A | 0 | 0
2022-08-23 05:30 | 5.0946 | 0 | N/A | 0 | 0
2022-08-23 06:00 | 5.7062 | 0 | N/A | 0 | 0
2022-08-23 06:30 | 6.5539 | 0 | N/A | 0 | 0
2022-08-23 07:00 | 7.4373 | 0 | N/A | 0 | 0
2022-08-23 07:30 | 7.6452 | 0 | N/A | 0 | 0
2022-08-23 08:00 | 7.6904 | 0 | N/A | 0 | 0
2022-08-23 08:30 | 6.9749 | 0 | N/A | 0 | 0
2022-08-23 09:00 | 6.9813 | 0 | N/A | 0 | 0
2022-08-23 09:30 | 6.4125 | 0 | N/A | 0 | 0
2022-08-23 10:00 | 4.87 | 0 | N/A | 0 | 0
2022-08-23 10:30 | 4.0848 | 0 | N/A | 0 | 0
2022-08-23 11:00 | 4.3299 | 0 | N/A | 0 | 0
2022-08-23 11:30 | 5.0764 | 0 | N/A | 0 | 0
2022-08-23 12:00 | 4.4846 | 0 | N/A | 0 | 0
2022-08-23 12:30 | 4.6667 | 0 | N/A | 0 | 0
2022-08-23 13:00 | 4.229 | 0 | N/A | 0 | 0
2022-08-23 13:30 | 5.0075 | 0 | N/A | 0 | 0
2022-08-23 14:00 | 3.5528 | 0 | N/A | 0 | 0
2022-08-23 14:30 | 5.8812 | 0 | N/A | 0 | 0
2022-08-23 15:00 | 4.7688 | 0 | N/A | 0 | 0
2022-08-23 15:30 | 4.6182 | 0 | N/A | 0 | 0
2022-08-23 16:00 | 5.1648 | 0 | N/A | 0 | 0
2022-08-23 16:30 | 5.8035 | 0 | N/A | 0 | 0
2022-08-23 17:00 | 6.3568 | 0 | N/A | 0 | 0
2022-08-23 17:30 | 7.6955 | 0 | N/A | 0 | 0
2022-08-23 18:00 | 9.0564 | 0 | N/A | 0 | 0
2022-08-23 18:30 | 9.7243 | 0 | N/A | 0 | 0
2022-08-23 19:00 | 9.7935 | 0 | N/A | 0 | 0
2022-08-23 19:30 | 9.4496 | 0 | N/A | 0 | 0
2022-08-23 20:00 | 9.2381 | 0 | N/A | 0 | 0
2022-08-23 20:30 | 8.7691 | 0 | N/A | 0 | 0
2022-08-23 21:00 | 8.2557 | 0 | N/A | 0 | 0
2022-08-23 21:30 | 8.1903 | 0 | N/A | 0 | 0
2022-08-23 22:00 | 7.9868 | 0 | N/A | 0 | 0
2022-08-23 22:30 | 7.2184 | 0 | N/A | 0 | 0
2022-08-23 23:00 | 6.7689 | 0 | N/A | 0 | 0
2022-08-23 23:30 | 6.8019 | 0 | N/A | 0 | 0
2022-08-24 | 7.1546 | 0 | N/A | 0 | 0
2022-08-24 00:30 | 6.5902 | 0 | N/A | 0 | 0
2022-08-24 01:00 | 6.0067 | 0 | N/A | 0 | 0
2022-08-24 01:30 | 5.8481 | 0 | N/A | 0 | 0
2022-08-24 02:00 | 5.5156 | 0 | N/A | 0 | 0
2022-08-24 02:30 | 5.065 | 0 | N/A | 0 | 0
2022-08-24 03:00 | 4.7692 | 0 | N/A | 0 | 0
2022-08-24 03:30 | 4.5367 | 0 | N/A | 0 | 0
2022-08-24 04:00 | 4.3992 | 0 | N/A | 0 | 0
2022-08-24 04:30 | 4.3345 | 0 | N/A | 0 | 0
2022-08-24 05:00 | 4.4528 | 0 | N/A | 0 | 0
2022-08-24 05:30 | 4.7734 | 0 | N/A | 0 | 0
2022-08-24 06:00 | 5.2755 | 0 | N/A | 0 | 0
2022-08-24 06:30 | 6.0619 | 0 | N/A | 0 | 0
2022-08-24 07:00 | 6.7869 | 0 | N/A | 0 | 0
2022-08-24 07:30 | 7.1003 | 0 | N/A | 0 | 0
2022-08-24 08:00 | 7.7546 | 0 | N/A | 0 | 0
2022-08-24 08:30 | 7.8235 | 0 | N/A | 0 | 0
2022-08-24 09:00 | 7.6932 | 0 | N/A | 0 | 0
2022-08-24 09:30 | 7.4108 | 0 | N/A | 0 | 0
2022-08-24 10:00 | 7.2117 | 0 | N/A | 0 | 0
2022-08-24 10:30 | 7.0807 | 0 | N/A | 0 | 0
2022-08-24 11:00 | 7.3583 | 0 | N/A | 0 | 0
2022-08-24 11:30 | 7.2166 | 0 | N/A | 0 | 0
2022-08-24 12:00 | 7.2399 | 0 | N/A | 0 | 0
2022-08-24 12:30 | 7.1333 | 0 | N/A | 0 | 0
2022-08-24 13:00 | 7.4064 | 0 | N/A | 0 | 0
2022-08-24 13:30 | 7.514 | 0 | N/A | 0 | 0
2022-08-24 14:00 | 7.74 | 0 | N/A | 0 | 0
2022-08-24 14:30 | 7.2139 | 0 | N/A | 0 | 0
2022-08-24 15:00 | 7.379 | 0 | N/A | 0 | 0
2022-08-24 15:30 | 7.2501 | 0 | N/A | 0 | 0
2022-08-24 16:00 | 6.8723 | 0 | N/A | 0 | 0
2022-08-24 16:30 | 7.5383 | 0 | N/A | 0 | 0
2022-08-24 17:00 | 8.2043 | 0 | N/A | 0 | 0
2022-08-24 17:30 | 8.9289 | 0 | N/A | 0 | 0
2022-08-24 18:00 | 9.5239 | 0 | N/A | 0 | 0
2022-08-24 18:30 | 9.7413 | 0 | N/A | 0 | 0
2022-08-24 19:00 | 9.6233 | 0 | N/A | 0 | 0
2022-08-24 19:30 | 9.2132 | 0 | N/A | 0 | 0
2022-08-24 20:00 | 8.7903 | 0 | N/A | 0 | 0
2022-08-24 20:30 | 8.3937 | 0 | N/A | 0 | 0
2022-08-24 21:00 | 7.9593 | 0 | N/A | 0 | 0
2022-08-24 21:30 | 7.9754 | 0 | N/A | 0 | 0
2022-08-24 22:00 | 7.7557 | 0 | N/A | 0 | 0
2022-08-24 22:30 | 6.9662 | 0 | N/A | 0 | 0
2022-08-24 23:00 | 6.6087 | 0 | N/A | 0 | 0
2022-08-24 23:30 | 6.6312 | 0 | N/A | 0 | 0
2022-08-25 | 6.8792 | 0 | N/A | 0 | 0
2022-08-25 00:30 | 6.297 | 0 | N/A | 0 | 0
2022-08-25 01:00 | 5.7132 | 0 | N/A | 0 | 0
2022-08-25 01:30 | 5.4554 | 0 | N/A | 0 | 0
2022-08-25 02:00 | 5.142 | 0 | N/A | 0 | 0
2022-08-25 02:30 | 4.5906 | 0 | N/A | 0 | 0
2022-08-25 03:00 | 4.2481 | 0 | N/A | 0 | 0
2022-08-25 03:30 | 4.1473 | 0 | N/A | 0 | 0
2022-08-25 04:00 | 4.0393 | 0 | N/A | 0 | 0
2022-08-25 04:30 | 3.9888 | 0 | N/A | 0 | 0
2022-08-25 05:00 | 4.0648 | 0 | N/A | 0 | 0
2022-08-25 05:30 | 4.4354 | 0 | N/A | 0 | 0
2022-08-25 06:00 | 4.8185 | 0 | N/A | 0 | 0
2022-08-25 06:30 | 5.6817 | 0 | N/A | 0 | 0
2022-08-25 07:00 | 6.3223 | 0 | N/A | 0 | 0
2022-08-25 07:30 | 6.8173 | 0 | N/A | 0 | 0
2022-08-25 08:00 | 7.2081 | 0 | N/A | 0 | 0
2022-08-25 08:30 | 7.4555 | 0 | N/A | 0 | 0
2022-08-25 09:00 | 7.1333 | 0 | N/A | 0 | 0
2022-08-25 09:30 | 6.7629 | 0 | N/A | 0 | 0
2022-08-25 10:00 | 6.0727 | 0 | N/A | 0 | 0
2022-08-25 10:30 | 5.6451 | 0 | N/A | 0 | 0
2022-08-25 11:00 | 4.8189 | 0 | N/A | 0 | 0
2022-08-25 11:30 | 4.5834 | 0 | N/A | 0 | 0
2022-08-25 12:00 | 4.2278 | 0 | N/A | 0 | 0
2022-08-25 12:30 | 3.9111 | 0 | N/A | 0 | 0
2022-08-25 13:00 | 3.8208 | 0 | N/A | 0 | 0
2022-08-25 13:30 | 4.0552 | 0 | N/A | 0 | 0
2022-08-25 14:00 | 3.7755 | 0 | N/A | 0 | 0
2022-08-25 14:30 | 4.4475 | 0 | N/A | 0 | 0
2022-08-25 15:00 | 4.0354 | 0 | N/A | 0 | 0
2022-08-25 15:30 | 4.9102 | 0 | N/A | 0 | 0
2022-08-25 16:00 | 4.7671 | 0 | N/A | 0 | 0
2022-08-25 16:30 | 5.039 | 0 | N/A | 0 | 0
2022-08-25 17:00 | 5.8927 | 0 | N/A | 0 | 0
2022-08-25 17:30 | 7.1527 | 0 | N/A | 0 | 0
2022-08-25 18:00 | 8.2113 | 0 | N/A | 0 | 0
2022-08-25 18:30 | 8.7325 | 0 | N/A | 0 | 0
2022-08-25 19:00 | 8.8066 | 0 | N/A | 0 | 0
2022-08-25 19:30 | 7.993 | 0 | N/A | 0 | 0
2022-08-25 20:00 | 7.8389 | 0 | N/A | 0 | 0
2022-08-25 20:30 | 7.5444 | 0 | N/A | 0 | 0
2022-08-25 21:00 | 7.2948 | 0 | N/A | 0 | 0
2022-08-25 21:30 | 7.2956 | 0 | N/A | 0 | 0
2022-08-25 22:00 | 7.2369 | 0 | N/A | 0 | 0
2022-08-25 22:30 | 6.6044 | 0 | N/A | 0 | 0
2022-08-25 23:00 | 6.3933 | 0 | N/A | 0 | 0
2022-08-25 23:30 | 6.4685 | 0 | N/A | 0 | 0
2022-08-26 | 6.6127 | 0 | N/A | 0 | 0
2022-08-27 00:30 | 6.0532 | 0 | N/A | 0 | 0
2022-08-27 01:00 | 5.4886 | 0 | N/A | 0 | 0
2022-08-27 01:30 | 5.3621 | 0 | N/A | 0 | 0
2022-08-27 02:00 | 5.0135 | 0 | N/A | 0 | 0
2022-08-27 02:30 | 4.4929 | 0 | N/A | 0 | 0
2022-08-27 03:00 | 4.1444 | 0 | N/A | 0 | 0
2022-08-27 03:30 | 4.0397 | 0 | N/A | 0 | 0
2022-08-27 04:00 | 4.0323 | 0 | N/A | 0 | 0
2022-08-27 04:30 | 3.9564 | 0 | N/A | 0 | 0
2022-08-27 05:00 | 4.0326 | 0 | N/A | 0 | 0
2022-08-27 05:30 | 4.1795 | 0 | N/A | 0 | 0
2022-08-27 06:00 | 4.3572 | 0 | N/A | 0 | 0
2022-08-27 06:30 | 4.7894 | 0 | N/A | 0 | 0
2022-08-27 07:00 | 5.1323 | 0 | N/A | 0 | 0
2022-08-27 07:30 | 5.1607 | 0 | N/A | 0 | 0
2022-08-27 08:00 | 5.3857 | 0 | N/A | 0 | 0
2022-08-27 08:30 | 5.8319 | 0 | N/A | 0 | 0
2022-08-27 09:00 | 6.0579 | 0 | N/A | 0 | 0
2022-08-27 09:30 | 5.6672 | 0 | N/A | 0 | 0
2022-08-27 10:00 | 4.9312 | 0 | N/A | 0 | 0
2022-08-27 10:30 | 4.1776 | 0 | N/A | 0 | 0
2022-08-27 11:00 | 3.6835 | 0 | N/A | 0 | 0
2022-08-27 11:30 | 2.7202 | 0 | N/A | 0 | 0
2022-08-27 12:00 | 2.5516 | 0 | N/A | 0 | 0
2022-08-27 12:30 | 1.4248 | 0 | N/A | 0 | 0
2022-08-27 13:00 | 1.666 | 0 | N/A | 0 | 0
2022-08-27 13:30 | 1.3003 | 0 | N/A | 0 | 0
2022-08-27 14:00 | 2.3533 | 0 | N/A | 0 | 0
2022-08-27 14:30 | 2.8503 | 0 | N/A | 0 | 0
2022-08-27 15:00 | 2.9863 | 0 | N/A | 0 | 0
2022-08-27 15:30 | 2.9427 | 0 | N/A | 0 | 0
2022-08-27 16:00 | 3.581 | 0 | N/A | 0 | 0
2022-08-27 16:30 | 5.0701 | 0 | N/A | 0 | 0
2022-08-27 17:00 | 5.159 | 0 | N/A | 0 | 0
2022-08-27 17:30 | 5.6841 | 0 | N/A | 0 | 0
2022-08-27 18:00 | 6.9056 | 0 | N/A | 0 | 0
2022-08-27 18:30 | 7.6021 | 0 | N/A | 0 | 0
2022-08-27 19:00 | 7.853 | 0 | N/A | 0 | 0
2022-08-27 19:30 | 7.7349 | 0 | N/A | 0 | 0
2022-08-27 20:00 | 7.4273 | 0 | N/A | 0 | 0
2022-08-27 20:30 | 7.1845 | 0 | N/A | 0 | 0
2022-08-27 21:00 | 6.9646 | 0 | N/A | 0 | 0
2022-08-27 21:30 | 7.1516 | 0 | N/A | 0 | 0
2022-08-27 22:00 | 7.3658 | 0 | N/A | 0 | 0
2022-08-27 22:30 | 6.9424 | 0 | N/A | 0 | 0
2022-08-27 23:00 | 6.8402 | 0 | N/A | 0 | 0
2022-08-27 23:30 | 6.9552 | 0 | N/A | 0 | 0
2022-08-28 | 7.125 | 0 | N/A | 0 | 0
2022-08-28 00:30 | 6.5979 | 0 | N/A | 0 | 0
2022-08-28 01:00 | 5.8678 | 0 | N/A | 0 | 0
2022-08-28 01:30 | 5.5882 | 0 | N/A | 0 | 0
2022-08-28 02:00 | 5.2203 | 0 | N/A | 0 | 0
2022-08-28 02:30 | 4.7188 | 0 | N/A | 0 | 0
2022-08-28 03:00 | 4.5133 | 0 | N/A | 0 | 0
2022-08-28 03:30 | 4.4061 | 0 | N/A | 0 | 0
2022-08-28 04:00 | 4.1648 | 0 | N/A | 0 | 0
2022-08-28 04:30 | 4.0541 | 0 | N/A | 0 | 0
2022-08-28 05:00 | 4.0288 | 0 | N/A | 0 | 0
2022-08-28 05:30 | 4.0857 | 0 | N/A | 0 | 0
2022-08-28 06:00 | 4.2306 | 0 | N/A | 0 | 0
2022-08-28 06:30 | 4.5498 | 0 | N/A | 0 | 0
2022-08-28 07:00 | 4.7312 | 0 | N/A | 0 | 0
2022-08-28 07:30 | 4.8622 | 0 | N/A | 0 | 0
2022-08-28 08:00 | 4.8088 | 0 | N/A | 0 | 0
2022-08-28 08:30 | 4.5476 | 0 | N/A | 0 | 0
2022-08-28 09:00 | 4.1172 | 0 | N/A | 0 | 0
2022-08-28 09:30 | 3.4186 | 0 | N/A | 0 | 0
2022-08-28 10:00 | 2.8872 | 0 | N/A | 0 | 0
2022-08-28 10:30 | 1.7281 | 0 | N/A | 0 | 0
2022-08-28 11:00 | 1.2281 | 0 | N/A | 0 | 0
2022-08-28 11:30 | 1.0587 | 0 | N/A | 0 | 0
2022-08-28 12:00 | 0.88003 | 0 | N/A | 0 | 0
2022-08-28 12:30 | 0.86882 | 0 | N/A | 0 | 0
2022-08-28 13:00 | 1.1121 | 0 | N/A | 0 | 0
2022-08-28 13:30 | 0.97092 | 0 | N/A | 0 | 0
2022-08-28 14:00 | 1.2172 | 0 | N/A | 0 | 0
2022-08-28 14:30 | 1.5958 | 0 | N/A | 0 | 0
2022-08-28 15:00 | 1.6962 | 0 | N/A | 0 | 0
2022-08-28 15:30 | 2.2615 | 0 | N/A | 0 | 0
2022-08-28 16:00 | 2.8654 | 0 | N/A | 0 | 0
2022-08-28 16:30 | 3.5865 | 0 | N/A | 0 | 0
2022-08-28 17:00 | 4.7183 | 0 | N/A | 0 | 0
2022-08-28 17:30 | 5.8562 | 0 | N/A | 0 | 0
2022-08-28 18:00 | 7.0747 | 0 | N/A | 0 | 0
2022-08-28 18:30 | 7.7479 | 0 | N/A | 0 | 0
2022-08-28 19:00 | 8.0025 | 0 | N/A | 0 | 0
2022-08-28 19:30 | 7.6519 | 0 | N/A | 0 | 0
2022-08-28 20:00 | 7.4184 | 0 | N/A | 0 | 0
2022-08-28 20:30 | 6.9985 | 0 | N/A | 0 | 0
2022-08-28 21:00 | 6.6746 | 0 | N/A | 0 | 0
2022-08-28 21:30 | 6.776 | 0 | N/A | 0 | 0
2022-08-28 22:00 | 6.7187 | 0 | N/A | 0 | 0
2022-08-28 22:30 | 6.4094 | 0 | N/A | 0 | 0
2022-08-28 23:00 | 6.264 | 0 | N/A | 0 | 0
2022-08-28 23:30 | 6.1569 | 0 | N/A | 0 | 0
2022-08-29 | 6.4307 | 0 | N/A | 0 | 0
2022-08-30 00:30 | 5.4004 | 0 | N/A | 0 | 0
2022-08-30 01:00 | 4.7953 | 0 | N/A | 0 | 0
2022-08-30 01:30 | 4.6212 | 0 | N/A | 0 | 0
2022-08-30 02:00 | 4.2654 | 0 | N/A | 0 | 0
2022-08-30 02:30 | 3.9366 | 0 | N/A | 0 | 0
2022-08-30 03:00 | 3.7189 | 0 | N/A | 0 | 0
2022-08-30 03:30 | 3.5628 | 0 | N/A | 0 | 0
2022-08-30 04:00 | 3.5838 | 0 | N/A | 0 | 0
2022-08-30 04:30 | 3.576 | 0 | N/A | 0 | 0
2022-08-30 05:00 | 3.8143 | 0 | N/A | 0 | 0
2022-08-30 05:30 | 4.1599 | 0 | N/A | 0 | 0
2022-08-30 06:00 | 4.6145 | 0 | N/A | 0 | 0
2022-08-30 06:30 | 5.3926 | 0 | N/A | 0 | 0
2022-08-30 07:00 | 6.1646 | 0 | N/A | 0 | 0
2022-08-30 07:30 | 6.7661 | 0 | N/A | 0 | 0
2022-08-30 08:00 | 7.722 | 0 | N/A | 0 | 0
2022-08-30 08:30 | 7.6146 | 0 | N/A | 0 | 0
2022-08-30 09:00 | 7.1085 | 0 | N/A | 0 | 0
2022-08-30 09:30 | 6.431 | 0 | N/A | 0 | 0
2022-08-30 10:00 | 6.5168 | 0 | N/A | 0 | 0
2022-08-30 10:30 | 6.2316 | 0 | N/A | 0 | 0
2022-08-30 11:00 | 6.1249 | 0 | N/A | 0 | 0
2022-08-30 11:30 | 6.2214 | 0 | N/A | 0 | 0
2022-08-30 12:00 | 6.3065 | 0 | N/A | 0 | 0
2022-08-30 12:30 | 6.5564 | 0 | N/A | 0 | 0
2022-08-30 13:00 | 6.5107 | 0 | N/A | 0 | 0
2022-08-30 13:30 | 6.5329 | 0 | N/A | 0 | 0
2022-08-30 14:00 | 6.0912 | 0 | N/A | 0 | 0
2022-08-30 14:30 | 6.0381 | 0 | N/A | 0 | 0
2022-08-30 15:00 | 6.1363 | 0 | N/A | 0 | 0
2022-08-30 15:30 | 6.2249 | 0 | N/A | 0 | 0
2022-08-30 16:00 | 6.5169 | 0 | N/A | 0 | 0
2022-08-30 16:30 | 6.8947 | 0 | N/A | 0 | 0
2022-08-30 17:00 | 7.5497 | 0 | N/A | 0 | 0
2022-08-30 17:30 | 8.374 | 0 | N/A | 0 | 0
2022-08-30 18:00 | 9.2723 | 0 | N/A | 0 | 0
2022-08-30 18:30 | 9.5957 | 0 | N/A | 0 | 0
2022-08-30 19:00 | 9.751 | 0 | N/A | 0 | 0
2022-08-30 19:30 | 9.3138 | 0 | N/A | 0 | 0
2022-08-30 20:00 | 9.0858 | 0 | N/A | 0 | 0
2022-08-30 20:30 | 8.6613 | 0 | N/A | 0 | 0
2022-08-30 21:00 | 8.1876 | 0 | N/A | 0 | 0
2022-08-30 21:30 | 8.1274 | 0 | N/A | 0 | 0
2022-08-30 22:00 | 7.9466 | 0 | N/A | 0 | 0
2022-08-30 22:30 | 7.1627 | 0 | N/A | 0 | 0
2022-08-30 23:00 | 6.8434 | 0 | N/A | 0 | 0
2022-08-30 23:30 | 6.8529 | 0 | N/A | 0 | 0
2022-08-31 | 7.0862 | 0 | N/A | 0 | 0
2022-08-31 00:30 | 6.4533 | 0 | N/A | 0 | 0
2022-08-31 01:00 | 5.8253 | 0 | N/A | 0 | 0
2022-08-31 01:30 | 5.713 | 0 | N/A | 0 | 0
2022-08-31 02:00 | 5.3807 | 0 | N/A | 0 | 0
2022-08-31 02:30 | 4.8577 | 0 | N/A | 0 | 0
2022-08-31 03:00 | 4.631 | 0 | N/A | 0 | 0
2022-08-31 03:30 | 4.5019 | 0 | N/A | 0 | 0
2022-08-31 04:00 | 4.39 | 0 | N/A | 0 | 0
2022-08-31 04:30 | 4.401 | 0 | N/A | 0 | 0
2022-08-31 05:00 | 4.5489 | 0 | N/A | 0 | 0
2022-08-31 05:30 | 4.9866 | 0 | N/A | 0 | 0
2022-08-31 06:00 | 5.5545 | 0 | N/A | 0 | 0
2022-08-31 06:30 | 6.5509 | 0 | N/A | 0 | 0
2022-08-31 07:00 | 7.345 | 0 | N/A | 0 | 0
2022-08-31 07:30 | 7.8538 | 0 | N/A | 0 | 0
2022-08-31 08:00 | 8.0439 | 0 | N/A | 0 | 0
2022-08-31 08:30 | 7.3281 | 0 | N/A | 0 | 0
2022-08-31 09:00 | 6.4495 | 0 | N/A | 0 | 0
2022-08-31 09:30 | 5.241 | 0 | N/A | 0 | 0
2022-08-31 10:00 | 4.0632 | 0 | N/A | 0 | 0
2022-08-31 10:30 | 3.2467 | 0 | N/A | 0 | 0
2022-08-31 11:00 | 2.9614 | 0 | N/A | 0 | 0
2022-08-31 11:30 | 3.1767 | 0 | N/A | 0 | 0
2022-08-31 12:00 | 3.3567 | 0 | N/A | 0 | 0
2022-08-31 12:30 | 3.12 | 0 | N/A | 0 | 0
2022-08-31 13:00 | 3.0369 | 0 | N/A | 0 | 0
2022-08-31 13:30 | 3.0717 | 0 | N/A | 0 | 0
2022-08-31 14:00 | 3.0984 | 0 | N/A | 0 | 0
2022-08-31 14:30 | 3.4909 | 0 | N/A | 0 | 0
2022-08-31 15:00 | 3.13 | 0 | N/A | 0 | 0
2022-08-31 15:30 | 3.6366 | 0 | N/A | 0 | 0
2022-08-31 16:00 | 3.742 | 0 | N/A | 0 | 0
2022-08-31 16:30 | 3.8707 | 0 | N/A | 0 | 0
2022-08-31 17:00 | 4.8746 | 0 | N/A | 0 | 0
2022-08-31 17:30 | 5.9701 | 0 | N/A | 0 | 0
2022-08-31 18:00 | 7.3422 | 0 | N/A | 0 | 0
2022-08-31 18:30 | 8.1676 | 0 | N/A | 0 | 0
2022-08-31 19:00 | 8.6528 | 0 | N/A | 0 | 0
2022-08-31 19:30 | 8.5883 | 0 | N/A | 0 | 0
2022-08-31 20:00 | 8.3969 | 0 | N/A | 0 | 0
2022-08-31 20:30 | 7.9731 | 0 | N/A | 0 | 0
2022-08-31 21:00 | 7.691 | 0 | N/A | 0 | 0
2022-08-31 21:30 | 7.8745 | 0 | N/A | 0 | 0
2022-08-31 22:00 | 7.8387 | 0 | N/A | 0 | 0
2022-08-31 22:30 | 7.236 | 0 | N/A | 0 | 0
2022-08-31 23:00 | 6.7638 | 0 | N/A | 0 | 0
2022-08-31 23:30 | 6.7441 | 0 | N/A | 0 | 0
2022-09-01 | 6.9274 | 0 | N/A | 0 | 0
2022-09-03 00:30 | 6.6016 | 0 | N/A | 0 | 0
2022-09-03 01:00 | 5.8495 | 0 | N/A | 0 | 0
2022-09-03 01:30 | 5.7069 | 0 | N/A | 0 | 0
2022-09-03 02:00 | 5.4244 | 0 | N/A | 0 | 0
2022-09-03 02:30 | 4.972 | 0 | N/A | 0 | 0
2022-09-03 03:00 | 4.5753 | 0 | N/A | 0 | 0
2022-09-03 03:30 | 4.4162 | 0 | N/A | 0 | 0
2022-09-03 04:00 | 4.227 | 0 | N/A | 0 | 0
2022-09-03 04:30 | 4.1648 | 0 | N/A | 0 | 0
2022-09-03 05:00 | 4.164 | 0 | N/A | 0 | 0
2022-09-03 05:30 | 4.2528 | 0 | N/A | 0 | 0
2022-09-03 06:00 | 4.4107 | 0 | N/A | 0 | 0
2022-09-03 06:30 | 4.8911 | 0 | N/A | 0 | 0
2022-09-03 07:00 | 5.1874 | 0 | N/A | 0 | 0
2022-09-03 07:30 | 5.1908 | 0 | N/A | 0 | 0
2022-09-03 08:00 | 5.4161 | 0 | N/A | 0 | 0
2022-09-03 08:30 | 5.4148 | 0 | N/A | 0 | 0
2022-09-03 09:00 | 5.3423 | 0 | N/A | 0 | 0
2022-09-03 09:30 | 5.2115 | 0 | N/A | 0 | 0
2022-09-03 10:00 | 4.3942 | 0 | N/A | 0 | 0
2022-09-03 10:30 | 4.072 | 0 | N/A | 0 | 0
2022-09-03 11:00 | 4.014 | 0 | N/A | 0 | 0
2022-09-03 11:30 | 3.286 | 0 | N/A | 0 | 0
2022-09-03 12:00 | 3.3057 | 0 | N/A | 0 | 0
2022-09-03 12:30 | 2.5285 | 0 | N/A | 0 | 0
2022-09-03 13:00 | 2.6864 | 0 | N/A | 0 | 0
2022-09-03 13:30 | 2.2857 | 0 | N/A | 0 | 0
2022-09-03 14:00 | 2.9367 | 0 | N/A | 0 | 0
2022-09-03 14:30 | 3.8869 | 0 | N/A | 0 | 0
2022-09-03 15:00 | 3.9033 | 0 | N/A | 0 | 0
2022-09-03 15:30 | 3.1979 | 0 | N/A | 0 | 0
2022-09-03 16:00 | 4.3662 | 0 | N/A | 0 | 0
2022-09-03 16:30 | 5.6547 | 0 | N/A | 0 | 0
2022-09-03 17:00 | 5.8559 | 0 | N/A | 0 | 0
2022-09-03 17:30 | 6.4234 | 0 | N/A | 0 | 0
2022-09-03 18:00 | 7.4974 | 0 | N/A | 0 | 0
2022-09-03 18:30 | 7.7188 | 0 | N/A | 0 | 0
2022-09-03 19:00 | 7.8347 | 0 | N/A | 0 | 0
2022-09-03 19:30 | 7.6205 | 0 | N/A | 0 | 0
2022-09-03 20:00 | 7.4796 | 0 | N/A | 0 | 0
2022-09-03 20:30 | 7.1836 | 0 | N/A | 0 | 0
2022-09-03 21:00 | 6.7504 | 0 | N/A | 0 | 0
2022-09-03 21:30 | 7.0634 | 0 | N/A | 0 | 0
2022-09-03 22:00 | 7.183 | 0 | N/A | 0 | 0
2022-09-03 22:30 | 6.9146 | 0 | N/A | 0 | 0
2022-09-03 23:00 | 6.8635 | 0 | N/A | 0 | 0
2022-09-03 23:30 | 6.734 | 0 | N/A | 0 | 0
2022-09-04 | 6.8208 | 0 | N/A | 0 | 0
2022-09-04 00:30 | 6.1928 | 0 | N/A | 0 | 0
2022-09-04 01:00 | 5.4596 | 0 | N/A | 0 | 0
2022-09-04 01:30 | 5.3152 | 0 | N/A | 0 | 0
2022-09-04 02:00 | 5.0473 | 0 | N/A | 0 | 0
2022-09-04 02:30 | 4.5343 | 0 | N/A | 0 | 0
2022-09-04 03:00 | 4.2472 | 0 | N/A | 0 | 0
2022-09-04 03:30 | 4.0667 | 0 | N/A | 0 | 0
2022-09-04 04:00 | 3.9186 | 0 | N/A | 0 | 0
2022-09-04 04:30 | 3.9154 | 0 | N/A | 0 | 0
2022-09-04 05:00 | 3.862 | 0 | N/A | 0 | 0
2022-09-04 05:30 | 3.8497 | 0 | N/A | 0 | 0
2022-09-04 06:00 | 3.9772 | 0 | N/A | 0 | 0
2022-09-04 06:30 | 4.3125 | 0 | N/A | 0 | 0
2022-09-04 07:00 | 4.5476 | 0 | N/A | 0 | 0
2022-09-04 07:30 | 4.6163 | 0 | N/A | 0 | 0
2022-09-04 08:00 | 4.9545 | 0 | N/A | 0 | 0
2022-09-04 08:30 | 5.1982 | 0 | N/A | 0 | 0
2022-09-04 09:00 | 5.1552 | 0 | N/A | 0 | 0
2022-09-04 09:30 | 4.8034 | 0 | N/A | 0 | 0
2022-09-04 10:00 | 5.0372 | 0 | N/A | 0 | 0
2022-09-04 10:30 | 4.9629 | 0 | N/A | 0 | 0
2022-09-04 11:00 | 4.8106 | 0 | N/A | 0 | 0
2022-09-04 11:30 | 4.4493 | 0 | N/A | 0 | 0
2022-09-04 12:00 | 4.2128 | 0 | N/A | 0 | 0
2022-09-04 12:30 | 4.0411 | 0 | N/A | 0 | 0
2022-09-04 13:00 | 3.9592 | 0 | N/A | 0 | 0
2022-09-04 13:30 | 4.3417 | 0 | N/A | 0 | 0
2022-09-04 14:00 | 3.9285 | 0 | N/A | 0 | 0
2022-09-04 14:30 | 3.7324 | 0 | N/A | 0 | 0
2022-09-04 15:00 | 4.7653 | 0 | N/A | 0 | 0
2022-09-04 15:30 | 5.0925 | 0 | N/A | 0 | 0
2022-09-04 16:00 | 4.9507 | 0 | N/A | 0 | 0
2022-09-04 16:30 | 5.9365 | 0 | N/A | 0 | 0
2022-09-04 17:00 | 6.7142 | 0 | N/A | 0 | 0
2022-09-04 17:30 | 7.2809 | 0 | N/A | 0 | 0
2022-09-04 18:00 | 7.9508 | 0 | N/A | 0 | 0
2022-09-04 18:30 | 8.2945 | 0 | N/A | 0 | 0
2022-09-04 19:00 | 8.3715 | 0 | N/A | 0 | 0
2022-09-04 19:30 | 8.1399 | 0 | N/A | 0 | 0
2022-09-04 20:00 | 7.878 | 0 | N/A | 0 | 0
2022-09-04 20:30 | 7.5776 | 0 | N/A | 0 | 0
2022-09-04 21:00 | 7.2605 | 0 | N/A | 0 | 0
2022-09-04 21:30 | 7.4818 | 0 | N/A | 0 | 0
2022-09-04 22:00 | 7.3415 | 0 | N/A | 0 | 0
2022-09-04 22:30 | 6.7812 | 0 | N/A | 0 | 0
2022-09-04 23:00 | 6.6153 | 0 | N/A | 0 | 0
2022-09-04 23:30 | 6.4709 | 0 | N/A | 0 | 0
2022-09-05 | 6.7577 | 0 | N/A | 0 | 0
2022-09-05 00:30 | 6.2692 | 0 | N/A | 0 | 0
2022-09-05 01:00 | 5.57 | 0 | N/A | 0 | 0
2022-09-05 01:30 | 5.4211 | 0 | N/A | 0 | 0
2022-09-05 02:00 | 5.2328 | 0 | N/A | 0 | 0
2022-09-05 02:30 | 4.8128 | 0 | N/A | 0 | 0
2022-09-05 03:00 | 4.5237 | 0 | N/A | 0 | 0
2022-09-05 03:30 | 4.3672 | 0 | N/A | 0 | 0
2022-09-05 04:00 | 4.2617 | 0 | N/A | 0 | 0
2022-09-05 04:30 | 4.2123 | 0 | N/A | 0 | 0
2022-09-05 05:00 | 4.2704 | 0 | N/A | 0 | 0
2022-09-05 05:30 | 4.6616 | 0 | N/A | 0 | 0
2022-09-05 06:00 | 5.0536 | 0 | N/A | 0 | 0
2022-09-05 06:30 | 5.9021 | 0 | N/A | 0 | 0
2022-09-05 07:00 | 6.7068 | 0 | N/A | 0 | 0
2022-09-05 07:30 | 7.1417 | 0 | N/A | 0 | 0
2022-09-05 08:00 | 8.0095 | 0 | N/A | 0 | 0
2022-09-05 08:30 | 7.3967 | 0 | N/A | 0 | 0
2022-09-05 09:00 | 6.4169 | 0 | N/A | 0 | 0
2022-09-05 09:30 | 6.0073 | 0 | N/A | 0 | 0
2022-09-05 10:00 | 5.5708 | 0 | N/A | 0 | 0
2022-09-05 10:30 | 5.77 | 0 | N/A | 0 | 0
2022-09-05 11:00 | 4.5152 | 0 | N/A | 0 | 0
2022-09-05 11:30 | 3.3767 | 0 | N/A | 0 | 0
2022-09-05 12:00 | 3.5553 | 0 | N/A | 0 | 0
2022-09-05 12:30 | 3.3039 | 0 | N/A | 0 | 0
2022-09-05 13:00 | 2.7437 | 0 | N/A | 0 | 0
2022-09-05 13:30 | 2.6127 | 0 | N/A | 0 | 0
2022-09-05 14:00 | 2.9185 | 0 | N/A | 0 | 0
2022-09-05 14:30 | 2.5751 | 0 | N/A | 0 | 0
2022-09-05 15:00 | 2.8079 | 0 | N/A | 0 | 0
2022-09-05 15:30 | 3.5768 | 0 | N/A | 0 | 0
2022-09-05 16:00 | 4.1064 | 0 | N/A | 0 | 0
2022-09-05 16:30 | 4.663 | 0 | N/A | 0 | 0
2022-09-05 17:00 | 5.5405 | 0 | N/A | 0 | 0
2022-09-05 17:30 | 6.7004 | 0 | N/A | 0 | 0
2022-09-05 18:00 | 7.9769 | 0 | N/A | 0 | 0
2022-09-05 18:30 | 8.8415 | 0 | N/A | 0 | 0
2022-09-05 19:00 | 9.1832 | 0 | N/A | 0 | 0
2022-09-05 19:30 | 8.954 | 0 | N/A | 0 | 0
2022-09-05 20:00 | 8.5511 | 0 | N/A | 0 | 0
2022-09-05 20:30 | 8.1378 | 0 | N/A | 0 | 0
2022-09-05 21:00 | 7.6781 | 0 | N/A | 0 | 0
2022-09-05 21:30 | 7.6343 | 0 | N/A | 0 | 0
2022-09-05 22:00 | 7.6239 | 0 | N/A | 0 | 0
2022-09-05 22:30 | 6.8385 | 0 | N/A | 0 | 0
2022-09-05 23:00 | 6.5027 | 0 | N/A | 0 | 0
2022-09-05 23:30 | 6.5195 | 0 | N/A | 0 | 0
2022-09-06 | 6.685 | 0 | N/A | 0 | 0
2022-09-06 00:30 | 6.0902 | 0 | N/A | 0 | 0
2022-09-06 01:00 | 5.4764 | 0 | N/A | 0 | 0
2022-09-06 01:30 | 5.3439 | 0 | N/A | 0 | 0
2022-09-06 02:00 | 5.1446 | 0 | N/A | 0 | 0
2022-09-06 02:30 | 4.6566 | 0 | N/A | 0 | 0
2022-09-06 03:00 | 4.4246 | 0 | N/A | 0 | 0
2022-09-06 03:30 | 4.2807 | 0 | N/A | 0 | 0
2022-09-06 04:00 | 4.2915 | 0 | N/A | 0 | 0
2022-09-06 04:30 | 4.2968 | 0 | N/A | 0 | 0
2022-09-06 05:00 | 4.4515 | 0 | N/A | 0 | 0
2022-09-06 05:30 | 4.9049 | 0 | N/A | 0 | 0
2022-09-06 06:00 | 5.3685 | 0 | N/A | 0 | 0
2022-09-06 06:30 | 6.3203 | 0 | N/A | 0 | 0
2022-09-06 07:00 | 6.9377 | 0 | N/A | 0 | 0
2022-09-06 07:30 | 7.0341 | 0 | N/A | 0 | 0
2022-09-06 08:00 | 7.7447 | 0 | N/A | 0 | 0
2022-09-06 08:30 | 7.4281 | 0 | N/A | 0 | 0
2022-09-06 09:00 | 6.5155 | 0 | N/A | 0 | 0
2022-09-06 09:30 | 5.7105 | 0 | N/A | 0 | 0
2022-09-06 10:00 | 4.2764 | 0 | N/A | 0 | 0
2022-09-06 10:30 | 2.7626 | 0 | N/A | 0 | 0
2022-09-06 11:00 | 1.8354 | 0 | N/A | 0 | 0
2022-09-06 11:30 | 1.066 | 0 | N/A | 0 | 0
2022-09-06 12:00 | 0.94546 | 0 | N/A | 0 | 0
2022-09-06 12:30 | 1.2083 | 0 | N/A | 0 | 0
2022-09-06 13:00 | 1.01 | 0 | N/A | 0 | 0
2022-09-06 13:30 | 1.6976 | 0 | N/A | 0 | 0
2022-09-06 14:00 | 2.1419 | 0 | N/A | 0 | 0
2022-09-06 14:30 | 3.1955 | 0 | N/A | 0 | 0
2022-09-06 15:00 | 3.1813 | 0 | N/A | 0 | 0
2022-09-06 15:30 | 3.0046 | 0 | N/A | 0 | 0
2022-09-06 16:00 | 3.0737 | 0 | N/A | 0 | 0
2022-09-06 16:30 | 3.6717 | 0 | N/A | 0 | 0
2022-09-06 17:00 | 4.8468 | 0 | N/A | 0 | 0
2022-09-06 17:30 | 5.8195 | 0 | N/A | 0 | 0
2022-09-06 18:00 | 6.9169 | 0 | N/A | 0 | 0
2022-09-06 18:30 | 7.7976 | 0 | N/A | 0 | 0
2022-09-06 19:00 | 8.1682 | 0 | N/A | 0 | 0
2022-09-06 19:30 | 8.1229 | 0 | N/A | 0 | 0
2022-09-06 20:00 | 7.8932 | 0 | N/A | 0 | 0
2022-09-06 20:30 | 7.5773 | 0 | N/A | 0 | 0
2022-09-06 21:00 | 7.3269 | 0 | N/A | 0 | 0
2022-09-06 21:30 | 7.3776 | 0 | N/A | 0 | 0
2022-09-06 22:00 | 7.2201 | 0 | N/A | 0 | 0
2022-09-06 22:30 | 6.6023 | 0 | N/A | 0 | 0
2022-09-06 23:00 | 6.2597 | 0 | N/A | 0 | 0
2022-09-06 23:30 | 6.2189 | 0 | N/A | 0 | 0
2022-09-07 | 6.5627 | 0 | N/A | 0 | 0
2022-09-07 00:30 | 5.8622 | 0 | N/A | 0 | 0
2022-09-07 01:00 | 5.28 | 0 | N/A | 0 | 0
2022-09-07 01:30 | 5.1912 | 0 | N/A | 0 | 0
2022-09-07 02:00 | 4.939 | 0 | N/A | 0 | 0
2022-09-07 02:30 | 4.4785 | 0 | N/A | 0 | 0
2022-09-07 03:00 | 4.1314 | 0 | N/A | 0 | 0
2022-09-07 03:30 | 4.0372 | 0 | N/A | 0 | 0
2022-09-07 04:00 | 3.9728 | 0 | N/A | 0 | 0
2022-09-07 04:30 | 3.8968 | 0 | N/A | 0 | 0
2022-09-07 05:00 | 4.0497 | 0 | N/A | 0 | 0
2022-09-07 05:30 | 4.4853 | 0 | N/A | 0 | 0
2022-09-07 06:00 | 4.4244 | 0 | N/A | 0 | 0
2022-09-07 06:30 | 5.1679 | 0 | N/A | 0 | 0
2022-09-07 07:00 | 5.803 | 0 | N/A | 0 | 0
2022-09-07 07:30 | 6.6789 | 0 | N/A | 0 | 0
2022-09-07 08:00 | 6.6625 | 0 | N/A | 0 | 0
2022-09-07 08:30 | 5.7548 | 0 | N/A | 0 | 0
2022-09-07 09:00 | 4.7335 | 0 | N/A | 0 | 0
2022-09-07 09:30 | 5.4983 | 0 | N/A | 0 | 0
2022-09-07 10:00 | 5.6037 | 0 | N/A | 0 | 0
2022-09-07 10:30 | 5.1945 | 0 | N/A | 0 | 0
2022-09-07 11:00 | 4.3621 | 0 | N/A | 0 | 0
2022-09-07 11:30 | 4.0324 | 0 | N/A | 0 | 0
2022-09-07 12:00 | 3.3791 | 0 | N/A | 0 | 0
2022-09-07 12:30 | 1.7163 | 0 | N/A | 0 | 0
2022-09-07 13:00 | 2.6216 | 0 | N/A | 0 | 0
2022-09-07 13:30 | 1.0367 | 0 | N/A | 0 | 0
2022-09-07 14:00 | 2.0945 | 0 | N/A | 0 | 0
2022-09-07 14:30 | 2.0647 | 0 | N/A | 0 | 0
2022-09-07 15:00 | 2.9398 | 0 | N/A | 0 | 0
2022-09-07 15:30 | 2.1576 | 0 | N/A | 0 | 0
2022-09-07 16:00 | 3.6526 | 0 | N/A | 0 | 0
2022-09-07 16:30 | 4.0298 | 0 | N/A | 0 | 0
2022-09-07 17:00 | 4.3787 | 0 | N/A | 0 | 0
2022-09-07 17:30 | 5.0397 | 0 | N/A | 0 | 0
2022-09-07 18:00 | 6.3595 | 0 | N/A | 0 | 0
2022-09-07 18:30 | 7.2305 | 0 | N/A | 0 | 0
2022-09-07 19:00 | 7.596 | 0 | N/A | 0 | 0
2022-09-07 19:30 | 7.5668 | 0 | N/A | 0 | 0
2022-09-07 20:00 | 7.3108 | 0 | N/A | 0 | 0
2022-09-07 20:30 | 7.0579 | 0 | N/A | 0 | 0
2022-09-07 21:00 | 6.6806 | 0 | N/A | 0 | 0
2022-09-07 21:30 | 6.7496 | 0 | N/A | 0 | 0
2022-09-07 22:00 | 6.6998 | 0 | N/A | 0 | 0
2022-09-07 22:30 | 6.1535 | 0 | N/A | 0 | 0
2022-09-07 23:00 | 5.8147 | 0 | N/A | 0 | 0
2022-09-07 23:30 | 5.9092 | 0 | N/A | 0 | 0
2022-09-08 | 6.0526 | 0 | N/A | 0 | 0
2022-09-08 00:30 | 5.3738 | 0 | N/A | 0 | 0
2022-09-08 01:00 | 4.837 | 0 | N/A | 0 | 0
2022-09-08 01:30 | 4.7073 | 0 | N/A | 0 | 0
2022-09-08 02:00 | 4.4354 | 0 | N/A | 0 | 0
2022-09-08 02:30 | 3.8774 | 0 | N/A | 0 | 0
2022-09-08 03:00 | 3.6039 | 0 | N/A | 0 | 0
2022-09-08 03:30 | 3.527 | 0 | N/A | 0 | 0
2022-09-08 04:00 | 3.3996 | 0 | N/A | 0 | 0
2022-09-08 04:30 | 3.358 | 0 | N/A | 0 | 0
2022-09-08 05:00 | 3.4231 | 0 | N/A | 0 | 0
2022-09-08 05:30 | 3.7071 | 0 | N/A | 0 | 0
2022-09-08 06:00 | 4.0557 | 0 | N/A | 0 | 0
2022-09-08 06:30 | 4.7368 | 0 | N/A | 0 | 0
2022-09-08 07:00 | 5.3561 | 0 | N/A | 0 | 0
2022-09-08 07:30 | 6.2291 | 0 | N/A | 0 | 0
2022-09-08 08:00 | 6.598 | 0 | N/A | 0 | 0
2022-09-08 08:30 | 6.7033 | 0 | N/A | 0 | 0
2022-09-08 09:00 | 6.7276 | 0 | N/A | 0 | 0
2022-09-08 09:30 | 6.8386 | 0 | N/A | 0 | 0
2022-09-08 10:00 | 6.3211 | 0 | N/A | 0 | 0
2022-09-08 10:30 | 6.4565 | 0 | N/A | 0 | 0
2022-09-08 11:00 | 6.031 | 0 | N/A | 0 | 0
2022-09-08 11:30 | 6.4823 | 0 | N/A | 0 | 0
2022-09-08 12:00 | 6.2357 | 0 | N/A | 0 | 0
2022-09-08 12:30 | 5.516 | 0 | N/A | 0 | 0
2022-09-08 13:00 | 5.4531 | 0 | N/A | 0 | 0
2022-09-08 13:30 | 5.901 | 0 | N/A | 0 | 0
2022-09-08 14:00 | 5.1542 | 0 | N/A | 0 | 0
2022-09-08 14:30 | 5.6142 | 0 | N/A | 0 | 0
2022-09-08 15:00 | 5.7454 | 0 | N/A | 0 | 0
2022-09-08 15:30 | 5.8625 | 0 | N/A | 0 | 0
2022-09-08 16:00 | 5.4964 | 0 | N/A | 0 | 0
2022-09-08 16:30 | 5.6543 | 0 | N/A | 0 | 0
2022-09-08 17:00 | 6.3513 | 0 | N/A | 0 | 0
2022-09-08 17:30 | 7.111 | 0 | N/A | 0 | 0
2022-09-08 18:00 | 7.9527 | 0 | N/A | 0 | 0
2022-09-08 18:30 | 8.4029 | 0 | N/A | 0 | 0
2022-09-08 19:00 | 8.4224 | 0 | N/A | 0 | 0
2022-09-08 19:30 | 8.047 | 0 | N/A | 0 | 0
2022-09-08 20:00 | 7.7291 | 0 | N/A | 0 | 0
2022-09-08 20:30 | 7.3989 | 0 | N/A | 0 | 0
2022-09-08 21:00 | 6.9319 | 0 | N/A | 0 | 0
2022-09-08 21:30 | 6.9882 | 0 | N/A | 0 | 0
2022-09-08 22:00 | 6.9483 | 0 | N/A | 0 | 0
2022-09-08 22:30 | 6.3365 | 0 | N/A | 0 | 0
2022-09-08 23:00 | 5.9685 | 0 | N/A | 0 | 0
2022-09-08 23:30 | 6.1528 | 0 | N/A | 0 | 0
2022-09-09 | 6.3949 | 0 | N/A | 0 | 0
2022-09-09 00:30 | 5.7325 | 0 | N/A | 0 | 0
2022-09-09 01:00 | 5.036 | 0 | N/A | 0 | 0
2022-09-09 01:30 | 4.8802 | 0 | N/A | 0 | 0
2022-09-09 02:00 | 4.581 | 0 | N/A | 0 | 0
2022-09-09 02:30 | 4.1928 | 0 | N/A | 0 | 0
2022-09-09 03:00 | 3.9474 | 0 | N/A | 0 | 0
2022-09-09 03:30 | 3.7963 | 0 | N/A | 0 | 0
2022-09-09 04:00 | 3.6937 | 0 | N/A | 0 | 0
2022-09-09 04:30 | 3.5786 | 0 | N/A | 0 | 0
2022-09-09 05:00 | 3.6736 | 0 | N/A | 0 | 0
2022-09-09 05:30 | 4.006 | 0 | N/A | 0 | 0
2022-09-09 06:00 | 4.4432 | 0 | N/A | 0 | 0
2022-09-09 06:30 | 5.1786 | 0 | N/A | 0 | 0
2022-09-09 07:00 | 5.6737 | 0 | N/A | 0 | 0
2022-09-09 07:30 | 5.855 | 0 | N/A | 0 | 0
2022-09-09 08:00 | 5.8907 | 0 | N/A | 0 | 0
2022-09-09 08:30 | 4.9772 | 0 | N/A | 0 | 0
2022-09-09 09:00 | 3.6267 | 0 | N/A | 0 | 0
2022-09-09 09:30 | 2.7004 | 0 | N/A | 0 | 0
2022-09-09 10:00 | 1.7036 | 0 | N/A | 0 | 0
2022-09-09 10:30 | 0.94641 | 0 | N/A | 0 | 0
2022-09-09 11:00 | 0.71554 | 0 | N/A | 0 | 0
2022-09-09 11:30 | 1.0512 | 0 | N/A | 0 | 0
2022-09-09 12:00 | 0.75587 | 0 | N/A | 0 | 0
2022-09-09 12:30 | 1.0699 | 0 | N/A | 0 | 0
2022-09-09 13:00 | 0.9781 | 0 | N/A | 0 | 0
2022-09-09 13:30 | 2.1931 | 0 | N/A | 0 | 0
2022-09-09 14:00 | 3.1501 | 0 | N/A | 0 | 0
2022-09-09 14:30 | 3.1878 | 0 | N/A | 0 | 0
2022-09-09 15:00 | 3.4078 | 0 | N/A | 0 | 0
2022-09-09 15:30 | 3.3426 | 0 | N/A | 0 | 0
2022-09-09 16:00 | 3.6094 | 0 | N/A | 0 | 0
2022-09-09 16:30 | 3.7505 | 0 | N/A | 0 | 0
2022-09-09 17:00 | 4.3897 | 0 | N/A | 0 | 0
2022-09-09 17:30 | 5.1906 | 0 | N/A | 0 | 0
2022-09-09 18:00 | 6.0139 | 0 | N/A | 0 | 0
2022-09-09 18:30 | 6.6837 | 0 | N/A | 0 | 0
2022-09-09 19:00 | 7.0154 | 0 | N/A | 0 | 0
2022-09-09 19:30 | 7.0076 | 0 | N/A | 0 | 0
2022-09-09 20:00 | 6.7285 | 0 | N/A | 0 | 0
2022-09-09 20:30 | 6.5346 | 0 | N/A | 0 | 0
2022-09-09 21:00 | 6.3787 | 0 | N/A | 0 | 0
2022-09-09 21:30 | 6.6181 | 0 | N/A | 0 | 0
2022-09-09 22:00 | 6.6199 | 0 | N/A | 0 | 0
2022-09-09 22:30 | 6.0981 | 0 | N/A | 0 | 0
2022-09-09 23:00 | 5.9521 | 0 | N/A | 0 | 0
2022-09-09 23:30 | 6.0594 | 0 | N/A | 0 | 0
2022-09-10 | 6.2318 | 0 | N/A | 0 | 0
2022-09-10 00:30 | 5.5257 | 0 | N/A | 0 | 0
2022-09-10 01:00 | 4.8493 | 0 | N/A | 0 | 0
2022-09-10 01:30 | 4.7142 | 0 | N/A | 0 | 0
2022-09-10 02:00 | 4.4236 | 0 | N/A | 0 | 0
2022-09-10 02:30 | 3.9809 | 0 | N/A | 0 | 0
2022-09-10 03:00 | 3.7506 | 0 | N/A | 0 | 0
2022-09-10 03:30 | 3.6638 | 0 | N/A | 0 | 0
2022-09-10 04:00 | 3.516 | 0 | N/A | 0 | 0
2022-09-10 04:30 | 3.46 | 0 | N/A | 0 | 0
2022-09-10 05:00 | 3.459 | 0 | N/A | 0 | 0
2022-09-10 05:30 | 3.6587 | 0 | N/A | 0 | 0
2022-09-10 06:00 | 3.8378 | 0 | N/A | 0 | 0
2022-09-10 06:30 | 4.1067 | 0 | N/A | 0 | 0
2022-09-10 07:00 | 4.4147 | 0 | N/A | 0 | 0
2022-09-10 07:30 | 4.5337 | 0 | N/A | 0 | 0
2022-09-10 08:00 | 4.8636 | 0 | N/A | 0 | 0
2022-09-10 08:30 | 5.2063 | 0 | N/A | 0 | 0
2022-09-10 09:00 | 5.3446 | 0 | N/A | 0 | 0
2022-09-10 09:30 | 4.4133 | 0 | N/A | 0 | 0
2022-09-10 10:00 | 4.3544 | 0 | N/A | 0 | 0
2022-09-10 10:30 | 2.5703 | 0 | N/A | 0 | 0
2022-09-10 11:00 | 3.8149 | 0 | N/A | 0 | 0
2022-09-10 11:30 | 3.3805 | 0 | N/A | 0 | 0
2022-09-10 12:00 | 2.961 | 0 | N/A | 0 | 0
2022-09-10 12:30 | 2.5787 | 0 | N/A | 0 | 0
2022-09-10 13:00 | 2.4612 | 0 | N/A | 0 | 0
2022-09-10 13:30 | 2.4183 | 0 | N/A | 0 | 0
2022-09-10 14:00 | 2.5133 | 0 | N/A | 0 | 0
2022-09-10 14:30 | 2.8585 | 0 | N/A | 0 | 0
2022-09-10 15:00 | 3.4388 | 0 | N/A | 0 | 0
2022-09-10 15:30 | 3.4932 | 0 | N/A | 0 | 0
2022-09-10 16:00 | 4.2197 | 0 | N/A | 0 | 0
2022-09-10 16:30 | 4.5387 | 0 | N/A | 0 | 0
2022-09-10 17:00 | 5.2642 | 0 | N/A | 0 | 0
2022-09-10 17:30 | 6.1169 | 0 | N/A | 0 | 0
2022-09-10 18:00 | 7.2344 | 0 | N/A | 0 | 0
2022-09-10 18:30 | 7.7868 | 0 | N/A | 0 | 0
2022-09-10 19:00 | 8.0834 | 0 | N/A | 0 | 0
2022-09-10 19:30 | 7.7855 | 0 | N/A | 0 | 0
2022-09-10 20:00 | 7.4234 | 0 | N/A | 0 | 0
2022-09-10 20:30 | 7.153 | 0 | N/A | 0 | 0
2022-09-10 21:00 | 6.969 | 0 | N/A | 0 | 0
2022-09-10 21:30 | 7.0911 | 0 | N/A | 0 | 0
2022-09-10 22:00 | 7.1972 | 0 | N/A | 0 | 0
2022-09-10 22:30 | 6.7696 | 0 | N/A | 0 | 0
2022-09-10 23:00 | 6.6132 | 0 | N/A | 0 | 0
2022-09-10 23:30 | 6.7272 | 0 | N/A | 0 | 0
2022-09-11 | 6.8742 | 0 | N/A | 0 | 0
2022-09-11 00:30 | 6.1757 | 0 | N/A | 0 | 0
2022-09-11 01:00 | 5.5574 | 0 | N/A | 0 | 0
2022-09-11 01:30 | 5.3342 | 0 | N/A | 0 | 0
2022-09-11 02:00 | 5.0212 | 0 | N/A | 0 | 0
2022-09-11 02:30 | 4.6084 | 0 | N/A | 0 | 0
2022-09-11 03:00 | 4.2408 | 0 | N/A | 0 | 0
2022-09-11 03:30 | 4.1173 | 0 | N/A | 0 | 0
2022-09-11 04:00 | 3.9313 | 0 | N/A | 0 | 0
2022-09-11 04:30 | 3.8842 | 0 | N/A | 0 | 0
2022-09-11 05:00 | 3.7875 | 0 | N/A | 0 | 0
2022-09-11 05:30 | 3.9419 | 0 | N/A | 0 | 0
2022-09-11 06:00 | 4.0615 | 0 | N/A | 0 | 0
2022-09-11 06:30 | 4.2631 | 0 | N/A | 0 | 0
2022-09-11 07:00 | 4.5115 | 0 | N/A | 0 | 0
2022-09-11 07:30 | 4.4593 | 0 | N/A | 0 | 0
2022-09-11 08:00 | 4.5079 | 0 | N/A | 0 | 0
2022-09-11 08:30 | 4.7049 | 0 | N/A | 0 | 0
2022-09-11 09:00 | 4.7255 | 0 | N/A | 0 | 0
2022-09-11 09:30 | 4.5606 | 0 | N/A | 0 | 0
2022-09-11 10:00 | 4.2564 | 0 | N/A | 0 | 0
2022-09-11 10:30 | 2.9595 | 0 | N/A | 0 | 0
2022-09-11 11:00 | 3.6582 | 0 | N/A | 0 | 0
2022-09-11 11:30 | 3.9894 | 0 | N/A | 0 | 0
2022-09-11 12:00 | 3.9545 | 0 | N/A | 0 | 0
2022-09-11 12:30 | 3.001 | 0 | N/A | 0 | 0
2022-09-11 13:00 | 3.2058 | 0 | N/A | 0 | 0
2022-09-11 13:30 | 2.9309 | 0 | N/A | 0 | 0
2022-09-11 14:00 | 3.7374 | 0 | N/A | 0 | 0
2022-09-11 14:30 | 2.7142 | 0 | N/A | 0 | 0
2022-09-11 15:00 | 3.1191 | 0 | N/A | 0 | 0
2022-09-11 15:30 | 3.5439 | 0 | N/A | 0 | 0
2022-09-11 16:00 | 3.9167 | 0 | N/A | 0 | 0
2022-09-11 16:30 | 5.3829 | 0 | N/A | 0 | 0
2022-09-11 17:00 | 6.0216 | 0 | N/A | 0 | 0
2022-09-11 17:30 | 7.4157 | 0 | N/A | 0 | 0
2022-09-11 18:00 | 8.2572 | 0 | N/A | 0 | 0
2022-09-11 18:30 | 8.6455 | 0 | N/A | 0 | 0
2022-09-11 19:00 | 8.666 | 0 | N/A | 0 | 0
2022-09-11 19:30 | 8.3936 | 0 | N/A | 0 | 0
2022-09-11 20:00 | 7.9619 | 0 | N/A | 0 | 0
2022-09-11 20:30 | 7.4539 | 0 | N/A | 0 | 0
2022-09-11 21:00 | 7.0065 | 0 | N/A | 0 | 0
2022-09-11 21:30 | 7.1649 | 0 | N/A | 0 | 0
2022-09-11 22:00 | 7.0936 | 0 | N/A | 0 | 0
2022-09-11 22:30 | 6.6757 | 0 | N/A | 0 | 0
2022-09-11 23:00 | 6.399 | 0 | N/A | 0 | 0
2022-09-11 23:30 | 6.3743 | 0 | N/A | 0 | 0
2022-09-12 | 6.6647 | 0 | N/A | 0 | 0
2022-09-12 00:30 | 6.1626 | 0 | N/A | 0 | 0
2022-09-12 01:00 | 5.6224 | 0 | N/A | 0 | 0
2022-09-12 01:30 | 5.4844 | 0 | N/A | 0 | 0
2022-09-12 02:00 | 5.1377 | 0 | N/A | 0 | 0
2022-09-12 02:30 | 4.595 | 0 | N/A | 0 | 0
2022-09-12 03:00 | 4.2524 | 0 | N/A | 0 | 0
2022-09-12 03:30 | 4.0565 | 0 | N/A | 0 | 0
2022-09-12 04:00 | 3.9785 | 0 | N/A | 0 | 0
2022-09-12 04:30 | 3.9565 | 0 | N/A | 0 | 0
2022-09-12 05:00 | 4.027 | 0 | N/A | 0 | 0
2022-09-12 05:30 | 4.4272 | 0 | N/A | 0 | 0
2022-09-12 06:00 | 4.8101 | 0 | N/A | 0 | 0
2022-09-12 06:30 | 5.5835 | 0 | N/A | 0 | 0
2022-09-12 07:00 | 6.3368 | 0 | N/A | 0 | 0
2022-09-12 07:30 | 6.4121 | 0 | N/A | 0 | 0
2022-09-12 08:00 | 6.6861 | 0 | N/A | 0 | 0
2022-09-12 08:30 | 6.5931 | 0 | N/A | 0 | 0
2022-09-12 09:00 | 5.3852 | 0 | N/A | 0 | 0
2022-09-12 09:30 | 5.3317 | 0 | N/A | 0 | 0
2022-09-12 10:00 | 4.7359 | 0 | N/A | 0 | 0
2022-09-12 10:30 | 4.4022 | 0 | N/A | 0 | 0
2022-09-12 11:00 | 4.4777 | 0 | N/A | 0 | 0
2022-09-12 11:30 | 4.0092 | 0 | N/A | 0 | 0
2022-09-12 12:00 | 3.1807 | 0 | N/A | 0 | 0
2022-09-12 12:30 | 3.5849 | 0 | N/A | 0 | 0
2022-09-12 13:00 | 4.2158 | 0 | N/A | 0 | 0
2022-09-12 13:30 | 3.3504 | 0 | N/A | 0 | 0
2022-09-12 14:00 | 2.4014 | 0 | N/A | 0 | 0
2022-09-12 14:30 | 3.6252 | 0 | N/A | 0 | 0
2022-09-12 15:00 | 3.8791 | 0 | N/A | 0 | 0
2022-09-12 15:30 | 3.8054 | 0 | N/A | 0 | 0
2022-09-12 16:00 | 4.5463 | 0 | N/A | 0 | 0
2022-09-12 16:30 | 3.7683 | 0 | N/A | 0 | 0
2022-09-12 17:00 | 4.9085 | 0 | N/A | 0 | 0
2022-09-12 17:30 | 6.2561 | 0 | N/A | 0 | 0
2022-09-12 18:00 | 7.7381 | 0 | N/A | 0 | 0
2022-09-12 18:30 | 8.7096 | 0 | N/A | 0 | 0
2022-09-12 19:00 | 9.1741 | 0 | N/A | 0 | 0
2022-09-12 19:30 | 9.0246 | 0 | N/A | 0 | 0
2022-09-12 20:00 | 8.8111 | 0 | N/A | 0 | 0
2022-09-12 20:30 | 8.408 | 0 | N/A | 0 | 0
2022-09-12 21:00 | 8.0349 | 0 | N/A | 0 | 0
2022-09-12 21:30 | 8.0269 | 0 | N/A | 0 | 0
2022-09-12 22:00 | 7.8833 | 0 | N/A | 0 | 0
2022-09-12 22:30 | 7.1651 | 0 | N/A | 0 | 0
2022-09-12 23:00 | 6.8142 | 0 | N/A | 0 | 0
2022-09-12 23:30 | 6.7904 | 0 | N/A | 0 | 0
2022-09-13 | 7.0721 | 0 | N/A | 0 | 0
2022-09-13 00:30 | 6.5497 | 0 | N/A | 0 | 0
2022-09-13 01:00 | 5.9665 | 0 | N/A | 0 | 0
2022-09-13 01:30 | 5.791 | 0 | N/A | 0 | 0
2022-09-13 02:00 | 5.4216 | 0 | N/A | 0 | 0
2022-09-13 02:30 | 5.0581 | 0 | N/A | 0 | 0
2022-09-13 03:00 | 4.7729 | 0 | N/A | 0 | 0
2022-09-13 03:30 | 4.6809 | 0 | N/A | 0 | 0
2022-09-13 04:00 | 4.5995 | 0 | N/A | 0 | 0
2022-09-13 04:30 | 4.6005 | 0 | N/A | 0 | 0
2022-09-13 05:00 | 4.8279 | 0 | N/A | 0 | 0
2022-09-13 05:30 | 5.234 | 0 | N/A | 0 | 0
2022-09-13 06:00 | 5.7553 | 0 | N/A | 0 | 0
2022-09-13 06:30 | 6.4791 | 0 | N/A | 0 | 0
2022-09-13 07:00 | 7.2404 | 0 | N/A | 0 | 0
2022-09-13 07:30 | 7.555 | 0 | N/A | 0 | 0
2022-09-13 08:00 | 7.287 | 0 | N/A | 0 | 0
2022-09-13 08:30 | 6.4541 | 0 | N/A | 0 | 0
2022-09-13 09:00 | 5.1829 | 0 | N/A | 0 | 0
2022-09-13 09:30 | 4.0757 | 0 | N/A | 0 | 0
2022-09-13 10:00 | 3.4672 | 0 | N/A | 0 | 0
2022-09-13 10:30 | 3.5234 | 0 | N/A | 0 | 0
2022-09-13 11:00 | 2.4165 | 0 | N/A | 0 | 0
2022-09-13 11:30 | 2.2774 | 0 | N/A | 0 | 0
2022-09-13 12:00 | 2.7286 | 0 | N/A | 0 | 0
2022-09-13 12:30 | 2.2509 | 0 | N/A | 0 | 0
2022-09-13 13:00 | 1.796 | 0 | N/A | 0 | 0
2022-09-13 13:30 | 1.582 | 0 | N/A | 0 | 0
2022-09-13 14:00 | 2.1066 | 0 | N/A | 0 | 0
2022-09-13 14:30 | 1.6684 | 0 | N/A | 0 | 0
2022-09-13 15:00 | 1.9125 | 0 | N/A | 0 | 0
2022-09-13 15:30 | 2.7681 | 0 | N/A | 0 | 0
2022-09-13 16:00 | 2.491 | 0 | N/A | 0 | 0
2022-09-13 16:30 | 3.001 | 0 | N/A | 0 | 0
2022-09-13 17:00 | 4.0479 | 0 | N/A | 0 | 0
2022-09-13 17:30 | 5.4289 | 0 | N/A | 0 | 0
2022-09-13 18:00 | 6.9282 | 0 | N/A | 0 | 0
2022-09-13 18:30 | 8.0658 | 0 | N/A | 0 | 0
2022-09-13 19:00 | 8.6858 | 0 | N/A | 0 | 0
2022-09-13 19:30 | 8.7604 | 0 | N/A | 0 | 0
2022-09-13 20:00 | 8.5721 | 0 | N/A | 0 | 0
2022-09-13 20:30 | 8.3267 | 0 | N/A | 0 | 0
2022-09-13 21:00 | 8.0184 | 0 | N/A | 0 | 0
2022-09-13 21:30 | 8.0607 | 0 | N/A | 0 | 0
2022-09-13 22:00 | 7.981 | 0 | N/A | 0 | 0
2022-09-13 22:30 | 7.339 | 0 | N/A | 0 | 0
2022-09-13 23:00 | 6.8321 | 0 | N/A | 0 | 0
2022-09-13 23:30 | 6.8196 | 0 | N/A | 0 | 0
2022-09-14 | 7.0114 | 0 | N/A | 0 | 0
2022-09-15 00:30 | 6.0312 | 0 | N/A | 0 | 0
2022-09-15 01:00 | 5.3774 | 0 | N/A | 0 | 0
2022-09-15 01:30 | 5.1874 | 0 | N/A | 0 | 0
2022-09-15 02:00 | 4.8204 | 0 | N/A | 0 | 0
2022-09-15 02:30 | 4.4598 | 0 | N/A | 0 | 0
2022-09-15 03:00 | 4.189 | 0 | N/A | 0 | 0
2022-09-15 03:30 | 3.9724 | 0 | N/A | 0 | 0
2022-09-15 04:00 | 3.8492 | 0 | N/A | 0 | 0
2022-09-15 04:30 | 3.7344 | 0 | N/A | 0 | 0
2022-09-15 05:00 | 3.8708 | 0 | N/A | 0 | 0
2022-09-15 05:30 | 4.124 | 0 | N/A | 0 | 0
2022-09-15 06:00 | 4.467 | 0 | N/A | 0 | 0
2022-09-15 06:30 | 5.1373 | 0 | N/A | 0 | 0
2022-09-15 07:00 | 5.7777 | 0 | N/A | 0 | 0
2022-09-15 07:30 | 6.615 | 0 | N/A | 0 | 0
2022-09-15 08:00 | 7.053 | 0 | N/A | 0 | 0
2022-09-15 08:30 | 7.3594 | 0 | N/A | 0 | 0
2022-09-15 09:00 | 6.7176 | 0 | N/A | 0 | 0
2022-09-15 09:30 | 6.3864 | 0 | N/A | 0 | 0
2022-09-15 10:00 | 6.1082 | 0 | N/A | 0 | 0
2022-09-15 10:30 | 5.7012 | 0 | N/A | 0 | 0
2022-09-15 11:00 | 5.4939 | 0 | N/A | 0 | 0
2022-09-15 11:30 | 5.437 | 0 | N/A | 0 | 0
2022-09-15 12:00 | 5.6311 | 0 | N/A | 0 | 0
2022-09-15 12:30 | 5.2787 | 0 | N/A | 0 | 0
2022-09-15 13:00 | 5.0905 | 0 | N/A | 0 | 0
2022-09-15 13:30 | 5.4733 | 0 | N/A | 0 | 0
2022-09-15 14:00 | 5.6903 | 0 | N/A | 0 | 0
2022-09-15 14:30 | 5.7643 | 0 | N/A | 0 | 0
2022-09-15 15:00 | 5.6564 | 0 | N/A | 0 | 0
2022-09-15 15:30 | 5.4337 | 0 | N/A | 0 | 0
2022-09-15 16:00 | 5.1194 | 0 | N/A | 0 | 0
2022-09-15 16:30 | 4.9632 | 0 | N/A | 0 | 0
2022-09-15 17:00 | 5.2839 | 0 | N/A | 0 | 0
2022-09-15 17:30 | 5.8813 | 0 | N/A | 0 | 0
2022-09-15 18:00 | 6.8954 | 0 | N/A | 0 | 0
2022-09-15 18:30 | 7.606 | 0 | N/A | 0 | 0
2022-09-15 19:00 | 8.1523 | 0 | N/A | 0 | 0
2022-09-15 19:30 | 7.9406 | 0 | N/A | 0 | 0
2022-09-15 20:00 | 7.7955 | 0 | N/A | 0 | 0
2022-09-15 20:30 | 7.4034 | 0 | N/A | 0 | 0
2022-09-15 21:00 | 7.1331 | 0 | N/A | 0 | 0
2022-09-15 21:30 | 7.2746 | 0 | N/A | 0 | 0
2022-09-15 22:00 | 7.1984 | 0 | N/A | 0 | 0
2022-09-15 22:30 | 6.4957 | 0 | N/A | 0 | 0
2022-09-15 23:00 | 6.1752 | 0 | N/A | 0 | 0
2022-09-15 23:30 | 6.2628 | 0 | N/A | 0 | 0
2022-09-16 | 6.4731 | 0 | N/A | 0 | 0
2022-09-17 00:30 | 6.3816 | 0 | N/A | 0 | 0
2022-09-17 01:00 | 5.7051 | 0 | N/A | 0 | 0
2022-09-17 01:30 | 5.4644 | 0 | N/A | 0 | 0
2022-09-17 02:00 | 5.1129 | 0 | N/A | 0 | 0
2022-09-17 02:30 | 4.6209 | 0 | N/A | 0 | 0
2022-09-17 03:00 | 4.3373 | 0 | N/A | 0 | 0
2022-09-17 03:30 | 4.1079 | 0 | N/A | 0 | 0
2022-09-17 04:00 | 3.9902 | 0 | N/A | 0 | 0
2022-09-17 04:30 | 3.9062 | 0 | N/A | 0 | 0
2022-09-17 05:00 | 3.9345 | 0 | N/A | 0 | 0
2022-09-17 05:30 | 4.011 | 0 | N/A | 0 | 0
2022-09-17 06:00 | 4.1742 | 0 | N/A | 0 | 0
2022-09-17 06:30 | 4.4853 | 0 | N/A | 0 | 0
2022-09-17 07:00 | 4.8608 | 0 | N/A | 0 | 0
2022-09-17 07:30 | 4.7896 | 0 | N/A | 0 | 0
2022-09-17 08:00 | 4.9963 | 0 | N/A | 0 | 0
2022-09-17 08:30 | 5.4535 | 0 | N/A | 0 | 0
2022-09-17 09:00 | 6.1519 | 0 | N/A | 0 | 0
2022-09-17 09:30 | 6.2641 | 0 | N/A | 0 | 0
2022-09-17 10:00 | 5.8545 | 0 | N/A | 0 | 0
2022-09-17 10:30 | 6.2266 | 0 | N/A | 0 | 0
2022-09-17 11:00 | 6.8897 | 0 | N/A | 0 | 0
2022-09-17 11:30 | 6.1408 | 0 | N/A | 0 | 0
2022-09-17 12:00 | 5.6102 | 0 | N/A | 0 | 0
2022-09-17 12:30 | 6.8889 | 0 | N/A | 0 | 0
2022-09-17 13:00 | 6.8707 | 0 | N/A | 0 | 0
2022-09-17 13:30 | 3.8481 | 0 | N/A | 0 | 0
2022-09-17 14:00 | 5.1526 | 0 | N/A | 0 | 0
2022-09-17 14:30 | 7.2831 | 0 | N/A | 0 | 0
2022-09-17 15:00 | 5.1827 | 0 | N/A | 0 | 0
2022-09-17 15:30 | 5.5798 | 0 | N/A | 0 | 0
2022-09-17 16:00 | 4.2878 | 0 | N/A | 0 | 0
2022-09-17 16:30 | 5.9883 | 0 | N/A | 0 | 0
2022-09-17 17:00 | 6.5161 | 0 | N/A | 0 | 0
2022-09-17 17:30 | 7.3988 | 0 | N/A | 0 | 0
2022-09-17 18:00 | 7.7527 | 0 | N/A | 0 | 0
2022-09-17 18:30 | 8.2615 | 0 | N/A | 0 | 0
2022-09-17 19:00 | 8.4827 | 0 | N/A | 0 | 0
2022-09-17 19:30 | 8.1623 | 0 | N/A | 0 | 0
2022-09-17 20:00 | 7.8289 | 0 | N/A | 0 | 0
2022-09-17 20:30 | 7.6038 | 0 | N/A | 0 | 0
2022-09-17 21:00 | 7.2406 | 0 | N/A | 0 | 0
2022-09-17 21:30 | 7.3367 | 0 | N/A | 0 | 0
2022-09-17 22:00 | 7.4491 | 0 | N/A | 0 | 0
2022-09-17 22:30 | 7.0136 | 0 | N/A | 0 | 0
2022-09-17 23:00 | 6.8629 | 0 | N/A | 0 | 0
2022-09-17 23:30 | 6.9412 | 0 | N/A | 0 | 0
2022-09-18 | 7.1231 | 0 | N/A | 0 | 0
2022-09-18 00:30 | 6.5146 | 0 | N/A | 0 | 0
2022-09-18 01:00 | 5.7563 | 0 | N/A | 0 | 0
2022-09-18 01:30 | 5.6641 | 0 | N/A | 0 | 0
2022-09-18 02:00 | 5.3603 | 0 | N/A | 0 | 0
2022-09-18 02:30 | 4.8274 | 0 | N/A | 0 | 0
2022-09-18 03:00 | 4.5487 | 0 | N/A | 0 | 0
2022-09-18 03:30 | 4.3552 | 0 | N/A | 0 | 0
2022-09-18 04:00 | 4.2589 | 0 | N/A | 0 | 0
2022-09-18 04:30 | 4.1606 | 0 | N/A | 0 | 0
2022-09-18 05:00 | 4.1352 | 0 | N/A | 0 | 0
2022-09-18 05:30 | 4.1616 | 0 | N/A | 0 | 0
2022-09-18 06:00 | 4.261 | 0 | N/A | 0 | 0
2022-09-18 06:30 | 4.5069 | 0 | N/A | 0 | 0
2022-09-18 07:00 | 4.6149 | 0 | N/A | 0 | 0
2022-09-18 07:30 | 4.616 | 0 | N/A | 0 | 0
2022-09-18 08:00 | 4.6734 | 0 | N/A | 0 | 0
2022-09-18 08:30 | 5.1681 | 0 | N/A | 0 | 0
2022-09-18 09:00 | 4.9023 | 0 | N/A | 0 | 0
2022-09-18 09:30 | 4.8028 | 0 | N/A | 0 | 0
2022-09-18 10:00 | 4.789 | 0 | N/A | 0 | 0
2022-09-18 10:30 | 4.6563 | 0 | N/A | 0 | 0
2022-09-18 11:00 | 3.4066 | 0 | N/A | 0 | 0
2022-09-18 11:30 | 3.6761 | 0 | N/A | 0 | 0
2022-09-18 12:00 | 3.2403 | 0 | N/A | 0 | 0
2022-09-18 12:30 | 3.539 | 0 | N/A | 0 | 0
2022-09-18 13:00 | 2.4975 | 0 | N/A | 0 | 0
2022-09-18 13:30 | 1.4307 | 0 | N/A | 0 | 0
2022-09-18 14:00 | 4.0032 | 0 | N/A | 0 | 0
2022-09-18 14:30 | 2.7973 | 0 | N/A | 0 | 0
2022-09-18 15:00 | 2.3389 | 0 | N/A | 0 | 0
2022-09-18 15:30 | 2.8878 | 0 | N/A | 0 | 0
2022-09-18 16:00 | 4.3198 | 0 | N/A | 0 | 0
2022-09-18 16:30 | 5.5891 | 0 | N/A | 0 | 0
2022-09-18 17:00 | 6.5314 | 0 | N/A | 0 | 0
2022-09-18 17:30 | 7.4803 | 0 | N/A | 0 | 0
2022-09-18 18:00 | 8.3262 | 0 | N/A | 0 | 0
2022-09-18 18:30 | 8.6796 | 0 | N/A | 0 | 0
2022-09-18 19:00 | 8.6515 | 0 | N/A | 0 | 0
2022-09-18 19:30 | 8.2248 | 0 | N/A | 0 | 0
2022-09-18 20:00 | 7.9681 | 0 | N/A | 0 | 0
2022-09-18 20:30 | 7.6251 | 0 | N/A | 0 | 0
2022-09-18 21:00 | 7.2977 | 0 | N/A | 0 | 0
2022-09-18 21:30 | 7.5268 | 0 | N/A | 0 | 0
2022-09-18 22:00 | 7.3483 | 0 | N/A | 0 | 0
2022-09-18 22:30 | 7.0207 | 0 | N/A | 0 | 0
2022-09-18 23:00 | 6.8764 | 0 | N/A | 0 | 0
2022-09-18 23:30 | 6.8133 | 0 | N/A | 0 | 0
2022-09-19 | 6.9331 | 0 | N/A | 0 | 0
2022-09-19 00:30 | 6.3268 | 0 | N/A | 0 | 0
2022-09-19 01:00 | 5.6326 | 0 | N/A | 0 | 0
2022-09-19 01:30 | 5.566 | 0 | N/A | 0 | 0
2022-09-19 02:00 | 5.3189 | 0 | N/A | 0 | 0
2022-09-19 02:30 | 4.7673 | 0 | N/A | 0 | 0
2022-09-19 03:00 | 4.4792 | 0 | N/A | 0 | 0
2022-09-19 03:30 | 4.3479 | 0 | N/A | 0 | 0
2022-09-19 04:00 | 4.2155 | 0 | N/A | 0 | 0
2022-09-19 04:30 | 4.2396 | 0 | N/A | 0 | 0
2022-09-19 05:00 | 4.2933 | 0 | N/A | 0 | 0
2022-09-19 05:30 | 4.6776 | 0 | N/A | 0 | 0
2022-09-19 06:00 | 5.1701 | 0 | N/A | 0 | 0
2022-09-19 06:30 | 5.8727 | 0 | N/A | 0 | 0
2022-09-19 07:00 | 6.337 | 0 | N/A | 0 | 0
2022-09-19 07:30 | 6.1463 | 0 | N/A | 0 | 0
2022-09-19 08:00 | 6.3016 | 0 | N/A | 0 | 0
2022-09-19 08:30 | 5.6251 | 0 | N/A | 0 | 0
2022-09-19 09:00 | 5.4167 | 0 | N/A | 0 | 0
2022-09-19 09:30 | 5.7898 | 0 | N/A | 0 | 0
2022-09-19 10:00 | 5.3513 | 0 | N/A | 0 | 0
2022-09-19 10:30 | 4.6032 | 0 | N/A | 0 | 0
2022-09-19 11:00 | 3.3364 | 0 | N/A | 0 | 0
2022-09-19 11:30 | 3.0164 | 0 | N/A | 0 | 0
2022-09-19 12:00 | 2.8321 | 0 | N/A | 0 | 0
2022-09-19 12:30 | 3.1508 | 0 | N/A | 0 | 0
2022-09-19 13:00 | 3.6975 | 0 | N/A | 0 | 0
2022-09-19 13:30 | 3.4707 | 0 | N/A | 0 | 0
2022-09-19 14:00 | 3.9186 | 0 | N/A | 0 | 0
2022-09-19 14:30 | 3.8164 | 0 | N/A | 0 | 0
2022-09-19 15:00 | 4.8603 | 0 | N/A | 0 | 0
2022-09-19 15:30 | 5.233 | 0 | N/A | 0 | 0
2022-09-19 16:00 | 5.3068 | 0 | N/A | 0 | 0
2022-09-19 16:30 | 5.1182 | 0 | N/A | 0 | 0
2022-09-19 17:00 | 5.6698 | 0 | N/A | 0 | 0
2022-09-19 17:30 | 6.5174 | 0 | N/A | 0 | 0
2022-09-19 18:00 | 7.4998 | 0 | N/A | 0 | 0
2022-09-19 18:30 | 8.1423 | 0 | N/A | 0 | 0
2022-09-19 19:00 | 8.3209 | 0 | N/A | 0 | 0
2022-09-19 19:30 | 8.0923 | 0 | N/A | 0 | 0
2022-09-19 20:00 | 7.5845 | 0 | N/A | 0 | 0
2022-09-19 20:30 | 7.4034 | 0 | N/A | 0 | 0
2022-09-19 21:00 | 7.1215 | 0 | N/A | 0 | 0
2022-09-19 21:30 | 7.1854 | 0 | N/A | 0 | 0
2022-09-19 22:00 | 7.1532 | 0 | N/A | 0 | 0
2022-09-19 22:30 | 6.6074 | 0 | N/A | 0 | 0
2022-09-19 23:00 | 6.4012 | 0 | N/A | 0 | 0
2022-09-19 23:30 | 6.4736 | 0 | N/A | 0 | 0
2022-09-20 | 6.742 | 0 | N/A | 0 | 0
2022-09-20 00:30 | 6.1197 | 0 | N/A | 0 | 0
2022-09-20 01:00 | 5.4703 | 0 | N/A | 0 | 0
2022-09-20 01:30 | 5.3042 | 0 | N/A | 0 | 0
2022-09-20 02:00 | 5.0569 | 0 | N/A | 0 | 0
2022-09-20 02:30 | 4.6341 | 0 | N/A | 0 | 0
2022-09-20 03:00 | 4.261 | 0 | N/A | 0 | 0
2022-09-20 03:30 | 4.0952 | 0 | N/A | 0 | 0
2022-09-20 04:00 | 4.0141 | 0 | N/A | 0 | 0
2022-09-20 04:30 | 4.052 | 0 | N/A | 0 | 0
2022-09-20 05:00 | 4.1732 | 0 | N/A | 0 | 0
2022-09-20 05:30 | 4.5666 | 0 | N/A | 0 | 0
2022-09-20 06:00 | 5.0047 | 0 | N/A | 0 | 0
2022-09-20 06:30 | 5.7247 | 0 | N/A | 0 | 0
2022-09-20 07:00 | 6.0214 | 0 | N/A | 0 | 0
2022-09-20 07:30 | 5.747 | 0 | N/A | 0 | 0
2022-09-20 08:00 | 5.5024 | 0 | N/A | 0 | 0
2022-09-20 08:30 | 4.9945 | 0 | N/A | 0 | 0
2022-09-20 09:00 | 4.2648 | 0 | N/A | 0 | 0
2022-09-20 09:30 | 3.6314 | 0 | N/A | 0 | 0
2022-09-20 10:00 | 2.9739 | 0 | N/A | 0 | 0
2022-09-20 10:30 | 2.4787 | 0 | N/A | 0 | 0
2022-09-20 11:00 | 1.3075 | 0 | N/A | 0 | 0
2022-09-20 11:30 | 1.0828 | 0 | N/A | 0 | 0
2022-09-20 12:00 | 1.849 | 0 | N/A | 0 | 0
2022-09-20 12:30 | 1.228 | 0 | N/A | 0 | 0
2022-09-20 13:00 | 1.6345 | 0 | N/A | 0 | 0
2022-09-20 13:30 | 1.3931 | 0 | N/A | 0 | 0
2022-09-20 14:00 | 1.096 | 0 | N/A | 0 | 0
2022-09-20 14:30 | 1.0254 | 0 | N/A | 0 | 0
2022-09-20 15:00 | 2.8684 | 0 | N/A | 0 | 0
2022-09-20 15:30 | 2.4006 | 0 | N/A | 0 | 0
2022-09-20 16:00 | 3.6565 | 0 | N/A | 0 | 0
2022-09-20 16:30 | 4.5455 | 0 | N/A | 0 | 0
2022-09-20 17:00 | 5.0549 | 0 | N/A | 0 | 0
2022-09-20 17:30 | 6.2431 | 0 | N/A | 0 | 0
2022-09-20 18:00 | 7.4078 | 0 | N/A | 0 | 0
2022-09-20 18:30 | 8.1709 | 0 | N/A | 0 | 0
2022-09-20 19:00 | 8.4923 | 0 | N/A | 0 | 0
2022-09-20 19:30 | 8.1288 | 0 | N/A | 0 | 0
2022-09-20 20:00 | 7.758 | 0 | N/A | 0 | 0
2022-09-20 20:30 | 7.6504 | 0 | N/A | 0 | 0
2022-09-20 21:00 | 7.1994 | 0 | N/A | 0 | 0
2022-09-20 21:30 | 7.3198 | 0 | N/A | 0 | 0
2022-09-20 22:00 | 7.2573 | 0 | N/A | 0 | 0
2022-09-20 22:30 | 6.5289 | 0 | N/A | 0 | 0
2022-09-20 23:00 | 6.2297 | 0 | N/A | 0 | 0
2022-09-20 23:30 | 6.3272 | 0 | N/A | 0 | 0
2022-09-21 | 6.5318 | 0 | N/A | 0 | 0
2022-09-21 00:30 | 5.8758 | 0 | N/A | 0 | 0
2022-09-21 01:00 | 5.2179 | 0 | N/A | 0 | 0
2022-09-21 01:30 | 5.134 | 0 | N/A | 0 | 0
2022-09-21 02:00 | 4.8456 | 0 | N/A | 0 | 0
2022-09-21 02:30 | 4.4924 | 0 | N/A | 0 | 0
2022-09-21 03:00 | 4.1942 | 0 | N/A | 0 | 0
2022-09-21 03:30 | 4.0547 | 0 | N/A | 0 | 0
2022-09-21 04:00 | 3.9143 | 0 | N/A | 0 | 0
2022-09-21 04:30 | 3.9065 | 0 | N/A | 0 | 0
2022-09-21 05:00 | 4.0363 | 0 | N/A | 0 | 0
2022-09-21 05:30 | 4.3371 | 0 | N/A | 0 | 0
2022-09-21 06:00 | 4.662 | 0 | N/A | 0 | 0
2022-09-21 06:30 | 5.1301 | 0 | N/A | 0 | 0
2022-09-21 07:00 | 5.484 | 0 | N/A | 0 | 0
2022-09-21 07:30 | 5.6987 | 0 | N/A | 0 | 0
2022-09-21 08:00 | 5.9548 | 0 | N/A | 0 | 0
2022-09-21 08:30 | 6.3636 | 0 | N/A | 0 | 0
2022-09-21 09:00 | 6.6031 | 0 | N/A | 0 | 0
2022-09-21 09:30 | 5.8674 | 0 | N/A | 0 | 0
2022-09-21 10:00 | 4.9163 | 0 | N/A | 0 | 0
2022-09-21 10:30 | 5.2128 | 0 | N/A | 0 | 0
2022-09-21 11:00 | 5.239 | 0 | N/A | 0 | 0
2022-09-21 11:30 | 4.708 | 0 | N/A | 0 | 0
2022-09-21 12:00 | 4.2108 | 0 | N/A | 0 | 0
2022-09-21 12:30 | 4.3079 | 0 | N/A | 0 | 0
2022-09-21 13:00 | 4.3072 | 0 | N/A | 0 | 0
2022-09-21 13:30 | 3.2878 | 0 | N/A | 0 | 0
2022-09-21 14:00 | 3.2849 | 0 | N/A | 0 | 0
2022-09-21 14:30 | 4.0738 | 0 | N/A | 0 | 0
2022-09-21 15:00 | 4.828 | 0 | N/A | 0 | 0
2022-09-21 15:30 | 4.6139 | 0 | N/A | 0 | 0
2022-09-21 16:00 | 4.2927 | 0 | N/A | 0 | 0
2022-09-21 16:30 | 4.4484 | 0 | N/A | 0 | 0
2022-09-21 17:00 | 4.8371 | 0 | N/A | 0 | 0
2022-09-21 17:30 | 5.0776 | 0 | N/A | 0 | 0
2022-09-21 18:00 | 5.9342 | 0 | N/A | 0 | 0
2022-09-21 18:30 | 6.4255 | 0 | N/A | 0 | 0
2022-09-21 19:00 | 6.6229 | 0 | N/A | 0 | 0
2022-09-21 19:30 | 6.5025 | 0 | N/A | 0 | 0
2022-09-21 20:00 | 6.3049 | 0 | N/A | 0 | 0
2022-09-21 20:30 | 6.1632 | 0 | N/A | 0 | 0
2022-09-21 21:00 | 6.0473 | 0 | N/A | 0 | 0
2022-09-21 21:30 | 6.2271 | 0 | N/A | 0 | 0
2022-09-21 22:00 | 6.236 | 0 | N/A | 0 | 0
2022-09-21 22:30 | 5.834 | 0 | N/A | 0 | 0
2022-09-21 23:00 | 5.6178 | 0 | N/A | 0 | 0
2022-09-21 23:30 | 5.7747 | 0 | N/A | 0 | 0
2022-09-22 | 5.9194 | 0 | N/A | 0 | 0
2022-09-22 00:30 | 5.3465 | 0 | N/A | 0 | 0
2022-09-22 01:00 | 4.6575 | 0 | N/A | 0 | 0
2022-09-22 01:30 | 4.4638 | 0 | N/A | 0 | 0
2022-09-22 02:00 | 4.0742 | 0 | N/A | 0 | 0
2022-09-22 02:30 | 3.6431 | 0 | N/A | 0 | 0
2022-09-22 03:00 | 3.4397 | 0 | N/A | 0 | 0
2022-09-22 03:30 | 3.2714 | 0 | N/A | 0 | 0
2022-09-22 04:00 | 3.1722 | 0 | N/A | 0 | 0
2022-09-22 04:30 | 3.1603 | 0 | N/A | 0 | 0
2022-09-22 05:00 | 3.2335 | 0 | N/A | 0 | 0
2022-09-22 05:30 | 3.4319 | 0 | N/A | 0 | 0
2022-09-22 06:00 | 3.6549 | 0 | N/A | 0 | 0
2022-09-22 06:30 | 3.9074 | 0 | N/A | 0 | 0
2022-09-22 07:00 | 4.0584 | 0 | N/A | 0 | 0
2022-09-22 07:30 | 3.9361 | 0 | N/A | 0 | 0
2022-09-22 08:00 | 3.8645 | 0 | N/A | 0 | 0
2022-09-22 08:30 | 3.8121 | 0 | N/A | 0 | 0
2022-09-22 09:00 | 3.6875 | 0 | N/A | 0 | 0
2022-09-22 09:30 | 3.025 | 0 | N/A | 0 | 0
2022-09-22 10:00 | 2.4062 | 0 | N/A | 0 | 0
2022-09-22 10:30 | 1.8928 | 0 | N/A | 0 | 0
2022-09-22 11:00 | 1.2794 | 0 | N/A | 0 | 0
2022-09-22 11:30 | -1.0085 | 0 | N/A | 0 | 0
2022-09-22 12:00 | -1.0226 | 0 | N/A | 0 | 0
2022-09-22 12:30 | -0.99286 | 0 | N/A | 0 | 0
2022-09-22 13:00 | 1.0415 | 0 | N/A | 0 | 0
2022-09-22 13:30 | 1.3877 | 0 | N/A | 0 | 0
2022-09-22 14:00 | 1.7492 | 0 | N/A | 0 | 0
2022-09-22 14:30 | 2.07 | 0 | N/A | 0 | 0
2022-09-22 15:00 | 2.0381 | 0 | N/A | 0 | 0
2022-09-22 15:30 | 2.5734 | 0 | N/A | 0 | 0
2022-09-22 16:00 | 3.3024 | 0 | N/A | 0 | 0
2022-09-22 16:30 | 3.2002 | 0 | N/A | 0 | 0
2022-09-22 17:00 | 3.4723 | 0 | N/A | 0 | 0
2022-09-22 17:30 | 4.1247 | 0 | N/A | 0 | 0
2022-09-22 18:00 | 5.1053 | 0 | N/A | 0 | 0
2022-09-22 18:30 | 5.7888 | 0 | N/A | 0 | 0
2022-09-22 19:00 | 6.1619 | 0 | N/A | 0 | 0
2022-09-22 19:30 | 6.2645 | 0 | N/A | 0 | 0
2022-09-22 20:00 | 5.9814 | 0 | N/A | 0 | 0
2022-09-22 20:30 | 5.8093 | 0 | N/A | 0 | 0
2022-09-22 21:00 | 5.5622 | 0 | N/A | 0 | 0
2022-09-22 21:30 | 5.7819 | 0 | N/A | 0 | 0
2022-09-22 22:00 | 5.8707 | 0 | N/A | 0 | 0
2022-09-22 22:30 | 5.4349 | 0 | N/A | 0 | 0
2022-09-22 23:00 | 5.3463 | 0 | N/A | 0 | 0
2022-09-22 23:30 | 5.5555 | 0 | N/A | 0 | 0
2022-09-23 | 5.7097 | 0 | N/A | 0 | 0
2022-09-23 00:30 | 5.0127 | 0 | N/A | 0 | 0
2022-09-23 01:00 | 4.3704 | 0 | N/A | 0 | 0
2022-09-23 01:30 | 4.3321 | 0 | N/A | 0 | 0
2022-09-23 02:00 | 3.9852 | 0 | N/A | 0 | 0
2022-09-23 02:30 | 3.5698 | 0 | N/A | 0 | 0
2022-09-23 03:00 | 3.325 | 0 | N/A | 0 | 0
2022-09-23 03:30 | 3.2233 | 0 | N/A | 0 | 0
2022-09-23 04:00 | 3.0515 | 0 | N/A | 0 | 0
2022-09-23 04:30 | 3.0028 | 0 | N/A | 0 | 0
2022-09-23 05:00 | 2.9983 | 0 | N/A | 0 | 0
2022-09-23 05:30 | 3.1735 | 0 | N/A | 0 | 0
2022-09-23 06:00 | 3.2938 | 0 | N/A | 0 | 0
2022-09-23 06:30 | 3.5556 | 0 | N/A | 0 | 0
2022-09-23 07:00 | 3.5951 | 0 | N/A | 0 | 0
2022-09-23 07:30 | 3.509 | 0 | N/A | 0 | 0
2022-09-23 08:00 | 3.498 | 0 | N/A | 0 | 0
2022-09-23 08:30 | 3.761 | 0 | N/A | 0 | 0
2022-09-23 09:00 | 4.0648 | 0 | N/A | 0 | 0
2022-09-23 09:30 | 4.298 | 0 | N/A | 0 | 0
2022-09-23 10:00 | 4.3425 | 0 | N/A | 0 | 0
2022-09-23 10:30 | 4.4698 | 0 | N/A | 0 | 0
2022-09-23 11:00 | 4.438 | 0 | N/A | 0 | 0
2022-09-23 11:30 | 4.4375 | 0 | N/A | 0 | 0
2022-09-23 12:00 | 4.3667 | 0 | N/A | 0 | 0
2022-09-23 12:30 | 3.361 | 0 | N/A | 0 | 0
2022-09-23 13:00 | 2.6684 | 0 | N/A | 0 | 0
2022-09-23 13:30 | 2.2738 | 0 | N/A | 0 | 0
2022-09-23 14:00 | 2.151 | 0 | N/A | 0 | 0
2022-09-23 14:30 | 1.7728 | 0 | N/A | 0 | 0
2022-09-23 15:00 | 2.746 | 0 | N/A | 0 | 0
2022-09-23 15:30 | 2.4126 | 0 | N/A | 0 | 0
2022-09-23 16:00 | 3.5628 | 0 | N/A | 0 | 0
2022-09-23 16:30 | 4.5595 | 0 | N/A | 0 | 0
2022-09-23 17:00 | 5.4643 | 0 | N/A | 0 | 0
2022-09-23 17:30 | 6.0404 | 0 | N/A | 0 | 0
2022-09-23 18:00 | 6.7426 | 0 | N/A | 0 | 0
2022-09-23 18:30 | 7.1382 | 0 | N/A | 0 | 0
2022-09-23 19:00 | 7.4464 | 0 | N/A | 0 | 0
2022-09-23 19:30 | 6.6793 | 0 | N/A | 0 | 0
2022-09-23 20:00 | 6.1424 | 0 | N/A | 0 | 0
2022-09-23 20:30 | 5.9064 | 0 | N/A | 0 | 0
2022-09-23 21:00 | 5.7092 | 0 | N/A | 0 | 0
2022-09-23 21:30 | 6.1032 | 0 | N/A | 0 | 0
2022-09-23 22:00 | 6.2374 | 0 | N/A | 0 | 0
2022-09-23 22:30 | 5.7699 | 0 | N/A | 0 | 0
2022-09-23 23:00 | 5.6131 | 0 | N/A | 0 | 0
2022-09-23 23:30 | 5.9313 | 0 | N/A | 0 | 0
2022-09-24 | 6.2033 | 0 | N/A | 0 | 0
2022-09-24 00:30 | 5.5072 | 0 | N/A | 0 | 0
2022-09-24 01:00 | 4.88 | 0 | N/A | 0 | 0
2022-09-24 01:30 | 4.6841 | 0 | N/A | 0 | 0
2022-09-24 02:00 | 4.3524 | 0 | N/A | 0 | 0
2022-09-24 02:30 | 3.9525 | 0 | N/A | 0 | 0
2022-09-24 03:00 | 3.6146 | 0 | N/A | 0 | 0
2022-09-24 03:30 | 3.4837 | 0 | N/A | 0 | 0
2022-09-24 04:00 | 3.4593 | 0 | N/A | 0 | 0
2022-09-24 04:30 | 3.4045 | 0 | N/A | 0 | 0
2022-09-24 05:00 | 3.4251 | 0 | N/A | 0 | 0
2022-09-24 05:30 | 3.6031 | 0 | N/A | 0 | 0
2022-09-24 06:00 | 3.7846 | 0 | N/A | 0 | 0
2022-09-24 06:30 | 4.1843 | 0 | N/A | 0 | 0
2022-09-24 07:00 | 4.1804 | 0 | N/A | 0 | 0
2022-09-24 07:30 | 3.639 | 0 | N/A | 0 | 0
2022-09-24 08:00 | 3.2687 | 0 | N/A | 0 | 0
2022-09-24 08:30 | 2.8809 | 0 | N/A | 0 | 0
2022-09-24 09:00 | 2.2958 | 0 | N/A | 0 | 0
2022-09-24 09:30 | 1.8648 | 0 | N/A | 0 | 0
2022-09-24 10:00 | 1.3341 | 0 | N/A | 0 | 0
2022-09-24 10:30 | 0.88695 | 0 | N/A | 0 | 0
2022-09-24 11:00 | -0.93291 | 0 | N/A | 0 | 0
2022-09-24 11:30 | -0.96764 | 0 | N/A | 0 | 0
2022-09-24 12:00 | 1.1921 | 0 | N/A | 0 | 0
2022-09-24 12:30 | 1.6244 | 0 | N/A | 0 | 0
2022-09-24 13:00 | 1.8147 | 0 | N/A | 0 | 0
2022-09-24 13:30 | 1.7694 | 0 | N/A | 0 | 0
2022-09-24 14:00 | 2.1259 | 0 | N/A | 0 | 0
2022-09-24 14:30 | 1.8887 | 0 | N/A | 0 | 0
2022-09-24 15:00 | 1.7376 | 0 | N/A | 0 | 0
2022-09-24 15:30 | 3.4639 | 0 | N/A | 0 | 0
2022-09-24 16:00 | 3.4768 | 0 | N/A | 0 | 0
2022-09-24 16:30 | 3.6925 | 0 | N/A | 0 | 0
2022-09-24 17:00 | 4.1394 | 0 | N/A | 0 | 0
2022-09-24 17:30 | 4.7316 | 0 | N/A | 0 | 0
2022-09-24 18:00 | 5.7786 | 0 | N/A | 0 | 0
2022-09-24 18:30 | 6.5291 | 0 | N/A | 0 | 0
2022-09-24 19:00 | 7.0294 | 0 | N/A | 0 | 0
2022-09-24 19:30 | 7.0919 | 0 | N/A | 0 | 0
2022-09-24 20:00 | 5.949 | 0 | N/A | 0 | 0
2022-09-24 20:30 | 0.57714 | 0 | N/A | 0 | 0
2022-09-24 21:00 | 1.5976 | 0 | N/A | 0 | 0
2022-09-24 21:30 | 6.5046 | 0 | N/A | 0 | 0
2022-09-24 22:00 | 6.9158 | 0 | N/A | 0 | 0
2022-09-24 22:30 | 7.7629 | 0 | N/A | 0 | 0
2022-09-24 23:00 | 7.8522 | 0 | N/A | 0 | 0
2022-09-24 23:30 | 8.124 | 0 | N/A | 0 | 0
2022-09-25 | 8.2266 | 0 | N/A | 0 | 0
2022-09-25 00:30 | 7.5156 | 0 | N/A | 0 | 0
2022-09-25 01:00 | 6.8375 | 0 | N/A | 0 | 0
2022-09-25 01:30 | 6.0895 | 0 | N/A | 0 | 0
2022-09-25 02:00 | 4.9761 | 0 | N/A | 0 | 0
2022-09-25 02:30 | 4.6652 | 0 | N/A | 0 | 0
2022-09-25 03:00 | 4.3978 | 0 | N/A | 0 | 0
2022-09-25 03:30 | 4.2602 | 0 | N/A | 0 | 0
2022-09-25 04:00 | 4.1352 | 0 | N/A | 0 | 0
2022-09-25 04:30 | 4.1384 | 0 | N/A | 0 | 0
2022-09-25 05:00 | 4.111 | 0 | N/A | 0 | 0
2022-09-25 05:30 | 4.3157 | 0 | N/A | 0 | 0
2022-09-25 06:00 | 4.4931 | 0 | N/A | 0 | 0
2022-09-25 06:30 | 4.6973 | 0 | N/A | 0 | 0
2022-09-25 07:00 | 4.6785 | 0 | N/A | 0 | 0
2022-09-25 07:30 | 3.9931 | 0 | N/A | 0 | 0
2022-09-25 08:00 | 3.6223 | 0 | N/A | 0 | 0
2022-09-25 08:30 | 3.039 | 0 | N/A | 0 | 0
2022-09-25 09:00 | 2.2243 | 0 | N/A | 0 | 0
2022-09-25 09:30 | 1.7239 | 0 | N/A | 0 | 0
2022-09-25 10:00 | 1.0419 | 0 | N/A | 0 | 0
2022-09-25 10:30 | -0.88717 | 0 | N/A | 0 | 0
2022-09-25 11:00 | -1.1815 | 0 | N/A | 0 | 0
2022-09-25 11:30 | -1.2823 | 0 | N/A | 0 | 0
2022-09-25 12:00 | -1.3734 | 0 | N/A | 0 | 0
2022-09-25 12:30 | -1.3952 | 0 | N/A | 0 | 0
2022-09-25 13:00 | -1.7276 | 0 | N/A | 0 | 0
2022-09-25 13:30 | -1.3437 | 0 | N/A | 0 | 0
2022-09-25 14:00 | -1.2313 | 0 | N/A | 0 | 0
2022-09-25 14:30 | -1.4951 | 0 | N/A | 0 | 0
2022-09-25 15:00 | -1.3955 | 0 | N/A | 0 | 0
2022-09-25 15:30 | 1.1236 | 0 | N/A | 0 | 0
2022-09-25 16:00 | 1.2957 | 0 | N/A | 0 | 0
2022-09-25 16:30 | 1.7913 | 0 | N/A | 0 | 0
2022-09-25 17:00 | 2.949 | 0 | N/A | 0 | 0
2022-09-25 17:30 | 4.3195 | 0 | N/A | 0 | 0
2022-09-25 18:00 | 5.4555 | 0 | N/A | 0 | 0
2022-09-25 18:30 | 6.3457 | 0 | N/A | 0 | 0
2022-09-25 19:00 | 7.1091 | 0 | N/A | 0 | 0
2022-09-25 19:30 | 7.2112 | 0 | N/A | 0 | 0
2022-09-25 20:00 | 7.0372 | 0 | N/A | 0 | 0
2022-09-25 20:30 | 6.5935 | 0 | N/A | 0 | 0
2022-09-25 21:00 | 6.1831 | 0 | N/A | 0 | 0
2022-09-25 21:30 | 6.3262 | 0 | N/A | 0 | 0
2022-09-25 22:00 | 6.208 | 0 | N/A | 0 | 0
2022-09-25 22:30 | 5.8351 | 0 | N/A | 0 | 0
2022-09-25 23:00 | 5.7351 | 0 | N/A | 0 | 0
2022-09-25 23:30 | 5.7259 | 0 | N/A | 0 | 0
2022-09-26 | 5.9335 | 0 | N/A | 0 | 0
2022-09-26 00:30 | 5.4252 | 0 | N/A | 0 | 0
2022-09-26 01:00 | 4.7743 | 0 | N/A | 0 | 0
2022-09-26 01:30 | 4.6624 | 0 | N/A | 0 | 0
2022-09-26 02:00 | 4.3037 | 0 | N/A | 0 | 0
2022-09-26 02:30 | 3.8941 | 0 | N/A | 0 | 0
2022-09-26 03:00 | 3.5537 | 0 | N/A | 0 | 0
2022-09-26 03:30 | 3.3985 | 0 | N/A | 0 | 0
2022-09-26 04:00 | 3.2722 | 0 | N/A | 0 | 0
2022-09-26 04:30 | 3.306 | 0 | N/A | 0 | 0
2022-09-26 05:00 | 3.3528 | 0 | N/A | 0 | 0
2022-09-26 05:30 | 3.6063 | 0 | N/A | 0 | 0
2022-09-26 06:00 | 3.9824 | 0 | N/A | 0 | 0
2022-09-26 06:30 | 4.5837 | 0 | N/A | 0 | 0
2022-09-26 07:00 | 4.9019 | 0 | N/A | 0 | 0
2022-09-26 07:30 | 4.7595 | 0 | N/A | 0 | 0
2022-09-26 08:00 | 5.0302 | 0 | N/A | 0 | 0
2022-09-26 08:30 | 5.5134 | 0 | N/A | 0 | 0
2022-09-26 09:00 | 5.331 | 0 | N/A | 0 | 0
2022-09-26 09:30 | 4.6377 | 0 | N/A | 0 | 0
2022-09-26 10:00 | 4.5373 | 0 | N/A | 0 | 0
2022-09-26 10:30 | 3.6559 | 0 | N/A | 0 | 0
2022-09-26 11:00 | 3.4134 | 0 | N/A | 0 | 0
2022-09-26 11:30 | 3.3389 | 0 | N/A | 0 | 0
2022-09-26 12:00 | 3.1727 | 0 | N/A | 0 | 0
2022-09-26 12:30 | 2.374 | 0 | N/A | 0 | 0
2022-09-26 13:00 | 1.9736 | 0 | N/A | 0 | 0
2022-09-26 13:30 | 2.882 | 0 | N/A | 0 | 0
2022-09-26 14:00 | 3.9963 | 0 | N/A | 0 | 0
2022-09-26 14:30 | 4.2526 | 0 | N/A | 0 | 0
2022-09-26 15:00 | 3.5578 | 0 | N/A | 0 | 0
2022-09-26 15:30 | 3.174 | 0 | N/A | 0 | 0
2022-09-26 16:00 | 3.6413 | 0 | N/A | 0 | 0
2022-09-26 16:30 | 4.0605 | 0 | N/A | 0 | 0
2022-09-26 17:00 | 5.3469 | 0 | N/A | 0 | 0
2022-09-26 17:30 | 6.4543 | 0 | N/A | 0 | 0
2022-09-26 18:00 | 7.395 | 0 | N/A | 0 | 0
2022-09-26 18:30 | 7.8641 | 0 | N/A | 0 | 0
2022-09-26 19:00 | 8.0185 | 0 | N/A | 0 | 0
2022-09-26 19:30 | 7.7762 | 0 | N/A | 0 | 0
2022-09-26 20:00 | 7.5564 | 0 | N/A | 0 | 0
2022-09-26 20:30 | 7.1554 | 0 | N/A | 0 | 0
2022-09-26 21:00 | 6.8561 | 0 | N/A | 0 | 0
2022-09-26 21:30 | 7.0095 | 0 | N/A | 0 | 0
2022-09-26 22:00 | 6.8719 | 0 | N/A | 0 | 0
2022-09-26 22:30 | 6.2658 | 0 | N/A | 0 | 0
2022-09-26 23:00 | 5.9531 | 0 | N/A | 0 | 0
2022-09-26 23:30 | 6.0068 | 0 | N/A | 0 | 0
2022-09-27 | 6.1952 | 0 | N/A | 0 | 0
2022-09-27 00:30 | 5.5646 | 0 | N/A | 0 | 0
2022-09-27 01:00 | 4.7918 | 0 | N/A | 0 | 0
2022-09-27 01:30 | 4.6177 | 0 | N/A | 0 | 0
2022-09-27 02:00 | 4.3418 | 0 | N/A | 0 | 0
2022-09-27 02:30 | 3.8896 | 0 | N/A | 0 | 0
2022-09-27 03:00 | 3.6728 | 0 | N/A | 0 | 0
2022-09-27 03:30 | 3.5494 | 0 | N/A | 0 | 0
2022-09-27 04:00 | 3.454 | 0 | N/A | 0 | 0
2022-09-27 04:30 | 3.4175 | 0 | N/A | 0 | 0
2022-09-27 05:00 | 3.4855 | 0 | N/A | 0 | 0
2022-09-27 05:30 | 3.8136 | 0 | N/A | 0 | 0
2022-09-27 06:00 | 4.1754 | 0 | N/A | 0 | 0
2022-09-27 06:30 | 4.6985 | 0 | N/A | 0 | 0
2022-09-27 07:00 | 5.0342 | 0 | N/A | 0 | 0
2022-09-27 07:30 | 5.3162 | 0 | N/A | 0 | 0
2022-09-27 08:00 | 5.8022 | 0 | N/A | 0 | 0
2022-09-27 08:30 | 5.8143 | 0 | N/A | 0 | 0
2022-09-27 09:00 | 5.3306 | 0 | N/A | 0 | 0
2022-09-27 09:30 | 5.5862 | 0 | N/A | 0 | 0
2022-09-27 10:00 | 5.8852 | 0 | N/A | 0 | 0
2022-09-27 10:30 | 5.1603 | 0 | N/A | 0 | 0
2022-09-27 11:00 | 5.4014 | 0 | N/A | 0 | 0
2022-09-27 11:30 | 5.686 | 0 | N/A | 0 | 0
2022-09-27 12:00 | 5.6058 | 0 | N/A | 0 | 0
2022-09-27 12:30 | 5.7227 | 0 | N/A | 0 | 0
2022-09-27 13:00 | 5.6767 | 0 | N/A | 0 | 0
2022-09-27 13:30 | 5.8312 | 0 | N/A | 0 | 0
2022-09-27 14:00 | 5.728 | 0 | N/A | 0 | 0
2022-09-27 14:30 | 5.7698 | 0 | N/A | 0 | 0
2022-09-27 15:00 | 5.5052 | 0 | N/A | 0 | 0
2022-09-27 15:30 | 5.5477 | 0 | N/A | 0 | 0
2022-09-27 16:00 | 5.544 | 0 | N/A | 0 | 0
2022-09-27 16:30 | 6.2523 | 0 | N/A | 0 | 0
2022-09-27 17:00 | 6.7621 | 0 | N/A | 0 | 0
2022-09-27 17:30 | 7.4944 | 0 | N/A | 0 | 0
2022-09-27 18:00 | 8.2174 | 0 | N/A | 0 | 0
2022-09-27 18:30 | 8.4986 | 0 | N/A | 0 | 0
2022-09-27 19:00 | 8.4126 | 0 | N/A | 0 | 0
2022-09-27 19:30 | 8.1637 | 0 | N/A | 0 | 0
2022-09-27 20:00 | 7.761 | 0 | N/A | 0 | 0
2022-09-27 20:30 | 7.4628 | 0 | N/A | 0 | 0
2022-09-27 21:00 | 7.107 | 0 | N/A | 0 | 0
2022-09-27 21:30 | 7.2704 | 0 | N/A | 0 | 0
2022-09-27 22:00 | 7.1104 | 0 | N/A | 0 | 0
2022-09-27 22:30 | 6.3712 | 0 | N/A | 0 | 0
2022-09-27 23:00 | 6.0965 | 0 | N/A | 0 | 0
2022-09-27 23:30 | 6.1968 | 0 | N/A | 0 | 0
2022-09-28 | 6.4615 | 0 | N/A | 0 | 0
2022-09-30 00:30 | 5.87 | 0 | N/A | 0 | 0
2022-09-30 01:00 | 5.1193 | 0 | N/A | 0 | 0
2022-09-30 01:30 | 5.0448 | 0 | N/A | 0 | 0
2022-09-30 02:00 | 4.7371 | 0 | N/A | 0 | 0
2022-09-30 02:30 | 4.2144 | 0 | N/A | 0 | 0
2022-09-30 03:00 | 3.9051 | 0 | N/A | 0 | 0
2022-09-30 03:30 | 3.7278 | 0 | N/A | 0 | 0
2022-09-30 04:00 | 3.6755 | 0 | N/A | 0 | 0
2022-09-30 04:30 | 3.6654 | 0 | N/A | 0 | 0
2022-09-30 05:00 | 3.7161 | 0 | N/A | 0 | 0
2022-09-30 05:30 | 4.0626 | 0 | N/A | 0 | 0
2022-09-30 06:00 | 4.4515 | 0 | N/A | 0 | 0
2022-09-30 06:30 | 5.3025 | 0 | N/A | 0 | 0
2022-09-30 07:00 | 5.6144 | 0 | N/A | 0 | 0
2022-09-30 07:30 | 5.4812 | 0 | N/A | 0 | 0
2022-09-30 08:00 | 5.8425 | 0 | N/A | 0 | 0
2022-09-30 08:30 | 5.4953 | 0 | N/A | 0 | 0
2022-09-30 09:00 | 4.689 | 0 | N/A | 0 | 0
2022-09-30 09:30 | 3.1667 | 0 | N/A | 0 | 0
2022-09-30 10:00 | 2.1928 | 0 | N/A | 0 | 0
2022-09-30 10:30 | 1.548 | 0 | N/A | 0 | 0
2022-09-30 11:00 | 0.92154 | 0 | N/A | 0 | 0
2022-09-30 11:30 | -0.80367 | 0 | N/A | 0 | 0
2022-09-30 12:00 | -0.80236 | 0 | N/A | 0 | 0
2022-09-30 12:30 | -1.0586 | 0 | N/A | 0 | 0
2022-09-30 13:00 | -1.0512 | 0 | N/A | 0 | 0
2022-09-30 13:30 | -0.9055 | 0 | N/A | 0 | 0
2022-09-30 14:00 | -0.95053 | 0 | N/A | 0 | 0
2022-09-30 14:30 | 1.4238 | 0 | N/A | 0 | 0
2022-09-30 15:00 | 1.8678 | 0 | N/A | 0 | 0
2022-09-30 15:30 | 1.8979 | 0 | N/A | 0 | 0
2022-09-30 16:00 | 1.4613 | 0 | N/A | 0 | 0
2022-09-30 16:30 | 2.1544 | 0 | N/A | 0 | 0
2022-09-30 17:00 | 3.0599 | 0 | N/A | 0 | 0
2022-09-30 17:30 | 4.0661 | 0 | N/A | 0 | 0
2022-09-30 18:00 | 4.917 | 0 | N/A | 0 | 0
2022-09-30 18:30 | 5.9057 | 0 | N/A | 0 | 0
2022-09-30 19:00 | 6.5344 | 0 | N/A | 0 | 0
2022-09-30 19:30 | 6.8232 | 0 | N/A | 0 | 0
2022-09-30 20:00 | 6.6954 | 0 | N/A | 0 | 0
2022-09-30 20:30 | 6.5557 | 0 | N/A | 0 | 0
2022-09-30 21:00 | 6.4713 | 0 | N/A | 0 | 0
2022-09-30 21:30 | 6.7501 | 0 | N/A | 0 | 0
2022-09-30 22:00 | 6.6938 | 0 | N/A | 0 | 0
2022-09-30 22:30 | 6.1217 | 0 | N/A | 0 | 0
2022-09-30 23:00 | 5.971 | 0 | N/A | 0 | 0
2022-09-30 23:30 | 6.2378 | 0 | N/A | 0 | 0
2022-10-01 | 6.4067 | 0 | N/A | 0 | 0
2022-10-01 00:30 | 5.6351 | 0 | N/A | 0 | 0
2022-10-01 01:00 | 5.0391 | 0 | N/A | 0 | 0
2022-10-01 01:30 | 4.8585 | 0 | N/A | 0 | 0
2022-10-01 02:00 | 4.4093 | 0 | N/A | 0 | 0
2022-10-01 02:30 | 3.9847 | 0 | N/A | 0 | 0
2022-10-01 03:00 | 3.7365 | 0 | N/A | 0 | 0
2022-10-01 03:30 | 3.6 | 0 | N/A | 0 | 0
2022-10-01 04:00 | 3.4464 | 0 | N/A | 0 | 0
2022-10-01 04:30 | 3.393 | 0 | N/A | 0 | 0
2022-10-01 05:00 | 3.4503 | 0 | N/A | 0 | 0
2022-10-01 05:30 | 3.649 | 0 | N/A | 0 | 0
2022-10-01 06:00 | 3.811 | 0 | N/A | 0 | 0
2022-10-01 06:30 | 4.1724 | 0 | N/A | 0 | 0
2022-10-01 07:00 | 4.1409 | 0 | N/A | 0 | 0
2022-10-01 07:30 | 3.8807 | 0 | N/A | 0 | 0
2022-10-01 08:00 | 4.1302 | 0 | N/A | 0 | 0
2022-10-01 08:30 | 3.7931 | 0 | N/A | 0 | 0
2022-10-01 09:00 | 2.6213 | 0 | N/A | 0 | 0
2022-10-01 09:30 | 1.4622 | 0 | N/A | 0 | 0
2022-10-01 10:00 | 0.98268 | 0 | N/A | 0 | 0
2022-10-01 10:30 | -1.1326 | 0 | N/A | 0 | 0
2022-10-01 11:00 | -1.512 | 0 | N/A | 0 | 0
2022-10-01 11:30 | -1.8844 | 0 | N/A | 0 | 0
2022-10-01 12:00 | -2.091 | 0 | N/A | 0 | 0
2022-10-01 12:30 | -2.2183 | 0 | N/A | 0 | 0
2022-10-01 13:00 | -2.2234 | 0 | N/A | 0 | 0
2022-10-01 13:30 | -2.1085 | 0 | N/A | 0 | 0
2022-10-01 14:00 | -1.9588 | 0 | N/A | 0 | 0
2022-10-01 14:30 | -1.8346 | 0 | N/A | 0 | 0
2022-10-01 15:00 | -1.4527 | 0 | N/A | 0 | 0
2022-10-01 15:30 | -1.1353 | 0 | N/A | 0 | 0
2022-10-01 16:00 | 1.2462 | 0 | N/A | 0 | 0
2022-10-01 16:30 | 1.9668 | 0 | N/A | 0 | 0
2022-10-01 17:00 | 2.4398 | 0 | N/A | 0 | 0
2022-10-01 17:30 | 3.5274 | 0 | N/A | 0 | 0
2022-10-01 18:00 | 4.6349 | 0 | N/A | 0 | 0
2022-10-01 18:30 | 5.5168 | 0 | N/A | 0 | 0
2022-10-01 19:00 | 6.2034 | 0 | N/A | 0 | 0
2022-10-01 19:30 | 6.354 | 0 | N/A | 0 | 0
2022-10-01 20:00 | 6.1781 | 0 | N/A | 0 | 0
2022-10-01 20:30 | 6.0391 | 0 | N/A | 0 | 0
2022-10-01 21:00 | 5.7562 | 0 | N/A | 0 | 0
2022-10-01 21:30 | 6.083 | 0 | N/A | 0 | 0
2022-10-01 22:00 | 6.2231 | 0 | N/A | 0 | 0
2022-10-01 22:30 | 5.8798 | 0 | N/A | 0 | 0
2022-10-01 23:00 | 5.8504 | 0 | N/A | 0 | 0
2022-10-01 23:30 | 6.1137 | 0 | N/A | 0 | 0
2022-10-02 | 6.2912 | 0 | N/A | 0 | 0
2022-10-02 00:30 | 5.6959 | 0 | N/A | 0 | 0
2022-10-02 01:00 | 5.078 | 0 | N/A | 0 | 0
2022-10-02 01:30 | 4.9493 | 0 | N/A | 0 | 0
2022-10-02 02:00 | 4.7225 | 0 | N/A | 0 | 0
2022-10-02 03:30 | 4.2118 | 0 | N/A | 0 | 0
2022-10-02 04:00 | 3.951 | 0 | N/A | 0 | 0
2022-10-02 04:30 | 3.7214 | 0 | N/A | 0 | 0
2022-10-02 05:00 | 3.6421 | 0 | N/A | 0 | 0
2022-10-02 05:30 | 3.7152 | 0 | N/A | 0 | 0
2022-10-02 06:00 | 3.7411 | 0 | N/A | 0 | 0
2022-10-02 06:30 | 4.0702 | 0 | N/A | 0 | 0
2022-10-02 07:00 | 4.304 | 0 | N/A | 0 | 0
2022-10-02 07:30 | 4.5983 | 0 | N/A | 0 | 0
2022-10-02 08:00 | 4.4986 | 0 | N/A | 0 | 0
2022-10-02 08:30 | 3.8665 | 0 | N/A | 0 | 0
2022-10-02 09:00 | 3.3702 | 0 | N/A | 0 | 0
2022-10-02 09:30 | 2.5961 | 0 | N/A | 0 | 0
2022-10-02 10:00 | 1.7453 | 0 | N/A | 0 | 0
2022-10-02 10:30 | 1.0891 | 0 | N/A | 0 | 0
2022-10-02 11:00 | -0.83156 | 0 | N/A | 0 | 0
2022-10-02 11:30 | -0.94071 | 0 | N/A | 0 | 0
2022-10-02 12:00 | -1.4006 | 0 | N/A | 0 | 0
2022-10-02 12:30 | -1.3207 | 0 | N/A | 0 | 0
2022-10-02 13:00 | -1.0419 | 0 | N/A | 0 | 0
2022-10-02 13:30 | -1.3054 | 0 | N/A | 0 | 0
2022-10-02 14:00 | -1.1766 | 0 | N/A | 0 | 0
2022-10-02 14:30 | -1.5023 | 0 | N/A | 0 | 0
2022-10-02 15:00 | -1.4385 | 0 | N/A | 0 | 0
2022-10-02 15:30 | -1.681 | 0 | N/A | 0 | 0
2022-10-02 16:00 | -1.3038 | 0 | N/A | 0 | 0
2022-10-02 16:30 | -0.91691 | 0 | N/A | 0 | 0
2022-10-02 17:00 | 0.98419 | 0 | N/A | 0 | 0
2022-10-02 17:30 | 1.8407 | 0 | N/A | 0 | 0
2022-10-02 18:00 | 3.0092 | 0 | N/A | 0 | 0
2022-10-02 18:30 | 4.2715 | 0 | N/A | 0 | 0
2022-10-02 19:00 | 5.1648 | 0 | N/A | 0 | 0
2022-10-02 19:30 | 5.7355 | 0 | N/A | 0 | 0
2022-10-02 20:00 | 6.1561 | 0 | N/A | 0 | 0
2022-10-02 20:30 | 6.2477 | 0 | N/A | 0 | 0
2022-10-02 21:00 | 6.0795 | 0 | N/A | 0 | 0
2022-10-02 21:30 | 5.8737 | 0 | N/A | 0 | 0
2022-10-02 22:00 | 5.5037 | 0 | N/A | 0 | 0
2022-10-02 22:30 | 5.6285 | 0 | N/A | 0 | 0
2022-10-02 23:00 | 5.6233 | 0 | N/A | 0 | 0
2022-10-02 23:30 | 5.275 | 0 | N/A | 0 | 0
2022-10-03 | 5.2008 | 0 | N/A | 0 | 0
2022-10-03 00:30 | 5.3148 | 0 | N/A | 0 | 0
2022-10-03 01:00 | 5.6212 | 0 | N/A | 0 | 0
2022-10-03 01:30 | 5.1668 | 0 | N/A | 0 | 0
2022-10-03 02:00 | 4.6368 | 0 | N/A | 0 | 0
2022-10-03 02:30 | 4.6296 | 0 | N/A | 0 | 0
2022-10-03 03:00 | 4.4121 | 0 | N/A | 0 | 0
2022-10-03 03:30 | 3.9796 | 0 | N/A | 0 | 0
2022-10-03 04:00 | 3.7282 | 0 | N/A | 0 | 0
2022-10-03 04:30 | 3.6049 | 0 | N/A | 0 | 0
2022-10-03 05:00 | 3.6041 | 0 | N/A | 0 | 0
2022-10-03 05:30 | 3.8188 | 0 | N/A | 0 | 0
2022-10-03 06:00 | 4.2347 | 0 | N/A | 0 | 0
2022-10-03 06:30 | 4.8774 | 0 | N/A | 0 | 0
2022-10-03 07:00 | 5.7332 | 0 | N/A | 0 | 0
2022-10-03 07:30 | 7.1429 | 0 | N/A | 0 | 0
2022-10-03 08:00 | 7.4692 | 0 | N/A | 0 | 0
2022-10-03 08:30 | 6.6464 | 0 | N/A | 0 | 0
2022-10-03 09:00 | 5.211 | 0 | N/A | 0 | 0
2022-10-03 09:30 | 4.4776 | 0 | N/A | 0 | 0
2022-10-03 10:00 | 3.5989 | 0 | N/A | 0 | 0
2022-10-03 10:30 | 2.9483 | 0 | N/A | 0 | 0
2022-10-03 11:00 | 1.4056 | 0 | N/A | 0 | 0
2022-10-03 11:30 | 0.79404 | 0 | N/A | 0 | 0
2022-10-03 12:00 | -0.79468 | 0 | N/A | 0 | 0
2022-10-03 12:30 | -0.88155 | 0 | N/A | 0 | 0
2022-10-03 13:00 | -0.88818 | 0 | N/A | 0 | 0
2022-10-03 13:30 | -0.7446 | 0 | N/A | 0 | 0
2022-10-03 14:00 | -0.79076 | 0 | N/A | 0 | 0
2022-10-03 14:30 | -0.87669 | 0 | N/A | 0 | 0
2022-10-03 15:00 | -0.80964 | 0 | N/A | 0 | 0
2022-10-03 15:30 | 1.5288 | 0 | N/A | 0 | 0
2022-10-03 16:00 | 1.7991 | 0 | N/A | 0 | 0
2022-10-03 16:30 | 2.2479 | 0 | N/A | 0 | 0
2022-10-03 17:00 | 3.6129 | 0 | N/A | 0 | 0
2022-10-03 17:30 | 4.7715 | 0 | N/A | 0 | 0
2022-10-03 18:00 | 5.5874 | 0 | N/A | 0 | 0
2022-10-03 18:30 | 5.8144 | 0 | N/A | 0 | 0
2022-10-03 19:00 | 6.1012 | 0 | N/A | 0 | 0
2022-10-03 19:30 | 6.273 | 0 | N/A | 0 | 0
2022-10-03 20:00 | 6.3624 | 0 | N/A | 0 | 0
2022-10-03 20:30 | 6.2654 | 0 | N/A | 0 | 0
2022-10-03 21:00 | 6.0044 | 0 | N/A | 0 | 0
2022-10-03 21:30 | 5.6936 | 0 | N/A | 0 | 0
2022-10-03 22:00 | 5.3122 | 0 | N/A | 0 | 0
2022-10-03 22:30 | 5.2885 | 0 | N/A | 0 | 0
2022-10-03 23:00 | 5.2574 | 0 | N/A | 0 | 0
2022-10-03 23:30 | 4.7548 | 0 | N/A | 0 | 0
2022-10-04 | 4.573 | 0 | N/A | 0 | 0
2022-10-04 00:30 | 4.7664 | 0 | N/A | 0 | 0
2022-10-04 01:00 | 5.1058 | 0 | N/A | 0 | 0
2022-10-04 01:30 | 4.6584 | 0 | N/A | 0 | 0
2022-10-04 02:00 | 4.1573 | 0 | N/A | 0 | 0
2022-10-04 02:30 | 4.2197 | 0 | N/A | 0 | 0
2022-10-04 03:00 | 3.827 | 0 | N/A | 0 | 0
2022-10-04 03:30 | 3.5446 | 0 | N/A | 0 | 0
2022-10-04 04:00 | 3.2955 | 0 | N/A | 0 | 0
2022-10-04 04:30 | 3.2504 | 0 | N/A | 0 | 0
2022-10-04 05:00 | 3.2633 | 0 | N/A | 0 | 0
2022-10-04 05:30 | 3.5694 | 0 | N/A | 0 | 0
2022-10-04 06:00 | 3.9093 | 0 | N/A | 0 | 0
2022-10-04 06:30 | 4.6947 | 0 | N/A | 0 | 0
2022-10-04 07:00 | 5.3723 | 0 | N/A | 0 | 0
2022-10-04 07:30 | 6.7028 | 0 | N/A | 0 | 0
2022-10-04 08:00 | 6.5829 | 0 | N/A | 0 | 0
2022-10-04 08:30 | 5.8628 | 0 | N/A | 0 | 0
2022-10-04 09:00 | 4.9772 | 0 | N/A | 0 | 0
2022-10-04 09:30 | 3.7732 | 0 | N/A | 0 | 0
2022-10-04 10:00 | 2.964 | 0 | N/A | 0 | 0
2022-10-04 10:30 | 2.3467 | 0 | N/A | 0 | 0
2022-10-04 11:00 | 2.1282 | 0 | N/A | 0 | 0
2022-10-04 11:30 | 2.1312 | 0 | N/A | 0 | 0
2022-10-04 12:00 | 1.5066 | 0 | N/A | 0 | 0
2022-10-04 12:30 | 1.3739 | 0 | N/A | 0 | 0
2022-10-04 13:00 | 2.4821 | 0 | N/A | 0 | 0
2022-10-04 13:30 | 2.8211 | 0 | N/A | 0 | 0
2022-10-04 14:00 | 2.9527 | 0 | N/A | 0 | 0
2022-10-04 14:30 | 3.8952 | 0 | N/A | 0 | 0
2022-10-04 15:00 | 4.3352 | 0 | N/A | 0 | 0
2022-10-04 15:30 | 4.8029 | 0 | N/A | 0 | 0
2022-10-04 16:00 | 5.3057 | 0 | N/A | 0 | 0
2022-10-04 16:30 | 5.1442 | 0 | N/A | 0 | 0
2022-10-04 17:00 | 5.239 | 0 | N/A | 0 | 0
2022-10-04 17:30 | 5.452 | 0 | N/A | 0 | 0
2022-10-04 18:00 | 6.2176 | 0 | N/A | 0 | 0
2022-10-04 18:30 | 6.7133 | 0 | N/A | 0 | 0
2022-10-04 19:00 | 7.1163 | 0 | N/A | 0 | 0
2022-10-04 19:30 | 7.4241 | 0 | N/A | 0 | 0
2022-10-04 20:00 | 7.5746 | 0 | N/A | 0 | 0
2022-10-04 20:30 | 7.6754 | 0 | N/A | 0 | 0
2022-10-04 21:00 | 7.4117 | 0 | N/A | 0 | 0
2022-10-04 21:30 | 6.9275 | 0 | N/A | 0 | 0
2022-10-04 22:00 | 6.4833 | 0 | N/A | 0 | 0
2022-10-04 22:30 | 6.3323 | 0 | N/A | 0 | 0
2022-10-04 23:00 | 6.0758 | 0 | N/A | 0 | 0
2022-10-04 23:30 | 5.4646 | 0 | N/A | 0 | 0
2022-10-05 | 5.2849 | 0 | N/A | 0 | 0
2022-10-05 00:30 | 5.4862 | 0 | N/A | 0 | 0
2022-10-05 01:00 | 5.8598 | 0 | N/A | 0 | 0
2022-10-05 01:30 | 5.3253 | 0 | N/A | 0 | 0
2022-10-05 02:00 | 4.7733 | 0 | N/A | 0 | 0
2022-10-05 02:30 | 4.5657 | 0 | N/A | 0 | 0
2022-10-05 03:00 | 4.352 | 0 | N/A | 0 | 0
2022-10-05 03:30 | 3.9584 | 0 | N/A | 0 | 0
2022-10-05 04:00 | 3.7751 | 0 | N/A | 0 | 0
2022-10-05 04:30 | 3.6779 | 0 | N/A | 0 | 0
2022-10-05 05:00 | 3.709 | 0 | N/A | 0 | 0
2022-10-05 05:30 | 3.9821 | 0 | N/A | 0 | 0
2022-10-05 06:00 | 4.3608 | 0 | N/A | 0 | 0
2022-10-05 06:30 | 4.9759 | 0 | N/A | 0 | 0
2022-10-05 07:00 | 5.9207 | 0 | N/A | 0 | 0
2022-10-05 07:30 | 7.3114 | 0 | N/A | 0 | 0
2022-10-05 08:00 | 7.922 | 0 | N/A | 0 | 0
2022-10-05 08:30 | 7.1625 | 0 | N/A | 0 | 0
2022-10-05 09:00 | 6.9133 | 0 | N/A | 0 | 0
2022-10-05 09:30 | 7.0991 | 0 | N/A | 0 | 0
2022-10-05 10:00 | 6.8189 | 0 | N/A | 0 | 0
2022-10-05 10:30 | 6.2216 | 0 | N/A | 0 | 0
2022-10-05 11:00 | 6.1299 | 0 | N/A | 0 | 0
2022-10-05 11:30 | 6.0798 | 0 | N/A | 0 | 0
2022-10-05 12:00 | 5.8282 | 0 | N/A | 0 | 0
2022-10-05 12:30 | 5.9253 | 0 | N/A | 0 | 0
2022-10-05 13:00 | 5.9841 | 0 | N/A | 0 | 0
2022-10-05 13:30 | 5.8042 | 0 | N/A | 0 | 0
2022-10-05 14:00 | 5.5701 | 0 | N/A | 0 | 0
2022-10-05 14:30 | 5.8251 | 0 | N/A | 0 | 0
2022-10-05 15:00 | 6.0644 | 0 | N/A | 0 | 0
2022-10-05 15:30 | 6.046 | 0 | N/A | 0 | 0
2022-10-05 16:00 | 6.0595 | 0 | N/A | 0 | 0
2022-10-05 16:30 | 6.0929 | 0 | N/A | 0 | 0
2022-10-05 17:00 | 6.7113 | 0 | N/A | 0 | 0
2022-10-05 17:30 | 7.1207 | 0 | N/A | 0 | 0
2022-10-05 18:00 | 7.8712 | 0 | N/A | 0 | 0
2022-10-05 18:30 | 8.0559 | 0 | N/A | 0 | 0
2022-10-05 19:00 | 8.0164 | 0 | N/A | 0 | 0
2022-10-05 19:30 | 7.9799 | 0 | N/A | 0 | 0
2022-10-05 20:00 | 7.8115 | 0 | N/A | 0 | 0
2022-10-05 20:30 | 7.5173 | 0 | N/A | 0 | 0
2022-10-05 21:00 | 7.1491 | 0 | N/A | 0 | 0
2022-10-05 21:30 | 6.7686 | 0 | N/A | 0 | 0
2022-10-05 22:00 | 6.2506 | 0 | N/A | 0 | 0
2022-10-05 22:30 | 6.0264 | 0 | N/A | 0 | 0
2022-10-05 23:00 | 5.791 | 0 | N/A | 0 | 0
2022-10-05 23:30 | 5.4445 | 0 | N/A | 0 | 0
2022-10-06 | 5.3897 | 0 | N/A | 0 | 0
2022-10-06 00:30 | 5.5211 | 0 | N/A | 0 | 0
2022-10-06 01:00 | 5.8382 | 0 | N/A | 0 | 0
2022-10-06 01:30 | 5.2907 | 0 | N/A | 0 | 0
2022-10-06 02:00 | 4.6886 | 0 | N/A | 0 | 0
2022-10-06 02:30 | 4.5833 | 0 | N/A | 0 | 0
2022-10-06 03:00 | 4.2411 | 0 | N/A | 0 | 0
2022-10-06 03:30 | 3.8201 | 0 | N/A | 0 | 0
2022-10-06 04:00 | 3.5629 | 0 | N/A | 0 | 0
2022-10-06 04:30 | 3.498 | 0 | N/A | 0 | 0
2022-10-06 05:00 | 3.5196 | 0 | N/A | 0 | 0
2022-10-06 05:30 | 3.8822 | 0 | N/A | 0 | 0
2022-10-06 06:00 | 4.2167 | 0 | N/A | 0 | 0
2022-10-06 06:30 | 4.768 | 0 | N/A | 0 | 0
2022-10-06 07:00 | 5.4799 | 0 | N/A | 0 | 0
2022-10-06 07:30 | 6.6255 | 0 | N/A | 0 | 0
2022-10-06 08:00 | 7.2266 | 0 | N/A | 0 | 0
2022-10-06 08:30 | 6.5277 | 0 | N/A | 0 | 0
2022-10-06 09:00 | 5.3964 | 0 | N/A | 0 | 0
2022-10-06 09:30 | 4.9389 | 0 | N/A | 0 | 0
2022-10-06 10:00 | 4.8155 | 0 | N/A | 0 | 0
2022-10-06 10:30 | 4.0772 | 0 | N/A | 0 | 0
2022-10-06 11:00 | 2.8799 | 0 | N/A | 0 | 0
2022-10-06 11:30 | 2.2818 | 0 | N/A | 0 | 0
2022-10-06 12:00 | 1.8014 | 0 | N/A | 0 | 0
2022-10-06 12:30 | 2.1293 | 0 | N/A | 0 | 0
2022-10-06 13:00 | 1.7876 | 0 | N/A | 0 | 0
2022-10-06 13:30 | 1.8073 | 0 | N/A | 0 | 0
2022-10-06 14:00 | 1.8944 | 0 | N/A | 0 | 0
2022-10-06 14:30 | 1.8691 | 0 | N/A | 0 | 0
2022-10-06 15:00 | 2.8355 | 0 | N/A | 0 | 0
2022-10-06 15:30 | 2.6058 | 0 | N/A | 0 | 0
2022-10-06 16:00 | 3.3117 | 0 | N/A | 0 | 0
2022-10-06 16:30 | 3.9747 | 0 | N/A | 0 | 0
2022-10-06 17:00 | 4.7054 | 0 | N/A | 0 | 0
2022-10-06 17:30 | 5.5103 | 0 | N/A | 0 | 0
2022-10-06 18:00 | 6.1573 | 0 | N/A | 0 | 0
2022-10-06 18:30 | 6.6796 | 0 | N/A | 0 | 0
2022-10-06 19:00 | 7.0523 | 0 | N/A | 0 | 0
2022-10-06 19:30 | 6.9661 | 0 | N/A | 0 | 0
2022-10-06 20:00 | 6.8983 | 0 | N/A | 0 | 0
2022-10-06 20:30 | 6.8186 | 0 | N/A | 0 | 0
2022-10-06 21:00 | 6.4887 | 0 | N/A | 0 | 0
2022-10-06 21:30 | 6.0635 | 0 | N/A | 0 | 0
2022-10-06 22:00 | 5.505 | 0 | N/A | 0 | 0
2022-10-06 22:30 | 5.488 | 0 | N/A | 0 | 0
2022-10-06 23:00 | 5.3861 | 0 | N/A | 0 | 0
2022-10-06 23:30 | 4.9106 | 0 | N/A | 0 | 0
2022-10-07 | 4.8235 | 0 | N/A | 0 | 0
2022-10-07 00:30 | 5.0432 | 0 | N/A | 0 | 0
2022-10-07 01:00 | 5.3805 | 0 | N/A | 0 | 0
2022-10-07 01:30 | 4.7627 | 0 | N/A | 0 | 0
2022-10-07 02:00 | 4.1766 | 0 | N/A | 0 | 0
2022-10-07 02:30 | 4.0605 | 0 | N/A | 0 | 0
2022-10-07 03:00 | 3.7498 | 0 | N/A | 0 | 0
2022-10-07 03:30 | 3.4595 | 0 | N/A | 0 | 0
2022-10-07 04:00 | 3.328 | 0 | N/A | 0 | 0
2022-10-07 04:30 | 3.2263 | 0 | N/A | 0 | 0
2022-10-07 05:00 | 3.2202 | 0 | N/A | 0 | 0
2022-10-07 05:30 | 3.441 | 0 | N/A | 0 | 0
2022-10-07 06:00 | 3.7091 | 0 | N/A | 0 | 0
2022-10-07 06:30 | 4.3038 | 0 | N/A | 0 | 0
2022-10-07 07:00 | 4.91 | 0 | N/A | 0 | 0
2022-10-07 07:30 | 5.6473 | 0 | N/A | 0 | 0
2022-10-07 08:00 | 5.9331 | 0 | N/A | 0 | 0
2022-10-07 08:30 | 5.77 | 0 | N/A | 0 | 0
2022-10-07 09:00 | 5.9108 | 0 | N/A | 0 | 0
2022-10-07 09:30 | 5.8888 | 0 | N/A | 0 | 0
2022-10-07 10:00 | 5.9802 | 0 | N/A | 0 | 0
2022-10-07 10:30 | 6.2948 | 0 | N/A | 0 | 0
2022-10-07 11:00 | 6.0138 | 0 | N/A | 0 | 0
2022-10-07 11:30 | 4.9256 | 0 | N/A | 0 | 0
2022-10-07 12:00 | 0.98433 | 0 | N/A | 0 | 0
2022-10-07 12:30 | 0.49817 | 0 | N/A | 0 | 0
2022-10-07 13:00 | 1.1799 | 0 | N/A | 0 | 0
2022-10-07 13:30 | 1.7536 | 0 | N/A | 0 | 0
2022-10-07 14:00 | 0.66577 | 0 | N/A | 0 | 0
2022-10-07 14:30 | -0.50926 | 0 | N/A | 0 | 0
2022-10-07 15:00 | 0.58211 | 0 | N/A | 0 | 0
2022-10-07 15:30 | 0.72403 | 0 | N/A | 0 | 0
2022-10-10 16:00 | -1.2631 | 0 | N/A | 0 | 0
2022-10-10 16:30 | -0.92727 | 0 | N/A | 0 | 0
2022-10-10 17:00 | 1.3193 | 0 | N/A | 0 | 0
2022-10-10 17:30 | 1.9215 | 0 | N/A | 0 | 0
2022-10-10 18:00 | 3.3134 | 0 | N/A | 0 | 0
2022-10-10 18:30 | 4.1312 | 0 | N/A | 0 | 0
2022-10-10 19:00 | 4.9857 | 0 | N/A | 0 | 0
2022-10-10 19:30 | 5.6424 | 0 | N/A | 0 | 0
2022-10-10 20:00 | 6.2547 | 0 | N/A | 0 | 0
2022-10-10 20:30 | 6.4709 | 0 | N/A | 0 | 0
2022-10-10 21:00 | 6.3621 | 0 | N/A | 0 | 0
2022-10-10 21:30 | 6.1212 | 0 | N/A | 0 | 0
2022-10-10 22:00 | 5.7276 | 0 | N/A | 0 | 0
2022-10-10 22:30 | 5.7601 | 0 | N/A | 0 | 0
2022-10-10 23:00 | 5.506 | 0 | N/A | 0 | 0
2022-10-10 23:30 | 5.0706 | 0 | N/A | 0 | 0
2022-10-11 | 4.9133 | 0 | N/A | 0 | 0
2022-10-11 00:30 | 5.3162 | 0 | N/A | 0 | 0
2022-10-11 01:00 | 5.5868 | 0 | N/A | 0 | 0
2022-10-11 01:30 | 4.9955 | 0 | N/A | 0 | 0
2022-10-11 02:00 | 4.5286 | 0 | N/A | 0 | 0
2022-10-11 02:30 | 4.4402 | 0 | N/A | 0 | 0
2022-10-11 03:00 | 4.2227 | 0 | N/A | 0 | 0
2022-10-11 03:30 | 3.8364 | 0 | N/A | 0 | 0
2022-10-11 04:00 | 3.6255 | 0 | N/A | 0 | 0
2022-10-11 04:30 | 3.5536 | 0 | N/A | 0 | 0
2022-10-11 05:00 | 3.6628 | 0 | N/A | 0 | 0
2022-10-11 05:30 | 4.0899 | 0 | N/A | 0 | 0
2022-10-11 06:00 | 4.4465 | 0 | N/A | 0 | 0
2022-10-11 06:30 | 5.1482 | 0 | N/A | 0 | 0
2022-10-11 07:00 | 6.1512 | 0 | N/A | 0 | 0
2022-10-11 07:30 | 7.2442 | 0 | N/A | 0 | 0
2022-10-11 08:00 | 7.3826 | 0 | N/A | 0 | 0
2022-10-11 08:30 | 6.1097 | 0 | N/A | 0 | 0
2022-10-11 09:00 | 5.7761 | 0 | N/A | 0 | 0
2022-10-11 09:30 | 5.1755 | 0 | N/A | 0 | 0
2022-10-11 10:00 | 3.5972 | 0 | N/A | 0 | 0
2022-10-11 10:30 | 2.7885 | 0 | N/A | 0 | 0
2022-10-11 11:00 | 1.147 | 0 | N/A | 0 | 0
2022-10-11 11:30 | 1.21 | 0 | N/A | 0 | 0
2022-10-11 12:00 | 1.2666 | 0 | N/A | 0 | 0
2022-10-11 12:30 | 2.003 | 0 | N/A | 0 | 0
2022-10-11 13:00 | 0.98595 | 0 | N/A | 0 | 0
2022-10-11 13:30 | 0.71512 | 0 | N/A | 0 | 0
2022-10-11 14:00 | 0.62738 | 0 | N/A | 0 | 0
2022-10-11 14:30 | -0.76155 | 0 | N/A | 0 | 0
2022-10-11 15:00 | -1.0615 | 0 | N/A | 0 | 0
2022-10-11 15:30 | -1.119 | 0 | N/A | 0 | 0
2022-10-11 16:00 | -0.85907 | 0 | N/A | 0 | 0
2022-10-11 16:30 | -0.85796 | 0 | N/A | 0 | 0
2022-10-11 17:00 | 1.6787 | 0 | N/A | 0 | 0
2022-10-11 17:30 | 2.72 | 0 | N/A | 0 | 0
2022-10-11 18:00 | 3.7676 | 0 | N/A | 0 | 0
2022-10-11 18:30 | 4.7388 | 0 | N/A | 0 | 0
2022-10-11 19:00 | 5.6341 | 0 | N/A | 0 | 0
2022-10-11 19:30 | 6.0091 | 0 | N/A | 0 | 0
2022-10-11 20:00 | 6.1629 | 0 | N/A | 0 | 0
2022-10-11 20:30 | 6.3256 | 0 | N/A | 0 | 0
2022-10-11 21:00 | 6.1619 | 0 | N/A | 0 | 0
2022-10-11 21:30 | 5.5501 | 0 | N/A | 0 | 0
2022-10-11 22:00 | 5.3365 | 0 | N/A | 0 | 0
2022-10-11 22:30 | 5.2632 | 0 | N/A | 0 | 0
2022-10-11 23:00 | 5.0305 | 0 | N/A | 0 | 0
2022-10-11 23:30 | 4.5593 | 0 | N/A | 0 | 0
2022-10-12 | 4.4976 | 0 | N/A | 0 | 0
2022-10-12 00:30 | 4.8779 | 0 | N/A | 0 | 0
2022-10-12 01:00 | 5.0846 | 0 | N/A | 0 | 0
2022-10-12 01:30 | 4.505 | 0 | N/A | 0 | 0
2022-10-12 02:00 | 3.9795 | 0 | N/A | 0 | 0
2022-10-12 02:30 | 3.7669 | 0 | N/A | 0 | 0
2022-10-12 03:00 | 3.5984 | 0 | N/A | 0 | 0
2022-10-12 03:30 | 3.326 | 0 | N/A | 0 | 0
2022-10-12 04:00 | 3.0778 | 0 | N/A | 0 | 0
2022-10-12 04:30 | 3.0276 | 0 | N/A | 0 | 0
2022-10-12 05:00 | 3.1223 | 0 | N/A | 0 | 0
2022-10-12 05:30 | 3.2786 | 0 | N/A | 0 | 0
2022-10-12 06:00 | 3.6207 | 0 | N/A | 0 | 0
2022-10-12 06:30 | 4.2221 | 0 | N/A | 0 | 0
2022-10-12 07:00 | 4.8364 | 0 | N/A | 0 | 0
2022-10-12 07:30 | 5.3953 | 0 | N/A | 0 | 0
2022-10-12 08:00 | 2.4537 | 0 | N/A | 0 | 0
2022-10-12 08:30 | 1.196 | 0 | N/A | 0 | 0
2022-10-12 09:00 | 3.8997 | 0 | N/A | 0 | 0
2022-10-12 09:30 | 4.8845 | 0 | N/A | 0 | 0
2022-10-12 10:00 | 4.6213 | 0 | N/A | 0 | 0
2022-10-12 10:30 | 4.3739 | 0 | N/A | 0 | 0
2022-10-12 11:00 | 4.8349 | 0 | N/A | 0 | 0
2022-10-12 11:30 | 4.5694 | 0 | N/A | 0 | 0
2022-10-12 12:00 | 4.0942 | 0 | N/A | 0 | 0
2022-10-12 12:30 | 4.4823 | 0 | N/A | 0 | 0
2022-10-12 13:00 | 4.6648 | 0 | N/A | 0 | 0
2022-10-12 13:30 | 4.5427 | 0 | N/A | 0 | 0
2022-10-12 14:00 | 3.971 | 0 | N/A | 0 | 0
2022-10-12 14:30 | 4.4711 | 0 | N/A | 0 | 0
2022-10-12 15:00 | 4.3807 | 0 | N/A | 0 | 0
2022-10-12 15:30 | 4.5451 | 0 | N/A | 0 | 0
2022-10-12 16:00 | 4.887 | 0 | N/A | 0 | 0
2022-10-12 16:30 | 5.1786 | 0 | N/A | 0 | 0
2022-10-12 17:00 | 5.4746 | 0 | N/A | 0 | 0
2022-10-12 17:30 | 6.0124 | 0 | N/A | 0 | 0
2022-10-12 18:00 | 6.5115 | 0 | N/A | 0 | 0
2022-10-12 18:30 | 6.9103 | 0 | N/A | 0 | 0
2022-10-12 19:00 | 6.932 | 0 | N/A | 0 | 0
2022-10-12 19:30 | 6.9023 | 0 | N/A | 0 | 0
2022-10-12 20:00 | 6.8231 | 0 | N/A | 0 | 0
2022-10-12 20:30 | 6.5714 | 0 | N/A | 0 | 0
2022-10-12 21:00 | 6.2204 | 0 | N/A | 0 | 0
2022-10-12 21:30 | 5.8789 | 0 | N/A | 0 | 0
2022-10-12 22:00 | 5.4442 | 0 | N/A | 0 | 0
2022-10-12 22:30 | 5.3386 | 0 | N/A | 0 | 0
2022-10-12 23:00 | 5.2166 | 0 | N/A | 0 | 0
2022-10-12 23:30 | 4.6365 | 0 | N/A | 0 | 0
2022-10-13 | 4.5499 | 0 | N/A | 0 | 0
2022-10-13 00:30 | 4.9357 | 0 | N/A | 0 | 0
2022-10-13 01:00 | 5.2956 | 0 | N/A | 0 | 0
2022-10-13 01:30 | 4.7178 | 0 | N/A | 0 | 0
2022-10-13 02:00 | 4.1246 | 0 | N/A | 0 | 0
2022-10-13 02:30 | 4.0161 | 0 | N/A | 0 | 0
2022-10-13 03:00 | 3.7074 | 0 | N/A | 0 | 0
2022-10-13 03:30 | 3.3731 | 0 | N/A | 0 | 0
2022-10-13 04:00 | 3.2163 | 0 | N/A | 0 | 0
2022-10-13 04:30 | 3.084 | 0 | N/A | 0 | 0
2022-10-13 05:00 | 3.174 | 0 | N/A | 0 | 0
2022-10-13 05:30 | 3.3354 | 0 | N/A | 0 | 0
2022-10-13 06:00 | 3.6911 | 0 | N/A | 0 | 0
2022-10-13 06:30 | 4.3168 | 0 | N/A | 0 | 0
2022-10-13 07:00 | 4.9023 | 0 | N/A | 0 | 0
2022-10-13 07:30 | 6.1496 | 0 | N/A | 0 | 0
2022-10-13 08:00 | 7.0556 | 0 | N/A | 0 | 0
2022-10-13 08:30 | 6.7166 | 0 | N/A | 0 | 0
2022-10-13 09:00 | 6.7509 | 0 | N/A | 0 | 0
2022-10-13 09:30 | 6.6128 | 0 | N/A | 0 | 0
2022-10-13 10:00 | 6.4862 | 0 | N/A | 0 | 0
2022-10-13 10:30 | 6.1819 | 0 | N/A | 0 | 0
2022-10-13 11:00 | 6.2697 | 0 | N/A | 0 | 0
2022-10-13 11:30 | 6.5333 | 0 | N/A | 0 | 0
2022-10-13 12:00 | 6.5533 | 0 | N/A | 0 | 0
2022-10-13 12:30 | 6.6038 | 0 | N/A | 0 | 0
2022-10-13 13:00 | 6.4551 | 0 | N/A | 0 | 0
2022-10-13 13:30 | 6.4446 | 0 | N/A | 0 | 0
2022-10-13 14:00 | 6.4203 | 0 | N/A | 0 | 0
2022-10-13 14:30 | 6.5144 | 0 | N/A | 0 | 0
2022-10-13 15:00 | 6.6946 | 0 | N/A | 0 | 0
2022-10-13 15:30 | 6.6448 | 0 | N/A | 0 | 0
2022-10-13 16:00 | 6.6484 | 0 | N/A | 0 | 0
2022-10-13 16:30 | 6.5545 | 0 | N/A | 0 | 0
2022-10-13 17:00 | 6.9202 | 0 | N/A | 0 | 0
2022-10-13 17:30 | 7.6964 | 0 | N/A | 0 | 0
2022-10-13 18:00 | 8.3122 | 0 | N/A | 0 | 0
2022-10-13 18:30 | 8.5143 | 0 | N/A | 0 | 0
2022-10-13 19:00 | 8.6777 | 0 | N/A | 0 | 0
2022-10-13 19:30 | 8.6342 | 0 | N/A | 0 | 0
2022-10-13 20:00 | 8.3556 | 0 | N/A | 0 | 0
2022-10-13 20:30 | 8.2158 | 0 | N/A | 0 | 0
2022-10-13 21:00 | 7.82 | 0 | N/A | 0 | 0
2022-10-13 21:30 | 7.3527 | 0 | N/A | 0 | 0
2022-10-13 22:00 | 6.7083 | 0 | N/A | 0 | 0
2022-10-13 22:30 | 6.4894 | 0 | N/A | 0 | 0
2022-10-13 23:00 | 6.1765 | 0 | N/A | 0 | 0
2022-10-13 23:30 | 5.7384 | 0 | N/A | 0 | 0
2022-10-14 | 5.6576 | 0 | N/A | 0 | 0
2022-10-14 00:30 | 5.9227 | 0 | N/A | 0 | 0
2022-10-14 01:00 | 6.3245 | 0 | N/A | 0 | 0
2022-10-14 01:30 | 5.7261 | 0 | N/A | 0 | 0
2022-10-14 02:00 | 5.0751 | 0 | N/A | 0 | 0
2022-10-14 02:30 | 4.9008 | 0 | N/A | 0 | 0
2022-10-14 03:00 | 4.6444 | 0 | N/A | 0 | 0
2022-10-14 03:30 | 4.2614 | 0 | N/A | 0 | 0
2022-10-14 04:00 | 4.0256 | 0 | N/A | 0 | 0
2022-10-14 04:30 | 3.8868 | 0 | N/A | 0 | 0
2022-10-14 05:00 | 3.9406 | 0 | N/A | 0 | 0
2022-10-14 05:30 | 4.2369 | 0 | N/A | 0 | 0
2022-10-14 06:00 | 4.6151 | 0 | N/A | 0 | 0
2022-10-14 06:30 | 5.2756 | 0 | N/A | 0 | 0
2022-10-14 07:00 | 6.0793 | 0 | N/A | 0 | 0
2022-10-14 07:30 | 7.1439 | 0 | N/A | 0 | 0
2022-10-14 08:00 | 7.3446 | 0 | N/A | 0 | 0
2022-10-14 08:30 | 6.1184 | 0 | N/A | 0 | 0
2022-10-14 09:00 | 5.6375 | 0 | N/A | 0 | 0
2022-10-14 09:30 | 4.6736 | 0 | N/A | 0 | 0
2022-10-14 10:00 | 5.1461 | 0 | N/A | 0 | 0
2022-10-14 10:30 | 5.6347 | 0 | N/A | 0 | 0
2022-10-14 11:00 | 4.998 | 0 | N/A | 0 | 0
2022-10-14 11:30 | 5.2131 | 0 | N/A | 0 | 0
2022-10-14 12:00 | 4.9858 | 0 | N/A | 0 | 0
2022-10-14 12:30 | 4.0494 | 0 | N/A | 0 | 0
2022-10-14 13:00 | 3.0424 | 0 | N/A | 0 | 0
2022-10-14 13:30 | 2.6421 | 0 | N/A | 0 | 0
2022-10-14 14:00 | 3.0642 | 0 | N/A | 0 | 0
2022-10-14 14:30 | 1.3879 | 0 | N/A | 0 | 0
2022-10-14 15:00 | 2.2849 | 0 | N/A | 0 | 0
2022-10-14 15:30 | 2.1985 | 0 | N/A | 0 | 0
2022-10-14 16:00 | 2.9057 | 0 | N/A | 0 | 0
2022-10-14 16:30 | 3.6009 | 0 | N/A | 0 | 0
2022-10-14 17:00 | 3.9861 | 0 | N/A | 0 | 0
2022-10-14 17:30 | 5.6326 | 0 | N/A | 0 | 0
2022-10-14 18:00 | 5.8284 | 0 | N/A | 0 | 0
2022-10-14 18:30 | 6.3461 | 0 | N/A | 0 | 0
2022-10-14 19:00 | 7.1102 | 0 | N/A | 0 | 0
2022-10-14 19:30 | 7.0419 | 0 | N/A | 0 | 0
2022-10-14 20:00 | 7.2095 | 0 | N/A | 0 | 0
2022-10-14 20:30 | 7.3297 | 0 | N/A | 0 | 0
2022-10-14 21:00 | 7.1217 | 0 | N/A | 0 | 0
2022-10-14 21:30 | 6.8501 | 0 | N/A | 0 | 0
2022-10-14 22:00 | 6.5163 | 0 | N/A | 0 | 0
2022-10-14 22:30 | 6.5302 | 0 | N/A | 0 | 0
2022-10-14 23:00 | 6.4094 | 0 | N/A | 0 | 0
2022-10-14 23:30 | 5.9951 | 0 | N/A | 0 | 0
2022-10-15 | 5.8934 | 0 | N/A | 0 | 0
2022-10-15 00:30 | 6.1531 | 0 | N/A | 0 | 0
2022-10-15 01:00 | 6.3138 | 0 | N/A | 0 | 0
2022-10-15 01:30 | 5.7901 | 0 | N/A | 0 | 0
2022-10-15 02:00 | 5.1866 | 0 | N/A | 0 | 0
2022-10-15 02:30 | 4.9633 | 0 | N/A | 0 | 0
2022-10-15 03:00 | 4.7578 | 0 | N/A | 0 | 0
2022-10-15 03:30 | 4.3145 | 0 | N/A | 0 | 0
2022-10-15 04:00 | 4.0066 | 0 | N/A | 0 | 0
2022-10-15 04:30 | 3.9647 | 0 | N/A | 0 | 0
2022-10-15 05:00 | 3.886 | 0 | N/A | 0 | 0
2022-10-15 05:30 | 3.9384 | 0 | N/A | 0 | 0
2022-10-15 06:00 | 4.1153 | 0 | N/A | 0 | 0
2022-10-15 06:30 | 4.4761 | 0 | N/A | 0 | 0
2022-10-15 07:00 | 4.7893 | 0 | N/A | 0 | 0
2022-10-15 07:30 | 5.337 | 0 | N/A | 0 | 0
2022-10-15 08:00 | 5.4247 | 0 | N/A | 0 | 0
2022-10-15 08:30 | 4.9633 | 0 | N/A | 0 | 0
2022-10-15 09:00 | 3.8039 | 0 | N/A | 0 | 0
2022-10-15 09:30 | 2.9024 | 0 | N/A | 0 | 0
2022-10-15 10:00 | 2.2481 | 0 | N/A | 0 | 0
2022-10-15 10:30 | 3.3449 | 0 | N/A | 0 | 0
2022-10-15 11:00 | 2.8219 | 0 | N/A | 0 | 0
2022-10-15 11:30 | 2.0304 | 0 | N/A | 0 | 0
2022-10-15 12:00 | 2.0094 | 0 | N/A | 0 | 0
2022-10-15 12:30 | 1.1769 | 0 | N/A | 0 | 0
2022-10-15 13:00 | 1.1138 | 0 | N/A | 0 | 0
2022-10-15 13:30 | 1.1791 | 0 | N/A | 0 | 0
2022-10-15 14:00 | 1.044 | 0 | N/A | 0 | 0
2022-10-15 14:30 | 1.1926 | 0 | N/A | 0 | 0
2022-10-15 15:00 | 1.1211 | 0 | N/A | 0 | 0
2022-10-15 15:30 | 1.091 | 0 | N/A | 0 | 0
2022-10-15 16:00 | 1.2275 | 0 | N/A | 0 | 0
2022-10-15 16:30 | 1.2331 | 0 | N/A | 0 | 0
2022-10-15 17:00 | 1.5203 | 0 | N/A | 0 | 0
2022-10-15 17:30 | 2.5776 | 0 | N/A | 0 | 0
2022-10-15 18:00 | 3.7959 | 0 | N/A | 0 | 0
2022-10-15 18:30 | 4.5531 | 0 | N/A | 0 | 0
2022-10-15 19:00 | 5.3537 | 0 | N/A | 0 | 0
2022-10-15 19:30 | 5.7974 | 0 | N/A | 0 | 0
2022-10-15 20:00 | 6.0747 | 0 | N/A | 0 | 0
2022-10-15 20:30 | 6.0225 | 0 | N/A | 0 | 0
2022-10-15 21:00 | 5.8713 | 0 | N/A | 0 | 0
2022-10-15 21:30 | 5.6756 | 0 | N/A | 0 | 0
2022-10-15 22:00 | 5.4437 | 0 | N/A | 0 | 0
2022-10-15 22:30 | 5.6226 | 0 | N/A | 0 | 0
2022-10-15 23:00 | 5.558 | 0 | N/A | 0 | 0
2022-10-15 23:30 | 5.2678 | 0 | N/A | 0 | 0
2022-10-16 | 5.2852 | 0 | N/A | 0 | 0
2022-10-16 00:30 | 5.4852 | 0 | N/A | 0 | 0
2022-10-16 01:00 | 5.707 | 0 | N/A | 0 | 0
2022-10-16 01:30 | 5.0845 | 0 | N/A | 0 | 0
2022-10-16 02:00 | 4.4245 | 0 | N/A | 0 | 0
2022-10-16 02:30 | 4.3405 | 0 | N/A | 0 | 0
2022-10-16 03:00 | 4.1068 | 0 | N/A | 0 | 0
2022-10-16 03:30 | 3.7618 | 0 | N/A | 0 | 0
2022-10-16 04:00 | 3.5252 | 0 | N/A | 0 | 0
2022-10-16 04:30 | 3.4291 | 0 | N/A | 0 | 0
2022-10-16 05:00 | 3.334 | 0 | N/A | 0 | 0
2022-10-16 05:30 | 3.3998 | 0 | N/A | 0 | 0
2022-10-16 06:00 | 3.537 | 0 | N/A | 0 | 0
2022-10-16 06:30 | 3.6793 | 0 | N/A | 0 | 0
2022-10-16 07:00 | 3.9323 | 0 | N/A | 0 | 0
2022-10-16 07:30 | 4.1878 | 0 | N/A | 0 | 0
2022-10-16 08:00 | 4.3819 | 0 | N/A | 0 | 0
2022-10-16 08:30 | 3.9043 | 0 | N/A | 0 | 0
2022-10-16 09:00 | 2.9238 | 0 | N/A | 0 | 0
2022-10-16 09:30 | 3.0367 | 0 | N/A | 0 | 0
2022-10-16 10:00 | 3.3173 | 0 | N/A | 0 | 0
2022-10-16 10:30 | 3.5103 | 0 | N/A | 0 | 0
2022-10-16 11:00 | 2.5974 | 0 | N/A | 0 | 0
2022-10-16 11:30 | 2.3654 | 0 | N/A | 0 | 0
2022-10-16 12:00 | 2.3062 | 0 | N/A | 0 | 0
2022-10-16 12:30 | 2.3303 | 0 | N/A | 0 | 0
2022-10-16 13:00 | 1.8465 | 0 | N/A | 0 | 0
2022-10-16 13:30 | 1.2989 | 0 | N/A | 0 | 0
2022-10-16 14:00 | 1.4363 | 0 | N/A | 0 | 0
2022-10-16 14:30 | 1.7514 | 0 | N/A | 0 | 0
2022-10-16 15:00 | 1.4419 | 0 | N/A | 0 | 0
2022-10-16 15:30 | 2.1264 | 0 | N/A | 0 | 0
2022-10-16 16:00 | 1.844 | 0 | N/A | 0 | 0
2022-10-16 16:30 | 1.6975 | 0 | N/A | 0 | 0
2022-10-16 17:00 | 1.8348 | 0 | N/A | 0 | 0
2022-10-16 17:30 | 2.767 | 0 | N/A | 0 | 0
2022-10-16 18:00 | 4.0521 | 0 | N/A | 0 | 0
2022-10-16 18:30 | 4.7387 | 0 | N/A | 0 | 0
2022-10-16 19:00 | 5.6063 | 0 | N/A | 0 | 0
2022-10-16 19:30 | 6.1576 | 0 | N/A | 0 | 0
2022-10-16 20:00 | 6.5047 | 0 | N/A | 0 | 0
2022-10-16 20:30 | 6.5884 | 0 | N/A | 0 | 0
2022-10-16 21:00 | 6.5931 | 0 | N/A | 0 | 0
2022-10-16 21:30 | 6.3236 | 0 | N/A | 0 | 0
2022-10-16 22:00 | 5.913 | 0 | N/A | 0 | 0
2022-10-16 22:30 | 5.7232 | 0 | N/A | 0 | 0
2022-10-16 23:00 | 5.6463 | 0 | N/A | 0 | 0
2022-10-16 23:30 | 5.3842 | 0 | N/A | 0 | 0
2022-10-17 | 5.3424 | 0 | N/A | 0 | 0
2022-10-17 00:30 | 5.5249 | 0 | N/A | 0 | 0
2022-10-17 01:00 | 5.8913 | 0 | N/A | 0 | 0
2022-10-17 01:30 | 5.5024 | 0 | N/A | 0 | 0
2022-10-17 02:00 | 4.856 | 0 | N/A | 0 | 0
2022-10-17 02:30 | 4.7811 | 0 | N/A | 0 | 0
2022-10-17 03:00 | 4.6699 | 0 | N/A | 0 | 0
2022-10-17 03:30 | 4.2429 | 0 | N/A | 0 | 0
2022-10-17 04:00 | 4.0964 | 0 | N/A | 0 | 0
2022-10-17 04:30 | 4.0147 | 0 | N/A | 0 | 0
2022-10-17 05:00 | 4.0734 | 0 | N/A | 0 | 0
2022-10-17 05:30 | 4.4024 | 0 | N/A | 0 | 0
2022-10-17 06:00 | 4.8411 | 0 | N/A | 0 | 0
2022-10-17 06:30 | 5.5882 | 0 | N/A | 0 | 0
2022-10-17 07:00 | 6.7365 | 0 | N/A | 0 | 0
2022-10-17 07:30 | 7.8069 | 0 | N/A | 0 | 0
2022-10-17 08:00 | 7.908 | 0 | N/A | 0 | 0
2022-10-17 08:30 | 6.3132 | 0 | N/A | 0 | 0
2022-10-17 09:00 | 5.1467 | 0 | N/A | 0 | 0
2022-10-17 09:30 | 3.6507 | 0 | N/A | 0 | 0
2022-10-17 10:00 | 2.0824 | 0 | N/A | 0 | 0
2022-10-17 10:30 | 1.2729 | 0 | N/A | 0 | 0
2022-10-17 11:00 | 0.722 | 0 | N/A | 0 | 0
2022-10-17 11:30 | 0.77084 | 0 | N/A | 0 | 0
2022-10-17 12:00 | -0.78262 | 0 | N/A | 0 | 0
2022-10-17 12:30 | -1.3264 | 0 | N/A | 0 | 0
2022-10-17 13:00 | -1.4417 | 0 | N/A | 0 | 0
2022-10-17 13:30 | -1.5355 | 0 | N/A | 0 | 0
2022-10-17 14:00 | -1.6985 | 0 | N/A | 0 | 0
2022-10-17 14:30 | -1.7477 | 0 | N/A | 0 | 0
2022-10-17 15:00 | -1.6398 | 0 | N/A | 0 | 0
2022-10-17 15:30 | -1.686 | 0 | N/A | 0 | 0
2022-10-17 16:00 | -1.4197 | 0 | N/A | 0 | 0
2022-10-17 16:30 | -1.1114 | 0 | N/A | 0 | 0
2022-10-17 17:00 | 1.1545 | 0 | N/A | 0 | 0
2022-10-17 17:30 | 1.8825 | 0 | N/A | 0 | 0
2022-10-17 18:00 | 3.0514 | 0 | N/A | 0 | 0
2022-10-17 18:30 | 4.1163 | 0 | N/A | 0 | 0
2022-10-17 19:00 | 5.162 | 0 | N/A | 0 | 0
2022-10-17 19:30 | 5.8091 | 0 | N/A | 0 | 0
2022-10-17 20:00 | 6.2521 | 0 | N/A | 0 | 0
2022-10-17 20:30 | 6.6251 | 0 | N/A | 0 | 0
2022-10-17 21:00 | 6.6102 | 0 | N/A | 0 | 0
2022-10-17 21:30 | 6.3197 | 0 | N/A | 0 | 0
2022-10-17 22:00 | 5.9573 | 0 | N/A | 0 | 0
2022-10-17 22:30 | 5.8248 | 0 | N/A | 0 | 0
2022-10-17 23:00 | 5.6907 | 0 | N/A | 0 | 0
2022-10-17 23:30 | 5.1808 | 0 | N/A | 0 | 0
2022-10-18 | 5.04 | 0 | N/A | 0 | 0
2022-10-18 00:30 | 5.3719 | 0 | N/A | 0 | 0
2022-10-18 01:00 | 5.6713 | 0 | N/A | 0 | 0
2022-10-18 01:30 | 5.1498 | 0 | N/A | 0 | 0
2022-10-18 02:00 | 4.64 | 0 | N/A | 0 | 0
2022-10-18 02:30 | 4.5318 | 0 | N/A | 0 | 0
2022-10-18 03:00 | 4.3171 | 0 | N/A | 0 | 0
2022-10-18 03:30 | 4.051 | 0 | N/A | 0 | 0
2022-10-18 04:00 | 3.8637 | 0 | N/A | 0 | 0
2022-10-18 04:30 | 3.7922 | 0 | N/A | 0 | 0
2022-10-18 05:00 | 3.8825 | 0 | N/A | 0 | 0
2022-10-18 05:30 | 4.2217 | 0 | N/A | 0 | 0
2022-10-18 06:00 | 4.6936 | 0 | N/A | 0 | 0
2022-10-18 06:30 | 5.5431 | 0 | N/A | 0 | 0
2022-10-18 07:00 | 6.5201 | 0 | N/A | 0 | 0
2022-10-18 07:30 | 7.6714 | 0 | N/A | 0 | 0
2022-10-18 08:00 | 7.6801 | 0 | N/A | 0 | 0
2022-10-18 08:30 | 6.2895 | 0 | N/A | 0 | 0
2022-10-18 09:00 | 5.3347 | 0 | N/A | 0 | 0
2022-10-18 09:30 | 4.3267 | 0 | N/A | 0 | 0
2022-10-18 10:00 | 3.8325 | 0 | N/A | 0 | 0
2022-10-18 10:30 | 3.1646 | 0 | N/A | 0 | 0
2022-10-18 11:00 | 3.4004 | 0 | N/A | 0 | 0
2022-10-18 11:30 | 2.9766 | 0 | N/A | 0 | 0
2022-10-18 12:00 | 2.5944 | 0 | N/A | 0 | 0
2022-10-18 12:30 | 2.2526 | 0 | N/A | 0 | 0
2022-10-18 13:00 | 1.5504 | 0 | N/A | 0 | 0
2022-10-18 13:30 | 0.83241 | 0 | N/A | 0 | 0
2022-10-18 14:00 | -0.71629 | 0 | N/A | 0 | 0
2022-10-18 14:30 | -1.02 | 0 | N/A | 0 | 0
2022-10-18 15:00 | -0.73775 | 0 | N/A | 0 | 0
2022-10-18 15:30 | -0.98633 | 0 | N/A | 0 | 0
2022-10-18 16:00 | -1.0866 | 0 | N/A | 0 | 0
2022-10-18 16:30 | -1.0511 | 0 | N/A | 0 | 0
2022-10-18 17:00 | 1.0249 | 0 | N/A | 0 | 0
2022-10-18 17:30 | 1.674 | 0 | N/A | 0 | 0
2022-10-18 18:00 | 2.8339 | 0 | N/A | 0 | 0
2022-10-18 18:30 | 4.0478 | 0 | N/A | 0 | 0
2022-10-18 19:00 | 4.7645 | 0 | N/A | 0 | 0
2022-10-18 19:30 | 5.3391 | 0 | N/A | 0 | 0
2022-10-18 20:00 | 5.7299 | 0 | N/A | 0 | 0
2022-10-18 20:30 | 5.9918 | 0 | N/A | 0 | 0
2022-10-18 21:00 | 6.0517 | 0 | N/A | 0 | 0
2022-10-18 21:30 | 5.7855 | 0 | N/A | 0 | 0
2022-10-18 22:00 | 5.4325 | 0 | N/A | 0 | 0
2022-10-18 22:30 | 5.4875 | 0 | N/A | 0 | 0
2022-10-18 23:00 | 5.4119 | 0 | N/A | 0 | 0
2022-10-18 23:30 | 4.9372 | 0 | N/A | 0 | 0
2022-10-19 | 4.8427 | 0 | N/A | 0 | 0
2022-10-19 00:30 | 5.1696 | 0 | N/A | 0 | 0
2022-10-19 01:00 | 5.4779 | 0 | N/A | 0 | 0
2022-10-19 01:30 | 4.913 | 0 | N/A | 0 | 0
2022-10-19 02:00 | 4.3312 | 0 | N/A | 0 | 0
2022-10-19 02:30 | 4.2672 | 0 | N/A | 0 | 0
2022-10-19 03:00 | 4.0625 | 0 | N/A | 0 | 0
2022-10-19 03:30 | 3.8019 | 0 | N/A | 0 | 0
2022-10-19 04:00 | 3.6329 | 0 | N/A | 0 | 0
2022-10-19 04:30 | 3.5636 | 0 | N/A | 0 | 0
2022-10-19 05:00 | 3.6583 | 0 | N/A | 0 | 0
2022-10-19 05:30 | 3.9711 | 0 | N/A | 0 | 0
2022-10-19 06:00 | 4.5404 | 0 | N/A | 0 | 0
2022-10-19 06:30 | 5.3304 | 0 | N/A | 0 | 0
2022-10-19 07:00 | 6.39 | 0 | N/A | 0 | 0
2022-10-19 07:30 | 7.4148 | 0 | N/A | 0 | 0
2022-10-19 08:00 | 7.0108 | 0 | N/A | 0 | 0
2022-10-19 08:30 | 5.4904 | 0 | N/A | 0 | 0
2022-10-19 09:00 | 4.1932 | 0 | N/A | 0 | 0
2022-10-19 09:30 | 2.9137 | 0 | N/A | 0 | 0
2022-10-19 10:00 | 1.7478 | 0 | N/A | 0 | 0
2022-10-19 10:30 | 0.93339 | 0 | N/A | 0 | 0
2022-10-19 11:00 | -0.91727 | 0 | N/A | 0 | 0
2022-10-19 11:30 | -1.0563 | 0 | N/A | 0 | 0
2022-10-19 12:00 | -1.3744 | 0 | N/A | 0 | 0
2022-10-19 12:30 | -1.5894 | 0 | N/A | 0 | 0
2022-10-19 13:00 | -1.8469 | 0 | N/A | 0 | 0
2022-10-19 13:30 | -2.1833 | 0 | N/A | 0 | 0
2022-10-19 14:00 | -2.1915 | 0 | N/A | 0 | 0
2022-10-19 14:30 | -2.0055 | 0 | N/A | 0 | 0
2022-10-19 15:00 | -1.764 | 0 | N/A | 0 | 0
2022-10-19 15:30 | -1.6364 | 0 | N/A | 0 | 0
2022-10-19 16:00 | -1.4863 | 0 | N/A | 0 | 0
2022-10-19 16:30 | -1.2969 | 0 | N/A | 0 | 0
2022-10-19 17:00 | -0.91599 | 0 | N/A | 0 | 0
2022-10-19 17:30 | 1.3918 | 0 | N/A | 0 | 0
2022-10-19 18:00 | 2.4967 | 0 | N/A | 0 | 0
2022-10-19 18:30 | 3.5192 | 0 | N/A | 0 | 0
2022-10-19 19:00 | 4.2586 | 0 | N/A | 0 | 0
2022-10-19 19:30 | 4.778 | 0 | N/A | 0 | 0
2022-10-19 20:00 | 5.197 | 0 | N/A | 0 | 0
2022-10-19 20:30 | 5.4534 | 0 | N/A | 0 | 0
2022-10-19 21:00 | 5.4364 | 0 | N/A | 0 | 0
2022-10-19 21:30 | 5.2462 | 0 | N/A | 0 | 0
2022-10-19 22:00 | 4.9916 | 0 | N/A | 0 | 0
2022-10-19 22:30 | 5.0853 | 0 | N/A | 0 | 0
2022-10-19 23:00 | 4.9615 | 0 | N/A | 0 | 0
2022-10-19 23:30 | 4.516 | 0 | N/A | 0 | 0
2022-10-20 | 4.4231 | 0 | N/A | 0 | 0
2022-10-20 00:30 | 4.8049 | 0 | N/A | 0 | 0
2022-10-20 01:00 | 5.134 | 0 | N/A | 0 | 0
2022-10-20 01:30 | 4.5401 | 0 | N/A | 0 | 0
2022-10-20 02:00 | 3.9952 | 0 | N/A | 0 | 0
2022-10-20 02:30 | 3.8934 | 0 | N/A | 0 | 0
2022-10-20 03:00 | 3.6152 | 0 | N/A | 0 | 0
2022-10-20 03:30 | 3.3155 | 0 | N/A | 0 | 0
2022-10-20 04:00 | 3.1634 | 0 | N/A | 0 | 0
2022-10-20 04:30 | 3.0979 | 0 | N/A | 0 | 0
2022-10-20 05:00 | 3.2059 | 0 | N/A | 0 | 0
2022-10-20 05:30 | 3.4714 | 0 | N/A | 0 | 0
2022-10-20 06:00 | 3.8415 | 0 | N/A | 0 | 0
2022-10-20 06:30 | 4.5239 | 0 | N/A | 0 | 0
2022-10-20 07:00 | 5.266 | 0 | N/A | 0 | 0
2022-10-20 07:30 | 6.3442 | 0 | N/A | 0 | 0
2022-10-20 08:00 | 5.9419 | 0 | N/A | 0 | 0
2022-10-20 08:30 | 4.6688 | 0 | N/A | 0 | 0
2022-10-20 09:00 | 3.4784 | 0 | N/A | 0 | 0
2022-10-20 15:00 | -2.139 | 0 | N/A | 0 | 0
2022-10-20 15:30 | -1.9286 | 0 | N/A | 0 | 0
2022-10-20 16:00 | -1.6626 | 0 | N/A | 0 | 0
2022-10-20 16:30 | -1.2311 | 0 | N/A | 0 | 0
2022-10-20 17:00 | -0.86619 | 0 | N/A | 0 | 0
2022-10-20 17:30 | 1.3977 | 0 | N/A | 0 | 0
2022-10-20 18:00 | 2.4284 | 0 | N/A | 0 | 0
2022-10-20 18:30 | 3.446 | 0 | N/A | 0 | 0
2022-10-20 19:00 | 4.1688 | 0 | N/A | 0 | 0
2022-10-20 19:30 | 4.6505 | 0 | N/A | 0 | 0
2022-10-20 20:00 | 4.9906 | 0 | N/A | 0 | 0
2022-10-20 20:30 | 5.1225 | 0 | N/A | 0 | 0
2022-10-20 21:00 | 5.1037 | 0 | N/A | 0 | 0
2022-10-20 21:30 | 4.8234 | 0 | N/A | 0 | 0
2022-10-20 22:00 | 4.5087 | 0 | N/A | 0 | 0
2022-10-20 22:30 | 4.5958 | 0 | N/A | 0 | 0
2022-10-20 23:00 | 4.5714 | 0 | N/A | 0 | 0
2022-10-20 23:30 | 4.2327 | 0 | N/A | 0 | 0
2022-10-21 | 4.1723 | 0 | N/A | 0 | 0
2022-10-21 00:30 | 4.5235 | 0 | N/A | 0 | 0
2022-10-21 01:00 | 4.7042 | 0 | N/A | 0 | 0
2022-10-21 01:30 | 4.0342 | 0 | N/A | 0 | 0
2022-10-21 02:00 | 3.5654 | 0 | N/A | 0 | 0
2022-10-21 02:30 | 3.5456 | 0 | N/A | 0 | 0
2022-10-21 03:00 | 3.2421 | 0 | N/A | 0 | 0
2022-10-21 03:30 | 2.8952 | 0 | N/A | 0 | 0
2022-10-21 04:00 | 2.7144 | 0 | N/A | 0 | 0
2022-10-21 04:30 | 2.6485 | 0 | N/A | 0 | 0
2022-10-21 05:00 | 2.7475 | 0 | N/A | 0 | 0
2022-10-21 05:30 | 2.9134 | 0 | N/A | 0 | 0
2022-10-21 06:00 | 3.2813 | 0 | N/A | 0 | 0
2022-10-21 06:30 | 3.7805 | 0 | N/A | 0 | 0
2022-10-21 07:00 | 4.2518 | 0 | N/A | 0 | 0
2022-10-21 07:30 | 4.9239 | 0 | N/A | 0 | 0
2022-10-21 08:00 | 4.6337 | 0 | N/A | 0 | 0
2022-10-21 08:30 | 3.9301 | 0 | N/A | 0 | 0
2022-10-21 09:00 | 3.587 | 0 | N/A | 0 | 0
2022-10-21 09:30 | 2.8774 | 0 | N/A | 0 | 0
2022-10-21 10:00 | 1.8548 | 0 | N/A | 0 | 0
2022-10-21 10:30 | 1.569 | 0 | N/A | 0 | 0
2022-10-21 11:00 | 1.57 | 0 | N/A | 0 | 0
2022-10-21 11:30 | 1.003 | 0 | N/A | 0 | 0
2022-10-21 12:00 | 1.0732 | 0 | N/A | 0 | 0
2022-10-21 12:30 | 1.5661 | 0 | N/A | 0 | 0
2022-10-21 13:00 | 1.8253 | 0 | N/A | 0 | 0
2022-10-21 13:30 | 1.2642 | 0 | N/A | 0 | 0
2022-10-21 14:00 | 0.88655 | 0 | N/A | 0 | 0
2022-10-21 14:30 | 1.0025 | 0 | N/A | 0 | 0
2022-10-21 15:00 | 0.84698 | 0 | N/A | 0 | 0
2022-10-21 15:30 | 1.0858 | 0 | N/A | 0 | 0
2022-10-21 16:00 | -0.764 | 0 | N/A | 0 | 0
2022-10-21 16:30 | 1.4467 | 0 | N/A | 0 | 0
2022-10-21 17:00 | 3.0973 | 0 | N/A | 0 | 0
2022-10-21 17:30 | 3.8802 | 0 | N/A | 0 | 0
2022-10-21 18:00 | 4.5914 | 0 | N/A | 0 | 0
2022-10-21 18:30 | 4.6958 | 0 | N/A | 0 | 0
2022-10-21 19:00 | 5.0871 | 0 | N/A | 0 | 0
2022-10-21 19:30 | 5.0769 | 0 | N/A | 0 | 0
2022-10-21 20:00 | 5.0948 | 0 | N/A | 0 | 0
2022-10-21 20:30 | 5.0686 | 0 | N/A | 0 | 0
2022-10-21 21:00 | 4.9789 | 0 | N/A | 0 | 0
2022-10-21 21:30 | 4.7475 | 0 | N/A | 0 | 0
2022-10-21 22:00 | 4.445 | 0 | N/A | 0 | 0
2022-10-21 22:30 | 4.6681 | 0 | N/A | 0 | 0
2022-10-21 23:00 | 4.6423 | 0 | N/A | 0 | 0
2022-10-21 23:30 | 4.2643 | 0 | N/A | 0 | 0
2022-10-22 | 4.2564 | 0 | N/A | 0 | 0
2022-10-22 00:30 | 4.5824 | 0 | N/A | 0 | 0
2022-10-22 01:00 | 4.93 | 0 | N/A | 0 | 0
2022-10-22 01:30 | 4.2671 | 0 | N/A | 0 | 0
2022-10-22 02:00 | 3.7127 | 0 | N/A | 0 | 0
2022-10-22 02:30 | 3.52 | 0 | N/A | 0 | 0
2022-10-22 03:00 | 3.2783 | 0 | N/A | 0 | 0
2022-10-22 03:30 | 2.9513 | 0 | N/A | 0 | 0
2022-10-22 04:00 | 2.8353 | 0 | N/A | 0 | 0
2022-10-22 04:30 | 2.7864 | 0 | N/A | 0 | 0
2022-10-22 05:00 | 2.7675 | 0 | N/A | 0 | 0
2022-10-22 05:30 | 2.7777 | 0 | N/A | 0 | 0
2022-10-22 06:00 | 2.8088 | 0 | N/A | 0 | 0
2022-10-22 06:30 | 3.0724 | 0 | N/A | 0 | 0
2022-10-22 07:00 | 3.2569 | 0 | N/A | 0 | 0
2022-10-22 07:30 | 3.6183 | 0 | N/A | 0 | 0
2022-10-22 08:00 | 3.9845 | 0 | N/A | 0 | 0
2022-10-22 08:30 | 3.8317 | 0 | N/A | 0 | 0
2022-10-22 09:00 | 4.059 | 0 | N/A | 0 | 0
2022-10-22 09:30 | 3.9565 | 0 | N/A | 0 | 0
2022-10-22 10:00 | 4.0641 | 0 | N/A | 0 | 0
2022-10-22 10:30 | 3.742 | 0 | N/A | 0 | 0
2022-10-22 11:00 | 4.2727 | 0 | N/A | 0 | 0
2022-10-22 11:30 | 3.3448 | 0 | N/A | 0 | 0
2022-10-22 12:00 | 3.4881 | 0 | N/A | 0 | 0
2022-10-22 12:30 | 3.6844 | 0 | N/A | 0 | 0
2022-10-22 13:00 | 3.6582 | 0 | N/A | 0 | 0
2022-10-22 13:30 | 3.6666 | 0 | N/A | 0 | 0
2022-10-22 14:00 | 2.3488 | 0 | N/A | 0 | 0
2022-10-22 14:30 | 2.0274 | 0 | N/A | 0 | 0
2022-10-22 15:00 | 2.6134 | 0 | N/A | 0 | 0
2022-10-22 15:30 | 1.921 | 0 | N/A | 0 | 0
2022-10-22 16:00 | 0.92109 | 0 | N/A | 0 | 0
2022-10-22 16:30 | 1.2887 | 0 | N/A | 0 | 0
2022-10-22 17:00 | 2.3496 | 0 | N/A | 0 | 0
2022-10-22 17:30 | 4.1665 | 0 | N/A | 0 | 0
2022-10-22 18:00 | 5.1001 | 0 | N/A | 0 | 0
2022-10-22 18:30 | 5.4244 | 0 | N/A | 0 | 0
2022-10-22 19:00 | 5.8037 | 0 | N/A | 0 | 0
2022-10-22 19:30 | 5.9056 | 0 | N/A | 0 | 0
2022-10-22 20:00 | 5.6305 | 0 | N/A | 0 | 0
2022-10-22 20:30 | 5.4161 | 0 | N/A | 0 | 0
2022-10-22 21:00 | 5.1733 | 0 | N/A | 0 | 0
2022-10-22 21:30 | 4.9537 | 0 | N/A | 0 | 0
2022-10-22 22:00 | 4.7036 | 0 | N/A | 0 | 0
2022-10-22 22:30 | 4.8568 | 0 | N/A | 0 | 0
2022-10-22 23:00 | 4.9768 | 0 | N/A | 0 | 0
2022-10-22 23:30 | 4.7303 | 0 | N/A | 0 | 0
2022-10-23 | 4.7344 | 0 | N/A | 0 | 0
2022-10-23 00:30 | 4.8908 | 0 | N/A | 0 | 0
2022-10-23 01:00 | 5.1693 | 0 | N/A | 0 | 0
2022-10-23 01:30 | 4.4989 | 0 | N/A | 0 | 0
2022-10-23 02:00 | 4.0426 | 0 | N/A | 0 | 0
2022-10-23 02:30 | 3.8733 | 0 | N/A | 0 | 0
2022-10-23 03:00 | 3.6126 | 0 | N/A | 0 | 0
2022-10-23 03:30 | 3.2556 | 0 | N/A | 0 | 0
2022-10-23 04:00 | 3.1104 | 0 | N/A | 0 | 0
2022-10-23 04:30 | 3.004 | 0 | N/A | 0 | 0
2022-10-23 05:00 | 2.9614 | 0 | N/A | 0 | 0
2022-10-23 05:30 | 2.9777 | 0 | N/A | 0 | 0
2022-10-23 06:00 | 3.05 | 0 | N/A | 0 | 0
2022-10-23 06:30 | 3.2417 | 0 | N/A | 0 | 0
2022-10-23 07:00 | 3.3902 | 0 | N/A | 0 | 0
2022-10-23 07:30 | 3.6387 | 0 | N/A | 0 | 0
2022-10-23 08:00 | 3.6578 | 0 | N/A | 0 | 0
2022-10-23 08:30 | 3.5047 | 0 | N/A | 0 | 0
2022-10-23 09:00 | 3.5754 | 0 | N/A | 0 | 0
2022-10-23 09:30 | 3.3419 | 0 | N/A | 0 | 0
2022-10-23 10:00 | 3.5544 | 0 | N/A | 0 | 0
2022-10-23 10:30 | 3.5419 | 0 | N/A | 0 | 0
2022-10-23 11:00 | 3.0854 | 0 | N/A | 0 | 0
2022-10-23 11:30 | 2.9257 | 0 | N/A | 0 | 0
2022-10-23 12:00 | 3.2508 | 0 | N/A | 0 | 0
2022-10-23 12:30 | 2.6187 | 0 | N/A | 0 | 0
2022-10-23 13:00 | 1.9044 | 0 | N/A | 0 | 0
2022-10-23 13:30 | 1.5833 | 0 | N/A | 0 | 0
2022-10-23 14:00 | 1.739 | 0 | N/A | 0 | 0
2022-10-23 14:30 | 2.1298 | 0 | N/A | 0 | 0
2022-10-23 15:00 | 2.4605 | 0 | N/A | 0 | 0
2022-10-23 15:30 | 1.608 | 0 | N/A | 0 | 0
2022-10-23 16:00 | 1.67 | 0 | N/A | 0 | 0
2022-10-23 16:30 | 1.4826 | 0 | N/A | 0 | 0
2022-10-23 17:00 | 2.5099 | 0 | N/A | 0 | 0
2022-10-23 17:30 | 4.4065 | 0 | N/A | 0 | 0
2022-10-23 18:00 | 5.133 | 0 | N/A | 0 | 0
2022-10-23 18:30 | 5.8943 | 0 | N/A | 0 | 0
2022-10-23 19:00 | 6.1606 | 0 | N/A | 0 | 0
2022-10-23 19:30 | 6.3426 | 0 | N/A | 0 | 0
2022-10-23 20:00 | 6.3848 | 0 | N/A | 0 | 0
2022-10-23 20:30 | 6.209 | 0 | N/A | 0 | 0
2022-10-23 21:00 | 5.9274 | 0 | N/A | 0 | 0
2022-10-23 21:30 | 5.6233 | 0 | N/A | 0 | 0
2022-10-23 22:00 | 5.1156 | 0 | N/A | 0 | 0
2022-10-23 22:30 | 5.1687 | 0 | N/A | 0 | 0
2022-10-23 23:00 | 5.0746 | 0 | N/A | 0 | 0
2022-10-23 23:30 | 4.7731 | 0 | N/A | 0 | 0
2022-10-24 | 4.7784 | 0 | N/A | 0 | 0
2022-10-24 00:30 | 4.9072 | 0 | N/A | 0 | 0
2022-10-24 01:00 | 5.2598 | 0 | N/A | 0 | 0
2022-10-24 01:30 | 4.6681 | 0 | N/A | 0 | 0
2022-10-24 02:00 | 4.1135 | 0 | N/A | 0 | 0
2022-10-24 02:30 | 4.1047 | 0 | N/A | 0 | 0
2022-10-24 03:00 | 3.8652 | 0 | N/A | 0 | 0
2022-10-24 03:30 | 3.4944 | 0 | N/A | 0 | 0
2022-10-24 04:00 | 3.2999 | 0 | N/A | 0 | 0
2022-10-24 04:30 | 3.1406 | 0 | N/A | 0 | 0
2022-10-24 05:00 | 3.1825 | 0 | N/A | 0 | 0
2022-10-24 05:30 | 3.4917 | 0 | N/A | 0 | 0
2022-10-24 06:00 | 3.9343 | 0 | N/A | 0 | 0
2022-10-24 06:30 | 4.5245 | 0 | N/A | 0 | 0
2022-10-24 07:00 | 5.2442 | 0 | N/A | 0 | 0
2022-10-24 07:30 | 6.4691 | 0 | N/A | 0 | 0
2022-10-24 08:00 | 6.905 | 0 | N/A | 0 | 0
2022-10-24 08:30 | 6.3328 | 0 | N/A | 0 | 0
2022-10-24 09:00 | 6.2738 | 0 | N/A | 0 | 0
2022-10-24 09:30 | 6.3443 | 0 | N/A | 0 | 0
2022-10-24 10:00 | 6.0811 | 0 | N/A | 0 | 0
2022-10-24 10:30 | 5.6223 | 0 | N/A | 0 | 0
2022-10-24 11:00 | 5.8883 | 0 | N/A | 0 | 0
2022-10-24 11:30 | 5.7544 | 0 | N/A | 0 | 0
2022-10-24 12:00 | 5.8382 | 0 | N/A | 0 | 0
2022-10-24 12:30 | 5.2079 | 0 | N/A | 0 | 0
2022-10-24 13:00 | 5.3844 | 0 | N/A | 0 | 0
2022-10-24 13:30 | 5.4117 | 0 | N/A | 0 | 0
2022-10-24 14:00 | 5.5395 | 0 | N/A | 0 | 0
2022-10-24 14:30 | 5.1421 | 0 | N/A | 0 | 0
2022-10-24 15:00 | 5.4255 | 0 | N/A | 0 | 0
2022-10-24 15:30 | 5.2257 | 0 | N/A | 0 | 0
2022-10-24 16:00 | 5.188 | 0 | N/A | 0 | 0
2022-10-24 16:30 | 5.6237 | 0 | N/A | 0 | 0
2022-10-24 17:00 | 5.9196 | 0 | N/A | 0 | 0
2022-10-24 17:30 | 6.2909 | 0 | N/A | 0 | 0
2022-10-24 18:00 | 6.9684 | 0 | N/A | 0 | 0
2022-10-24 18:30 | 7.4148 | 0 | N/A | 0 | 0
2022-10-24 19:00 | 7.2214 | 0 | N/A | 0 | 0
2022-10-24 19:30 | 7.1355 | 0 | N/A | 0 | 0
2022-10-24 20:00 | 7.1179 | 0 | N/A | 0 | 0
2022-10-24 20:30 | 7.0034 | 0 | N/A | 0 | 0
2022-10-24 21:00 | 6.6263 | 0 | N/A | 0 | 0
2022-10-24 21:30 | 6.1563 | 0 | N/A | 0 | 0
2022-10-24 22:00 | 5.6137 | 0 | N/A | 0 | 0
2022-10-24 22:30 | 5.4436 | 0 | N/A | 0 | 0
2022-10-24 23:00 | 5.2891 | 0 | N/A | 0 | 0
2022-10-24 23:30 | 4.8338 | 0 | N/A | 0 | 0
2022-10-25 | 4.6127 | 0 | N/A | 0 | 0
2022-10-25 00:30 | 4.9068 | 0 | N/A | 0 | 0
2022-10-25 01:00 | 5.2211 | 0 | N/A | 0 | 0
2022-10-25 01:30 | 4.6245 | 0 | N/A | 0 | 0
2022-10-25 02:00 | 4.0414 | 0 | N/A | 0 | 0
2022-10-25 02:30 | 3.9479 | 0 | N/A | 0 | 0
2022-10-25 03:00 | 3.6458 | 0 | N/A | 0 | 0
2022-10-25 03:30 | 3.4018 | 0 | N/A | 0 | 0
2022-10-25 04:00 | 3.1738 | 0 | N/A | 0 | 0
2022-10-25 04:30 | 3.1384 | 0 | N/A | 0 | 0
2022-10-25 05:00 | 3.1446 | 0 | N/A | 0 | 0
2022-10-25 05:30 | 3.4242 | 0 | N/A | 0 | 0
2022-10-25 06:00 | 3.8173 | 0 | N/A | 0 | 0
2022-10-25 06:30 | 4.3431 | 0 | N/A | 0 | 0
2022-10-25 07:00 | 4.8267 | 0 | N/A | 0 | 0
2022-10-25 07:30 | 5.6149 | 0 | N/A | 0 | 0
2022-10-25 08:00 | 5.5566 | 0 | N/A | 0 | 0
2022-10-25 08:30 | 4.3242 | 0 | N/A | 0 | 0
2022-10-25 09:00 | 2.947 | 0 | N/A | 0 | 0
2022-10-25 09:30 | 2.1151 | 0 | N/A | 0 | 0
2022-10-25 10:00 | 1.5937 | 0 | N/A | 0 | 0
2022-10-25 10:30 | 1.1396 | 0 | N/A | 0 | 0
2022-10-25 11:00 | 0.87943 | 0 | N/A | 0 | 0
2022-10-25 11:30 | 0.65809 | 0 | N/A | 0 | 0
2022-10-25 12:00 | 0.5642 | 0 | N/A | 0 | 0
2022-10-25 12:30 | -0.54496 | 0 | N/A | 0 | 0
2022-10-25 13:00 | -0.49121 | 0 | N/A | 0 | 0
2022-10-25 13:30 | 0.41419 | 0 | N/A | 0 | 0
2022-10-25 14:00 | -0.66233 | 0 | N/A | 0 | 0
2022-10-25 14:30 | -0.78137 | 0 | N/A | 0 | 0
2022-10-25 15:00 | -0.71005 | 0 | N/A | 0 | 0
2022-10-25 15:30 | -0.60959 | 0 | N/A | 0 | 0
2022-10-25 16:00 | -0.7398 | 0 | N/A | 0 | 0
2022-10-25 16:30 | 1.2072 | 0 | N/A | 0 | 0
2022-10-25 17:00 | 1.6208 | 0 | N/A | 0 | 0
2022-10-25 17:30 | 1.7085 | 0 | N/A | 0 | 0
2022-10-25 18:00 | 2.9055 | 0 | N/A | 0 | 0
2022-10-25 18:30 | 3.7809 | 0 | N/A | 0 | 0
2022-10-25 19:00 | 4.5427 | 0 | N/A | 0 | 0
2022-10-25 19:30 | 4.9809 | 0 | N/A | 0 | 0
2022-10-25 20:00 | 5.0755 | 0 | N/A | 0 | 0
2022-10-25 20:30 | 5.1973 | 0 | N/A | 0 | 0
2022-10-25 21:00 | 5.1515 | 0 | N/A | 0 | 0
2022-10-25 21:30 | 4.8613 | 0 | N/A | 0 | 0
2022-10-25 22:00 | 4.4588 | 0 | N/A | 0 | 0
2022-10-25 22:30 | 4.5202 | 0 | N/A | 0 | 0
2022-10-25 23:00 | 4.5809 | 0 | N/A | 0 | 0
2022-10-25 23:30 | 4.1653 | 0 | N/A | 0 | 0
2022-10-26 | 4.1582 | 0 | N/A | 0 | 0
2022-10-26 00:30 | 4.3924 | 0 | N/A | 0 | 0
2022-10-26 01:00 | 4.6279 | 0 | N/A | 0 | 0
2022-10-26 01:30 | 4.0077 | 0 | N/A | 0 | 0
2022-10-26 02:00 | 3.5007 | 0 | N/A | 0 | 0
2022-10-26 02:30 | 3.4032 | 0 | N/A | 0 | 0
2022-10-26 03:00 | 3.1453 | 0 | N/A | 0 | 0
2022-10-26 03:30 | 2.8883 | 0 | N/A | 0 | 0
2022-10-26 04:00 | 2.7475 | 0 | N/A | 0 | 0
2022-10-26 04:30 | 2.6852 | 0 | N/A | 0 | 0
2022-10-26 05:00 | 2.7579 | 0 | N/A | 0 | 0
2022-10-26 05:30 | 2.9559 | 0 | N/A | 0 | 0
2022-10-26 06:00 | 3.2699 | 0 | N/A | 0 | 0
2022-10-26 06:30 | 3.7645 | 0 | N/A | 0 | 0
2022-10-26 07:00 | 4.1939 | 0 | N/A | 0 | 0
2022-10-26 07:30 | 4.8758 | 0 | N/A | 0 | 0
2022-10-26 08:00 | 5.2324 | 0 | N/A | 0 | 0
2022-10-26 08:30 | 4.6752 | 0 | N/A | 0 | 0
2022-10-26 09:00 | 4.4412 | 0 | N/A | 0 | 0
2022-10-26 09:30 | 4.264 | 0 | N/A | 0 | 0
2022-10-26 10:00 | 4.1442 | 0 | N/A | 0 | 0
2022-10-26 10:30 | 3.6413 | 0 | N/A | 0 | 0
2022-10-26 11:00 | 3.0766 | 0 | N/A | 0 | 0
2022-10-26 11:30 | 3.2308 | 0 | N/A | 0 | 0
2022-10-26 12:00 | 3.7275 | 0 | N/A | 0 | 0
2022-10-26 12:30 | 3.7262 | 0 | N/A | 0 | 0
2022-10-26 13:00 | 3.4896 | 0 | N/A | 0 | 0
2022-10-26 13:30 | 3.563 | 0 | N/A | 0 | 0
2022-10-26 14:00 | 3.5126 | 0 | N/A | 0 | 0
2022-10-26 14:30 | 2.4241 | 0 | N/A | 0 | 0
2022-10-26 15:00 | 2.7152 | 0 | N/A | 0 | 0
2022-10-26 15:30 | 2.1214 | 0 | N/A | 0 | 0
2022-10-26 16:00 | 1.2986 | 0 | N/A | 0 | 0
2022-10-26 16:30 | 2.1175 | 0 | N/A | 0 | 0
2022-10-26 17:00 | 2.6372 | 0 | N/A | 0 | 0
2022-10-26 17:30 | 3.3129 | 0 | N/A | 0 | 0
2022-10-26 18:00 | 4.5493 | 0 | N/A | 0 | 0
2022-10-26 18:30 | 5.0221 | 0 | N/A | 0 | 0
2022-10-26 19:00 | 5.6808 | 0 | N/A | 0 | 0
2022-10-26 19:30 | 5.8406 | 0 | N/A | 0 | 0
2022-10-26 20:00 | 5.8276 | 0 | N/A | 0 | 0
2022-10-26 20:30 | 5.8612 | 0 | N/A | 0 | 0
2022-10-26 21:00 | 5.7251 | 0 | N/A | 0 | 0
2022-10-26 21:30 | 5.3907 | 0 | N/A | 0 | 0
2022-10-26 22:00 | 4.9945 | 0 | N/A | 0 | 0
2022-10-26 22:30 | 4.9964 | 0 | N/A | 0 | 0
2022-10-26 23:00 | 4.9347 | 0 | N/A | 0 | 0
2022-10-26 23:30 | 4.5716 | 0 | N/A | 0 | 0
2022-10-27 | 4.3736 | 0 | N/A | 0 | 0
2022-10-27 00:30 | 4.6979 | 0 | N/A | 0 | 0
2022-10-27 01:00 | 5.0486 | 0 | N/A | 0 | 0
2022-10-27 01:30 | 4.3841 | 0 | N/A | 0 | 0
2022-10-27 02:00 | 3.7387 | 0 | N/A | 0 | 0
2022-10-27 02:30 | 3.6525 | 0 | N/A | 0 | 0
2022-10-27 03:00 | 3.3839 | 0 | N/A | 0 | 0
2022-10-27 03:30 | 3.0998 | 0 | N/A | 0 | 0
2022-10-27 04:00 | 2.9137 | 0 | N/A | 0 | 0
2022-10-27 04:30 | 2.8952 | 0 | N/A | 0 | 0
2022-10-27 05:00 | 3.0063 | 0 | N/A | 0 | 0
2022-10-27 05:30 | 3.2021 | 0 | N/A | 0 | 0
2022-10-27 06:00 | 3.5908 | 0 | N/A | 0 | 0
2022-10-27 06:30 | 4.1862 | 0 | N/A | 0 | 0
2022-10-27 07:00 | 4.8215 | 0 | N/A | 0 | 0
2022-10-27 07:30 | 5.9862 | 0 | N/A | 0 | 0
2022-10-27 08:00 | 6.4492 | 0 | N/A | 0 | 0
2022-10-27 08:30 | 5.5961 | 0 | N/A | 0 | 0
2022-10-27 09:00 | 5.254 | 0 | N/A | 0 | 0
2022-10-27 09:30 | 4.8778 | 0 | N/A | 0 | 0
2022-10-27 10:00 | 4.3637 | 0 | N/A | 0 | 0
2022-10-27 10:30 | 4.5544 | 0 | N/A | 0 | 0
2022-10-27 11:00 | 4.529 | 0 | N/A | 0 | 0
2022-10-27 11:30 | 3.5269 | 0 | N/A | 0 | 0
2022-10-27 12:00 | 3.6822 | 0 | N/A | 0 | 0
2022-10-27 12:30 | 2.3531 | 0 | N/A | 0 | 0
2022-10-27 13:00 | 2.1209 | 0 | N/A | 0 | 0
2022-10-27 13:30 | 2.5773 | 0 | N/A | 0 | 0
2022-10-27 14:00 | 2.2958 | 0 | N/A | 0 | 0
2022-10-27 14:30 | 4.3376 | 0 | N/A | 0 | 0
2022-10-27 15:00 | 3.538 | 0 | N/A | 0 | 0
2022-10-27 15:30 | 3.0622 | 0 | N/A | 0 | 0
2022-10-27 16:00 | 4.3513 | 0 | N/A | 0 | 0
2022-10-27 16:30 | 4.2779 | 0 | N/A | 0 | 0
2022-10-27 17:00 | 4.5144 | 0 | N/A | 0 | 0
2022-10-27 17:30 | 3.9537 | 0 | N/A | 0 | 0
2022-10-27 18:00 | 4.9814 | 0 | N/A | 0 | 0
2022-10-27 18:30 | 6.0571 | 0 | N/A | 0 | 0
2022-10-27 19:00 | 6.2834 | 0 | N/A | 0 | 0
2022-10-27 19:30 | 6.8189 | 0 | N/A | 0 | 0
2022-10-27 20:00 | 6.9608 | 0 | N/A | 0 | 0
2022-10-27 20:30 | 6.9954 | 0 | N/A | 0 | 0
2022-10-27 21:00 | 6.8753 | 0 | N/A | 0 | 0
2022-10-27 21:30 | 6.433 | 0 | N/A | 0 | 0
2022-10-27 22:00 | 5.9535 | 0 | N/A | 0 | 0
2022-10-27 22:30 | 5.8473 | 0 | N/A | 0 | 0
2022-10-27 23:00 | 5.6939 | 0 | N/A | 0 | 0
2022-10-27 23:30 | 5.2473 | 0 | N/A | 0 | 0
2022-10-28 | 5.1096 | 0 | N/A | 0 | 0
2022-10-28 00:30 | 5.3076 | 0 | N/A | 0 | 0
2022-10-28 01:00 | 5.6913 | 0 | N/A | 0 | 0
2022-10-28 01:30 | 5.1218 | 0 | N/A | 0 | 0
2022-10-28 02:00 | 4.6206 | 0 | N/A | 0 | 0
2022-10-28 02:30 | 4.4735 | 0 | N/A | 0 | 0
2022-10-28 03:00 | 4.0657 | 0 | N/A | 0 | 0
2022-10-28 03:30 | 3.7695 | 0 | N/A | 0 | 0
2022-10-28 04:00 | 3.5704 | 0 | N/A | 0 | 0
2022-10-28 04:30 | 3.4632 | 0 | N/A | 0 | 0
2022-10-28 05:00 | 3.6001 | 0 | N/A | 0 | 0
2022-10-28 05:30 | 3.8578 | 0 | N/A | 0 | 0
2022-10-28 06:00 | 4.2472 | 0 | N/A | 0 | 0
2022-10-28 06:30 | 4.9265 | 0 | N/A | 0 | 0
2022-10-28 07:00 | 5.5511 | 0 | N/A | 0 | 0
2022-10-28 07:30 | 6.9164 | 0 | N/A | 0 | 0
2022-10-28 08:00 | 7.7334 | 0 | N/A | 0 | 0
2022-10-28 08:30 | 7.2739 | 0 | N/A | 0 | 0
2022-10-28 09:00 | 6.9153 | 0 | N/A | 0 | 0
2022-10-28 09:30 | 6.6067 | 0 | N/A | 0 | 0
2022-10-28 10:00 | 6.1375 | 0 | N/A | 0 | 0
2022-10-28 10:30 | 6.1 | 0 | N/A | 0 | 0
2022-10-28 11:00 | 5.5146 | 0 | N/A | 0 | 0
2022-10-28 11:30 | 4.4964 | 0 | N/A | 0 | 0
2022-10-28 12:00 | 4.526 | 0 | N/A | 0 | 0
2022-10-28 12:30 | 3.8579 | 0 | N/A | 0 | 0
2022-10-28 13:00 | 2.7913 | 0 | N/A | 0 | 0
2022-10-28 13:30 | 2.8619 | 0 | N/A | 0 | 0
2022-10-28 14:00 | 3.8208 | 0 | N/A | 0 | 0
2022-10-28 14:30 | 2.3113 | 0 | N/A | 0 | 0
2022-10-28 15:00 | 3.1761 | 0 | N/A | 0 | 0
2022-10-28 15:30 | 4.1695 | 0 | N/A | 0 | 0
2022-10-28 16:00 | 4.5308 | 0 | N/A | 0 | 0
2022-10-28 16:30 | 4.7936 | 0 | N/A | 0 | 0
2022-10-28 17:00 | 5.2743 | 0 | N/A | 0 | 0
2022-10-28 17:30 | 5.8647 | 0 | N/A | 0 | 0
2022-10-28 18:00 | 6.5818 | 0 | N/A | 0 | 0
2022-10-28 18:30 | 7.2941 | 0 | N/A | 0 | 0
2022-10-28 19:00 | 7.4991 | 0 | N/A | 0 | 0
2022-10-28 19:30 | 7.6062 | 0 | N/A | 0 | 0
2022-10-28 20:00 | 7.7542 | 0 | N/A | 0 | 0
2022-10-28 20:30 | 7.6785 | 0 | N/A | 0 | 0
2022-10-28 21:00 | 7.5768 | 0 | N/A | 0 | 0
2022-10-28 21:30 | 7.1326 | 0 | N/A | 0 | 0
2022-10-28 22:00 | 6.732 | 0 | N/A | 0 | 0
2022-10-28 22:30 | 6.6906 | 0 | N/A | 0 | 0
2022-10-28 23:00 | 6.538 | 0 | N/A | 0 | 0
2022-10-28 23:30 | 5.9974 | 0 | N/A | 0 | 0
2022-10-29 | 5.802 | 0 | N/A | 0 | 0
2022-10-29 00:30 | 5.942 | 0 | N/A | 0 | 0
2022-10-29 01:00 | 6.2066 | 0 | N/A | 0 | 0
2022-10-29 01:30 | 5.5206 | 0 | N/A | 0 | 0
2022-10-29 02:00 | 4.8928 | 0 | N/A | 0 | 0
2022-10-29 02:30 | 4.749 | 0 | N/A | 0 | 0
2022-10-29 03:00 | 4.4182 | 0 | N/A | 0 | 0
2022-10-29 03:30 | 4.1121 | 0 | N/A | 0 | 0
2022-10-29 04:00 | 3.8854 | 0 | N/A | 0 | 0
2022-10-29 04:30 | 3.8139 | 0 | N/A | 0 | 0
2022-10-29 05:00 | 3.7067 | 0 | N/A | 0 | 0
2022-10-29 05:30 | 3.8107 | 0 | N/A | 0 | 0
2022-10-29 06:00 | 3.9794 | 0 | N/A | 0 | 0
2022-10-29 06:30 | 4.3336 | 0 | N/A | 0 | 0
2022-10-29 07:00 | 4.5717 | 0 | N/A | 0 | 0
2022-10-29 07:30 | 4.8733 | 0 | N/A | 0 | 0
2022-10-29 08:00 | 5.2338 | 0 | N/A | 0 | 0
2022-10-29 08:30 | 5.1415 | 0 | N/A | 0 | 0
2022-10-29 09:00 | 4.9814 | 0 | N/A | 0 | 0
2022-10-29 09:30 | 4.0622 | 0 | N/A | 0 | 0
2022-10-29 10:00 | 2.9689 | 0 | N/A | 0 | 0
2022-10-29 10:30 | 2.2395 | 0 | N/A | 0 | 0
2022-10-29 11:00 | 2.4592 | 0 | N/A | 0 | 0
2022-10-29 11:30 | 1.9106 | 0 | N/A | 0 | 0
2022-10-29 12:00 | 1.6264 | 0 | N/A | 0 | 0
2022-10-29 12:30 | 1.3649 | 0 | N/A | 0 | 0
2022-10-29 13:00 | 1.058 | 0 | N/A | 0 | 0
2022-10-29 13:30 | 1.1076 | 0 | N/A | 0 | 0
2022-10-29 14:00 | 0.96667 | 0 | N/A | 0 | 0
2022-10-29 14:30 | 1.1544 | 0 | N/A | 0 | 0
2022-10-29 15:00 | 1.2873 | 0 | N/A | 0 | 0
2022-10-29 15:30 | 2.8926 | 0 | N/A | 0 | 0
2022-10-29 16:00 | 3.4045 | 0 | N/A | 0 | 0
2022-10-29 16:30 | 3.3805 | 0 | N/A | 0 | 0
2022-10-29 17:00 | 3.3962 | 0 | N/A | 0 | 0
2022-10-29 17:30 | 3.8705 | 0 | N/A | 0 | 0
2022-10-29 18:00 | 5.0958 | 0 | N/A | 0 | 0
2022-10-29 18:30 | 6.0406 | 0 | N/A | 0 | 0
2022-10-29 19:00 | 6.4479 | 0 | N/A | 0 | 0
2022-10-29 19:30 | 6.5587 | 0 | N/A | 0 | 0
2022-10-29 20:00 | 6.6223 | 0 | N/A | 0 | 0
2022-10-29 20:30 | 6.5859 | 0 | N/A | 0 | 0
2022-10-29 21:00 | 6.3895 | 0 | N/A | 0 | 0
2022-10-29 21:30 | 6.1387 | 0 | N/A | 0 | 0
2022-10-29 22:00 | 5.8452 | 0 | N/A | 0 | 0
2022-10-29 22:30 | 6.004 | 0 | N/A | 0 | 0
2022-10-29 23:00 | 5.9623 | 0 | N/A | 0 | 0
2022-10-29 23:30 | 5.5671 | 0 | N/A | 0 | 0
2022-10-30 | 5.512 | 0 | N/A | 0 | 0
2022-10-30 00:30 | 5.6959 | 0 | N/A | 0 | 0
2022-10-30 01:00 | 4.0462 | 0 | N/A | 0 | 0
2022-10-30 01:30 | 2.1699 | 0 | N/A | 0 | 0
2022-10-30 02:00 | 5.0035 | 0 | N/A | 0 | 0
2022-10-30 02:30 | 5.3481 | 0 | N/A | 0 | 0
2022-10-30 03:00 | 4.6838 | 0 | N/A | 0 | 0
2022-10-30 03:30 | 4.1913 | 0 | N/A | 0 | 0
2022-10-30 04:00 | 3.9112 | 0 | N/A | 0 | 0
2022-10-30 04:30 | 3.7656 | 0 | N/A | 0 | 0
2022-10-30 05:00 | 3.7363 | 0 | N/A | 0 | 0
2022-10-30 05:30 | 3.7731 | 0 | N/A | 0 | 0
2022-10-30 06:00 | 3.8127 | 0 | N/A | 0 | 0
2022-10-30 06:30 | 4.0109 | 0 | N/A | 0 | 0
2022-10-30 07:00 | 4.1975 | 0 | N/A | 0 | 0
2022-10-30 07:30 | 4.3669 | 0 | N/A | 0 | 0
2022-10-30 08:00 | 4.1503 | 0 | N/A | 0 | 0
2022-10-30 08:30 | 3.4037 | 0 | N/A | 0 | 0
2022-10-30 09:00 | 2.674 | 0 | N/A | 0 | 0
2022-10-30 09:30 | 2.0527 | 0 | N/A | 0 | 0
2022-10-30 10:00 | 1.2308 | 0 | N/A | 0 | 0
2022-10-30 10:30 | 0.8025 | 0 | N/A | 0 | 0
2022-10-30 11:00 | -1.0605 | 0 | N/A | 0 | 0
2022-10-30 11:30 | -1.1011 | 0 | N/A | 0 | 0
2022-10-30 12:00 | -1.8244 | 0 | N/A | 0 | 0
2022-10-30 12:30 | -1.9621 | 0 | N/A | 0 | 0
2022-10-30 13:00 | -1.2463 | 0 | N/A | 0 | 0
2022-10-30 13:30 | -1.9805 | 0 | N/A | 0 | 0
2022-10-30 14:00 | -1.5434 | 0 | N/A | 0 | 0
2022-10-30 14:30 | -1.0853 | 0 | N/A | 0 | 0
2022-10-30 15:00 | 1.1809 | 0 | N/A | 0 | 0
2022-10-30 15:30 | 1.6641 | 0 | N/A | 0 | 0
2022-10-30 16:00 | 1.8142 | 0 | N/A | 0 | 0
2022-10-30 16:30 | 3.5283 | 0 | N/A | 0 | 0
2022-10-30 17:00 | 5.2136 | 0 | N/A | 0 | 0
2022-10-30 17:30 | 5.6678 | 0 | N/A | 0 | 0
2022-10-30 18:00 | 6.0494 | 0 | N/A | 0 | 0
2022-10-30 18:30 | 5.733 | 0 | N/A | 0 | 0
2022-10-30 19:00 | 6.0587 | 0 | N/A | 0 | 0
2022-10-30 19:30 | 6.0106 | 0 | N/A | 0 | 0
2022-10-30 20:00 | 6.2864 | 0 | N/A | 0 | 0
2022-10-30 20:30 | 6.312 | 0 | N/A | 0 | 0
2022-10-30 21:00 | 6.1737 | 0 | N/A | 0 | 0
2022-10-30 21:30 | 5.7969 | 0 | N/A | 0 | 0
2022-10-30 22:00 | 5.3756 | 0 | N/A | 0 | 0
2022-10-30 22:30 | 5.2586 | 0 | N/A | 0 | 0
2022-10-30 23:00 | 5.1346 | 0 | N/A | 0 | 0
2022-10-30 23:30 | 4.8075 | 0 | N/A | 0 | 0
2022-10-31 | 4.7577 | 0 | N/A | 0 | 0
2022-10-31 00:30 | 4.9092 | 0 | N/A | 0 | 0
2022-10-31 01:00 | 5.067 | 0 | N/A | 0 | 0
2022-10-31 01:30 | 4.4549 | 0 | N/A | 0 | 0
2022-10-31 02:00 | 3.976 | 0 | N/A | 0 | 0
2022-10-31 02:30 | 3.8896 | 0 | N/A | 0 | 0
2022-10-31 03:00 | 3.6595 | 0 | N/A | 0 | 0
2022-10-31 03:30 | 3.2748 | 0 | N/A | 0 | 0
2022-10-31 04:00 | 3.0186 | 0 | N/A | 0 | 0
2022-10-31 04:30 | 2.84 | 0 | N/A | 0 | 0
2022-10-31 05:00 | 2.9248 | 0 | N/A | 0 | 0
2022-10-31 05:30 | 3.054 | 0 | N/A | 0 | 0
2022-10-31 06:00 | 3.2753 | 0 | N/A | 0 | 0
2022-10-31 06:30 | 3.5768 | 0 | N/A | 0 | 0
2022-10-31 07:00 | 3.9815 | 0 | N/A | 0 | 0
2022-10-31 07:30 | 4.3154 | 0 | N/A | 0 | 0
2022-10-31 08:00 | 4.3276 | 0 | N/A | 0 | 0
2022-10-31 08:30 | 3.7523 | 0 | N/A | 0 | 0
2022-10-31 09:00 | 2.7204 | 0 | N/A | 0 | 0
2022-10-31 09:30 | 2.6069 | 0 | N/A | 0 | 0
2022-10-31 10:00 | 2.5403 | 0 | N/A | 0 | 0
2022-10-31 10:30 | 2.9325 | 0 | N/A | 0 | 0
2022-10-31 11:00 | 2.7206 | 0 | N/A | 0 | 0
2022-10-31 11:30 | 3.0537 | 0 | N/A | 0 | 0
2022-10-31 12:00 | 3.7527 | 0 | N/A | 0 | 0
2022-10-31 12:30 | 3.2405 | 0 | N/A | 0 | 0
2022-10-31 13:00 | 2.0677 | 0 | N/A | 0 | 0
2022-10-31 13:30 | 3.2499 | 0 | N/A | 0 | 0
2022-10-31 14:00 | 3.0647 | 0 | N/A | 0 | 0
2022-10-31 14:30 | 2.6883 | 0 | N/A | 0 | 0
2022-10-31 15:00 | 2.5358 | 0 | N/A | 0 | 0
2022-10-31 15:30 | 3.6716 | 0 | N/A | 0 | 0
2022-10-31 16:00 | 3.9573 | 0 | N/A | 0 | 0
2022-10-31 16:30 | 4.4282 | 0 | N/A | 0 | 0
2022-10-31 17:00 | 5.0172 | 0 | N/A | 0 | 0
2022-10-31 17:30 | 5.6007 | 0 | N/A | 0 | 0
2022-10-31 18:00 | 5.9044 | 0 | N/A | 0 | 0
2022-10-31 18:30 | 6.4599 | 0 | N/A | 0 | 0
2022-10-31 19:00 | 6.6069 | 0 | N/A | 0 | 0
2022-10-31 19:30 | 6.9266 | 0 | N/A | 0 | 0
2022-10-31 20:00 | 6.9985 | 0 | N/A | 0 | 0
2022-10-31 20:30 | 6.9877 | 0 | N/A | 0 | 0
2022-10-31 21:00 | 6.7864 | 0 | N/A | 0 | 0
2022-10-31 21:30 | 6.4729 | 0 | N/A | 0 | 0
2022-10-31 22:00 | 6.1241 | 0 | N/A | 0 | 0
2022-10-31 22:30 | 6.1058 | 0 | N/A | 0 | 0
2022-10-31 23:00 | 5.884 | 0 | N/A | 0 | 0
2022-10-31 23:30 | 5.3246 | 0 | N/A | 0 | 0
2022-11-01 | 5.1758 | 0 | N/A | 0 | 0
2022-11-01 00:30 | 5.2849 | 0 | N/A | 0 | 0
2022-11-01 01:00 | 5.6406 | 0 | N/A | 0 | 0
2022-11-01 01:30 | 3.6147 | 0 | N/A | 0 | 0
2022-11-01 02:00 | 5.6425 | 0 | N/A | 0 | 0
2022-11-01 02:30 | 5.9237 | 0 | N/A | 0 | 0
2022-11-01 03:00 | 5.7028 | 0 | N/A | 0 | 0
2022-11-01 03:30 | 5.2381 | 0 | N/A | 0 | 0
2022-11-01 04:00 | 3.7711 | 0 | N/A | 0 | 0
2022-11-01 04:30 | 3.3299 | 0 | N/A | 0 | 0
2022-11-01 05:00 | 3.3199 | 0 | N/A | 0 | 0
2022-11-01 05:30 | 3.4701 | 0 | N/A | 0 | 0
2022-11-01 06:00 | 3.6502 | 0 | N/A | 0 | 0
2022-11-01 06:30 | 3.9771 | 0 | N/A | 0 | 0
2022-11-01 07:00 | 4.1183 | 0 | N/A | 0 | 0
2022-11-01 07:30 | 4.3764 | 0 | N/A | 0 | 0
2022-11-01 08:00 | 4.2367 | 0 | N/A | 0 | 0
2022-11-01 08:30 | 3.4323 | 0 | N/A | 0 | 0
2022-11-01 09:00 | 3.4013 | 0 | N/A | 0 | 0
2022-11-01 09:30 | 3.0548 | 0 | N/A | 0 | 0
2022-11-01 10:00 | 4.1724 | 0 | N/A | 0 | 0
2022-11-01 10:30 | 5.2417 | 0 | N/A | 0 | 0
2022-11-01 11:00 | 5.4663 | 0 | N/A | 0 | 0
2022-11-01 11:30 | 6.3748 | 0 | N/A | 0 | 0
2022-11-01 12:00 | 4.9668 | 0 | N/A | 0 | 0
2022-11-01 12:30 | 4.1798 | 0 | N/A | 0 | 0
2022-11-01 13:00 | 5.7243 | 0 | N/A | 0 | 0
2022-11-01 13:30 | 3.6889 | 0 | N/A | 0 | 0
2022-11-01 14:00 | 2.6497 | 0 | N/A | 0 | 0
2022-11-01 14:30 | 3.5263 | 0 | N/A | 0 | 0
2022-11-01 15:00 | 1.7741 | 0 | N/A | 0 | 0
2022-11-01 15:30 | 1.3413 | 0 | N/A | 0 | 0
2022-11-01 16:00 | 2.1764 | 0 | N/A | 0 | 0
2022-11-01 16:30 | 2.7518 | 0 | N/A | 0 | 0
2022-11-01 17:00 | 3.3736 | 0 | N/A | 0 | 0
2022-11-01 17:30 | 3.9963 | 0 | N/A | 0 | 0
2022-11-01 18:00 | 5.4582 | 0 | N/A | 0 | 0
2022-11-01 18:30 | 7.0849 | 0 | N/A | 0 | 0
2022-11-01 19:00 | 7.1483 | 0 | N/A | 0 | 0
2022-11-01 19:30 | 7.7052 | 0 | N/A | 0 | 0
2022-11-01 20:00 | 8.1194 | 0 | N/A | 0 | 0
2022-11-01 20:30 | 8.0895 | 0 | N/A | 0 | 0
2022-11-01 21:00 | 7.8232 | 0 | N/A | 0 | 0
2022-11-01 21:30 | 7.4973 | 0 | N/A | 0 | 0
2022-11-01 22:00 | 6.8884 | 0 | N/A | 0 | 0
2022-11-01 22:30 | 6.7354 | 0 | N/A | 0 | 0
2022-11-01 23:00 | 6.5781 | 0 | N/A | 0 | 0
2022-11-01 23:30 | 6.0703 | 0 | N/A | 0 | 0
2022-11-02 | 5.8911 | 0 | N/A | 0 | 0
2022-11-02 00:30 | 6.1742 | 0 | N/A | 0 | 0
2022-11-02 01:00 | 6.4982 | 0 | N/A | 0 | 0
2022-11-02 01:30 | 5.9787 | 0 | N/A | 0 | 0
2022-11-02 02:00 | 5.4457 | 0 | N/A | 0 | 0
2022-11-02 02:30 | 5.3954 | 0 | N/A | 0 | 0
2022-11-02 03:00 | 5.0772 | 0 | N/A | 0 | 0
2022-11-02 03:30 | 4.6858 | 0 | N/A | 0 | 0
2022-11-02 04:00 | 4.4478 | 0 | N/A | 0 | 0
2022-11-02 04:30 | 4.3378 | 0 | N/A | 0 | 0
2022-11-02 05:00 | 4.3906 | 0 | N/A | 0 | 0
2022-11-02 05:30 | 4.6996 | 0 | N/A | 0 | 0
2022-11-02 06:00 | 5.1201 | 0 | N/A | 0 | 0
2022-11-02 06:30 | 5.8777 | 0 | N/A | 0 | 0
2022-11-02 07:00 | 6.6657 | 0 | N/A | 0 | 0
2022-11-02 07:30 | 7.4105 | 0 | N/A | 0 | 0
2022-11-02 08:00 | 7.7601 | 0 | N/A | 0 | 0
2022-11-02 08:30 | 7.3332 | 0 | N/A | 0 | 0
2022-11-02 09:00 | 7.0863 | 0 | N/A | 0 | 0
2022-11-02 09:30 | 6.4106 | 0 | N/A | 0 | 0
2022-11-02 10:00 | 5.7401 | 0 | N/A | 0 | 0
2022-11-02 10:30 | 4.9002 | 0 | N/A | 0 | 0
2022-11-02 11:00 | 5.0996 | 0 | N/A | 0 | 0
2022-11-02 11:30 | 2.4388 | 0 | N/A | 0 | 0
2022-11-02 12:00 | 2.6032 | 0 | N/A | 0 | 0
2022-11-02 12:30 | 1.8239 | 0 | N/A | 0 | 0
2022-11-02 13:00 | 2.5665 | 0 | N/A | 0 | 0
2022-11-02 13:30 | 2.1993 | 0 | N/A | 0 | 0
2022-11-02 14:00 | 2.3444 | 0 | N/A | 0 | 0
2022-11-02 14:30 | 3.6532 | 0 | N/A | 0 | 0
2022-11-02 15:00 | 4.165 | 0 | N/A | 0 | 0
2022-11-02 15:30 | 3.8751 | 0 | N/A | 0 | 0
2022-11-02 16:00 | 5.3572 | 0 | N/A | 0 | 0
2022-11-02 16:30 | 5.3386 | 0 | N/A | 0 | 0
2022-11-02 17:00 | 6.1155 | 0 | N/A | 0 | 0
2022-11-02 17:30 | 6.3403 | 0 | N/A | 0 | 0
2022-11-02 18:00 | 6.4966 | 0 | N/A | 0 | 0
2022-11-02 18:30 | 7.3506 | 0 | N/A | 0 | 0
2022-11-02 19:00 | 7.7207 | 0 | N/A | 0 | 0
2022-11-02 19:30 | 7.6077 | 0 | N/A | 0 | 0
2022-11-02 20:00 | 7.8709 | 0 | N/A | 0 | 0
2022-11-02 20:30 | 7.9837 | 0 | N/A | 0 | 0
2022-11-02 21:00 | 7.6967 | 0 | N/A | 0 | 0
2022-11-02 21:30 | 7.1943 | 0 | N/A | 0 | 0
2022-11-02 22:00 | 6.6314 | 0 | N/A | 0 | 0
2022-11-02 22:30 | 6.5362 | 0 | N/A | 0 | 0
2022-11-02 23:00 | 6.2303 | 0 | N/A | 0 | 0
2022-11-02 23:30 | 5.6972 | 0 | N/A | 0 | 0
2022-11-03 | 5.5586 | 0 | N/A | 0 | 0
2022-11-03 00:30 | 5.7881 | 0 | N/A | 0 | 0
2022-11-03 01:00 | 6.0842 | 0 | N/A | 0 | 0
2022-11-03 01:30 | 5.5824 | 0 | N/A | 0 | 0
2022-11-03 02:00 | 5.048 | 0 | N/A | 0 | 0
2022-11-03 02:30 | 4.8984 | 0 | N/A | 0 | 0
2022-11-03 03:00 | 4.7353 | 0 | N/A | 0 | 0
2022-11-03 03:30 | 4.2578 | 0 | N/A | 0 | 0
2022-11-03 04:00 | 4.0099 | 0 | N/A | 0 | 0
2022-11-03 04:30 | 3.9868 | 0 | N/A | 0 | 0
2022-11-03 05:00 | 4.0867 | 0 | N/A | 0 | 0
2022-11-03 05:30 | 4.3892 | 0 | N/A | 0 | 0
2022-11-03 06:00 | 4.7771 | 0 | N/A | 0 | 0
2022-11-03 06:30 | 5.5216 | 0 | N/A | 0 | 0
2022-11-03 07:00 | 6.28 | 0 | N/A | 0 | 0
2022-11-03 07:30 | 7.3405 | 0 | N/A | 0 | 0
2022-11-03 08:00 | 7.2112 | 0 | N/A | 0 | 0
2022-11-03 08:30 | 6.1761 | 0 | N/A | 0 | 0
2022-11-03 09:00 | 5.8334 | 0 | N/A | 0 | 0
2022-11-03 09:30 | 5.1917 | 0 | N/A | 0 | 0
2022-11-03 10:00 | 4.0499 | 0 | N/A | 0 | 0
2022-11-03 10:30 | 3.0674 | 0 | N/A | 0 | 0
2022-11-03 11:00 | 2.1578 | 0 | N/A | 0 | 0
2022-11-03 11:30 | 2.7424 | 0 | N/A | 0 | 0
2022-11-03 12:00 | 2.9332 | 0 | N/A | 0 | 0
2022-11-03 12:30 | 2.9675 | 0 | N/A | 0 | 0
2022-11-03 13:00 | 2.9828 | 0 | N/A | 0 | 0
2022-11-03 13:30 | 2.7976 | 0 | N/A | 0 | 0
2022-11-03 14:00 | 1.8681 | 0 | N/A | 0 | 0
2022-11-03 14:30 | 3.3017 | 0 | N/A | 0 | 0
2022-11-03 15:00 | 3.1142 | 0 | N/A | 0 | 0
2022-11-03 15:30 | 2.9749 | 0 | N/A | 0 | 0
2022-11-03 16:00 | 3.5386 | 0 | N/A | 0 | 0
2022-11-03 16:30 | 4.0593 | 0 | N/A | 0 | 0
2022-11-03 17:00 | 4.723 | 0 | N/A | 0 | 0
2022-11-03 17:30 | 5.5874 | 0 | N/A | 0 | 0
2022-11-03 18:00 | 6.25 | 0 | N/A | 0 | 0
2022-11-03 18:30 | 6.5205 | 0 | N/A | 0 | 0
2022-11-03 19:00 | 7.094 | 0 | N/A | 0 | 0
2022-11-03 19:30 | 7.25 | 0 | N/A | 0 | 0
2022-11-03 20:00 | 7.3902 | 0 | N/A | 0 | 0
2022-11-03 20:30 | 7.4133 | 0 | N/A | 0 | 0
2022-11-03 21:00 | 7.2403 | 0 | N/A | 0 | 0
2022-11-03 21:30 | 6.7576 | 0 | N/A | 0 | 0
2022-11-03 22:00 | 6.2725 | 0 | N/A | 0 | 0
2022-11-03 22:30 | 6.2462 | 0 | N/A | 0 | 0
2022-11-03 23:00 | 6.0535 | 0 | N/A | 0 | 0
2022-11-03 23:30 | 5.4049 | 0 | N/A | 0 | 0
2022-11-04 | 5.1959 | 0 | N/A | 0 | 0
2022-11-04 00:30 | 5.4993 | 0 | N/A | 0 | 0
2022-11-04 01:00 | 5.8219 | 0 | N/A | 0 | 0
2022-11-04 01:30 | 5.1685 | 0 | N/A | 0 | 0
2022-11-04 02:00 | 4.6484 | 0 | N/A | 0 | 0
2022-11-04 02:30 | 4.527 | 0 | N/A | 0 | 0
2022-11-04 03:00 | 4.2515 | 0 | N/A | 0 | 0
2022-11-04 03:30 | 3.9984 | 0 | N/A | 0 | 0
2022-11-04 04:00 | 3.7085 | 0 | N/A | 0 | 0
2022-11-04 04:30 | 3.6173 | 0 | N/A | 0 | 0
2022-11-04 05:00 | 3.6966 | 0 | N/A | 0 | 0
2022-11-04 05:30 | 3.99 | 0 | N/A | 0 | 0
2022-11-04 06:00 | 4.3457 | 0 | N/A | 0 | 0
2022-11-04 06:30 | 5.0005 | 0 | N/A | 0 | 0
2022-11-04 07:00 | 5.5909 | 0 | N/A | 0 | 0
2022-11-04 07:30 | 6.6243 | 0 | N/A | 0 | 0
2022-11-04 08:00 | 6.6797 | 0 | N/A | 0 | 0
2022-11-04 08:30 | 5.5331 | 0 | N/A | 0 | 0
2022-11-04 09:00 | 4.6777 | 0 | N/A | 0 | 0
2022-11-04 09:30 | 4.6239 | 0 | N/A | 0 | 0
2022-11-04 10:00 | 4.0335 | 0 | N/A | 0 | 0
2022-11-04 10:30 | 2.9873 | 0 | N/A | 0 | 0
2022-11-04 11:00 | 3.4987 | 0 | N/A | 0 | 0
2022-11-04 11:30 | 3.1396 | 0 | N/A | 0 | 0
2022-11-04 12:00 | 2.6523 | 0 | N/A | 0 | 0
2022-11-04 12:30 | 1.7343 | 0 | N/A | 0 | 0
2022-11-04 13:00 | 0.99161 | 0 | N/A | 0 | 0
2022-11-04 13:30 | 0.99815 | 0 | N/A | 0 | 0
2022-11-04 14:00 | 0.88334 | 0 | N/A | 0 | 0
2022-11-04 14:30 | -0.88484 | 0 | N/A | 0 | 0
2022-11-04 15:00 | -0.91735 | 0 | N/A | 0 | 0
2022-11-04 15:30 | -0.86519 | 0 | N/A | 0 | 0
2022-11-04 16:00 | 1.0062 | 0 | N/A | 0 | 0
2022-11-04 16:30 | 1.0399 | 0 | N/A | 0 | 0
2022-11-04 17:00 | 1.4846 | 0 | N/A | 0 | 0
2022-11-04 17:30 | 2.2971 | 0 | N/A | 0 | 0
2022-11-04 18:00 | 3.563 | 0 | N/A | 0 | 0
2022-11-04 18:30 | 4.4929 | 0 | N/A | 0 | 0
2022-11-04 19:00 | 4.9287 | 0 | N/A | 0 | 0
2022-11-05 00:30 | 5.1304 | 0 | N/A | 0 | 0
2022-11-05 01:00 | 5.3781 | 0 | N/A | 0 | 0
2022-11-05 01:30 | 4.7675 | 0 | N/A | 0 | 0
2022-11-05 02:00 | 4.1859 | 0 | N/A | 0 | 0
2022-11-05 02:30 | 4.022 | 0 | N/A | 0 | 0
2022-11-05 03:00 | 3.691 | 0 | N/A | 0 | 0
2022-11-05 03:30 | 3.4231 | 0 | N/A | 0 | 0
2022-11-05 04:00 | 3.2187 | 0 | N/A | 0 | 0
2022-11-05 04:30 | 3.2023 | 0 | N/A | 0 | 0
2022-11-05 05:00 | 3.1633 | 0 | N/A | 0 | 0
2022-11-05 05:30 | 3.2623 | 0 | N/A | 0 | 0
2022-11-05 06:00 | 3.4197 | 0 | N/A | 0 | 0
2022-11-05 06:30 | 3.6967 | 0 | N/A | 0 | 0
2022-11-05 07:00 | 3.8247 | 0 | N/A | 0 | 0
2022-11-05 07:30 | 3.8382 | 0 | N/A | 0 | 0
2022-11-05 08:00 | 3.5707 | 0 | N/A | 0 | 0
2022-11-05 08:30 | 2.8862 | 0 | N/A | 0 | 0
2022-11-05 09:00 | 2.1589 | 0 | N/A | 0 | 0
2022-11-05 09:30 | 1.3955 | 0 | N/A | 0 | 0
2022-11-05 10:00 | 1.1187 | 0 | N/A | 0 | 0
2022-11-05 10:30 | 1.0035 | 0 | N/A | 0 | 0
2022-11-05 11:00 | 1.4337 | 0 | N/A | 0 | 0
2022-11-05 11:30 | 1.0348 | 0 | N/A | 0 | 0
2022-11-05 12:00 | 1.1747 | 0 | N/A | 0 | 0
2022-11-05 12:30 | -0.98947 | 0 | N/A | 0 | 0
2022-11-05 13:00 | 1.2155 | 0 | N/A | 0 | 0
2022-11-05 13:30 | -1.0341 | 0 | N/A | 0 | 0
2022-11-05 14:00 | -1.1646 | 0 | N/A | 0 | 0
2022-11-05 14:30 | 1.0065 | 0 | N/A | 0 | 0
2022-11-05 15:00 | -1.0169 | 0 | N/A | 0 | 0
2022-11-05 15:30 | -1.0087 | 0 | N/A | 0 | 0
2022-11-05 16:00 | 1.1132 | 0 | N/A | 0 | 0
2022-11-05 16:30 | 1.1048 | 0 | N/A | 0 | 0
2022-11-05 17:00 | 1.1607 | 0 | N/A | 0 | 0
2022-11-05 17:30 | 1.8339 | 0 | N/A | 0 | 0
2022-11-05 18:00 | 2.4484 | 0 | N/A | 0 | 0
2022-11-05 18:30 | 3.2606 | 0 | N/A | 0 | 0
2022-11-05 19:00 | 3.8421 | 0 | N/A | 0 | 0
2022-11-05 19:30 | 4.5229 | 0 | N/A | 0 | 0
2022-11-05 20:00 | 4.7183 | 0 | N/A | 0 | 0
2022-11-05 20:30 | 4.7055 | 0 | N/A | 0 | 0
2022-11-05 21:00 | 4.7044 | 0 | N/A | 0 | 0
2022-11-05 21:30 | 4.5391 | 0 | N/A | 0 | 0
2022-11-05 22:00 | 4.3956 | 0 | N/A | 0 | 0
2022-11-05 22:30 | 4.6306 | 0 | N/A | 0 | 0
2022-11-05 23:00 | 4.7709 | 0 | N/A | 0 | 0
2022-11-05 23:30 | 4.4968 | 0 | N/A | 0 | 0
2022-11-06 | 4.4871 | 0 | N/A | 0 | 0
2022-11-06 00:30 | 4.7491 | 0 | N/A | 0 | 0
2022-11-06 01:00 | 5.0213 | 0 | N/A | 0 | 0
2022-11-06 01:30 | 4.4233 | 0 | N/A | 0 | 0
2022-11-06 02:00 | 3.87 | 0 | N/A | 0 | 0
2022-11-06 02:30 | 3.8107 | 0 | N/A | 0 | 0
2022-11-06 03:00 | 3.5315 | 0 | N/A | 0 | 0
2022-11-06 03:30 | 3.2997 | 0 | N/A | 0 | 0
2022-11-06 04:00 | 3.0783 | 0 | N/A | 0 | 0
2022-11-06 04:30 | 2.9986 | 0 | N/A | 0 | 0
2022-11-06 05:00 | 2.9062 | 0 | N/A | 0 | 0
2022-11-06 05:30 | 2.9035 | 0 | N/A | 0 | 0
2022-11-06 06:00 | 3.0618 | 0 | N/A | 0 | 0
2022-11-06 06:30 | 3.3038 | 0 | N/A | 0 | 0
2022-11-06 07:00 | 3.3767 | 0 | N/A | 0 | 0
2022-11-06 07:30 | 3.4784 | 0 | N/A | 0 | 0
2022-11-06 08:00 | 3.0984 | 0 | N/A | 0 | 0
2022-11-06 08:30 | 2.4517 | 0 | N/A | 0 | 0
2022-11-06 09:00 | 1.7524 | 0 | N/A | 0 | 0
2022-11-06 09:30 | 1.3689 | 0 | N/A | 0 | 0
2022-11-06 10:00 | 1.1295 | 0 | N/A | 0 | 0
2022-11-06 10:30 | -1.1032 | 0 | N/A | 0 | 0
2022-11-06 11:00 | -1.2173 | 0 | N/A | 0 | 0
2022-11-06 11:30 | -1.8457 | 0 | N/A | 0 | 0
2022-11-06 12:00 | -1.3187 | 0 | N/A | 0 | 0
2022-11-06 12:30 | -1.1028 | 0 | N/A | 0 | 0
2022-11-06 13:00 | -2.0315 | 0 | N/A | 0 | 0
2022-11-06 13:30 | -1.943 | 0 | N/A | 0 | 0
2022-11-06 14:00 | -2.2664 | 0 | N/A | 0 | 0
2022-11-06 14:30 | -1.8053 | 0 | N/A | 0 | 0
2022-11-06 15:00 | -1.0956 | 0 | N/A | 0 | 0
2022-11-06 15:30 | -1.2483 | 0 | N/A | 0 | 0
2022-11-06 16:00 | -0.86018 | 0 | N/A | 0 | 0
2022-11-06 16:30 | -1.0342 | 0 | N/A | 0 | 0
2022-11-06 17:00 | 0.90144 | 0 | N/A | 0 | 0
2022-11-06 17:30 | 1.7393 | 0 | N/A | 0 | 0
2022-11-06 18:00 | 3.0533 | 0 | N/A | 0 | 0
2022-11-06 18:30 | 4.2256 | 0 | N/A | 0 | 0
2022-11-06 19:00 | 4.8126 | 0 | N/A | 0 | 0
2022-11-06 19:30 | 5.0401 | 0 | N/A | 0 | 0
2022-11-06 20:00 | 4.9477 | 0 | N/A | 0 | 0
2022-11-06 20:30 | 4.8483 | 0 | N/A | 0 | 0
2022-11-06 21:00 | 4.6939 | 0 | N/A | 0 | 0
2022-11-06 21:30 | 4.4906 | 0 | N/A | 0 | 0
2022-11-06 22:00 | 4.196 | 0 | N/A | 0 | 0
2022-11-06 22:30 | 4.3042 | 0 | N/A | 0 | 0
2022-11-06 23:00 | 4.2525 | 0 | N/A | 0 | 0
2022-11-06 23:30 | 4.0541 | 0 | N/A | 0 | 0
2022-11-07 | 4.0889 | 0 | N/A | 0 | 0
2022-11-07 00:30 | 4.3441 | 0 | N/A | 0 | 0
2022-11-07 01:00 | 4.5851 | 0 | N/A | 0 | 0
2022-11-07 01:30 | 3.9913 | 0 | N/A | 0 | 0
2022-11-07 02:00 | 3.5691 | 0 | N/A | 0 | 0
2022-11-07 02:30 | 3.5108 | 0 | N/A | 0 | 0
2022-11-07 03:00 | 3.2098 | 0 | N/A | 0 | 0
2022-11-07 03:30 | 2.9744 | 0 | N/A | 0 | 0
2022-11-07 04:00 | 2.7492 | 0 | N/A | 0 | 0
2022-11-07 04:30 | 2.7023 | 0 | N/A | 0 | 0
2022-11-07 05:00 | 2.6738 | 0 | N/A | 0 | 0
2022-11-07 05:30 | 2.8724 | 0 | N/A | 0 | 0
2022-11-07 06:00 | 3.2083 | 0 | N/A | 0 | 0
2022-11-07 06:30 | 3.6228 | 0 | N/A | 0 | 0
2022-11-07 07:00 | 3.948 | 0 | N/A | 0 | 0
2022-11-07 07:30 | 4.6549 | 0 | N/A | 0 | 0
2022-11-07 08:00 | 4.4586 | 0 | N/A | 0 | 0
2022-11-07 08:30 | 3.2427 | 0 | N/A | 0 | 0
2022-11-07 09:00 | 2.3046 | 0 | N/A | 0 | 0
2022-11-07 09:30 | 1.3315 | 0 | N/A | 0 | 0
2022-11-07 10:00 | 0.67702 | 0 | N/A | 0 | 0
2022-11-07 10:30 | -0.79784 | 0 | N/A | 0 | 0
2022-11-07 11:00 | -0.75603 | 0 | N/A | 0 | 0
2022-11-07 11:30 | -0.80416 | 0 | N/A | 0 | 0
2022-11-07 12:00 | 0.71557 | 0 | N/A | 0 | 0
2022-11-07 12:30 | -0.72396 | 0 | N/A | 0 | 0
2022-11-07 13:00 | -0.66804 | 0 | N/A | 0 | 0
2022-11-07 13:30 | -0.87026 | 0 | N/A | 0 | 0
2022-11-07 14:00 | -0.58565 | 0 | N/A | 0 | 0
2022-11-07 14:30 | -0.56699 | 0 | N/A | 0 | 0
2022-11-07 15:00 | -0.86953 | 0 | N/A | 0 | 0
2022-11-07 15:30 | 0.80687 | 0 | N/A | 0 | 0
2022-11-07 16:00 | 2.0802 | 0 | N/A | 0 | 0
2022-11-07 16:30 | 1.5154 | 0 | N/A | 0 | 0
2022-11-07 17:00 | 2.1721 | 0 | N/A | 0 | 0
2022-11-07 17:30 | 1.7503 | 0 | N/A | 0 | 0
2022-11-07 18:00 | 3.0821 | 0 | N/A | 0 | 0
2022-11-07 18:30 | 4.2827 | 0 | N/A | 0 | 0
2022-11-07 19:00 | 4.413 | 0 | N/A | 0 | 0
2022-11-07 19:30 | 4.8638 | 0 | N/A | 0 | 0
2022-11-07 20:00 | 4.883 | 0 | N/A | 0 | 0
2022-11-07 20:30 | 4.885 | 0 | N/A | 0 | 0
2022-11-07 21:00 | 4.8095 | 0 | N/A | 0 | 0
2022-11-07 21:30 | 4.5751 | 0 | N/A | 0 | 0
2022-11-07 22:00 | 4.2431 | 0 | N/A | 0 | 0
2022-11-07 22:30 | 4.4195 | 0 | N/A | 0 | 0
2022-11-07 23:00 | 4.3607 | 0 | N/A | 0 | 0
2022-11-07 23:30 | 4.0039 | 0 | N/A | 0 | 0
2022-11-08 | 3.9751 | 0 | N/A | 0 | 0
2022-11-08 00:30 | 4.3425 | 0 | N/A | 0 | 0
2022-11-08 01:00 | 4.5462 | 0 | N/A | 0 | 0
2022-11-08 01:30 | 3.946 | 0 | N/A | 0 | 0
2022-11-08 02:00 | 3.44 | 0 | N/A | 0 | 0
2022-11-08 02:30 | 3.3347 | 0 | N/A | 0 | 0
2022-11-08 03:00 | 3.0922 | 0 | N/A | 0 | 0
2022-11-08 03:30 | 2.8451 | 0 | N/A | 0 | 0
2022-11-08 04:00 | 2.707 | 0 | N/A | 0 | 0
2022-11-08 04:30 | 2.6394 | 0 | N/A | 0 | 0
2022-11-08 05:00 | 2.7053 | 0 | N/A | 0 | 0
2022-11-08 05:30 | 2.8659 | 0 | N/A | 0 | 0
2022-11-08 06:00 | 3.0998 | 0 | N/A | 0 | 0
2022-11-08 06:30 | 3.7001 | 0 | N/A | 0 | 0
2022-11-08 07:00 | 4.3106 | 0 | N/A | 0 | 0
2022-11-08 07:30 | 4.8343 | 0 | N/A | 0 | 0
2022-11-08 08:00 | 4.475 | 0 | N/A | 0 | 0
2022-11-08 08:30 | 3.2106 | 0 | N/A | 0 | 0
2022-11-08 09:00 | 2.2024 | 0 | N/A | 0 | 0
2022-11-08 09:30 | 1.1971 | 0 | N/A | 0 | 0
2022-11-08 10:00 | 0.73214 | 0 | N/A | 0 | 0
2022-11-08 10:30 | -0.75802 | 0 | N/A | 0 | 0
2022-11-08 11:00 | -1.1141 | 0 | N/A | 0 | 0
2022-11-08 11:30 | -1.4256 | 0 | N/A | 0 | 0
2022-11-08 12:00 | -1.6703 | 0 | N/A | 0 | 0
2022-11-08 12:30 | -1.9637 | 0 | N/A | 0 | 0
2022-11-08 13:00 | -1.7451 | 0 | N/A | 0 | 0
2022-11-08 13:30 | -1.7406 | 0 | N/A | 0 | 0
2022-11-08 14:00 | -1.7713 | 0 | N/A | 0 | 0
2022-11-08 14:30 | -1.6224 | 0 | N/A | 0 | 0
2022-11-08 15:00 | -1.2287 | 0 | N/A | 0 | 0
2022-11-08 15:30 | -1.2507 | 0 | N/A | 0 | 0
2022-11-08 16:00 | -0.62266 | 0 | N/A | 0 | 0
2022-11-08 16:30 | 1.1801 | 0 | N/A | 0 | 0
2022-11-08 17:00 | 1.2387 | 0 | N/A | 0 | 0
2022-11-08 17:30 | 1.7927 | 0 | N/A | 0 | 0
2022-11-08 18:00 | 2.6385 | 0 | N/A | 0 | 0
2022-11-08 18:30 | 3.8444 | 0 | N/A | 0 | 0
2022-11-08 19:00 | 4.2659 | 0 | N/A | 0 | 0
2022-11-08 19:30 | 4.7666 | 0 | N/A | 0 | 0
2022-11-08 20:00 | 4.8658 | 0 | N/A | 0 | 0
2022-11-08 20:30 | 4.9702 | 0 | N/A | 0 | 0
2022-11-08 21:00 | 4.9017 | 0 | N/A | 0 | 0
2022-11-08 21:30 | 4.6935 | 0 | N/A | 0 | 0
2022-11-08 22:00 | 4.3544 | 0 | N/A | 0 | 0
2022-11-08 22:30 | 4.335 | 0 | N/A | 0 | 0
2022-11-08 23:00 | 4.3634 | 0 | N/A | 0 | 0
2022-11-08 23:30 | 3.9754 | 0 | N/A | 0 | 0
2022-11-09 | 3.9775 | 0 | N/A | 0 | 0
2022-11-09 00:30 | 4.3503 | 0 | N/A | 0 | 0
2022-11-09 01:00 | 4.4354 | 0 | N/A | 0 | 0
2022-11-09 01:30 | 3.7493 | 0 | N/A | 0 | 0
2022-11-09 02:00 | 3.2626 | 0 | N/A | 0 | 0
2022-11-09 02:30 | 3.2048 | 0 | N/A | 0 | 0
2022-11-09 03:00 | 2.9411 | 0 | N/A | 0 | 0
2022-11-09 03:30 | 2.7053 | 0 | N/A | 0 | 0
2022-11-09 04:00 | 2.6256 | 0 | N/A | 0 | 0
2022-11-09 04:30 | 2.6394 | 0 | N/A | 0 | 0
2022-11-09 05:00 | 2.6253 | 0 | N/A | 0 | 0
2022-11-09 05:30 | 2.8263 | 0 | N/A | 0 | 0
2022-11-09 06:00 | 3.0712 | 0 | N/A | 0 | 0
2022-11-09 06:30 | 3.4948 | 0 | N/A | 0 | 0
2022-11-09 07:00 | 3.8452 | 0 | N/A | 0 | 0
2022-11-09 07:30 | 4.1085 | 0 | N/A | 0 | 0
2022-11-09 08:00 | 3.7404 | 0 | N/A | 0 | 0
2022-11-09 08:30 | 2.6483 | 0 | N/A | 0 | 0
2022-11-09 09:00 | 1.7384 | 0 | N/A | 0 | 0
2022-11-09 09:30 | 0.96336 | 0 | N/A | 0 | 0
2022-11-09 10:00 | -0.54103 | 0 | N/A | 0 | 0
2022-11-09 10:30 | -0.85654 | 0 | N/A | 0 | 0
2022-11-09 11:00 | -1.2987 | 0 | N/A | 0 | 0
2022-11-09 11:30 | -1.6925 | 0 | N/A | 0 | 0
2022-11-09 12:00 | -1.7567 | 0 | N/A | 0 | 0
2022-11-09 12:30 | -2.0981 | 0 | N/A | 0 | 0
2022-11-09 13:00 | -1.7077 | 0 | N/A | 0 | 0
2022-11-09 13:30 | -1.9559 | 0 | N/A | 0 | 0
2022-11-09 14:00 | -2.1312 | 0 | N/A | 0 | 0
2022-11-09 14:30 | -1.769 | 0 | N/A | 0 | 0
2022-11-09 15:00 | -1.4101 | 0 | N/A | 0 | 0
2022-11-09 15:30 | -1.3585 | 0 | N/A | 0 | 0
2022-11-09 16:00 | -1.0957 | 0 | N/A | 0 | 0
2022-11-09 16:30 | -0.76543 | 0 | N/A | 0 | 0
2022-11-09 17:00 | 0.77265 | 0 | N/A | 0 | 0
2022-11-09 17:30 | 1.695 | 0 | N/A | 0 | 0
2022-11-09 18:00 | 2.7075 | 0 | N/A | 0 | 0
2022-11-09 18:30 | 3.7081 | 0 | N/A | 0 | 0
2022-11-09 19:00 | 4.4985 | 0 | N/A | 0 | 0
2022-11-09 19:30 | 4.867 | 0 | N/A | 0 | 0
2022-11-09 20:00 | 4.9568 | 0 | N/A | 0 | 0
2022-11-09 20:30 | 5.0481 | 0 | N/A | 0 | 0
2022-11-09 21:00 | 4.9211 | 0 | N/A | 0 | 0
2022-11-09 21:30 | 4.6566 | 0 | N/A | 0 | 0
2022-11-09 22:00 | 4.2622 | 0 | N/A | 0 | 0
2022-11-09 22:30 | 4.4442 | 0 | N/A | 0 | 0
2022-11-09 23:00 | 4.3123 | 0 | N/A | 0 | 0
2022-11-09 23:30 | 3.9748 | 0 | N/A | 0 | 0
2022-11-10 | 3.9332 | 0 | N/A | 0 | 0
2022-11-10 00:30 | 4.2639 | 0 | N/A | 0 | 0
2022-11-10 01:00 | 4.4029 | 0 | N/A | 0 | 0
2022-11-10 01:30 | 3.7252 | 0 | N/A | 0 | 0
2022-11-10 02:00 | 3.2243 | 0 | N/A | 0 | 0
2022-11-10 02:30 | 3.1927 | 0 | N/A | 0 | 0
2022-11-10 03:00 | 2.9458 | 0 | N/A | 0 | 0
2022-11-10 03:30 | 2.6522 | 0 | N/A | 0 | 0
2022-11-10 04:00 | 2.6024 | 0 | N/A | 0 | 0
2022-11-10 04:30 | 2.5663 | 0 | N/A | 0 | 0
2022-11-10 05:00 | 2.6188 | 0 | N/A | 0 | 0
2022-11-10 05:30 | 2.7713 | 0 | N/A | 0 | 0
2022-11-10 06:00 | 3.0054 | 0 | N/A | 0 | 0
2022-11-10 06:30 | 3.3005 | 0 | N/A | 0 | 0
2022-11-10 07:00 | 3.4525 | 0 | N/A | 0 | 0
2022-11-10 07:30 | 3.7786 | 0 | N/A | 0 | 0
2022-11-10 08:00 | 3.6075 | 0 | N/A | 0 | 0
2022-11-10 08:30 | 2.1219 | 0 | N/A | 0 | 0
2022-11-10 09:00 | 1.5146 | 0 | N/A | 0 | 0
2022-11-10 09:30 | 1.4602 | 0 | N/A | 0 | 0
2022-11-10 10:00 | 1.5919 | 0 | N/A | 0 | 0
2022-11-10 10:30 | 1.445 | 0 | N/A | 0 | 0
2022-11-10 11:00 | 1.7487 | 0 | N/A | 0 | 0
2022-11-10 11:30 | 1.7931 | 0 | N/A | 0 | 0
2022-11-10 12:00 | 1.7091 | 0 | N/A | 0 | 0
2022-11-10 12:30 | 2.2204 | 0 | N/A | 0 | 0
2022-11-10 13:00 | 2.9305 | 0 | N/A | 0 | 0
2022-11-10 13:30 | 3.2271 | 0 | N/A | 0 | 0
2022-11-10 14:00 | 3.0169 | 0 | N/A | 0 | 0
2022-11-10 14:30 | 3.1922 | 0 | N/A | 0 | 0
2022-11-10 15:00 | 3.4831 | 0 | N/A | 0 | 0
2022-11-10 15:30 | 4.1786 | 0 | N/A | 0 | 0
2022-11-10 16:00 | 3.8128 | 0 | N/A | 0 | 0
2022-11-10 16:30 | 3.074 | 0 | N/A | 0 | 0
2022-11-10 17:00 | 2.3505 | 0 | N/A | 0 | 0
2022-11-10 17:30 | 2.7955 | 0 | N/A | 0 | 0
2022-11-10 18:00 | 2.7158 | 0 | N/A | 0 | 0
2022-11-10 18:30 | 3.0225 | 0 | N/A | 0 | 0
2022-11-10 19:00 | 4.5498 | 0 | N/A | 0 | 0
2022-11-10 19:30 | 5.0383 | 0 | N/A | 0 | 0
2022-11-10 20:00 | 5.0364 | 0 | N/A | 0 | 0
2022-11-10 20:30 | 5.0476 | 0 | N/A | 0 | 0
2022-11-10 21:00 | 4.9294 | 0 | N/A | 0 | 0
2022-11-10 21:30 | 4.584 | 0 | N/A | 0 | 0
2022-11-10 22:00 | 4.2201 | 0 | N/A | 0 | 0
2022-11-10 22:30 | 4.404 | 0 | N/A | 0 | 0
2022-11-10 23:00 | 4.4482 | 0 | N/A | 0 | 0
2022-11-10 23:30 | 4.0657 | 0 | N/A | 0 | 0
2022-11-11 | 4.0218 | 0 | N/A | 0 | 0
2022-11-11 00:30 | 4.3144 | 0 | N/A | 0 | 0
2022-11-11 01:00 | 4.5491 | 0 | N/A | 0 | 0
2022-11-11 01:30 | 3.9434 | 0 | N/A | 0 | 0
2022-11-11 02:00 | 3.3326 | 0 | N/A | 0 | 0
2022-11-11 02:30 | 2.5887 | 0 | N/A | 0 | 0
2022-11-11 03:00 | 1.9234 | 0 | N/A | 0 | 0
2022-11-11 03:30 | 1.92 | 0 | N/A | 0 | 0
2022-11-11 04:00 | 1.8813 | 0 | N/A | 0 | 0
2022-11-11 04:30 | 1.8701 | 0 | N/A | 0 | 0
2022-11-11 05:00 | 1.8645 | 0 | N/A | 0 | 0
2022-11-11 05:30 | 1.9505 | 0 | N/A | 0 | 0
2022-11-11 06:00 | 2.1104 | 0 | N/A | 0 | 0
2022-11-11 06:30 | 2.2754 | 0 | N/A | 0 | 0
2022-11-11 07:00 | 2.4008 | 0 | N/A | 0 | 0
2022-11-11 07:30 | 2.7664 | 0 | N/A | 0 | 0
2022-11-11 08:00 | 4.9958 | 0 | N/A | 0 | 0
2022-11-11 08:30 | 4.3527 | 0 | N/A | 0 | 0
2022-11-11 09:00 | 4.2143 | 0 | N/A | 0 | 0
2022-11-11 09:30 | 4.3139 | 0 | N/A | 0 | 0
2022-11-11 10:00 | 4.2832 | 0 | N/A | 0 | 0
2022-11-11 10:30 | 4.066 | 0 | N/A | 0 | 0
2022-11-11 11:00 | 3.579 | 0 | N/A | 0 | 0
2022-11-11 11:30 | 3.7116 | 0 | N/A | 0 | 0
2022-11-11 12:00 | 2.7059 | 0 | N/A | 0 | 0
2022-11-11 12:30 | 2.8595 | 0 | N/A | 0 | 0
2022-11-11 13:00 | 1.9333 | 0 | N/A | 0 | 0
2022-11-11 13:30 | 1.8495 | 0 | N/A | 0 | 0
2022-11-11 14:00 | 1.3224 | 0 | N/A | 0 | 0
2022-11-11 14:30 | 0.82471 | 0 | N/A | 0 | 0
2022-11-11 15:00 | 1.5879 | 0 | N/A | 0 | 0
2022-11-11 15:30 | 2.0194 | 0 | N/A | 0 | 0
2022-11-11 16:00 | 1.4128 | 0 | N/A | 0 | 0
2022-11-11 16:30 | 1.7402 | 0 | N/A | 0 | 0
2022-11-11 17:00 | 2.047 | 0 | N/A | 0 | 0
2022-11-11 17:30 | 2.58 | 0 | N/A | 0 | 0
2022-11-11 18:00 | 3.4902 | 0 | N/A | 0 | 0
2022-11-11 18:30 | 3.9714 | 0 | N/A | 0 | 0
2022-11-11 19:00 | 4.4859 | 0 | N/A | 0 | 0
2022-11-11 19:30 | 4.6781 | 0 | N/A | 0 | 0
2022-11-11 20:00 | 4.8582 | 0 | N/A | 0 | 0
2022-11-11 20:30 | 4.859 | 0 | N/A | 0 | 0
2022-11-11 21:00 | 4.7821 | 0 | N/A | 0 | 0
2022-11-11 21:30 | 4.5686 | 0 | N/A | 0 | 0
2022-11-11 22:00 | 4.3055 | 0 | N/A | 0 | 0
2022-11-11 22:30 | 4.4926 | 0 | N/A | 0 | 0
2022-11-11 23:00 | 4.5467 | 0 | N/A | 0 | 0
2022-11-11 23:30 | 4.2763 | 0 | N/A | 0 | 0
2022-11-12 | 4.3479 | 0 | N/A | 0 | 0
2022-11-12 00:30 | 4.604 | 0 | N/A | 0 | 0
2022-11-12 01:00 | 4.9191 | 0 | N/A | 0 | 0
2022-11-12 01:30 | 4.2071 | 0 | N/A | 0 | 0
2022-11-12 02:00 | 3.6544 | 0 | N/A | 0 | 0
2022-11-12 02:30 | 3.5196 | 0 | N/A | 0 | 0
2022-11-12 03:00 | 3.2827 | 0 | N/A | 0 | 0
2022-11-12 03:30 | 3.0372 | 0 | N/A | 0 | 0
2022-11-12 04:00 | 2.8505 | 0 | N/A | 0 | 0
2022-11-12 04:30 | 2.7808 | 0 | N/A | 0 | 0
2022-11-12 05:00 | 2.7246 | 0 | N/A | 0 | 0
2022-11-12 05:30 | 2.7722 | 0 | N/A | 0 | 0
2022-11-12 06:00 | 2.9006 | 0 | N/A | 0 | 0
2022-11-12 06:30 | 3.059 | 0 | N/A | 0 | 0
2022-11-12 07:00 | 3.1768 | 0 | N/A | 0 | 0
2022-11-12 07:30 | 3.6288 | 0 | N/A | 0 | 0
2022-11-12 08:00 | 3.4887 | 0 | N/A | 0 | 0
2022-11-12 08:30 | 3.3771 | 0 | N/A | 0 | 0
2022-11-12 09:00 | 3.1114 | 0 | N/A | 0 | 0
2022-11-12 09:30 | 3.0572 | 0 | N/A | 0 | 0
2022-11-12 10:00 | 2.8789 | 0 | N/A | 0 | 0
2022-11-12 10:30 | 2.0498 | 0 | N/A | 0 | 0
2022-11-12 11:00 | 2.169 | 0 | N/A | 0 | 0
2022-11-12 11:30 | 1.2261 | 0 | N/A | 0 | 0
2022-11-12 12:00 | -0.85871 | 0 | N/A | 0 | 0
2022-11-12 12:30 | -1.1132 | 0 | N/A | 0 | 0
2022-11-12 13:00 | -1.2705 | 0 | N/A | 0 | 0
2022-11-12 13:30 | -1.1725 | 0 | N/A | 0 | 0
2022-11-12 14:00 | -1.653 | 0 | N/A | 0 | 0
2022-11-12 14:30 | -1.35 | 0 | N/A | 0 | 0
2022-11-12 15:00 | -1.1131 | 0 | N/A | 0 | 0
2022-11-12 15:30 | 1.0104 | 0 | N/A | 0 | 0
2022-11-12 16:00 | 1.3452 | 0 | N/A | 0 | 0
2022-11-12 16:30 | 2.1229 | 0 | N/A | 0 | 0
2022-11-12 17:00 | 2.1929 | 0 | N/A | 0 | 0
2022-11-12 17:30 | 3.0603 | 0 | N/A | 0 | 0
2022-11-12 18:00 | 3.8866 | 0 | N/A | 0 | 0
2022-11-12 18:30 | 4.6575 | 0 | N/A | 0 | 0
2022-11-12 19:00 | 4.9542 | 0 | N/A | 0 | 0
2022-11-12 19:30 | 4.9493 | 0 | N/A | 0 | 0
2022-11-12 20:00 | 4.9289 | 0 | N/A | 0 | 0
2022-11-12 20:30 | 4.9343 | 0 | N/A | 0 | 0
2022-11-12 21:00 | 4.8732 | 0 | N/A | 0 | 0
2022-11-12 21:30 | 4.7054 | 0 | N/A | 0 | 0
2022-11-12 22:00 | 4.5212 | 0 | N/A | 0 | 0
2022-11-12 22:30 | 4.6976 | 0 | N/A | 0 | 0
2022-11-12 23:00 | 4.6736 | 0 | N/A | 0 | 0
2022-11-12 23:30 | 4.308 | 0 | N/A | 0 | 0
2022-11-13 | 4.3407 | 0 | N/A | 0 | 0
2022-11-13 00:30 | 4.6303 | 0 | N/A | 0 | 0
2022-11-13 01:00 | 4.8944 | 0 | N/A | 0 | 0
2022-11-13 01:30 | 4.1725 | 0 | N/A | 0 | 0
2022-11-13 02:00 | 3.5786 | 0 | N/A | 0 | 0
2022-11-13 02:30 | 3.4583 | 0 | N/A | 0 | 0
2022-11-13 03:00 | 3.2776 | 0 | N/A | 0 | 0
2022-11-13 03:30 | 2.9935 | 0 | N/A | 0 | 0
2022-11-13 04:00 | 2.7838 | 0 | N/A | 0 | 0
2022-11-13 04:30 | 2.6994 | 0 | N/A | 0 | 0
2022-11-13 05:00 | 2.6143 | 0 | N/A | 0 | 0
2022-11-13 05:30 | 2.5665 | 0 | N/A | 0 | 0
2022-11-13 06:00 | 2.7186 | 0 | N/A | 0 | 0
2022-11-13 06:30 | 2.8394 | 0 | N/A | 0 | 0
2022-11-13 07:00 | 2.8557 | 0 | N/A | 0 | 0
2022-11-13 07:30 | 2.5657 | 0 | N/A | 0 | 0
2022-11-13 08:00 | 2.6552 | 0 | N/A | 0 | 0
2022-11-13 08:30 | 2.0747 | 0 | N/A | 0 | 0
2022-11-13 09:00 | 1.6826 | 0 | N/A | 0 | 0
2022-11-13 09:30 | 2.1889 | 0 | N/A | 0 | 0
2022-11-13 10:00 | 2.3477 | 0 | N/A | 0 | 0
2022-11-13 10:30 | 3.6288 | 0 | N/A | 0 | 0
2022-11-13 11:00 | 1.8798 | 0 | N/A | 0 | 0
2022-11-13 11:30 | 0.96451 | 0 | N/A | 0 | 0
2022-11-13 12:00 | 0.98969 | 0 | N/A | 0 | 0
2022-11-13 12:30 | 0.82011 | 0 | N/A | 0 | 0
2022-11-13 13:00 | 0.85142 | 0 | N/A | 0 | 0
2022-11-13 13:30 | 1.0672 | 0 | N/A | 0 | 0
2022-11-13 14:00 | 1.4795 | 0 | N/A | 0 | 0
2022-11-13 14:30 | 1.3905 | 0 | N/A | 0 | 0
2022-11-13 15:00 | 0.86649 | 0 | N/A | 0 | 0
2022-11-13 15:30 | -0.78098 | 0 | N/A | 0 | 0
2022-11-13 16:00 | 0.8111 | 0 | N/A | 0 | 0
2022-11-13 16:30 | 1.6355 | 0 | N/A | 0 | 0
2022-11-13 17:00 | 1.8383 | 0 | N/A | 0 | 0
2022-11-13 17:30 | 2.9283 | 0 | N/A | 0 | 0
2022-11-13 18:00 | 3.1823 | 0 | N/A | 0 | 0
2022-11-13 18:30 | 4.1611 | 0 | N/A | 0 | 0
2022-11-13 19:00 | 4.6872 | 0 | N/A | 0 | 0
2022-11-13 19:30 | 4.8676 | 0 | N/A | 0 | 0
2022-11-13 20:00 | 4.8663 | 0 | N/A | 0 | 0
2022-11-13 20:30 | 4.8414 | 0 | N/A | 0 | 0
2022-11-13 21:00 | 4.6818 | 0 | N/A | 0 | 0
2022-11-13 21:30 | 4.5201 | 0 | N/A | 0 | 0
2022-11-13 22:00 | 4.1575 | 0 | N/A | 0 | 0
2022-11-13 22:30 | 4.2417 | 0 | N/A | 0 | 0
2022-11-13 23:00 | 4.4072 | 0 | N/A | 0 | 0
2022-11-13 23:30 | 4.0478 | 0 | N/A | 0 | 0
2022-11-14 | 4.1094 | 0 | N/A | 0 | 0
2022-11-14 00:30 | 4.4827 | 0 | N/A | 0 | 0
2022-11-14 01:00 | 4.9065 | 0 | N/A | 0 | 0
2022-11-14 01:30 | 4.2583 | 0 | N/A | 0 | 0
2022-11-14 02:00 | 3.5932 | 0 | N/A | 0 | 0
2022-11-14 02:30 | 3.5694 | 0 | N/A | 0 | 0
2022-11-14 03:00 | 3.4219 | 0 | N/A | 0 | 0
2022-11-14 03:30 | 3.1941 | 0 | N/A | 0 | 0
2022-11-14 04:00 | 3.024 | 0 | N/A | 0 | 0
2022-11-14 04:30 | 2.9639 | 0 | N/A | 0 | 0
2022-11-14 05:00 | 2.9362 | 0 | N/A | 0 | 0
2022-11-14 05:30 | 3.1341 | 0 | N/A | 0 | 0
2022-11-14 06:00 | 3.5266 | 0 | N/A | 0 | 0
2022-11-14 06:30 | 4.0162 | 0 | N/A | 0 | 0
2022-11-14 07:00 | 4.9349 | 0 | N/A | 0 | 0
2022-11-14 07:30 | 5.354 | 0 | N/A | 0 | 0
2022-11-14 08:00 | 5.7131 | 0 | N/A | 0 | 0
2022-11-14 08:30 | 5.0214 | 0 | N/A | 0 | 0
2022-11-14 09:00 | 4.712 | 0 | N/A | 0 | 0
2022-11-14 09:30 | 4.4854 | 0 | N/A | 0 | 0
2022-11-14 10:00 | 4.1485 | 0 | N/A | 0 | 0
2022-11-14 10:30 | 3.8724 | 0 | N/A | 0 | 0
2022-11-14 11:00 | 4.5795 | 0 | N/A | 0 | 0
2022-11-14 11:30 | 4.1535 | 0 | N/A | 0 | 0
2022-11-14 12:00 | 3.8868 | 0 | N/A | 0 | 0
2022-11-14 12:30 | 3.8043 | 0 | N/A | 0 | 0
2022-11-14 13:00 | 3.7976 | 0 | N/A | 0 | 0
2022-11-14 13:30 | 4.0773 | 0 | N/A | 0 | 0
2022-11-14 14:00 | 4.1124 | 0 | N/A | 0 | 0
2022-11-14 14:30 | 2.7197 | 0 | N/A | 0 | 0
2022-11-14 15:00 | 3.5103 | 0 | N/A | 0 | 0
2022-11-14 15:30 | 3.4764 | 0 | N/A | 0 | 0
2022-11-14 16:00 | 2.9504 | 0 | N/A | 0 | 0
2022-11-14 16:30 | 3.9895 | 0 | N/A | 0 | 0
2022-11-14 17:00 | 3.1994 | 0 | N/A | 0 | 0
2022-11-14 17:30 | 2.9058 | 0 | N/A | 0 | 0
2022-11-14 18:00 | 3.8476 | 0 | N/A | 0 | 0
2022-11-14 18:30 | 5.8495 | 0 | N/A | 0 | 0
2022-11-14 19:00 | 6.835 | 0 | N/A | 0 | 0
2022-11-14 19:30 | 6.9744 | 0 | N/A | 0 | 0
2022-11-14 20:00 | 6.9895 | 0 | N/A | 0 | 0
2022-11-14 20:30 | 7.138 | 0 | N/A | 0 | 0
2022-11-14 21:00 | 7.175 | 0 | N/A | 0 | 0
2022-11-14 21:30 | 6.8593 | 0 | N/A | 0 | 0
2022-11-14 22:00 | 6.2749 | 0 | N/A | 0 | 0
2022-11-14 22:30 | 6.2106 | 0 | N/A | 0 | 0
2022-11-14 23:00 | 5.9989 | 0 | N/A | 0 | 0
2022-11-14 23:30 | 5.6333 | 0 | N/A | 0 | 0
2022-11-15 | 5.4627 | 0 | N/A | 0 | 0
2022-11-15 00:30 | 5.7157 | 0 | N/A | 0 | 0
2022-11-15 01:00 | 6.0428 | 0 | N/A | 0 | 0
2022-11-15 01:30 | 5.3287 | 0 | N/A | 0 | 0
2022-11-15 02:00 | 4.7606 | 0 | N/A | 0 | 0
2022-11-15 02:30 | 4.6116 | 0 | N/A | 0 | 0
2022-11-15 03:00 | 4.3429 | 0 | N/A | 0 | 0
2022-11-15 03:30 | 3.9919 | 0 | N/A | 0 | 0
2022-11-15 04:00 | 3.8845 | 0 | N/A | 0 | 0
2022-11-15 04:30 | 3.817 | 0 | N/A | 0 | 0
2022-11-15 05:00 | 3.8857 | 0 | N/A | 0 | 0
2022-11-15 05:30 | 4.1013 | 0 | N/A | 0 | 0
2022-11-15 06:00 | 4.6055 | 0 | N/A | 0 | 0
2022-11-15 06:30 | 5.4828 | 0 | N/A | 0 | 0
2022-11-15 07:00 | 5.8982 | 0 | N/A | 0 | 0
2022-11-15 07:30 | 6.9223 | 0 | N/A | 0 | 0
2022-11-15 08:00 | 7.3112 | 0 | N/A | 0 | 0
2022-11-15 08:30 | 6.1185 | 0 | N/A | 0 | 0
2022-11-15 09:00 | 4.7963 | 0 | N/A | 0 | 0
2022-11-15 09:30 | 4.2464 | 0 | N/A | 0 | 0
2022-11-15 10:00 | 4.4483 | 0 | N/A | 0 | 0
2022-11-15 10:30 | 2.8916 | 0 | N/A | 0 | 0
2022-11-15 11:00 | 3.3967 | 0 | N/A | 0 | 0
2022-11-15 11:30 | 2.3027 | 0 | N/A | 0 | 0
2022-11-15 12:00 | 2.02 | 0 | N/A | 0 | 0
2022-11-15 12:30 | 2.6959 | 0 | N/A | 0 | 0
2022-11-15 13:00 | 1.5026 | 0 | N/A | 0 | 0
2022-11-15 13:30 | 2.3355 | 0 | N/A | 0 | 0
2022-11-15 14:00 | 1.5325 | 0 | N/A | 0 | 0
2022-11-15 14:30 | 2.8993 | 0 | N/A | 0 | 0
2022-11-15 15:00 | 2.5831 | 0 | N/A | 0 | 0
2022-11-15 15:30 | 2.0357 | 0 | N/A | 0 | 0
2022-11-15 16:00 | 1.3544 | 0 | N/A | 0 | 0
2022-11-15 16:30 | 2.5857 | 0 | N/A | 0 | 0
2022-11-15 17:00 | 1.8992 | 0 | N/A | 0 | 0
2022-11-15 17:30 | 3.9015 | 0 | N/A | 0 | 0
2022-11-15 18:00 | 5.9755 | 0 | N/A | 0 | 0
2022-11-15 18:30 | 6.2894 | 0 | N/A | 0 | 0
2022-11-15 19:00 | 7.4829 | 0 | N/A | 0 | 0
2022-11-15 19:30 | 7.4752 | 0 | N/A | 0 | 0
2022-11-15 20:00 | 7.6284 | 0 | N/A | 0 | 0
2022-11-15 20:30 | 7.8668 | 0 | N/A | 0 | 0
2022-11-15 21:00 | 7.8537 | 0 | N/A | 0 | 0
2022-11-15 21:30 | 7.4047 | 0 | N/A | 0 | 0
2022-11-15 22:00 | 6.877 | 0 | N/A | 0 | 0
2022-11-15 22:30 | 6.7101 | 0 | N/A | 0 | 0
2022-11-15 23:00 | 6.5007 | 0 | N/A | 0 | 0
2022-11-15 23:30 | 6.0266 | 0 | N/A | 0 | 0
2022-11-16 | 5.8171 | 0 | N/A | 0 | 0
2022-11-18 00:30 | 5.5589 | 0 | N/A | 0 | 0
2022-11-18 01:00 | 5.8322 | 0 | N/A | 0 | 0
2022-11-18 01:30 | 5.1525 | 0 | N/A | 0 | 0
2022-11-18 02:00 | 4.6674 | 0 | N/A | 0 | 0
2022-11-18 02:30 | 4.4679 | 0 | N/A | 0 | 0
2022-11-18 03:00 | 4.2601 | 0 | N/A | 0 | 0
2022-11-18 03:30 | 3.9328 | 0 | N/A | 0 | 0
2022-11-18 04:00 | 3.8121 | 0 | N/A | 0 | 0
2022-11-18 04:30 | 3.6892 | 0 | N/A | 0 | 0
2022-11-18 05:00 | 3.7234 | 0 | N/A | 0 | 0
2022-11-18 05:30 | 4.0562 | 0 | N/A | 0 | 0
2022-11-18 06:00 | 4.4635 | 0 | N/A | 0 | 0
2022-11-18 06:30 | 5.2877 | 0 | N/A | 0 | 0
2022-11-18 07:00 | 5.9435 | 0 | N/A | 0 | 0
2022-11-18 07:30 | 6.2584 | 0 | N/A | 0 | 0
2022-11-18 08:00 | 5.7158 | 0 | N/A | 0 | 0
2022-11-18 08:30 | 4.1272 | 0 | N/A | 0 | 0
2022-11-18 09:00 | 2.7908 | 0 | N/A | 0 | 0
2022-11-18 09:30 | 1.6384 | 0 | N/A | 0 | 0
2022-11-18 10:00 | 0.8174 | 0 | N/A | 0 | 0
2022-11-18 10:30 | -0.85136 | 0 | N/A | 0 | 0
2022-11-18 11:00 | -1.2956 | 0 | N/A | 0 | 0
2022-11-18 11:30 | -1.7828 | 0 | N/A | 0 | 0
2022-11-18 12:00 | -2.144 | 0 | N/A | 0 | 0
2022-11-18 12:30 | -2.3783 | 0 | N/A | 0 | 0
2022-11-18 13:00 | -2.5822 | 0 | N/A | 0 | 0
2022-11-18 13:30 | -2.6677 | 0 | N/A | 0 | 0
2022-11-18 14:00 | -2.6715 | 0 | N/A | 0 | 0
2022-11-18 14:30 | -2.6524 | 0 | N/A | 0 | 0
2022-11-18 15:00 | -2.4552 | 0 | N/A | 0 | 0
2022-11-18 15:30 | -2.4392 | 0 | N/A | 0 | 0
2022-11-18 16:00 | -2.1172 | 0 | N/A | 0 | 0
2022-11-18 16:30 | -1.3948 | 0 | N/A | 0 | 0
2022-11-18 17:00 | -1.212 | 0 | N/A | 0 | 0
2022-11-18 17:30 | 1.0026 | 0 | N/A | 0 | 0
2022-11-18 18:00 | 2.4077 | 0 | N/A | 0 | 0
2022-11-18 18:30 | 2.6753 | 0 | N/A | 0 | 0
2022-11-18 19:00 | 3.4736 | 0 | N/A | 0 | 0
2022-11-18 19:30 | 3.7739 | 0 | N/A | 0 | 0
2022-11-18 20:00 | 4.2807 | 0 | N/A | 0 | 0
2022-11-18 20:30 | 4.5437 | 0 | N/A | 0 | 0
2022-11-18 21:00 | 4.5918 | 0 | N/A | 0 | 0
2022-11-18 21:30 | 4.4859 | 0 | N/A | 0 | 0
2022-11-18 22:00 | 4.2429 | 0 | N/A | 0 | 0
2022-11-18 22:30 | 4.4478 | 0 | N/A | 0 | 0
2022-11-18 23:00 | 4.4699 | 0 | N/A | 0 | 0
2022-11-18 23:30 | 4.2248 | 0 | N/A | 0 | 0
2022-11-19 | 4.2582 | 0 | N/A | 0 | 0
2022-11-19 00:30 | 4.5018 | 0 | N/A | 0 | 0
2022-11-19 01:00 | 4.6982 | 0 | N/A | 0 | 0
2022-11-19 01:30 | 4.0068 | 0 | N/A | 0 | 0
2022-11-19 02:00 | 3.509 | 0 | N/A | 0 | 0
2022-11-19 02:30 | 3.4936 | 0 | N/A | 0 | 0
2022-11-19 03:00 | 3.2424 | 0 | N/A | 0 | 0
2022-11-19 03:30 | 2.9203 | 0 | N/A | 0 | 0
2022-11-19 04:00 | 2.7761 | 0 | N/A | 0 | 0
2022-11-19 04:30 | 2.7345 | 0 | N/A | 0 | 0
2022-11-19 05:00 | 2.6542 | 0 | N/A | 0 | 0
2022-11-19 05:30 | 2.6759 | 0 | N/A | 0 | 0
2022-11-19 06:00 | 2.7361 | 0 | N/A | 0 | 0
2022-11-19 06:30 | 2.9397 | 0 | N/A | 0 | 0
2022-11-19 07:00 | 3.0459 | 0 | N/A | 0 | 0
2022-11-19 07:30 | 2.6699 | 0 | N/A | 0 | 0
2022-11-19 08:00 | 3.3119 | 0 | N/A | 0 | 0
2022-11-19 08:30 | 3.3628 | 0 | N/A | 0 | 0
2022-11-19 09:00 | 2.7623 | 0 | N/A | 0 | 0
2022-11-19 09:30 | 3.3763 | 0 | N/A | 0 | 0
2022-11-19 10:00 | 3.6621 | 0 | N/A | 0 | 0
2022-11-19 10:30 | 4.1383 | 0 | N/A | 0 | 0
2022-11-19 11:00 | 4.1761 | 0 | N/A | 0 | 0
2022-11-19 11:30 | 4.07 | 0 | N/A | 0 | 0
2022-11-19 12:00 | 3.6283 | 0 | N/A | 0 | 0
2022-11-19 12:30 | 3.4933 | 0 | N/A | 0 | 0
2022-11-19 13:00 | 3.2186 | 0 | N/A | 0 | 0
2022-11-19 13:30 | 2.8022 | 0 | N/A | 0 | 0
2022-11-19 14:00 | 1.2642 | 0 | N/A | 0 | 0
2022-11-19 14:30 | 1.2274 | 0 | N/A | 0 | 0
2022-11-19 15:00 | 1.0947 | 0 | N/A | 0 | 0
2022-11-19 15:30 | -0.93941 | 0 | N/A | 0 | 0
2022-11-19 16:00 | 1.0989 | 0 | N/A | 0 | 0
2022-11-19 16:30 | 1.2063 | 0 | N/A | 0 | 0
2022-11-19 17:00 | 1.2726 | 0 | N/A | 0 | 0
2022-11-19 17:30 | 1.7577 | 0 | N/A | 0 | 0
2022-11-19 18:00 | 3.3405 | 0 | N/A | 0 | 0
2022-11-19 18:30 | 4.5511 | 0 | N/A | 0 | 0
2022-11-19 19:00 | 5.4346 | 0 | N/A | 0 | 0
2022-11-19 19:30 | 5.594 | 0 | N/A | 0 | 0
2022-11-19 20:00 | 5.4853 | 0 | N/A | 0 | 0
2022-11-19 20:30 | 5.209 | 0 | N/A | 0 | 0
2022-11-19 21:00 | 5.1095 | 0 | N/A | 0 | 0
2022-11-19 21:30 | 5.0024 | 0 | N/A | 0 | 0
2022-11-19 22:00 | 4.7186 | 0 | N/A | 0 | 0
2022-11-19 22:30 | 4.9246 | 0 | N/A | 0 | 0
2022-11-19 23:00 | 4.8395 | 0 | N/A | 0 | 0
2022-11-19 23:30 | 4.6572 | 0 | N/A | 0 | 0
2022-11-20 | 4.5771 | 0 | N/A | 0 | 0
2022-11-20 00:30 | 4.8709 | 0 | N/A | 0 | 0
2022-11-20 01:00 | 5.2113 | 0 | N/A | 0 | 0
2022-11-20 01:30 | 4.5535 | 0 | N/A | 0 | 0
2022-11-20 02:00 | 4.0424 | 0 | N/A | 0 | 0
2022-11-20 02:30 | 3.9154 | 0 | N/A | 0 | 0
2022-11-20 03:00 | 3.6837 | 0 | N/A | 0 | 0
2022-11-20 03:30 | 3.4062 | 0 | N/A | 0 | 0
2022-11-20 04:00 | 3.3317 | 0 | N/A | 0 | 0
2022-11-20 04:30 | 3.1872 | 0 | N/A | 0 | 0
2022-11-20 05:00 | 3.1875 | 0 | N/A | 0 | 0
2022-11-20 05:30 | 3.194 | 0 | N/A | 0 | 0
2022-11-20 06:00 | 3.3068 | 0 | N/A | 0 | 0
2022-11-20 06:30 | 3.5227 | 0 | N/A | 0 | 0
2022-11-20 07:00 | 3.6336 | 0 | N/A | 0 | 0
2022-11-20 07:30 | 3.669 | 0 | N/A | 0 | 0
2022-11-20 08:00 | 3.4193 | 0 | N/A | 0 | 0
2022-11-20 08:30 | 3.473 | 0 | N/A | 0 | 0
2022-11-20 09:00 | 3.0789 | 0 | N/A | 0 | 0
2022-11-20 09:30 | 2.9826 | 0 | N/A | 0 | 0
2022-11-20 10:00 | 2.8414 | 0 | N/A | 0 | 0
2022-11-20 10:30 | 2.1756 | 0 | N/A | 0 | 0
2022-11-20 11:00 | 2.3439 | 0 | N/A | 0 | 0
2022-11-20 11:30 | 1.3487 | 0 | N/A | 0 | 0
2022-11-20 12:00 | 0.97735 | 0 | N/A | 0 | 0
2022-11-20 12:30 | 1.1669 | 0 | N/A | 0 | 0
2022-11-20 13:00 | 1.2884 | 0 | N/A | 0 | 0
2022-11-20 13:30 | -0.84476 | 0 | N/A | 0 | 0
2022-11-20 14:00 | 1.5495 | 0 | N/A | 0 | 0
2022-11-20 14:30 | -1.5363 | 0 | N/A | 0 | 0
2022-11-20 15:00 | -0.87735 | 0 | N/A | 0 | 0
2022-11-20 15:30 | 0.9378 | 0 | N/A | 0 | 0
2022-11-20 16:00 | 1.6023 | 0 | N/A | 0 | 0
2022-11-20 16:30 | 1.9303 | 0 | N/A | 0 | 0
2022-11-20 17:00 | 4.1675 | 0 | N/A | 0 | 0
2022-11-20 17:30 | 2.947 | 0 | N/A | 0 | 0
2022-11-20 18:00 | 5.3228 | 0 | N/A | 0 | 0
2022-11-20 18:30 | 6.0726 | 0 | N/A | 0 | 0
2022-11-20 19:00 | 6.9362 | 0 | N/A | 0 | 0
2022-11-20 19:30 | 7.0051 | 0 | N/A | 0 | 0
2022-11-20 20:00 | 6.7742 | 0 | N/A | 0 | 0
2022-11-20 20:30 | 6.7855 | 0 | N/A | 0 | 0
2022-11-20 21:00 | 6.7387 | 0 | N/A | 0 | 0
2022-11-20 21:30 | 6.4988 | 0 | N/A | 0 | 0
2022-11-20 22:00 | 6.0674 | 0 | N/A | 0 | 0
2022-11-20 22:30 | 5.9874 | 0 | N/A | 0 | 0
2022-11-20 23:00 | 5.8482 | 0 | N/A | 0 | 0
2022-11-20 23:30 | 5.5159 | 0 | N/A | 0 | 0
2022-11-21 | 5.3859 | 0 | N/A | 0 | 0
2022-11-22 00:30 | 5.962 | 0 | N/A | 0 | 0
2022-11-22 01:00 | 6.2664 | 0 | N/A | 0 | 0
2022-11-22 01:30 | 5.6384 | 0 | N/A | 0 | 0
2022-11-22 02:00 | 5.0173 | 0 | N/A | 0 | 0
2022-11-22 02:30 | 5.0062 | 0 | N/A | 0 | 0
2022-11-22 03:00 | 4.7 | 0 | N/A | 0 | 0
2022-11-22 03:30 | 4.337 | 0 | N/A | 0 | 0
2022-11-22 04:00 | 4.09 | 0 | N/A | 0 | 0
2022-11-22 04:30 | 4.0731 | 0 | N/A | 0 | 0
2022-11-22 05:00 | 4.1805 | 0 | N/A | 0 | 0
2022-11-22 05:30 | 4.3584 | 0 | N/A | 0 | 0
2022-11-22 06:00 | 4.8514 | 0 | N/A | 0 | 0
2022-11-22 06:30 | 5.7599 | 0 | N/A | 0 | 0
2022-11-22 07:00 | 6.5283 | 0 | N/A | 0 | 0
2022-11-22 07:30 | 7.5927 | 0 | N/A | 0 | 0
2022-11-22 08:00 | 7.6032 | 0 | N/A | 0 | 0
2022-11-22 08:30 | 6.5185 | 0 | N/A | 0 | 0
2022-11-22 09:00 | 6.4942 | 0 | N/A | 0 | 0
2022-11-22 09:30 | 6.7014 | 0 | N/A | 0 | 0
2022-11-22 10:00 | 6.1999 | 0 | N/A | 0 | 0
2022-11-22 10:30 | 4.8918 | 0 | N/A | 0 | 0
2022-11-22 11:00 | 4.9602 | 0 | N/A | 0 | 0
2022-11-22 11:30 | 4.3015 | 0 | N/A | 0 | 0
2022-11-22 12:00 | 3.9758 | 0 | N/A | 0 | 0
2022-11-22 12:30 | 4.0416 | 0 | N/A | 0 | 0
2022-11-22 13:00 | 3.742 | 0 | N/A | 0 | 0
2022-11-22 13:30 | 2.3757 | 0 | N/A | 0 | 0
2022-11-22 14:00 | 1.37 | 0 | N/A | 0 | 0
2022-11-22 14:30 | 2.1662 | 0 | N/A | 0 | 0
2022-11-22 15:00 | 1.6713 | 0 | N/A | 0 | 0
2022-11-22 15:30 | 2.1049 | 0 | N/A | 0 | 0
2022-11-22 16:00 | 2.5949 | 0 | N/A | 0 | 0
2022-11-22 16:30 | 2.5842 | 0 | N/A | 0 | 0
2022-11-22 17:00 | 3.1797 | 0 | N/A | 0 | 0
2022-11-22 17:30 | 4.6739 | 0 | N/A | 0 | 0
2022-11-22 18:00 | 4.9782 | 0 | N/A | 0 | 0
2022-11-22 18:30 | 5.8228 | 0 | N/A | 0 | 0
2022-11-22 19:00 | 6.2012 | 0 | N/A | 0 | 0
2022-11-22 19:30 | 6.6346 | 0 | N/A | 0 | 0
2022-11-22 20:00 | 6.7293 | 0 | N/A | 0 | 0
2022-11-22 20:30 | 6.8275 | 0 | N/A | 0 | 0
2022-11-22 21:00 | 6.8552 | 0 | N/A | 0 | 0
2022-11-22 21:30 | 6.5115 | 0 | N/A | 0 | 0
2022-11-22 22:00 | 5.9697 | 0 | N/A | 0 | 0
2022-11-22 22:30 | 5.8686 | 0 | N/A | 0 | 0
2022-11-22 23:00 | 5.6187 | 0 | N/A | 0 | 0
2022-11-22 23:30 | 5.26 | 0 | N/A | 0 | 0
2022-11-23 | 5.1204 | 0 | N/A | 0 | 0
2022-11-25 00:30 | 5.0061 | 0 | N/A | 0 | 0
2022-11-25 01:00 | 5.2987 | 0 | N/A | 0 | 0
2022-11-25 01:30 | 4.5623 | 0 | N/A | 0 | 0
2022-11-25 02:00 | 4.0319 | 0 | N/A | 0 | 0
2022-11-25 02:30 | 3.9477 | 0 | N/A | 0 | 0
2022-11-25 03:00 | 3.743 | 0 | N/A | 0 | 0
2022-11-25 03:30 | 3.3949 | 0 | N/A | 0 | 0
2022-11-25 04:00 | 3.262 | 0 | N/A | 0 | 0
2022-11-25 04:30 | 3.2182 | 0 | N/A | 0 | 0
2022-11-25 05:00 | 3.26 | 0 | N/A | 0 | 0
2022-11-25 05:30 | 3.477 | 0 | N/A | 0 | 0
2022-11-25 06:00 | 3.9645 | 0 | N/A | 0 | 0
2022-11-25 06:30 | 4.8201 | 0 | N/A | 0 | 0
2022-11-25 07:00 | 5.353 | 0 | N/A | 0 | 0
2022-11-25 07:30 | 5.8351 | 0 | N/A | 0 | 0
2022-11-25 08:00 | 5.8016 | 0 | N/A | 0 | 0
2022-11-25 08:30 | 4.9603 | 0 | N/A | 0 | 0
2022-11-25 09:00 | 4.439 | 0 | N/A | 0 | 0
2022-11-25 09:30 | 3.4544 | 0 | N/A | 0 | 0
2022-11-25 10:00 | 1.7233 | 0 | N/A | 0 | 0
2022-11-25 10:30 | 0.6417 | 0 | N/A | 0 | 0
2022-11-25 11:00 | -0.859 | 0 | N/A | 0 | 0
2022-11-25 11:30 | -1.1245 | 0 | N/A | 0 | 0
2022-11-25 12:00 | -1.5506 | 0 | N/A | 0 | 0
2022-11-25 12:30 | -0.68212 | 0 | N/A | 0 | 0
2022-11-25 13:00 | 2.0932 | 0 | N/A | 0 | 0
2022-11-25 13:30 | 1.594 | 0 | N/A | 0 | 0
2022-11-25 14:00 | -1.0273 | 0 | N/A | 0 | 0
2022-11-25 14:30 | -1.9574 | 0 | N/A | 0 | 0
2022-11-25 15:00 | -1.8652 | 0 | N/A | 0 | 0
2022-11-25 15:30 | -1.692 | 0 | N/A | 0 | 0
2022-11-25 16:00 | -1.2841 | 0 | N/A | 0 | 0
2022-11-25 16:30 | -1.5151 | 0 | N/A | 0 | 0
2022-11-25 17:00 | -1.0654 | 0 | N/A | 0 | 0
2022-11-25 17:30 | 0.99108 | 0 | N/A | 0 | 0
2022-11-25 18:00 | 1.6626 | 0 | N/A | 0 | 0
2022-11-25 18:30 | 2.5322 | 0 | N/A | 0 | 0
2022-11-25 19:00 | 3.3407 | 0 | N/A | 0 | 0
2022-11-25 19:30 | 3.8547 | 0 | N/A | 0 | 0
2022-11-25 20:00 | 4.2167 | 0 | N/A | 0 | 0
2022-11-25 20:30 | 4.4054 | 0 | N/A | 0 | 0
2022-11-25 21:00 | 4.606 | 0 | N/A | 0 | 0
2022-11-25 21:30 | 4.5607 | 0 | N/A | 0 | 0
2022-11-25 22:00 | 4.3356 | 0 | N/A | 0 | 0
2022-11-25 22:30 | 4.5654 | 0 | N/A | 0 | 0
2022-11-25 23:00 | 4.6181 | 0 | N/A | 0 | 0
2022-11-25 23:30 | 4.2779 | 0 | N/A | 0 | 0
2022-11-26 | 4.3042 | 0 | N/A | 0 | 0
2022-11-26 00:30 | 4.6337 | 0 | N/A | 0 | 0
2022-11-26 01:00 | 4.8797 | 0 | N/A | 0 | 0
2022-11-26 01:30 | 4.2618 | 0 | N/A | 0 | 0
2022-11-26 02:00 | 3.6293 | 0 | N/A | 0 | 0
2022-11-26 02:30 | 3.5975 | 0 | N/A | 0 | 0
2022-11-26 03:00 | 3.3873 | 0 | N/A | 0 | 0
2022-11-26 03:30 | 3.092 | 0 | N/A | 0 | 0
2022-11-26 04:00 | 2.9335 | 0 | N/A | 0 | 0
2022-11-26 04:30 | 2.8792 | 0 | N/A | 0 | 0
2022-11-26 05:00 | 2.8443 | 0 | N/A | 0 | 0
2022-11-26 05:30 | 2.8987 | 0 | N/A | 0 | 0
2022-11-26 06:00 | 3.0204 | 0 | N/A | 0 | 0
2022-11-26 06:30 | 3.2156 | 0 | N/A | 0 | 0
2022-11-26 07:00 | 3.2234 | 0 | N/A | 0 | 0
2022-11-26 07:30 | 3.5635 | 0 | N/A | 0 | 0
2022-11-26 08:00 | 3.4836 | 0 | N/A | 0 | 0
2022-11-26 08:30 | 3.111 | 0 | N/A | 0 | 0
2022-11-26 09:00 | 1.9478 | 0 | N/A | 0 | 0
2022-11-26 09:30 | 2.873 | 0 | N/A | 0 | 0
2022-11-26 10:00 | 0.91404 | 0 | N/A | 0 | 0
2022-11-26 10:30 | -0.89468 | 0 | N/A | 0 | 0
2022-11-26 11:00 | -0.81934 | 0 | N/A | 0 | 0
2022-11-26 11:30 | 0.75667 | 0 | N/A | 0 | 0
2022-11-26 12:00 | -0.73479 | 0 | N/A | 0 | 0
2022-11-26 12:30 | -0.83864 | 0 | N/A | 0 | 0
2022-11-26 13:00 | -1.7844 | 0 | N/A | 0 | 0
2022-11-26 13:30 | -0.82439 | 0 | N/A | 0 | 0
2022-11-26 14:00 | -0.90907 | 0 | N/A | 0 | 0
2022-11-26 14:30 | -0.86683 | 0 | N/A | 0 | 0
2022-11-26 15:00 | 1.0009 | 0 | N/A | 0 | 0
2022-11-26 15:30 | 1.2867 | 0 | N/A | 0 | 0
2022-11-26 16:00 | 1.866 | 0 | N/A | 0 | 0
2022-11-26 16:30 | 2.5487 | 0 | N/A | 0 | 0
2022-11-26 17:00 | 2.5221 | 0 | N/A | 0 | 0
2022-11-26 17:30 | 4.4951 | 0 | N/A | 0 | 0
2022-11-26 18:00 | 4.9289 | 0 | N/A | 0 | 0
2022-11-26 18:30 | 4.715 | 0 | N/A | 0 | 0
2022-11-26 19:00 | 4.5235 | 0 | N/A | 0 | 0
2022-11-26 19:30 | 4.4131 | 0 | N/A | 0 | 0
2022-11-26 20:00 | 4.1319 | 0 | N/A | 0 | 0
2022-11-26 20:30 | 4.2552 | 0 | N/A | 0 | 0
2022-11-26 21:00 | 4.3524 | 0 | N/A | 0 | 0
2022-11-26 21:30 | 4.2516 | 0 | N/A | 0 | 0
2022-11-26 22:00 | 4.1236 | 0 | N/A | 0 | 0
2022-11-26 22:30 | 4.3775 | 0 | N/A | 0 | 0
2022-11-26 23:00 | 4.391 | 0 | N/A | 0 | 0
2022-11-26 23:30 | 4.248 | 0 | N/A | 0 | 0
2022-11-27 | 4.2461 | 0 | N/A | 0 | 0
2022-11-27 00:30 | 4.564 | 0 | N/A | 0 | 0
2022-11-27 01:00 | 4.8456 | 0 | N/A | 0 | 0
2022-11-27 01:30 | 4.1702 | 0 | N/A | 0 | 0
2022-11-27 02:00 | 3.6354 | 0 | N/A | 0 | 0
2022-11-27 02:30 | 3.5865 | 0 | N/A | 0 | 0
2022-11-27 03:00 | 3.2954 | 0 | N/A | 0 | 0
2022-11-27 03:30 | 2.9576 | 0 | N/A | 0 | 0
2022-11-27 04:00 | 2.8334 | 0 | N/A | 0 | 0
2022-11-27 04:30 | 2.7711 | 0 | N/A | 0 | 0
2022-11-27 05:00 | 2.7354 | 0 | N/A | 0 | 0
2022-11-27 05:30 | 2.7545 | 0 | N/A | 0 | 0
2022-11-27 06:00 | 2.7842 | 0 | N/A | 0 | 0
2022-11-27 06:30 | 2.8164 | 0 | N/A | 0 | 0
2022-11-27 07:00 | 2.8123 | 0 | N/A | 0 | 0
2022-11-27 07:30 | 2.96 | 0 | N/A | 0 | 0
2022-11-27 08:00 | 3.3019 | 0 | N/A | 0 | 0
2022-11-27 08:30 | 2.6661 | 0 | N/A | 0 | 0
2022-11-27 09:00 | 2.4497 | 0 | N/A | 0 | 0
2022-11-27 09:30 | 2.6132 | 0 | N/A | 0 | 0
2022-11-27 10:00 | 2.21 | 0 | N/A | 0 | 0
2022-11-27 10:30 | 2.0604 | 0 | N/A | 0 | 0
2022-11-27 11:00 | 2.653 | 0 | N/A | 0 | 0
2022-11-27 11:30 | 1.1369 | 0 | N/A | 0 | 0
2022-11-27 12:00 | 1.0392 | 0 | N/A | 0 | 0
2022-11-27 12:30 | 1.1115 | 0 | N/A | 0 | 0
2022-11-27 13:00 | 1.2014 | 0 | N/A | 0 | 0
2022-11-27 13:30 | -1.0157 | 0 | N/A | 0 | 0
2022-11-27 14:00 | -1.2347 | 0 | N/A | 0 | 0
2022-11-27 14:30 | 1.298 | 0 | N/A | 0 | 0
2022-11-27 15:00 | 1.0069 | 0 | N/A | 0 | 0
2022-11-27 15:30 | 1.0704 | 0 | N/A | 0 | 0
2022-11-27 16:00 | 2.053 | 0 | N/A | 0 | 0
2022-11-27 16:30 | 2.6513 | 0 | N/A | 0 | 0
2022-11-27 17:00 | 2.7047 | 0 | N/A | 0 | 0
2022-11-27 17:30 | 3.0263 | 0 | N/A | 0 | 0
2022-11-27 18:00 | 3.5004 | 0 | N/A | 0 | 0
2022-11-27 18:30 | 4.0309 | 0 | N/A | 0 | 0
2022-11-27 19:00 | 5.188 | 0 | N/A | 0 | 0
2022-11-27 19:30 | 5.1677 | 0 | N/A | 0 | 0
2022-11-27 20:00 | 5.5285 | 0 | N/A | 0 | 0
2022-11-27 20:30 | 5.6032 | 0 | N/A | 0 | 0
2022-11-27 21:00 | 5.7187 | 0 | N/A | 0 | 0
2022-11-27 21:30 | 5.6501 | 0 | N/A | 0 | 0
2022-11-27 22:00 | 5.3407 | 0 | N/A | 0 | 0
2022-11-27 22:30 | 5.2404 | 0 | N/A | 0 | 0
2022-11-27 23:00 | 5.1537 | 0 | N/A | 0 | 0
2022-11-27 23:30 | 4.7882 | 0 | N/A | 0 | 0
2022-11-28 | 4.8128 | 0 | N/A | 0 | 0
2022-11-28 00:30 | 4.9835 | 0 | N/A | 0 | 0
2022-11-28 01:00 | 5.2797 | 0 | N/A | 0 | 0
2022-11-28 01:30 | 4.8096 | 0 | N/A | 0 | 0
2022-11-28 02:00 | 4.3041 | 0 | N/A | 0 | 0
2022-11-28 02:30 | 4.2431 | 0 | N/A | 0 | 0
2022-11-28 03:00 | 3.9903 | 0 | N/A | 0 | 0
2022-11-28 03:30 | 3.65 | 0 | N/A | 0 | 0
2022-11-28 04:00 | 3.4589 | 0 | N/A | 0 | 0
2022-11-28 04:30 | 3.3954 | 0 | N/A | 0 | 0
2022-11-28 05:00 | 3.3951 | 0 | N/A | 0 | 0
2022-11-28 05:30 | 3.6967 | 0 | N/A | 0 | 0
2022-11-28 06:00 | 4.0327 | 0 | N/A | 0 | 0
2022-11-28 06:30 | 4.7148 | 0 | N/A | 0 | 0
2022-11-28 07:00 | 5.4941 | 0 | N/A | 0 | 0
2022-11-28 07:30 | 6.0048 | 0 | N/A | 0 | 0
2022-11-28 08:00 | 5.5687 | 0 | N/A | 0 | 0
2022-11-28 08:30 | 4.4204 | 0 | N/A | 0 | 0
2022-11-28 09:00 | 3.7864 | 0 | N/A | 0 | 0
2022-11-28 09:30 | 3.5746 | 0 | N/A | 0 | 0
2022-11-28 10:00 | 3.67 | 0 | N/A | 0 | 0
2022-11-28 10:30 | 3.1472 | 0 | N/A | 0 | 0
2022-11-28 11:00 | 2.947 | 0 | N/A | 0 | 0
2022-11-28 11:30 | 2.9608 | 0 | N/A | 0 | 0
2022-11-28 12:00 | 2.8929 | 0 | N/A | 0 | 0
2022-11-28 12:30 | 3.4379 | 0 | N/A | 0 | 0
2022-11-28 13:00 | 2.5483 | 0 | N/A | 0 | 0
2022-11-28 13:30 | 1.5422 | 0 | N/A | 0 | 0
2022-11-28 14:00 | 2.4035 | 0 | N/A | 0 | 0
2022-11-28 14:30 | 3.251 | 0 | N/A | 0 | 0
2022-11-28 15:00 | 2.5857 | 0 | N/A | 0 | 0
2022-11-28 15:30 | 2.2422 | 0 | N/A | 0 | 0
2022-11-28 16:00 | 2.0603 | 0 | N/A | 0 | 0
2022-11-28 16:30 | 2.9382 | 0 | N/A | 0 | 0
2022-11-28 17:00 | 3.7909 | 0 | N/A | 0 | 0
2022-11-28 17:30 | 4.9033 | 0 | N/A | 0 | 0
2022-11-28 18:00 | 5.2301 | 0 | N/A | 0 | 0
2022-11-28 18:30 | 6.0225 | 0 | N/A | 0 | 0
2022-11-28 19:00 | 6.2116 | 0 | N/A | 0 | 0
2022-11-28 19:30 | 6.3108 | 0 | N/A | 0 | 0
2022-11-28 20:00 | 6.3359 | 0 | N/A | 0 | 0
2022-11-28 20:30 | 6.3864 | 0 | N/A | 0 | 0
2022-11-28 21:00 | 6.3789 | 0 | N/A | 0 | 0
2022-11-28 21:30 | 6.0225 | 0 | N/A | 0 | 0
2022-11-28 22:00 | 5.569 | 0 | N/A | 0 | 0
2022-11-28 22:30 | 5.4677 | 0 | N/A | 0 | 0
2022-11-28 23:00 | 5.3072 | 0 | N/A | 0 | 0
2022-11-28 23:30 | 4.8379 | 0 | N/A | 0 | 0
2022-11-29 | 4.8734 | 0 | N/A | 0 | 0
2022-11-29 00:30 | 5.1135 | 0 | N/A | 0 | 0
2022-11-29 01:00 | 5.392 | 0 | N/A | 0 | 0
2022-11-29 01:30 | 4.7139 | 0 | N/A | 0 | 0
2022-11-29 02:00 | 4.1458 | 0 | N/A | 0 | 0
2022-11-29 02:30 | 4.0383 | 0 | N/A | 0 | 0
2022-11-29 03:00 | 3.7993 | 0 | N/A | 0 | 0
2022-11-29 03:30 | 3.553 | 0 | N/A | 0 | 0
2022-11-29 04:00 | 3.4233 | 0 | N/A | 0 | 0
2022-11-29 04:30 | 3.3371 | 0 | N/A | 0 | 0
2022-11-29 05:00 | 3.3671 | 0 | N/A | 0 | 0
2022-11-29 05:30 | 3.6635 | 0 | N/A | 0 | 0
2022-11-29 06:00 | 4.0256 | 0 | N/A | 0 | 0
2022-11-29 06:30 | 4.6008 | 0 | N/A | 0 | 0
2022-11-29 07:00 | 4.9752 | 0 | N/A | 0 | 0
2022-11-29 07:30 | 5.52 | 0 | N/A | 0 | 0
2022-11-29 08:00 | 5.584 | 0 | N/A | 0 | 0
2022-11-29 08:30 | 4.5828 | 0 | N/A | 0 | 0
2022-11-29 09:00 | 3.5211 | 0 | N/A | 0 | 0
2022-11-29 09:30 | 2.2741 | 0 | N/A | 0 | 0
2022-11-29 10:00 | 2.1411 | 0 | N/A | 0 | 0
2022-11-29 10:30 | 1.7385 | 0 | N/A | 0 | 0
2022-11-29 11:00 | 1.5564 | 0 | N/A | 0 | 0
2022-11-29 11:30 | 1.5534 | 0 | N/A | 0 | 0
2022-11-29 12:00 | 2.0105 | 0 | N/A | 0 | 0
2022-11-29 12:30 | 2.1228 | 0 | N/A | 0 | 0
2022-11-29 13:00 | 1.1574 | 0 | N/A | 0 | 0
2022-11-29 13:30 | 1.9812 | 0 | N/A | 0 | 0
2022-11-29 14:00 | 1.7116 | 0 | N/A | 0 | 0
2022-11-29 14:30 | 1.0429 | 0 | N/A | 0 | 0
2022-11-29 15:00 | 1.1396 | 0 | N/A | 0 | 0
2022-11-29 15:30 | 0.92196 | 0 | N/A | 0 | 0
2022-11-29 16:00 | 1.5331 | 0 | N/A | 0 | 0
2022-11-29 16:30 | 1.655 | 0 | N/A | 0 | 0
2022-11-29 17:00 | 1.4781 | 0 | N/A | 0 | 0
2022-11-29 17:30 | 2.5668 | 0 | N/A | 0 | 0
2022-11-29 18:00 | 3.1364 | 0 | N/A | 0 | 0
2022-11-29 18:30 | 3.8675 | 0 | N/A | 0 | 0
2022-11-29 19:00 | 4.163 | 0 | N/A | 0 | 0
2022-11-29 19:30 | 4.5853 | 0 | N/A | 0 | 0
2022-11-29 20:00 | 4.9445 | 0 | N/A | 0 | 0
2022-11-29 20:30 | 5.2252 | 0 | N/A | 0 | 0
2022-11-29 21:00 | 5.4613 | 0 | N/A | 0 | 0
2022-11-29 21:30 | 5.4454 | 0 | N/A | 0 | 0
2022-11-29 22:00 | 5.1216 | 0 | N/A | 0 | 0
2022-11-29 22:30 | 5.1838 | 0 | N/A | 0 | 0
2022-11-29 23:00 | 5.0716 | 0 | N/A | 0 | 0
2022-11-29 23:30 | 4.839 | 0 | N/A | 0 | 0
2022-11-30 | 4.6904 | 0 | N/A | 0 | 0
2022-11-30 00:30 | 4.87 | 0 | N/A | 0 | 0
2022-11-30 01:00 | 5.2889 | 0 | N/A | 0 | 0
2022-11-30 01:30 | 4.6859 | 0 | N/A | 0 | 0
2022-11-30 02:00 | 4.1426 | 0 | N/A | 0 | 0
2022-11-30 02:30 | 4.0509 | 0 | N/A | 0 | 0
2022-11-30 03:00 | 3.7786 | 0 | N/A | 0 | 0
2022-11-30 03:30 | 3.545 | 0 | N/A | 0 | 0
2022-11-30 04:00 | 3.4154 | 0 | N/A | 0 | 0
2022-11-30 04:30 | 3.3689 | 0 | N/A | 0 | 0
2022-11-30 05:00 | 3.5041 | 0 | N/A | 0 | 0
2022-11-30 05:30 | 3.6848 | 0 | N/A | 0 | 0
2022-11-30 06:00 | 4.0931 | 0 | N/A | 0 | 0
2022-11-30 06:30 | 5.0042 | 0 | N/A | 0 | 0
2022-11-30 07:00 | 5.5656 | 0 | N/A | 0 | 0
2022-11-30 07:30 | 5.9315 | 0 | N/A | 0 | 0
2022-11-30 08:00 | 5.8861 | 0 | N/A | 0 | 0
2022-11-30 08:30 | 4.8156 | 0 | N/A | 0 | 0
2022-11-30 09:00 | 4.2974 | 0 | N/A | 0 | 0
2022-11-30 09:30 | 3.9898 | 0 | N/A | 0 | 0
2022-11-30 10:00 | 3.4296 | 0 | N/A | 0 | 0
2022-11-30 10:30 | 2.3192 | 0 | N/A | 0 | 0
2022-11-30 11:00 | 1.2983 | 0 | N/A | 0 | 0
2022-11-30 11:30 | 0.85365 | 0 | N/A | 0 | 0
2022-11-30 12:00 | -0.72195 | 0 | N/A | 0 | 0
2022-11-30 12:30 | -0.77521 | 0 | N/A | 0 | 0
2022-11-30 13:00 | -0.72281 | 0 | N/A | 0 | 0
2022-11-30 13:30 | -0.87115 | 0 | N/A | 0 | 0
2022-11-30 14:00 | -0.69065 | 0 | N/A | 0 | 0
2022-11-30 14:30 | 0.73699 | 0 | N/A | 0 | 0
2022-11-30 15:00 | 0.86544 | 0 | N/A | 0 | 0
2022-11-30 15:30 | 1.6535 | 0 | N/A | 0 | 0
2022-11-30 16:00 | 1.9049 | 0 | N/A | 0 | 0
2022-11-30 16:30 | 2.6313 | 0 | N/A | 0 | 0
2022-11-30 17:00 | 3.3095 | 0 | N/A | 0 | 0
2022-11-30 17:30 | 3.8527 | 0 | N/A | 0 | 0
2022-11-30 18:00 | 4.1883 | 0 | N/A | 0 | 0
2022-11-30 18:30 | 4.402 | 0 | N/A | 0 | 0
2022-11-30 19:00 | 4.7363 | 0 | N/A | 0 | 0
2022-11-30 19:30 | 5.1261 | 0 | N/A | 0 | 0
2022-11-30 20:00 | 5.3402 | 0 | N/A | 0 | 0
2022-11-30 20:30 | 5.4976 | 0 | N/A | 0 | 0
2022-11-30 21:00 | 5.6339 | 0 | N/A | 0 | 0
2022-11-30 21:30 | 5.4922 | 0 | N/A | 0 | 0
2022-11-30 22:00 | 5.1772 | 0 | N/A | 0 | 0
2022-11-30 22:30 | 5.1971 | 0 | N/A | 0 | 0
2022-11-30 23:00 | 5.0619 | 0 | N/A | 0 | 0
2022-11-30 23:30 | 4.741 | 0 | N/A | 0 | 0
2022-12-01 | 4.6689 | 0 | N/A | 0 | 0
2022-12-01 00:30 | 4.9447 | 0 | N/A | 0 | 0
2022-12-01 01:00 | 5.2586 | 0 | N/A | 0 | 0
2022-12-01 01:30 | 4.6525 | 0 | N/A | 0 | 0
2022-12-01 02:00 | 4.1089 | 0 | N/A | 0 | 0
2022-12-01 02:30 | 4.0562 | 0 | N/A | 0 | 0
2022-12-01 03:00 | 3.8389 | 0 | N/A | 0 | 0
2022-12-01 03:30 | 3.4456 | 0 | N/A | 0 | 0
2022-12-01 04:00 | 3.2813 | 0 | N/A | 0 | 0
2022-12-01 04:30 | 3.2619 | 0 | N/A | 0 | 0
2022-12-01 05:00 | 3.2735 | 0 | N/A | 0 | 0
2022-12-01 05:30 | 3.4557 | 0 | N/A | 0 | 0
2022-12-01 06:00 | 3.8385 | 0 | N/A | 0 | 0
2022-12-01 06:30 | 4.6824 | 0 | N/A | 0 | 0
2022-12-01 07:00 | 5.2638 | 0 | N/A | 0 | 0
2022-12-01 07:30 | 5.7825 | 0 | N/A | 0 | 0
2022-12-01 08:00 | 5.7257 | 0 | N/A | 0 | 0
2022-12-01 08:30 | 4.6238 | 0 | N/A | 0 | 0
2022-12-01 09:00 | 3.9838 | 0 | N/A | 0 | 0
2022-12-01 09:30 | 3.1518 | 0 | N/A | 0 | 0
2022-12-01 10:00 | 2.489 | 0 | N/A | 0 | 0
2022-12-01 10:30 | 2.422 | 0 | N/A | 0 | 0
2022-12-01 11:00 | 2.2157 | 0 | N/A | 0 | 0
2022-12-01 11:30 | 1.8595 | 0 | N/A | 0 | 0
2022-12-01 12:00 | 1.3849 | 0 | N/A | 0 | 0
2022-12-01 12:30 | 1.7982 | 0 | N/A | 0 | 0
2022-12-01 13:00 | 2.067 | 0 | N/A | 0 | 0
2022-12-01 13:30 | 1.1937 | 0 | N/A | 0 | 0
2022-12-01 14:00 | 1.2916 | 0 | N/A | 0 | 0
2022-12-01 14:30 | 1.1654 | 0 | N/A | 0 | 0
2022-12-01 15:00 | 1.4435 | 0 | N/A | 0 | 0
2022-12-01 15:30 | 1.8991 | 0 | N/A | 0 | 0
2022-12-01 16:00 | 1.5 | 0 | N/A | 0 | 0
2022-12-01 16:30 | 2.4512 | 0 | N/A | 0 | 0
2022-12-01 17:00 | 2.7403 | 0 | N/A | 0 | 0
2022-12-01 17:30 | 2.8697 | 0 | N/A | 0 | 0
2022-12-01 18:00 | 2.9872 | 0 | N/A | 0 | 0
2022-12-01 18:30 | 3.1965 | 0 | N/A | 0 | 0
2022-12-01 19:00 | 3.7817 | 0 | N/A | 0 | 0
2022-12-01 19:30 | 4.5165 | 0 | N/A | 0 | 0
2022-12-01 20:00 | 4.93 | 0 | N/A | 0 | 0
2022-12-01 20:30 | 5.29 | 0 | N/A | 0 | 0
2022-12-01 21:00 | 5.5132 | 0 | N/A | 0 | 0
2022-12-01 21:30 | 5.5129 | 0 | N/A | 0 | 0
2022-12-01 22:00 | 5.2762 | 0 | N/A | 0 | 0
2022-12-01 22:30 | 5.271 | 0 | N/A | 0 | 0
2022-12-01 23:00 | 5.2495 | 0 | N/A | 0 | 0
2022-12-01 23:30 | 4.9377 | 0 | N/A | 0 | 0
2022-12-02 | 4.877 | 0 | N/A | 0 | 0
2022-12-03 00:30 | 4.5193 | 0 | N/A | 0 | 0
2022-12-03 01:00 | 4.6927 | 0 | N/A | 0 | 0
2022-12-03 01:30 | 4.0025 | 0 | N/A | 0 | 0
2022-12-03 02:00 | 3.5381 | 0 | N/A | 0 | 0
2022-12-03 02:30 | 3.4936 | 0 | N/A | 0 | 0
2022-12-03 03:00 | 3.1838 | 0 | N/A | 0 | 0
2022-12-03 03:30 | 2.9147 | 0 | N/A | 0 | 0
2022-12-03 04:00 | 2.7991 | 0 | N/A | 0 | 0
2022-12-03 04:30 | 2.7339 | 0 | N/A | 0 | 0
2022-12-03 05:00 | 2.72 | 0 | N/A | 0 | 0
2022-12-03 05:30 | 2.7896 | 0 | N/A | 0 | 0
2022-12-03 06:00 | 2.823 | 0 | N/A | 0 | 0
2022-12-03 06:30 | 2.934 | 0 | N/A | 0 | 0
2022-12-03 07:00 | 2.8995 | 0 | N/A | 0 | 0
2022-12-03 07:30 | 2.843 | 0 | N/A | 0 | 0
2022-12-03 08:00 | 2.671 | 0 | N/A | 0 | 0
2022-12-03 08:30 | 2.0141 | 0 | N/A | 0 | 0
2022-12-03 09:00 | 1.4547 | 0 | N/A | 0 | 0
2022-12-03 09:30 | 0.96602 | 0 | N/A | 0 | 0
2022-12-03 10:00 | -0.72573 | 0 | N/A | 0 | 0
2022-12-03 10:30 | -0.99744 | 0 | N/A | 0 | 0
2022-12-03 11:00 | -1.4902 | 0 | N/A | 0 | 0
2022-12-03 11:30 | -1.7698 | 0 | N/A | 0 | 0
2022-12-03 12:00 | -1.5542 | 0 | N/A | 0 | 0
2022-12-03 12:30 | -1.589 | 0 | N/A | 0 | 0
2022-12-03 13:00 | -1.6583 | 0 | N/A | 0 | 0
2022-12-03 13:30 | -1.6035 | 0 | N/A | 0 | 0
2022-12-03 14:00 | -1.926 | 0 | N/A | 0 | 0
2022-12-03 14:30 | -1.2032 | 0 | N/A | 0 | 0
2022-12-03 15:00 | -0.85097 | 0 | N/A | 0 | 0
2022-12-03 15:30 | -0.773 | 0 | N/A | 0 | 0
2022-12-03 16:00 | -0.8792 | 0 | N/A | 0 | 0
2022-12-03 16:30 | -0.71957 | 0 | N/A | 0 | 0
2022-12-03 17:00 | 1.0209 | 0 | N/A | 0 | 0
2022-12-03 17:30 | 1.6595 | 0 | N/A | 0 | 0
2022-12-03 18:00 | 2.561 | 0 | N/A | 0 | 0
2022-12-03 18:30 | 3.4941 | 0 | N/A | 0 | 0
2022-12-03 19:00 | 4.3297 | 0 | N/A | 0 | 0
2022-12-03 19:30 | 4.8087 | 0 | N/A | 0 | 0
2022-12-03 20:00 | 4.9068 | 0 | N/A | 0 | 0
2022-12-03 20:30 | 4.8246 | 0 | N/A | 0 | 0
2022-12-03 21:00 | 4.7115 | 0 | N/A | 0 | 0
2022-12-03 21:30 | 4.517 | 0 | N/A | 0 | 0
2022-12-03 22:00 | 4.3206 | 0 | N/A | 0 | 0
2022-12-03 22:30 | 4.4513 | 0 | N/A | 0 | 0
2022-12-03 23:00 | 4.474 | 0 | N/A | 0 | 0
2022-12-03 23:30 | 4.1562 | 0 | N/A | 0 | 0
2022-12-04 | 4.2495 | 0 | N/A | 0 | 0
2022-12-04 00:30 | 4.4984 | 0 | N/A | 0 | 0
2022-12-04 01:00 | 4.6204 | 0 | N/A | 0 | 0
2022-12-04 01:30 | 3.8826 | 0 | N/A | 0 | 0
2022-12-04 02:00 | 3.35 | 0 | N/A | 0 | 0
2022-12-04 02:30 | 3.2913 | 0 | N/A | 0 | 0
2022-12-04 03:00 | 2.9852 | 0 | N/A | 0 | 0
2022-12-04 03:30 | 2.7175 | 0 | N/A | 0 | 0
2022-12-04 04:00 | 2.6171 | 0 | N/A | 0 | 0
2022-12-04 04:30 | 2.5858 | 0 | N/A | 0 | 0
2022-12-04 05:00 | 2.5513 | 0 | N/A | 0 | 0
2022-12-04 05:30 | 2.5536 | 0 | N/A | 0 | 0
2022-12-04 06:00 | 2.631 | 0 | N/A | 0 | 0
2022-12-04 06:30 | 2.7975 | 0 | N/A | 0 | 0
2022-12-04 07:00 | 2.7773 | 0 | N/A | 0 | 0
2022-12-04 07:30 | 2.6334 | 0 | N/A | 0 | 0
2022-12-04 08:00 | 2.2809 | 0 | N/A | 0 | 0
2022-12-04 08:30 | 1.7667 | 0 | N/A | 0 | 0
2022-12-04 09:00 | 1.3207 | 0 | N/A | 0 | 0
2022-12-04 09:30 | 0.95954 | 0 | N/A | 0 | 0
2022-12-04 10:00 | -0.85917 | 0 | N/A | 0 | 0
2022-12-04 10:30 | -0.98093 | 0 | N/A | 0 | 0
2022-12-04 11:00 | -1.2464 | 0 | N/A | 0 | 0
2022-12-04 11:30 | -1.3768 | 0 | N/A | 0 | 0
2022-12-04 12:00 | -1.264 | 0 | N/A | 0 | 0
2022-12-04 12:30 | -1.2092 | 0 | N/A | 0 | 0
2022-12-04 13:00 | -0.81867 | 0 | N/A | 0 | 0
2022-12-04 13:30 | -0.6934 | 0 | N/A | 0 | 0
2022-12-04 14:00 | -0.51278 | 0 | N/A | 0 | 0
2022-12-04 14:30 | -0.51516 | 0 | N/A | 0 | 0
2022-12-04 15:00 | -0.56357 | 0 | N/A | 0 | 0
2022-12-04 15:30 | -0.43046 | 0 | N/A | 0 | 0
2022-12-04 16:00 | 0.78395 | 0 | N/A | 0 | 0
2022-12-04 16:30 | 1.7803 | 0 | N/A | 0 | 0
2022-12-04 17:00 | 2.5051 | 0 | N/A | 0 | 0
2022-12-04 17:30 | 3.3118 | 0 | N/A | 0 | 0
2022-12-04 18:00 | 4.7246 | 0 | N/A | 0 | 0
2022-12-04 18:30 | 6.4716 | 0 | N/A | 0 | 0
2022-12-04 19:00 | 6.7777 | 0 | N/A | 0 | 0
2022-12-04 19:30 | 6.1154 | 0 | N/A | 0 | 0
2022-12-04 20:00 | 6.1447 | 0 | N/A | 0 | 0
2022-12-04 20:30 | 5.6423 | 0 | N/A | 0 | 0
2022-12-04 21:00 | 5.4022 | 0 | N/A | 0 | 0
2022-12-04 21:30 | 5.1896 | 0 | N/A | 0 | 0
2022-12-04 22:00 | 4.8423 | 0 | N/A | 0 | 0
2022-12-04 22:30 | 4.7978 | 0 | N/A | 0 | 0
2022-12-04 23:00 | 4.6988 | 0 | N/A | 0 | 0
2022-12-04 23:30 | 4.2994 | 0 | N/A | 0 | 0
2022-12-05 | 4.245 | 0 | N/A | 0 | 0
2022-12-05 00:30 | 4.4874 | 0 | N/A | 0 | 0
2022-12-05 01:00 | 4.6252 | 0 | N/A | 0 | 0
2022-12-05 01:30 | 3.8646 | 0 | N/A | 0 | 0
2022-12-05 02:00 | 3.3613 | 0 | N/A | 0 | 0
2022-12-05 02:30 | 3.3239 | 0 | N/A | 0 | 0
2022-12-05 03:00 | 3.0978 | 0 | N/A | 0 | 0
2022-12-05 03:30 | 2.8505 | 0 | N/A | 0 | 0
2022-12-05 04:00 | 2.6787 | 0 | N/A | 0 | 0
2022-12-05 04:30 | 2.6634 | 0 | N/A | 0 | 0
2022-12-05 05:00 | 2.6912 | 0 | N/A | 0 | 0
2022-12-05 05:30 | 2.8128 | 0 | N/A | 0 | 0
2022-12-05 06:00 | 3.0845 | 0 | N/A | 0 | 0
2022-12-05 06:30 | 3.4903 | 0 | N/A | 0 | 0
2022-12-05 07:00 | 4.2252 | 0 | N/A | 0 | 0
2022-12-05 07:30 | 4.8711 | 0 | N/A | 0 | 0
2022-12-05 08:00 | 5.022 | 0 | N/A | 0 | 0
2022-12-05 08:30 | 5.0598 | 0 | N/A | 0 | 0
2022-12-05 09:00 | 4.8131 | 0 | N/A | 0 | 0
2022-12-05 09:30 | 4.4686 | 0 | N/A | 0 | 0
2022-12-05 10:00 | 4.6411 | 0 | N/A | 0 | 0
2022-12-05 10:30 | 4.0078 | 0 | N/A | 0 | 0
2022-12-05 11:00 | 3.4505 | 0 | N/A | 0 | 0
2022-12-05 11:30 | 2.9566 | 0 | N/A | 0 | 0
2022-12-05 12:00 | 2.802 | 0 | N/A | 0 | 0
2022-12-05 12:30 | 3.0267 | 0 | N/A | 0 | 0
2022-12-05 13:00 | 3.0815 | 0 | N/A | 0 | 0
2022-12-05 13:30 | 2.2969 | 0 | N/A | 0 | 0
2022-12-05 14:00 | 1.8996 | 0 | N/A | 0 | 0
2022-12-05 14:30 | 1.3241 | 0 | N/A | 0 | 0
2022-12-05 15:00 | 1.2974 | 0 | N/A | 0 | 0
2022-12-05 15:30 | 1.6848 | 0 | N/A | 0 | 0
2022-12-05 16:00 | 1.4332 | 0 | N/A | 0 | 0
2022-12-05 16:30 | 1.9486 | 0 | N/A | 0 | 0
2022-12-05 17:00 | 2.5855 | 0 | N/A | 0 | 0
2022-12-05 17:30 | 3.2054 | 0 | N/A | 0 | 0
2022-12-05 18:00 | 4.1755 | 0 | N/A | 0 | 0
2022-12-05 18:30 | 4.9623 | 0 | N/A | 0 | 0
2022-12-05 19:00 | 5.3244 | 0 | N/A | 0 | 0
2022-12-05 19:30 | 5.3749 | 0 | N/A | 0 | 0
2022-12-05 20:00 | 5.4436 | 0 | N/A | 0 | 0
2022-12-05 20:30 | 5.6785 | 0 | N/A | 0 | 0
2022-12-05 21:00 | 5.7396 | 0 | N/A | 0 | 0
2022-12-05 21:30 | 5.5245 | 0 | N/A | 0 | 0
2022-12-05 22:00 | 5.1614 | 0 | N/A | 0 | 0
2022-12-05 22:30 | 5.0957 | 0 | N/A | 0 | 0
2022-12-05 23:00 | 5.031 | 0 | N/A | 0 | 0
2022-12-05 23:30 | 4.6597 | 0 | N/A | 0 | 0
2022-12-06 | 4.5839 | 0 | N/A | 0 | 0
2022-12-07 00:30 | 4.5339 | 0 | N/A | 0 | 0
2022-12-07 01:00 | 4.7232 | 0 | N/A | 0 | 0
2022-12-07 01:30 | 4.0467 | 0 | N/A | 0 | 0
2022-12-07 02:00 | 3.4416 | 0 | N/A | 0 | 0
2022-12-07 02:30 | 3.3882 | 0 | N/A | 0 | 0
2022-12-07 03:00 | 3.1316 | 0 | N/A | 0 | 0
2022-12-07 03:30 | 2.9169 | 0 | N/A | 0 | 0
2022-12-07 04:00 | 2.7858 | 0 | N/A | 0 | 0
2022-12-07 04:30 | 2.8239 | 0 | N/A | 0 | 0
2022-12-07 05:00 | 2.8836 | 0 | N/A | 0 | 0
2022-12-07 05:30 | 3.0775 | 0 | N/A | 0 | 0
2022-12-07 06:00 | 3.3194 | 0 | N/A | 0 | 0
2022-12-07 06:30 | 3.8654 | 0 | N/A | 0 | 0
2022-12-07 07:00 | 4.518 | 0 | N/A | 0 | 0
2022-12-07 07:30 | 5.1658 | 0 | N/A | 0 | 0
2022-12-07 08:00 | 5.2599 | 0 | N/A | 0 | 0
2022-12-07 08:30 | 4.438 | 0 | N/A | 0 | 0
2022-12-07 09:00 | 3.3369 | 0 | N/A | 0 | 0
2022-12-07 09:30 | 2.0283 | 0 | N/A | 0 | 0
2022-12-07 10:00 | 1.1016 | 0 | N/A | 0 | 0
2022-12-07 10:30 | 1.2019 | 0 | N/A | 0 | 0
2022-12-07 11:00 | 1.113 | 0 | N/A | 0 | 0
2022-12-07 11:30 | -0.59427 | 0 | N/A | 0 | 0
2022-12-07 12:00 | 0.63395 | 0 | N/A | 0 | 0
2022-12-07 12:30 | 0.70868 | 0 | N/A | 0 | 0
2022-12-07 13:00 | 0.70246 | 0 | N/A | 0 | 0
2022-12-07 13:30 | 0.68842 | 0 | N/A | 0 | 0
2022-12-07 14:00 | -0.67536 | 0 | N/A | 0 | 0
2022-12-07 14:30 | -0.72007 | 0 | N/A | 0 | 0
2022-12-07 15:00 | -0.76214 | 0 | N/A | 0 | 0
2022-12-07 15:30 | -0.81805 | 0 | N/A | 0 | 0
2022-12-07 16:00 | -0.8512 | 0 | N/A | 0 | 0
2022-12-07 16:30 | 0.9927 | 0 | N/A | 0 | 0
2022-12-07 17:00 | 1.0585 | 0 | N/A | 0 | 0
2022-12-07 17:30 | 1.8354 | 0 | N/A | 0 | 0
2022-12-07 18:00 | 3.5432 | 0 | N/A | 0 | 0
2022-12-07 18:30 | 4.7705 | 0 | N/A | 0 | 0
2022-12-07 19:00 | 5.2485 | 0 | N/A | 0 | 0
2022-12-07 19:30 | 5.4987 | 0 | N/A | 0 | 0
2022-12-07 20:00 | 5.6531 | 0 | N/A | 0 | 0
2022-12-07 20:30 | 5.9375 | 0 | N/A | 0 | 0
2022-12-07 21:00 | 5.9182 | 0 | N/A | 0 | 0
2022-12-07 21:30 | 5.8652 | 0 | N/A | 0 | 0
2022-12-07 22:00 | 5.526 | 0 | N/A | 0 | 0
2022-12-07 22:30 | 5.539 | 0 | N/A | 0 | 0
2022-12-07 23:00 | 5.4988 | 0 | N/A | 0 | 0
2022-12-07 23:30 | 5.0537 | 0 | N/A | 0 | 0
2022-12-08 | 4.9487 | 0 | N/A | 0 | 0
2022-12-08 00:30 | 5.1377 | 0 | N/A | 0 | 0
2022-12-08 01:00 | 5.3601 | 0 | N/A | 0 | 0
2022-12-08 01:30 | 4.7023 | 0 | N/A | 0 | 0
2022-12-08 02:00 | 4.1742 | 0 | N/A | 0 | 0
2022-12-08 02:30 | 4.051 | 0 | N/A | 0 | 0
2022-12-08 03:00 | 3.8047 | 0 | N/A | 0 | 0
2022-12-08 03:30 | 3.5436 | 0 | N/A | 0 | 0
2022-12-08 04:00 | 3.4309 | 0 | N/A | 0 | 0
2022-12-08 04:30 | 3.4038 | 0 | N/A | 0 | 0
2022-12-08 05:00 | 3.4989 | 0 | N/A | 0 | 0
2022-12-08 05:30 | 3.7574 | 0 | N/A | 0 | 0
2022-12-08 06:00 | 4.1236 | 0 | N/A | 0 | 0
2022-12-08 06:30 | 4.8046 | 0 | N/A | 0 | 0
2022-12-08 07:00 | 5.1854 | 0 | N/A | 0 | 0
2022-12-08 07:30 | 5.6219 | 0 | N/A | 0 | 0
2022-12-08 08:00 | 5.5958 | 0 | N/A | 0 | 0
2022-12-08 08:30 | 4.8113 | 0 | N/A | 0 | 0
2022-12-08 09:00 | 4.2945 | 0 | N/A | 0 | 0
2022-12-08 09:30 | 4.2502 | 0 | N/A | 0 | 0
2022-12-08 10:00 | 2.5744 | 0 | N/A | 0 | 0
2022-12-08 10:30 | 2.8884 | 0 | N/A | 0 | 0
2022-12-08 11:00 | 1.5038 | 0 | N/A | 0 | 0
2022-12-08 11:30 | 2.1255 | 0 | N/A | 0 | 0
2022-12-08 12:00 | 1.4632 | 0 | N/A | 0 | 0
2022-12-08 12:30 | 1.6522 | 0 | N/A | 0 | 0
2022-12-08 13:00 | 1.3147 | 0 | N/A | 0 | 0
2022-12-08 13:30 | 1.6146 | 0 | N/A | 0 | 0
2022-12-08 14:00 | 1.1826 | 0 | N/A | 0 | 0
2022-12-08 14:30 | 1.0098 | 0 | N/A | 0 | 0
2022-12-08 15:00 | 1.0565 | 0 | N/A | 0 | 0
2022-12-08 15:30 | 1.5028 | 0 | N/A | 0 | 0
2022-12-08 16:00 | 1.8568 | 0 | N/A | 0 | 0
2022-12-08 16:30 | 1.2095 | 0 | N/A | 0 | 0
2022-12-08 17:00 | 2.3324 | 0 | N/A | 0 | 0
2022-12-08 17:30 | 2.7524 | 0 | N/A | 0 | 0
2022-12-08 18:00 | 3.6712 | 0 | N/A | 0 | 0
2022-12-08 18:30 | 3.557 | 0 | N/A | 0 | 0
2022-12-08 19:00 | 4.528 | 0 | N/A | 0 | 0
2022-12-08 19:30 | 5.4234 | 0 | N/A | 0 | 0
2022-12-08 20:00 | 5.6213 | 0 | N/A | 0 | 0
2022-12-08 20:30 | 6.0872 | 0 | N/A | 0 | 0
2022-12-08 21:00 | 6.3092 | 0 | N/A | 0 | 0
2022-12-08 21:30 | 6.2905 | 0 | N/A | 0 | 0
2022-12-08 22:00 | 5.9346 | 0 | N/A | 0 | 0
2022-12-08 22:30 | 5.9409 | 0 | N/A | 0 | 0
2022-12-08 23:00 | 5.8214 | 0 | N/A | 0 | 0
2022-12-08 23:30 | 5.3733 | 0 | N/A | 0 | 0
2022-12-09 | 5.2025 | 0 | N/A | 0 | 0
2022-12-10 00:30 | 5.3244 | 0 | N/A | 0 | 0
2022-12-10 01:00 | 5.5024 | 0 | N/A | 0 | 0
2022-12-10 01:30 | 4.742 | 0 | N/A | 0 | 0
2022-12-10 02:00 | 4.1776 | 0 | N/A | 0 | 0
2022-12-10 02:30 | 4.0744 | 0 | N/A | 0 | 0
2022-12-10 03:00 | 3.8528 | 0 | N/A | 0 | 0
2022-12-10 03:30 | 3.572 | 0 | N/A | 0 | 0
2022-12-10 04:00 | 3.3376 | 0 | N/A | 0 | 0
2022-12-10 04:30 | 3.3182 | 0 | N/A | 0 | 0
2022-12-10 05:00 | 3.3015 | 0 | N/A | 0 | 0
2022-12-10 05:30 | 3.3863 | 0 | N/A | 0 | 0
2022-12-10 06:00 | 3.4684 | 0 | N/A | 0 | 0
2022-12-10 06:30 | 3.7851 | 0 | N/A | 0 | 0
2022-12-10 07:00 | 3.8808 | 0 | N/A | 0 | 0
2022-12-10 07:30 | 3.9419 | 0 | N/A | 0 | 0
2022-12-10 08:00 | 3.645 | 0 | N/A | 0 | 0
2022-12-10 08:30 | 2.8371 | 0 | N/A | 0 | 0
2022-12-10 09:00 | 2.0562 | 0 | N/A | 0 | 0
2022-12-10 09:30 | 1.1876 | 0 | N/A | 0 | 0
2022-12-10 10:00 | -0.93528 | 0 | N/A | 0 | 0
2022-12-10 10:30 | -1.1411 | 0 | N/A | 0 | 0
2022-12-10 11:00 | -1.6607 | 0 | N/A | 0 | 0
2022-12-10 11:30 | -2.0866 | 0 | N/A | 0 | 0
2022-12-10 12:00 | -2.3241 | 0 | N/A | 0 | 0
2022-12-10 12:30 | -2.5452 | 0 | N/A | 0 | 0
2022-12-10 13:00 | -2.5172 | 0 | N/A | 0 | 0
2022-12-10 13:30 | -2.7503 | 0 | N/A | 0 | 0
2022-12-10 14:00 | -2.7602 | 0 | N/A | 0 | 0
2022-12-10 14:30 | -2.734 | 0 | N/A | 0 | 0
2022-12-10 15:00 | -2.6188 | 0 | N/A | 0 | 0
2022-12-10 15:30 | -2.4545 | 0 | N/A | 0 | 0
2022-12-10 16:00 | -2.1513 | 0 | N/A | 0 | 0
2022-12-10 16:30 | -1.7109 | 0 | N/A | 0 | 0
2022-12-10 17:00 | -0.95408 | 0 | N/A | 0 | 0
2022-12-10 17:30 | 1.6014 | 0 | N/A | 0 | 0
2022-12-10 18:00 | 2.9764 | 0 | N/A | 0 | 0
2022-12-10 18:30 | 3.5439 | 0 | N/A | 0 | 0
2022-12-10 19:00 | 3.9353 | 0 | N/A | 0 | 0
2022-12-10 19:30 | 3.8867 | 0 | N/A | 0 | 0
2022-12-10 20:00 | 4.1212 | 0 | N/A | 0 | 0
2022-12-10 20:30 | 4.366 | 0 | N/A | 0 | 0
2022-12-10 21:00 | 4.3147 | 0 | N/A | 0 | 0
2022-12-10 21:30 | 4.279 | 0 | N/A | 0 | 0
2022-12-10 22:00 | 4.0086 | 0 | N/A | 0 | 0
2022-12-10 22:30 | 4.2474 | 0 | N/A | 0 | 0
2022-12-10 23:00 | 4.3745 | 0 | N/A | 0 | 0
2022-12-10 23:30 | 4.0777 | 0 | N/A | 0 | 0
2022-12-11 | 4.0522 | 0 | N/A | 0 | 0
2022-12-11 00:30 | 4.3782 | 0 | N/A | 0 | 0
2022-12-11 01:00 | 4.6502 | 0 | N/A | 0 | 0
2022-12-11 01:30 | 3.9803 | 0 | N/A | 0 | 0
2022-12-11 02:00 | 3.4157 | 0 | N/A | 0 | 0
2022-12-11 02:30 | 3.2858 | 0 | N/A | 0 | 0
2022-12-11 03:00 | 3.1793 | 0 | N/A | 0 | 0
2022-12-11 03:30 | 2.8349 | 0 | N/A | 0 | 0
2022-12-11 04:00 | 2.7263 | 0 | N/A | 0 | 0
2022-12-11 04:30 | 2.5701 | 0 | N/A | 0 | 0
2022-12-11 05:00 | 2.577 | 0 | N/A | 0 | 0
2022-12-11 05:30 | 2.5617 | 0 | N/A | 0 | 0
2022-12-11 06:00 | 2.5869 | 0 | N/A | 0 | 0
2022-12-11 06:30 | 2.6857 | 0 | N/A | 0 | 0
2022-12-11 07:00 | 2.6222 | 0 | N/A | 0 | 0
2022-12-11 07:30 | 2.6253 | 0 | N/A | 0 | 0
2022-12-11 08:00 | 2.2802 | 0 | N/A | 0 | 0
2022-12-11 08:30 | 1.7584 | 0 | N/A | 0 | 0
2022-12-11 09:00 | 1.5052 | 0 | N/A | 0 | 0
2022-12-11 09:30 | 1.0883 | 0 | N/A | 0 | 0
2022-12-11 10:00 | 1.3501 | 0 | N/A | 0 | 0
2022-12-11 10:30 | 1.4614 | 0 | N/A | 0 | 0
2022-12-11 11:00 | 0.95079 | 0 | N/A | 0 | 0
2022-12-11 11:30 | -0.92174 | 0 | N/A | 0 | 0
2022-12-11 12:00 | -1.2068 | 0 | N/A | 0 | 0
2022-12-11 12:30 | -0.91872 | 0 | N/A | 0 | 0
2022-12-11 13:00 | 1.7567 | 0 | N/A | 0 | 0
2022-12-11 13:30 | 2.6625 | 0 | N/A | 0 | 0
2022-12-11 14:00 | 2.7921 | 0 | N/A | 0 | 0
2022-12-11 14:30 | 3.2274 | 0 | N/A | 0 | 0
2022-12-11 15:00 | 3.4289 | 0 | N/A | 0 | 0
2022-12-11 15:30 | 3.9708 | 0 | N/A | 0 | 0
2022-12-11 16:00 | 4.3914 | 0 | N/A | 0 | 0
2022-12-11 16:30 | 4.4566 | 0 | N/A | 0 | 0
2022-12-11 17:00 | 4.5183 | 0 | N/A | 0 | 0
2022-12-11 17:30 | 5.0472 | 0 | N/A | 0 | 0
2022-12-11 18:00 | 5.3693 | 0 | N/A | 0 | 0
2022-12-11 18:30 | 5.5137 | 0 | N/A | 0 | 0
2022-12-11 19:00 | 5.3344 | 0 | N/A | 0 | 0
2022-12-11 19:30 | 5.3607 | 0 | N/A | 0 | 0
2022-12-11 20:00 | 5.3355 | 0 | N/A | 0 | 0
2022-12-11 20:30 | 5.4037 | 0 | N/A | 0 | 0
2022-12-11 21:00 | 4.9645 | 0 | N/A | 0 | 0
2022-12-11 21:30 | 4.7329 | 0 | N/A | 0 | 0
2022-12-11 22:00 | 4.4458 | 0 | N/A | 0 | 0
2022-12-11 22:30 | 4.7254 | 0 | N/A | 0 | 0
2022-12-11 23:00 | 4.7248 | 0 | N/A | 0 | 0
2022-12-11 23:30 | 4.467 | 0 | N/A | 0 | 0
2022-12-12 | 4.3988 | 0 | N/A | 0 | 0
2022-12-12 00:30 | 4.6007 | 0 | N/A | 0 | 0
2022-12-12 01:00 | 4.7903 | 0 | N/A | 0 | 0
2022-12-12 01:30 | 4.2011 | 0 | N/A | 0 | 0
2022-12-12 02:00 | 3.6408 | 0 | N/A | 0 | 0
2022-12-12 02:30 | 3.5989 | 0 | N/A | 0 | 0
2022-12-12 03:00 | 3.4028 | 0 | N/A | 0 | 0
2022-12-12 03:30 | 3.1797 | 0 | N/A | 0 | 0
2022-12-12 04:00 | 3.0397 | 0 | N/A | 0 | 0
2022-12-12 04:30 | 2.9243 | 0 | N/A | 0 | 0
2022-12-12 05:00 | 2.9098 | 0 | N/A | 0 | 0
2022-12-12 05:30 | 3.162 | 0 | N/A | 0 | 0
2022-12-12 06:00 | 3.428 | 0 | N/A | 0 | 0
2022-12-12 06:30 | 4.1031 | 0 | N/A | 0 | 0
2022-12-12 07:00 | 4.8323 | 0 | N/A | 0 | 0
2022-12-12 07:30 | 5.2966 | 0 | N/A | 0 | 0
2022-12-12 08:00 | 5.2838 | 0 | N/A | 0 | 0
2022-12-12 08:30 | 4.8917 | 0 | N/A | 0 | 0
2022-12-12 09:00 | 4.8962 | 0 | N/A | 0 | 0
2022-12-12 09:30 | 3.6039 | 0 | N/A | 0 | 0
2022-12-12 10:00 | 3.8388 | 0 | N/A | 0 | 0
2022-12-12 10:30 | 3.652 | 0 | N/A | 0 | 0
2022-12-12 11:00 | 3.3641 | 0 | N/A | 0 | 0
2022-12-12 11:30 | 2.4988 | 0 | N/A | 0 | 0
2022-12-12 12:00 | 2.3181 | 0 | N/A | 0 | 0
2022-12-12 12:30 | 3.6249 | 0 | N/A | 0 | 0
2022-12-12 13:00 | 0.66253 | 0 | N/A | 0 | 0
2022-12-12 13:30 | 2.1617 | 0 | N/A | 0 | 0
2022-12-12 14:00 | 3.8478 | 0 | N/A | 0 | 0
2022-12-12 14:30 | 2.7301 | 0 | N/A | 0 | 0
2022-12-12 15:00 | 1.8641 | 0 | N/A | 0 | 0
2022-12-12 15:30 | 3.3107 | 0 | N/A | 0 | 0
2022-12-12 16:00 | 2.1034 | 0 | N/A | 0 | 0
2022-12-12 16:30 | 2.6178 | 0 | N/A | 0 | 0
2022-12-12 17:00 | 3.5555 | 0 | N/A | 0 | 0
2022-12-12 17:30 | 2.9359 | 0 | N/A | 0 | 0
2022-12-12 18:00 | 4.0611 | 0 | N/A | 0 | 0
2022-12-12 18:30 | 4.9072 | 0 | N/A | 0 | 0
2022-12-12 19:00 | 6.0267 | 0 | N/A | 0 | 0
2022-12-12 19:30 | 5.7369 | 0 | N/A | 0 | 0
2022-12-12 20:00 | 6.0535 | 0 | N/A | 0 | 0
2022-12-12 20:30 | 6.3925 | 0 | N/A | 0 | 0
2022-12-12 21:00 | 6.4538 | 0 | N/A | 0 | 0
2022-12-12 21:30 | 6.3212 | 0 | N/A | 0 | 0
2022-12-12 22:00 | 5.8703 | 0 | N/A | 0 | 0
2022-12-12 22:30 | 5.7586 | 0 | N/A | 0 | 0
2022-12-12 23:00 | 5.4888 | 0 | N/A | 0 | 0
2022-12-12 23:30 | 5.0925 | 0 | N/A | 0 | 0
2022-12-13 | 4.9888 | 0 | N/A | 0 | 0
2022-12-14 00:30 | 5.7822 | 0 | N/A | 0 | 0
2022-12-14 01:00 | 6.0058 | 0 | N/A | 0 | 0
2022-12-14 01:30 | 5.4016 | 0 | N/A | 0 | 0
2022-12-14 02:00 | 4.7807 | 0 | N/A | 0 | 0
2022-12-14 02:30 | 4.6464 | 0 | N/A | 0 | 0
2022-12-14 03:00 | 4.3143 | 0 | N/A | 0 | 0
2022-12-14 03:30 | 3.9605 | 0 | N/A | 0 | 0
2022-12-14 04:00 | 3.7828 | 0 | N/A | 0 | 0
2022-12-14 04:30 | 3.736 | 0 | N/A | 0 | 0
2022-12-14 05:00 | 3.7712 | 0 | N/A | 0 | 0
2022-12-14 05:30 | 4.0342 | 0 | N/A | 0 | 0
2022-12-14 06:00 | 4.4515 | 0 | N/A | 0 | 0
2022-12-14 06:30 | 5.4135 | 0 | N/A | 0 | 0
2022-12-14 07:00 | 6.1321 | 0 | N/A | 0 | 0
2022-12-14 07:30 | 6.9925 | 0 | N/A | 0 | 0
2022-12-14 08:00 | 7.2471 | 0 | N/A | 0 | 0
2022-12-14 08:30 | 6.5075 | 0 | N/A | 0 | 0
2022-12-14 09:00 | 5.5604 | 0 | N/A | 0 | 0
2022-12-14 09:30 | 4.8775 | 0 | N/A | 0 | 0
2022-12-14 10:00 | 3.6621 | 0 | N/A | 0 | 0
2022-12-14 10:30 | 3.1204 | 0 | N/A | 0 | 0
2022-12-14 11:00 | 2.9235 | 0 | N/A | 0 | 0
2022-12-14 11:30 | 2.1772 | 0 | N/A | 0 | 0
2022-12-14 12:00 | 1.7007 | 0 | N/A | 0 | 0
2022-12-14 12:30 | 2.3858 | 0 | N/A | 0 | 0
2022-12-14 13:00 | 1.497 | 0 | N/A | 0 | 0
2022-12-14 13:30 | 1.4907 | 0 | N/A | 0 | 0
2022-12-14 14:00 | 2.3093 | 0 | N/A | 0 | 0
2022-12-14 14:30 | 1.5444 | 0 | N/A | 0 | 0
2022-12-14 15:00 | 1.6503 | 0 | N/A | 0 | 0
2022-12-14 15:30 | 1.5402 | 0 | N/A | 0 | 0
2022-12-14 16:00 | 1.7773 | 0 | N/A | 0 | 0
2022-12-14 16:30 | 1.4267 | 0 | N/A | 0 | 0
2022-12-14 17:00 | 2.5119 | 0 | N/A | 0 | 0
2022-12-14 17:30 | 2.732 | 0 | N/A | 0 | 0
2022-12-14 18:00 | 4.0442 | 0 | N/A | 0 | 0
2022-12-14 18:30 | 4.7249 | 0 | N/A | 0 | 0
2022-12-14 19:00 | 5.5429 | 0 | N/A | 0 | 0
2022-12-14 19:30 | 5.578 | 0 | N/A | 0 | 0
2022-12-14 20:00 | 6.2094 | 0 | N/A | 0 | 0
2022-12-14 20:30 | 6.6705 | 0 | N/A | 0 | 0
2022-12-14 21:00 | 6.7516 | 0 | N/A | 0 | 0
2022-12-14 21:30 | 6.6447 | 0 | N/A | 0 | 0
2022-12-14 22:00 | 6.2423 | 0 | N/A | 0 | 0
2022-12-14 22:30 | 6.2763 | 0 | N/A | 0 | 0
2022-12-14 23:00 | 5.9897 | 0 | N/A | 0 | 0
2022-12-14 23:30 | 5.5317 | 0 | N/A | 0 | 0
2022-12-15 | 5.4154 | 0 | N/A | 0 | 0
2022-12-15 00:30 | 5.6298 | 0 | N/A | 0 | 0
2022-12-15 01:00 | 5.7891 | 0 | N/A | 0 | 0
2022-12-15 01:30 | 5.1062 | 0 | N/A | 0 | 0
2022-12-15 02:00 | 4.5288 | 0 | N/A | 0 | 0
2022-12-15 02:30 | 4.4201 | 0 | N/A | 0 | 0
2022-12-15 03:00 | 4.2174 | 0 | N/A | 0 | 0
2022-12-15 03:30 | 3.9813 | 0 | N/A | 0 | 0
2022-12-15 04:00 | 3.7777 | 0 | N/A | 0 | 0
2022-12-15 04:30 | 3.6844 | 0 | N/A | 0 | 0
2022-12-15 05:00 | 3.7336 | 0 | N/A | 0 | 0
2022-12-15 05:30 | 3.9477 | 0 | N/A | 0 | 0
2022-12-15 06:00 | 4.2707 | 0 | N/A | 0 | 0
2022-12-15 06:30 | 4.961 | 0 | N/A | 0 | 0
2022-12-15 07:00 | 5.7193 | 0 | N/A | 0 | 0
2022-12-15 07:30 | 6.6263 | 0 | N/A | 0 | 0
2022-12-15 08:00 | 6.9438 | 0 | N/A | 0 | 0
2022-12-15 08:30 | 6.3784 | 0 | N/A | 0 | 0
2022-12-15 09:00 | 4.9434 | 0 | N/A | 0 | 0
2022-12-15 09:30 | 3.7183 | 0 | N/A | 0 | 0
2022-12-15 10:00 | 3.4292 | 0 | N/A | 0 | 0
2022-12-15 10:30 | 2.4158 | 0 | N/A | 0 | 0
2022-12-15 11:00 | 2.3814 | 0 | N/A | 0 | 0
2022-12-15 11:30 | 2.3403 | 0 | N/A | 0 | 0
2022-12-15 12:00 | 1.7042 | 0 | N/A | 0 | 0
2022-12-15 12:30 | 1.48 | 0 | N/A | 0 | 0
2022-12-15 13:00 | 1.3254 | 0 | N/A | 0 | 0
2022-12-15 13:30 | -0.78768 | 0 | N/A | 0 | 0
2022-12-15 14:00 | 0.90706 | 0 | N/A | 0 | 0
2022-12-15 14:30 | 1.042 | 0 | N/A | 0 | 0
2022-12-15 15:00 | 1.3255 | 0 | N/A | 0 | 0
2022-12-15 15:30 | 1.5761 | 0 | N/A | 0 | 0
2022-12-15 16:00 | 2.126 | 0 | N/A | 0 | 0
2022-12-15 16:30 | 2.8007 | 0 | N/A | 0 | 0
2022-12-15 17:00 | 2.1296 | 0 | N/A | 0 | 0
2022-12-15 17:30 | 2.8708 | 0 | N/A | 0 | 0
2022-12-15 18:00 | 3.6778 | 0 | N/A | 0 | 0
2022-12-15 18:30 | 4.3101 | 0 | N/A | 0 | 0
2022-12-15 19:00 | 4.6762 | 0 | N/A | 0 | 0
2022-12-15 19:30 | 5.3923 | 0 | N/A | 0 | 0
2022-12-15 20:00 | 5.7145 | 0 | N/A | 0 | 0
2022-12-15 20:30 | 6.0638 | 0 | N/A | 0 | 0
2022-12-15 21:00 | 6.3409 | 0 | N/A | 0 | 0
2022-12-15 21:30 | 6.3097 | 0 | N/A | 0 | 0
2022-12-15 22:00 | 5.9635 | 0 | N/A | 0 | 0
2022-12-15 22:30 | 5.928 | 0 | N/A | 0 | 0
2022-12-15 23:00 | 5.8098 | 0 | N/A | 0 | 0
2022-12-15 23:30 | 5.3153 | 0 | N/A | 0 | 0
2022-12-16 | 5.228 | 0 | N/A | 0 | 0
2022-12-16 00:30 | 5.3366 | 0 | N/A | 0 | 0
2022-12-16 01:00 | 5.5722 | 0 | N/A | 0 | 0
2022-12-16 01:30 | 4.8694 | 0 | N/A | 0 | 0
2022-12-16 02:00 | 4.3013 | 0 | N/A | 0 | 0
2022-12-16 02:30 | 4.2228 | 0 | N/A | 0 | 0
2022-12-16 03:00 | 3.9985 | 0 | N/A | 0 | 0
2022-12-16 03:30 | 3.653 | 0 | N/A | 0 | 0
2022-12-16 04:00 | 3.4717 | 0 | N/A | 0 | 0
2022-12-16 04:30 | 3.3936 | 0 | N/A | 0 | 0
2022-12-16 05:00 | 3.4129 | 0 | N/A | 0 | 0
2022-12-16 05:30 | 3.641 | 0 | N/A | 0 | 0
2022-12-16 06:00 | 3.9087 | 0 | N/A | 0 | 0
2022-12-16 06:30 | 4.6244 | 0 | N/A | 0 | 0
2022-12-16 07:00 | 5.3711 | 0 | N/A | 0 | 0
2022-12-16 07:30 | 6.0159 | 0 | N/A | 0 | 0
2022-12-16 08:00 | 5.7753 | 0 | N/A | 0 | 0
2022-12-16 08:30 | 4.9938 | 0 | N/A | 0 | 0
2022-12-16 09:00 | 4.3878 | 0 | N/A | 0 | 0
2022-12-16 09:30 | 3.3965 | 0 | N/A | 0 | 0
2022-12-16 10:00 | 2.3885 | 0 | N/A | 0 | 0
2022-12-16 10:30 | 2.0927 | 0 | N/A | 0 | 0
2022-12-16 11:00 | 2.6821 | 0 | N/A | 0 | 0
2022-12-16 11:30 | 2.3093 | 0 | N/A | 0 | 0
2022-12-16 12:00 | 1.8521 | 0 | N/A | 0 | 0
2022-12-16 12:30 | 1.0678 | 0 | N/A | 0 | 0
2022-12-16 13:00 | 1.0937 | 0 | N/A | 0 | 0
2022-12-16 13:30 | 0.71614 | 0 | N/A | 0 | 0
2022-12-16 14:00 | -0.76161 | 0 | N/A | 0 | 0
2022-12-16 14:30 | -0.80056 | 0 | N/A | 0 | 0
2022-12-16 15:00 | -1.0285 | 0 | N/A | 0 | 0
2022-12-16 15:30 | -1.7038 | 0 | N/A | 0 | 0
2022-12-16 16:00 | -2.0075 | 0 | N/A | 0 | 0
2022-12-16 16:30 | -1.8575 | 0 | N/A | 0 | 0
2022-12-16 17:00 | -1.5331 | 0 | N/A | 0 | 0
2022-12-16 17:30 | 1.0641 | 0 | N/A | 0 | 0
2022-12-16 18:00 | 1.5508 | 0 | N/A | 0 | 0
2022-12-16 18:30 | 2.271 | 0 | N/A | 0 | 0
2022-12-16 19:00 | 3.0694 | 0 | N/A | 0 | 0
2022-12-16 19:30 | 3.7937 | 0 | N/A | 0 | 0
2022-12-16 20:00 | 4.3177 | 0 | N/A | 0 | 0
2022-12-16 20:30 | 4.8159 | 0 | N/A | 0 | 0
2022-12-16 21:00 | 5.1654 | 0 | N/A | 0 | 0
2022-12-16 21:30 | 5.2631 | 0 | N/A | 0 | 0
2022-12-16 22:00 | 5.1736 | 0 | N/A | 0 | 0
2022-12-16 22:30 | 5.3349 | 0 | N/A | 0 | 0
2022-12-16 23:00 | 5.3893 | 0 | N/A | 0 | 0
2022-12-16 23:30 | 5.0295 | 0 | N/A | 0 | 0
2022-12-17 | 4.96 | 0 | N/A | 0 | 0
2022-12-17 00:30 | 5.2479 | 0 | N/A | 0 | 0
2022-12-17 01:00 | 5.2895 | 0 | N/A | 0 | 0
2022-12-17 01:30 | 4.5229 | 0 | N/A | 0 | 0
2022-12-17 02:00 | 4.01 | 0 | N/A | 0 | 0
2022-12-17 02:30 | 3.9706 | 0 | N/A | 0 | 0
2022-12-17 03:00 | 3.6973 | 0 | N/A | 0 | 0
2022-12-17 03:30 | 3.4136 | 0 | N/A | 0 | 0
2022-12-17 04:00 | 3.2699 | 0 | N/A | 0 | 0
2022-12-17 04:30 | 3.1275 | 0 | N/A | 0 | 0
2022-12-17 05:00 | 3.1022 | 0 | N/A | 0 | 0
2022-12-17 05:30 | 3.2022 | 0 | N/A | 0 | 0
2022-12-17 06:00 | 3.2608 | 0 | N/A | 0 | 0
2022-12-17 06:30 | 3.5471 | 0 | N/A | 0 | 0
2022-12-17 07:00 | 3.6277 | 0 | N/A | 0 | 0
2022-12-17 07:30 | 3.6651 | 0 | N/A | 0 | 0
2022-12-17 08:00 | 3.6341 | 0 | N/A | 0 | 0
2022-12-17 08:30 | 2.9568 | 0 | N/A | 0 | 0
2022-12-17 09:00 | 2.2727 | 0 | N/A | 0 | 0
2022-12-17 09:30 | 1.6795 | 0 | N/A | 0 | 0
2022-12-17 10:00 | 1.674 | 0 | N/A | 0 | 0
2022-12-17 10:30 | 2.0455 | 0 | N/A | 0 | 0
2022-12-17 11:00 | 1.8851 | 0 | N/A | 0 | 0
2022-12-17 11:30 | 1.4577 | 0 | N/A | 0 | 0
2022-12-17 12:00 | 1.2454 | 0 | N/A | 0 | 0
2022-12-17 12:30 | 1.057 | 0 | N/A | 0 | 0
2022-12-17 13:00 | -0.9187 | 0 | N/A | 0 | 0
2022-12-17 13:30 | -1.1716 | 0 | N/A | 0 | 0
2022-12-17 14:00 | -1.3387 | 0 | N/A | 0 | 0
2022-12-17 14:30 | -0.89055 | 0 | N/A | 0 | 0
2022-12-17 15:00 | -0.95769 | 0 | N/A | 0 | 0
2022-12-17 15:30 | -1.0367 | 0 | N/A | 0 | 0
2022-12-17 16:00 | -1.0164 | 0 | N/A | 0 | 0
2022-12-17 16:30 | -0.98412 | 0 | N/A | 0 | 0
2022-12-17 17:00 | 1.2834 | 0 | N/A | 0 | 0
2022-12-17 17:30 | 1.7817 | 0 | N/A | 0 | 0
2022-12-17 18:00 | 2.6614 | 0 | N/A | 0 | 0
2022-12-17 18:30 | 2.9488 | 0 | N/A | 0 | 0
2022-12-17 19:00 | 3.3146 | 0 | N/A | 0 | 0
2022-12-17 19:30 | 3.8794 | 0 | N/A | 0 | 0
2022-12-17 20:00 | 4.3471 | 0 | N/A | 0 | 0
2022-12-17 20:30 | 4.5969 | 0 | N/A | 0 | 0
2022-12-17 21:00 | 4.8285 | 0 | N/A | 0 | 0
2022-12-17 21:30 | 4.9275 | 0 | N/A | 0 | 0
2022-12-17 22:00 | 4.7603 | 0 | N/A | 0 | 0
2022-12-17 22:30 | 4.9462 | 0 | N/A | 0 | 0
2022-12-17 23:00 | 4.972 | 0 | N/A | 0 | 0
2022-12-17 23:30 | 4.6675 | 0 | N/A | 0 | 0
2022-12-18 | 4.668 | 0 | N/A | 0 | 0
2022-12-18 00:30 | 4.9127 | 0 | N/A | 0 | 0
2022-12-18 01:00 | 5.0953 | 0 | N/A | 0 | 0
2022-12-18 01:30 | 4.529 | 0 | N/A | 0 | 0
2022-12-18 02:00 | 3.9748 | 0 | N/A | 0 | 0
2022-12-18 02:30 | 3.8792 | 0 | N/A | 0 | 0
2022-12-18 03:00 | 3.6716 | 0 | N/A | 0 | 0
2022-12-18 03:30 | 3.4163 | 0 | N/A | 0 | 0
2022-12-18 04:00 | 3.2128 | 0 | N/A | 0 | 0
2022-12-18 04:30 | 3.0652 | 0 | N/A | 0 | 0
2022-12-18 05:00 | 3.0058 | 0 | N/A | 0 | 0
2022-12-18 05:30 | 2.9774 | 0 | N/A | 0 | 0
2022-12-18 06:00 | 3.0832 | 0 | N/A | 0 | 0
2022-12-18 06:30 | 3.3109 | 0 | N/A | 0 | 0
2022-12-18 07:00 | 3.2975 | 0 | N/A | 0 | 0
2022-12-18 07:30 | 3.1931 | 0 | N/A | 0 | 0
2022-12-18 08:00 | 2.9755 | 0 | N/A | 0 | 0
2022-12-18 08:30 | 2.2827 | 0 | N/A | 0 | 0
2022-12-18 09:00 | 1.7407 | 0 | N/A | 0 | 0
2022-12-18 09:30 | 1.1747 | 0 | N/A | 0 | 0
2022-12-18 10:00 | -0.9294 | 0 | N/A | 0 | 0
2022-12-18 10:30 | -1.1942 | 0 | N/A | 0 | 0
2022-12-18 11:00 | -1.6921 | 0 | N/A | 0 | 0
2022-12-18 11:30 | -1.8899 | 0 | N/A | 0 | 0
2022-12-18 12:00 | -2.2353 | 0 | N/A | 0 | 0
2022-12-18 12:30 | -2.4279 | 0 | N/A | 0 | 0
2022-12-18 13:00 | -2.5735 | 0 | N/A | 0 | 0
2022-12-18 13:30 | -2.6889 | 0 | N/A | 0 | 0
2022-12-18 14:00 | -2.8673 | 0 | N/A | 0 | 0
2022-12-18 14:30 | -2.8582 | 0 | N/A | 0 | 0
2022-12-18 15:00 | -2.7916 | 0 | N/A | 0 | 0
2022-12-18 15:30 | -2.638 | 0 | N/A | 0 | 0
2022-12-18 16:00 | -2.3924 | 0 | N/A | 0 | 0
2022-12-18 16:30 | -1.8205 | 0 | N/A | 0 | 0
2022-12-18 17:00 | -1.2687 | 0 | N/A | 0 | 0
2022-12-18 17:30 | -0.91042 | 0 | N/A | 0 | 0
2022-12-18 18:00 | 1.3557 | 0 | N/A | 0 | 0
2022-12-18 18:30 | 2.2726 | 0 | N/A | 0 | 0
2022-12-18 19:00 | 3.1148 | 0 | N/A | 0 | 0
2022-12-18 19:30 | 3.7012 | 0 | N/A | 0 | 0
2022-12-18 20:00 | 4.1207 | 0 | N/A | 0 | 0
2022-12-18 20:30 | 4.4807 | 0 | N/A | 0 | 0
2022-12-18 21:00 | 4.6983 | 0 | N/A | 0 | 0
2022-12-18 21:30 | 4.8042 | 0 | N/A | 0 | 0
2022-12-18 22:00 | 4.652 | 0 | N/A | 0 | 0
2022-12-18 22:30 | 4.7449 | 0 | N/A | 0 | 0
2022-12-18 23:00 | 4.704 | 0 | N/A | 0 | 0
2022-12-18 23:30 | 4.4885 | 0 | N/A | 0 | 0
2022-12-19 | 4.469 | 0 | N/A | 0 | 0
2022-12-19 00:30 | 4.6021 | 0 | N/A | 0 | 0
2022-12-19 01:00 | 4.8949 | 0 | N/A | 0 | 0
2022-12-19 01:30 | 4.2885 | 0 | N/A | 0 | 0
2022-12-19 02:00 | 3.7075 | 0 | N/A | 0 | 0
2022-12-19 02:30 | 3.7183 | 0 | N/A | 0 | 0
2022-12-19 03:00 | 3.5303 | 0 | N/A | 0 | 0
2022-12-19 03:30 | 3.2325 | 0 | N/A | 0 | 0
2022-12-19 04:00 | 2.95 | 0 | N/A | 0 | 0
2022-12-19 04:30 | 2.9074 | 0 | N/A | 0 | 0
2022-12-19 05:00 | 2.8951 | 0 | N/A | 0 | 0
2022-12-19 05:30 | 3.0666 | 0 | N/A | 0 | 0
2022-12-19 06:00 | 3.3527 | 0 | N/A | 0 | 0
2022-12-19 06:30 | 3.7332 | 0 | N/A | 0 | 0
2022-12-19 07:00 | 4.2531 | 0 | N/A | 0 | 0
2022-12-19 07:30 | 4.6296 | 0 | N/A | 0 | 0
2022-12-19 08:00 | 4.3427 | 0 | N/A | 0 | 0
2022-12-19 08:30 | 3.2948 | 0 | N/A | 0 | 0
2022-12-19 09:00 | 2.4764 | 0 | N/A | 0 | 0
2022-12-19 09:30 | 1.558 | 0 | N/A | 0 | 0
2022-12-19 10:00 | 0.87613 | 0 | N/A | 0 | 0
2022-12-19 10:30 | -0.59034 | 0 | N/A | 0 | 0
2022-12-19 11:00 | -0.83113 | 0 | N/A | 0 | 0
2022-12-19 11:30 | -1.1164 | 0 | N/A | 0 | 0
2022-12-19 12:00 | -1.3373 | 0 | N/A | 0 | 0
2022-12-19 12:30 | -1.4921 | 0 | N/A | 0 | 0
2022-12-19 13:00 | -1.6011 | 0 | N/A | 0 | 0
2022-12-19 13:30 | -1.5395 | 0 | N/A | 0 | 0
2022-12-19 14:00 | -1.5317 | 0 | N/A | 0 | 0
2022-12-19 14:30 | -1.3093 | 0 | N/A | 0 | 0
2022-12-19 15:00 | -1.5906 | 0 | N/A | 0 | 0
2022-12-19 15:30 | -1.4448 | 0 | N/A | 0 | 0
2022-12-19 16:00 | -1.1947 | 0 | N/A | 0 | 0
2022-12-19 16:30 | -0.78786 | 0 | N/A | 0 | 0
2022-12-19 17:00 | -0.71169 | 0 | N/A | 0 | 0
2022-12-19 17:30 | 0.92021 | 0 | N/A | 0 | 0
2022-12-19 18:00 | 1.9135 | 0 | N/A | 0 | 0
2022-12-19 18:30 | 2.9006 | 0 | N/A | 0 | 0
2022-12-19 19:00 | 3.6672 | 0 | N/A | 0 | 0
2022-12-19 19:30 | 4.1745 | 0 | N/A | 0 | 0
2022-12-19 20:00 | 4.5169 | 0 | N/A | 0 | 0
2022-12-19 20:30 | 4.6821 | 0 | N/A | 0 | 0
2022-12-19 21:00 | 4.7257 | 0 | N/A | 0 | 0
2022-12-19 21:30 | 4.6764 | 0 | N/A | 0 | 0
2022-12-19 22:00 | 4.4993 | 0 | N/A | 0 | 0
2022-12-19 22:30 | 4.6519 | 0 | N/A | 0 | 0
2022-12-19 23:00 | 4.6486 | 0 | N/A | 0 | 0
2022-12-19 23:30 | 4.3587 | 0 | N/A | 0 | 0
2022-12-20 | 4.3571 | 0 | N/A | 0 | 0
2022-12-20 00:30 | 4.6878 | 0 | N/A | 0 | 0
2022-12-20 01:00 | 4.8224 | 0 | N/A | 0 | 0
2022-12-20 01:30 | 4.091 | 0 | N/A | 0 | 0
2022-12-20 02:00 | 3.6126 | 0 | N/A | 0 | 0
2022-12-20 02:30 | 3.4825 | 0 | N/A | 0 | 0
2022-12-20 03:00 | 3.2692 | 0 | N/A | 0 | 0
2022-12-20 03:30 | 3.0664 | 0 | N/A | 0 | 0
2022-12-20 04:00 | 2.8899 | 0 | N/A | 0 | 0
2022-12-20 04:30 | 2.859 | 0 | N/A | 0 | 0
2022-12-20 05:00 | 2.8603 | 0 | N/A | 0 | 0
2022-12-20 05:30 | 3.0196 | 0 | N/A | 0 | 0
2022-12-20 06:00 | 3.3257 | 0 | N/A | 0 | 0
2022-12-20 06:30 | 3.854 | 0 | N/A | 0 | 0
2022-12-20 07:00 | 4.2743 | 0 | N/A | 0 | 0
2022-12-20 07:30 | 4.451 | 0 | N/A | 0 | 0
2022-12-20 08:00 | 4.1513 | 0 | N/A | 0 | 0
2022-12-20 08:30 | 3.0259 | 0 | N/A | 0 | 0
2022-12-20 09:00 | 2.1599 | 0 | N/A | 0 | 0
2022-12-20 09:30 | 1.2771 | 0 | N/A | 0 | 0
2022-12-20 10:00 | 0.6148 | 0 | N/A | 0 | 0
2022-12-20 10:30 | -0.69642 | 0 | N/A | 0 | 0
2022-12-20 11:00 | -1.0011 | 0 | N/A | 0 | 0
2022-12-20 11:30 | -1.3003 | 0 | N/A | 0 | 0
2022-12-20 12:00 | -1.5202 | 0 | N/A | 0 | 0
2022-12-20 12:30 | -1.5766 | 0 | N/A | 0 | 0
2022-12-20 13:00 | -1.6421 | 0 | N/A | 0 | 0
2022-12-20 13:30 | -1.7199 | 0 | N/A | 0 | 0
2022-12-20 14:00 | -1.8128 | 0 | N/A | 0 | 0
2022-12-20 14:30 | -1.7763 | 0 | N/A | 0 | 0
2022-12-20 15:00 | -1.6194 | 0 | N/A | 0 | 0
2022-12-20 15:30 | -1.279 | 0 | N/A | 0 | 0
2022-12-20 16:00 | -0.59165 | 0 | N/A | 0 | 0
2022-12-20 16:30 | 1.2095 | 0 | N/A | 0 | 0
2022-12-20 17:00 | 1.356 | 0 | N/A | 0 | 0
2022-12-20 17:30 | 1.422 | 0 | N/A | 0 | 0
2022-12-20 18:00 | 2.4147 | 0 | N/A | 0 | 0
2022-12-20 18:30 | 3.1117 | 0 | N/A | 0 | 0
2022-12-20 19:00 | 3.7506 | 0 | N/A | 0 | 0
2022-12-20 19:30 | 4.1653 | 0 | N/A | 0 | 0
2022-12-20 20:00 | 4.5476 | 0 | N/A | 0 | 0
2022-12-20 20:30 | 4.702 | 0 | N/A | 0 | 0
2022-12-20 21:00 | 4.7281 | 0 | N/A | 0 | 0
2022-12-20 21:30 | 4.6863 | 0 | N/A | 0 | 0
2022-12-20 22:00 | 4.5384 | 0 | N/A | 0 | 0
2022-12-20 22:30 | 4.6734 | 0 | N/A | 0 | 0
2022-12-20 23:00 | 4.5889 | 0 | N/A | 0 | 0
2022-12-20 23:30 | 4.2854 | 0 | N/A | 0 | 0
2022-12-21 | 4.1403 | 0 | N/A | 0 | 0
2022-12-22 00:30 | 4.5078 | 0 | N/A | 0 | 0
2022-12-22 01:00 | 4.6779 | 0 | N/A | 0 | 0
2022-12-22 01:30 | 4.0042 | 0 | N/A | 0 | 0
2022-12-22 02:00 | 3.473 | 0 | N/A | 0 | 0
2022-12-22 02:30 | 3.3632 | 0 | N/A | 0 | 0
2022-12-22 03:00 | 3.1449 | 0 | N/A | 0 | 0
2022-12-22 03:30 | 2.8521 | 0 | N/A | 0 | 0
2022-12-22 04:00 | 2.7181 | 0 | N/A | 0 | 0
2022-12-22 04:30 | 2.7002 | 0 | N/A | 0 | 0
2022-12-22 05:00 | 2.7351 | 0 | N/A | 0 | 0
2022-12-22 05:30 | 2.7647 | 0 | N/A | 0 | 0
2022-12-22 06:30 | 0 | 0 | N/A | 0 | 0
2022-12-22 07:00 | 4.2969 | 0 | N/A | 0 | 0
2022-12-22 07:30 | 5.5532 | 0 | N/A | 0 | 0
2022-12-22 08:00 | 5.2078 | 0 | N/A | 0 | 0
2022-12-22 08:30 | 3.1604 | 0 | N/A | 0 | 0
2022-12-22 09:00 | 2.3336 | 0 | N/A | 0 | 0
2022-12-22 09:30 | 2.4581 | 0 | N/A | 0 | 0
2022-12-22 10:00 | 2.4751 | 0 | N/A | 0 | 0
2022-12-22 10:30 | 2.2587 | 0 | N/A | 0 | 0
2022-12-22 11:00 | -0.79298 | 0 | N/A | 0 | 0
2022-12-22 11:30 | -0.73932 | 0 | N/A | 0 | 0
2022-12-22 12:00 | 1.2059 | 0 | N/A | 0 | 0
2022-12-22 12:30 | 0.70229 | 0 | N/A | 0 | 0
2022-12-22 13:00 | -2.3767 | 0 | N/A | 0 | 0
2022-12-22 13:30 | -2.4282 | 0 | N/A | 0 | 0
2022-12-22 14:00 | -1.652 | 0 | N/A | 0 | 0
2022-12-22 14:30 | -1.2565 | 0 | N/A | 0 | 0
2022-12-22 15:00 | -0.77078 | 0 | N/A | 0 | 0
2022-12-22 15:30 | 1.349 | 0 | N/A | 0 | 0
2022-12-22 16:00 | 2.0795 | 0 | N/A | 0 | 0
2022-12-22 16:30 | -1.1606 | 0 | N/A | 0 | 0
2022-12-22 17:00 | -0.71525 | 0 | N/A | 0 | 0
2022-12-22 17:30 | 1.5525 | 0 | N/A | 0 | 0
2022-12-22 18:00 | 4.2234 | 0 | N/A | 0 | 0
2022-12-22 18:30 | 4.7852 | 0 | N/A | 0 | 0
2022-12-22 19:00 | 4.5736 | 0 | N/A | 0 | 0
2022-12-22 19:30 | 4.3314 | 0 | N/A | 0 | 0
2022-12-22 20:00 | 4.6274 | 0 | N/A | 0 | 0
2022-12-22 20:30 | 4.4586 | 0 | N/A | 0 | 0
2022-12-22 21:00 | 4.5088 | 0 | N/A | 0 | 0
2022-12-22 21:30 | 4.4417 | 0 | N/A | 0 | 0
2022-12-22 22:00 | 4.2789 | 0 | N/A | 0 | 0
2022-12-22 22:30 | 4.4821 | 0 | N/A | 0 | 0
2022-12-22 23:00 | 4.5589 | 0 | N/A | 0 | 0
2022-12-22 23:30 | 4.2326 | 0 | N/A | 0 | 0
2022-12-23 | 4.2614 | 0 | N/A | 0 | 0
2022-12-23 00:30 | 4.6301 | 0 | N/A | 0 | 0
2022-12-23 01:00 | 4.7012 | 0 | N/A | 0 | 0
2022-12-23 01:30 | 3.9254 | 0 | N/A | 0 | 0
2022-12-23 02:00 | 3.5023 | 0 | N/A | 0 | 0
2022-12-23 02:30 | 3.423 | 0 | N/A | 0 | 0
2022-12-23 03:00 | 3.144 | 0 | N/A | 0 | 0
2022-12-23 03:30 | 2.886 | 0 | N/A | 0 | 0
2022-12-23 04:00 | 2.7414 | 0 | N/A | 0 | 0
2022-12-23 04:30 | 2.692 | 0 | N/A | 0 | 0
2022-12-23 05:00 | 2.6663 | 0 | N/A | 0 | 0
2022-12-23 05:30 | 2.736 | 0 | N/A | 0 | 0
2022-12-23 06:00 | 2.9278 | 0 | N/A | 0 | 0
2022-12-23 06:30 | 3.1143 | 0 | N/A | 0 | 0
2022-12-23 07:00 | 3.2757 | 0 | N/A | 0 | 0
2022-12-23 07:30 | 3.3271 | 0 | N/A | 0 | 0
2022-12-23 08:00 | 3.2169 | 0 | N/A | 0 | 0
2022-12-23 08:30 | 2.9601 | 0 | N/A | 0 | 0
2022-12-23 09:00 | 2.9353 | 0 | N/A | 0 | 0
2022-12-23 09:30 | 2.6826 | 0 | N/A | 0 | 0
2022-12-23 10:00 | 2.6703 | 0 | N/A | 0 | 0
2022-12-23 10:30 | 2.4983 | 0 | N/A | 0 | 0
2022-12-23 11:00 | 2.6112 | 0 | N/A | 0 | 0
2022-12-23 11:30 | 2.6488 | 0 | N/A | 0 | 0
2022-12-23 12:00 | 2.2541 | 0 | N/A | 0 | 0
2022-12-23 12:30 | 2.1098 | 0 | N/A | 0 | 0
2022-12-23 13:00 | 0.8753 | 0 | N/A | 0 | 0
2022-12-23 13:30 | 0.89641 | 0 | N/A | 0 | 0
2022-12-23 14:00 | 0.91958 | 0 | N/A | 0 | 0
2022-12-23 14:30 | -0.90557 | 0 | N/A | 0 | 0
2022-12-23 15:00 | 0.94265 | 0 | N/A | 0 | 0
2022-12-23 15:30 | 1.4025 | 0 | N/A | 0 | 0
2022-12-23 16:00 | 1.0948 | 0 | N/A | 0 | 0
2022-12-23 16:30 | -0.86829 | 0 | N/A | 0 | 0
2022-12-23 17:00 | -0.86617 | 0 | N/A | 0 | 0
2022-12-23 17:30 | 1.1293 | 0 | N/A | 0 | 0
2022-12-23 18:00 | 2.0023 | 0 | N/A | 0 | 0
2022-12-23 18:30 | 2.8867 | 0 | N/A | 0 | 0
2022-12-23 19:00 | 3.7509 | 0 | N/A | 0 | 0
2022-12-23 19:30 | 4.1836 | 0 | N/A | 0 | 0
2022-12-23 20:00 | 4.4842 | 0 | N/A | 0 | 0
2022-12-23 20:30 | 4.5492 | 0 | N/A | 0 | 0
2022-12-23 21:00 | 4.5516 | 0 | N/A | 0 | 0
2022-12-23 21:30 | 4.4861 | 0 | N/A | 0 | 0
2022-12-23 22:00 | 4.3219 | 0 | N/A | 0 | 0
2022-12-23 22:30 | 4.6495 | 0 | N/A | 0 | 0
2022-12-23 23:00 | 4.7297 | 0 | N/A | 0 | 0
2022-12-23 23:30 | 4.4492 | 0 | N/A | 0 | 0
2022-12-24 | 4.4024 | 0 | N/A | 0 | 0
2022-12-24 00:30 | 4.7136 | 0 | N/A | 0 | 0
2022-12-24 01:00 | 4.8653 | 0 | N/A | 0 | 0
2022-12-24 01:30 | 4.1323 | 0 | N/A | 0 | 0
2022-12-24 02:00 | 3.6302 | 0 | N/A | 0 | 0
2022-12-24 02:30 | 3.4778 | 0 | N/A | 0 | 0
2022-12-24 03:00 | 3.2556 | 0 | N/A | 0 | 0
2022-12-24 03:30 | 2.9428 | 0 | N/A | 0 | 0
2022-12-24 04:00 | 2.75 | 0 | N/A | 0 | 0
2022-12-24 04:30 | 2.6681 | 0 | N/A | 0 | 0
2022-12-24 05:00 | 2.6549 | 0 | N/A | 0 | 0
2022-12-24 05:30 | 2.7074 | 0 | N/A | 0 | 0
2022-12-24 06:00 | 2.7498 | 0 | N/A | 0 | 0
2022-12-24 06:30 | 2.8519 | 0 | N/A | 0 | 0
2022-12-24 07:00 | 2.792 | 0 | N/A | 0 | 0
2022-12-24 07:30 | 2.895 | 0 | N/A | 0 | 0
2022-12-24 08:00 | 2.816 | 0 | N/A | 0 | 0
2022-12-24 08:30 | 2.2154 | 0 | N/A | 0 | 0
2022-12-24 09:00 | 2.1394 | 0 | N/A | 0 | 0
2022-12-24 09:30 | 1.4633 | 0 | N/A | 0 | 0
2022-12-24 10:00 | 1.0375 | 0 | N/A | 0 | 0
2022-12-24 10:30 | -0.93392 | 0 | N/A | 0 | 0
2022-12-24 11:00 | -1.2656 | 0 | N/A | 0 | 0
2022-12-24 11:30 | -1.5355 | 0 | N/A | 0 | 0
2022-12-24 12:00 | -1.7407 | 0 | N/A | 0 | 0
2022-12-24 12:30 | -1.9233 | 0 | N/A | 0 | 0
2022-12-24 13:00 | -2.0139 | 0 | N/A | 0 | 0
2022-12-24 13:30 | -2.1839 | 0 | N/A | 0 | 0
2022-12-24 14:00 | -2.2001 | 0 | N/A | 0 | 0
2022-12-24 14:30 | -2.1805 | 0 | N/A | 0 | 0
2022-12-24 15:00 | -1.9904 | 0 | N/A | 0 | 0
2022-12-24 15:30 | -1.7619 | 0 | N/A | 0 | 0
2022-12-24 16:00 | -1.3897 | 0 | N/A | 0 | 0
2022-12-24 16:30 | -0.9595 | 0 | N/A | 0 | 0
2022-12-24 17:00 | -0.67119 | 0 | N/A | 0 | 0
2022-12-24 17:30 | 1.0679 | 0 | N/A | 0 | 0
2022-12-24 18:00 | 1.8646 | 0 | N/A | 0 | 0
2022-12-24 18:30 | 2.8147 | 0 | N/A | 0 | 0
2022-12-24 19:00 | 3.6506 | 0 | N/A | 0 | 0
2022-12-24 19:30 | 4.2324 | 0 | N/A | 0 | 0
2022-12-24 20:00 | 4.4258 | 0 | N/A | 0 | 0
2022-12-24 20:30 | 4.4837 | 0 | N/A | 0 | 0
2022-12-24 21:00 | 4.5856 | 0 | N/A | 0 | 0
2022-12-24 21:30 | 4.5977 | 0 | N/A | 0 | 0
2022-12-24 22:00 | 4.4416 | 0 | N/A | 0 | 0
2022-12-24 22:30 | 4.6874 | 0 | N/A | 0 | 0
2022-12-24 23:00 | 4.8298 | 0 | N/A | 0 | 0
2022-12-24 23:30 | 4.58 | 0 | N/A | 0 | 0
2022-12-25 | 4.5578 | 0 | N/A | 0 | 0
2022-12-25 00:30 | 4.567 | 0 | N/A | 0 | 0
2022-12-25 01:00 | 4.7928 | 0 | N/A | 0 | 0
2022-12-25 01:30 | 4.1906 | 0 | N/A | 0 | 0
2022-12-25 02:00 | 3.676 | 0 | N/A | 0 | 0
2022-12-25 02:30 | 3.5779 | 0 | N/A | 0 | 0
2022-12-25 03:00 | 3.2661 | 0 | N/A | 0 | 0
2022-12-25 03:30 | 2.9218 | 0 | N/A | 0 | 0
2022-12-25 04:00 | 2.7784 | 0 | N/A | 0 | 0
2022-12-25 04:30 | 2.724 | 0 | N/A | 0 | 0
2022-12-25 05:00 | 2.6205 | 0 | N/A | 0 | 0
2022-12-25 05:30 | 2.6271 | 0 | N/A | 0 | 0
2022-12-25 06:00 | 2.6886 | 0 | N/A | 0 | 0
2022-12-25 06:30 | 2.7851 | 0 | N/A | 0 | 0
2022-12-25 07:00 | 2.8649 | 0 | N/A | 0 | 0
2022-12-25 07:30 | 2.9347 | 0 | N/A | 0 | 0
2022-12-25 08:00 | 2.6716 | 0 | N/A | 0 | 0
2022-12-25 08:30 | 2.2188 | 0 | N/A | 0 | 0
2022-12-25 09:00 | 1.7264 | 0 | N/A | 0 | 0
2022-12-25 09:30 | 1.2731 | 0 | N/A | 0 | 0
2022-12-25 10:00 | 0.97824 | 0 | N/A | 0 | 0
2022-12-25 10:30 | -0.87423 | 0 | N/A | 0 | 0
2022-12-25 11:00 | -0.90751 | 0 | N/A | 0 | 0
2022-12-25 11:30 | -1.05 | 0 | N/A | 0 | 0
2022-12-25 12:00 | -1.158 | 0 | N/A | 0 | 0
2022-12-25 12:30 | -1.2868 | 0 | N/A | 0 | 0
2022-12-25 13:00 | -1.535 | 0 | N/A | 0 | 0
2022-12-25 13:30 | -1.8599 | 0 | N/A | 0 | 0
2022-12-25 14:00 | -2.1013 | 0 | N/A | 0 | 0
2022-12-25 14:30 | -2.1238 | 0 | N/A | 0 | 0
2022-12-25 15:00 | -1.9226 | 0 | N/A | 0 | 0
2022-12-25 15:30 | -1.5692 | 0 | N/A | 0 | 0
2022-12-25 16:00 | -1.0956 | 0 | N/A | 0 | 0
2022-12-25 16:30 | -0.72523 | 0 | N/A | 0 | 0
2022-12-25 17:00 | 0.8998 | 0 | N/A | 0 | 0
2022-12-25 17:30 | 1.6241 | 0 | N/A | 0 | 0
2022-12-25 18:00 | 2.6064 | 0 | N/A | 0 | 0
2022-12-25 18:30 | 3.5977 | 0 | N/A | 0 | 0
2022-12-25 19:00 | 4.522 | 0 | N/A | 0 | 0
2022-12-25 19:30 | 5.1244 | 0 | N/A | 0 | 0
2022-12-25 20:00 | 5.2104 | 0 | N/A | 0 | 0
2022-12-25 20:30 | 5.251 | 0 | N/A | 0 | 0
2022-12-25 21:00 | 5.1227 | 0 | N/A | 0 | 0
2022-12-25 21:30 | 4.8547 | 0 | N/A | 0 | 0
2022-12-25 22:00 | 4.5837 | 0 | N/A | 0 | 0
2022-12-25 22:30 | 4.723 | 0 | N/A | 0 | 0
2022-12-25 23:00 | 4.707 | 0 | N/A | 0 | 0
2022-12-25 23:30 | 4.3357 | 0 | N/A | 0 | 0
2022-12-26 | 4.2998 | 0 | N/A | 0 | 0
2022-12-26 00:30 | 4.5192 | 0 | N/A | 0 | 0
2022-12-26 01:00 | 4.6535 | 0 | N/A | 0 | 0
2022-12-26 01:30 | 4.0184 | 0 | N/A | 0 | 0
2022-12-26 02:00 | 3.4292 | 0 | N/A | 0 | 0
2022-12-26 02:30 | 3.3877 | 0 | N/A | 0 | 0
2022-12-26 03:00 | 3.1457 | 0 | N/A | 0 | 0
2022-12-26 03:30 | 2.8461 | 0 | N/A | 0 | 0
2022-12-26 04:00 | 2.7103 | 0 | N/A | 0 | 0
2022-12-26 04:30 | 2.6523 | 0 | N/A | 0 | 0
2022-12-26 05:00 | 2.6433 | 0 | N/A | 0 | 0
2022-12-26 05:30 | 2.6773 | 0 | N/A | 0 | 0
2022-12-26 06:00 | 2.7106 | 0 | N/A | 0 | 0
2022-12-26 06:30 | 2.7331 | 0 | N/A | 0 | 0
2022-12-26 07:00 | 2.6765 | 0 | N/A | 0 | 0
2022-12-26 07:30 | 2.5806 | 0 | N/A | 0 | 0
2022-12-26 08:00 | 2.2998 | 0 | N/A | 0 | 0
2022-12-26 08:30 | 2.0915 | 0 | N/A | 0 | 0
2022-12-26 09:00 | 1.6769 | 0 | N/A | 0 | 0
2022-12-26 09:30 | 1.9415 | 0 | N/A | 0 | 0
2022-12-26 10:00 | 2.0203 | 0 | N/A | 0 | 0
2022-12-26 10:30 | 1.5544 | 0 | N/A | 0 | 0
2022-12-26 11:00 | 0.87677 | 0 | N/A | 0 | 0
2022-12-26 11:30 | 0.52684 | 0 | N/A | 0 | 0
2022-12-26 12:00 | -0.5362 | 0 | N/A | 0 | 0
2022-12-26 12:30 | -0.56475 | 0 | N/A | 0 | 0
2022-12-26 13:00 | -0.44294 | 0 | N/A | 0 | 0
2022-12-26 13:30 | -0.37204 | 0 | N/A | 0 | 0
2022-12-26 14:00 | 0.46236 | 0 | N/A | 0 | 0
2022-12-26 14:30 | 1.2133 | 0 | N/A | 0 | 0
2022-12-26 15:00 | 2.6988 | 0 | N/A | 0 | 0
2022-12-26 15:30 | 1.9403 | 0 | N/A | 0 | 0
2022-12-26 16:00 | 2.0748 | 0 | N/A | 0 | 0
2022-12-26 16:30 | 2.8492 | 0 | N/A | 0 | 0
2022-12-26 17:00 | 4.1235 | 0 | N/A | 0 | 0
2022-12-26 17:30 | 4.6249 | 0 | N/A | 0 | 0
2022-12-26 18:00 | 6.8672 | 0 | N/A | 0 | 0
2022-12-26 18:30 | 6.7887 | 0 | N/A | 0 | 0
2022-12-26 19:00 | 6.8467 | 0 | N/A | 0 | 0
2022-12-26 19:30 | 7.5706 | 0 | N/A | 0 | 0
2022-12-26 20:00 | 7.6838 | 0 | N/A | 0 | 0
2022-12-26 20:30 | 7.6081 | 0 | N/A | 0 | 0
2022-12-26 21:00 | 7.2293 | 0 | N/A | 0 | 0
2022-12-26 21:30 | 6.5921 | 0 | N/A | 0 | 0
2022-12-26 22:00 | 6.1139 | 0 | N/A | 0 | 0
2022-12-26 22:30 | 5.8935 | 0 | N/A | 0 | 0
2022-12-26 23:00 | 5.5621 | 0 | N/A | 0 | 0
2022-12-26 23:30 | 4.9928 | 0 | N/A | 0 | 0
2022-12-27 | 4.7726 | 0 | N/A | 0 | 0
2022-12-27 00:30 | 4.987 | 0 | N/A | 0 | 0
2022-12-27 01:00 | 5.0356 | 0 | N/A | 0 | 0
2022-12-27 01:30 | 4.2414 | 0 | N/A | 0 | 0
2022-12-27 02:00 | 3.6282 | 0 | N/A | 0 | 0
2022-12-27 02:30 | 3.5504 | 0 | N/A | 0 | 0
2022-12-27 03:00 | 3.2726 | 0 | N/A | 0 | 0
2022-12-27 03:30 | 3.0356 | 0 | N/A | 0 | 0
2022-12-27 04:00 | 2.9128 | 0 | N/A | 0 | 0
2022-12-27 04:30 | 2.8599 | 0 | N/A | 0 | 0
2022-12-27 05:00 | 2.7945 | 0 | N/A | 0 | 0
2022-12-27 05:30 | 2.7987 | 0 | N/A | 0 | 0
2022-12-27 06:00 | 2.8736 | 0 | N/A | 0 | 0
2022-12-27 06:30 | 3.0045 | 0 | N/A | 0 | 0
2022-12-27 07:00 | 2.8431 | 0 | N/A | 0 | 0
2022-12-27 07:30 | 2.8567 | 0 | N/A | 0 | 0
2022-12-27 08:00 | 2.6605 | 0 | N/A | 0 | 0
2022-12-27 08:30 | 2.1232 | 0 | N/A | 0 | 0
2022-12-27 09:00 | 1.8274 | 0 | N/A | 0 | 0
2022-12-27 09:30 | 1.5004 | 0 | N/A | 0 | 0
2022-12-27 10:00 | 1.1708 | 0 | N/A | 0 | 0
2022-12-27 10:30 | 0.85451 | 0 | N/A | 0 | 0
2022-12-27 11:00 | 0.72334 | 0 | N/A | 0 | 0
2022-12-27 11:30 | 0.68131 | 0 | N/A | 0 | 0
2022-12-27 12:00 | 0.73179 | 0 | N/A | 0 | 0
2022-12-27 12:30 | 1.0316 | 0 | N/A | 0 | 0
2022-12-27 13:00 | 1.2281 | 0 | N/A | 0 | 0
2022-12-27 13:30 | 1.4448 | 0 | N/A | 0 | 0
2022-12-27 14:00 | 1.695 | 0 | N/A | 0 | 0
2022-12-27 14:30 | 2.0361 | 0 | N/A | 0 | 0
2022-12-27 15:00 | 2.375 | 0 | N/A | 0 | 0
2022-12-27 15:30 | 4.1986 | 0 | N/A | 0 | 0
2022-12-27 16:00 | 5.0622 | 0 | N/A | 0 | 0
2022-12-27 16:30 | 4.8184 | 0 | N/A | 0 | 0
2022-12-27 17:00 | 4.9721 | 0 | N/A | 0 | 0
2022-12-27 17:30 | 6.2332 | 0 | N/A | 0 | 0
2022-12-27 18:00 | 6.9845 | 0 | N/A | 0 | 0
2022-12-27 18:30 | 7.9838 | 0 | N/A | 0 | 0
2022-12-27 19:00 | 8.9039 | 0 | N/A | 0 | 0
2022-12-27 19:30 | 9.2306 | 0 | N/A | 0 | 0
2022-12-27 20:00 | 9.2249 | 0 | N/A | 0 | 0
2022-12-27 20:30 | 8.8855 | 0 | N/A | 0 | 0
2022-12-27 21:00 | 8.2462 | 0 | N/A | 0 | 0
2022-12-27 21:30 | 7.659 | 0 | N/A | 0 | 0
2022-12-27 22:00 | 7.1218 | 0 | N/A | 0 | 0
2022-12-27 22:30 | 6.8512 | 0 | N/A | 0 | 0
2022-12-27 23:00 | 6.368 | 0 | N/A | 0 | 0
2022-12-27 23:30 | 5.7465 | 0 | N/A | 0 | 0
2022-12-28 | 5.4687 | 0 | N/A | 0 | 0
2022-12-28 00:30 | 5.4714 | 0 | N/A | 0 | 0
2022-12-28 01:00 | 5.3024 | 0 | N/A | 0 | 0
2022-12-28 01:30 | 4.4377 | 0 | N/A | 0 | 0
2022-12-28 02:00 | 3.9311 | 0 | N/A | 0 | 0
2022-12-28 02:30 | 3.8735 | 0 | N/A | 0 | 0
2022-12-28 03:00 | 3.614 | 0 | N/A | 0 | 0
2022-12-28 03:30 | 3.3525 | 0 | N/A | 0 | 0
2022-12-28 04:00 | 3.1916 | 0 | N/A | 0 | 0
2022-12-28 04:30 | 3.118 | 0 | N/A | 0 | 0
2022-12-28 05:00 | 3.1011 | 0 | N/A | 0 | 0
2022-12-28 05:30 | 3.1581 | 0 | N/A | 0 | 0
2022-12-28 06:00 | 3.2309 | 0 | N/A | 0 | 0
2022-12-28 06:30 | 3.4244 | 0 | N/A | 0 | 0
2022-12-28 07:00 | 3.5066 | 0 | N/A | 0 | 0
2022-12-28 07:30 | 3.7294 | 0 | N/A | 0 | 0
2022-12-28 08:00 | 3.8044 | 0 | N/A | 0 | 0
2022-12-28 08:30 | 3.5574 | 0 | N/A | 0 | 0
2022-12-28 09:00 | 3.422 | 0 | N/A | 0 | 0
2022-12-28 09:30 | 3.3195 | 0 | N/A | 0 | 0
2022-12-28 10:00 | 2.8759 | 0 | N/A | 0 | 0
2022-12-28 10:30 | 3.1101 | 0 | N/A | 0 | 0
2022-12-28 11:00 | 3.5427 | 0 | N/A | 0 | 0
2022-12-28 11:30 | 3.3802 | 0 | N/A | 0 | 0
2022-12-28 12:00 | 3.703 | 0 | N/A | 0 | 0
2022-12-28 12:30 | 4.1061 | 0 | N/A | 0 | 0
2022-12-28 13:00 | 4.3829 | 0 | N/A | 0 | 0
2022-12-28 13:30 | 4.3201 | 0 | N/A | 0 | 0
2022-12-28 14:00 | 4.059 | 0 | N/A | 0 | 0
2022-12-28 14:30 | 3.4084 | 0 | N/A | 0 | 0
2022-12-28 15:00 | 2.9863 | 0 | N/A | 0 | 0
2022-12-28 15:30 | 1.8834 | 0 | N/A | 0 | 0
2022-12-28 16:00 | 1.7757 | 0 | N/A | 0 | 0
2022-12-28 16:30 | -0.99546 | 0 | N/A | 0 | 0
2022-12-28 17:00 | -1.2213 | 0 | N/A | 0 | 0
2022-12-28 17:30 | -0.95058 | 0 | N/A | 0 | 0
2022-12-28 18:00 | 1.545 | 0 | N/A | 0 | 0
2022-12-28 18:30 | 2.6453 | 0 | N/A | 0 | 0
2022-12-28 19:00 | 3.119 | 0 | N/A | 0 | 0
2022-12-28 19:30 | 3.6806 | 0 | N/A | 0 | 0
2022-12-28 20:00 | 4.0284 | 0 | N/A | 0 | 0
2022-12-28 20:30 | 4.1773 | 0 | N/A | 0 | 0
2022-12-28 21:00 | 4.3172 | 0 | N/A | 0 | 0
2022-12-28 21:30 | 4.3317 | 0 | N/A | 0 | 0
2022-12-28 22:00 | 4.1739 | 0 | N/A | 0 | 0
2022-12-28 22:30 | 4.4551 | 0 | N/A | 0 | 0
2022-12-28 23:00 | 4.5526 | 0 | N/A | 0 | 0
2022-12-28 23:30 | 4.2892 | 0 | N/A | 0 | 0
2022-12-29 | 4.2067 | 0 | N/A | 0 | 0
2022-12-29 00:30 | 4.5531 | 0 | N/A | 0 | 0
2022-12-29 01:00 | 4.7432 | 0 | N/A | 0 | 0
2022-12-29 01:30 | 3.9173 | 0 | N/A | 0 | 0
2022-12-29 02:00 | 3.3671 | 0 | N/A | 0 | 0
2022-12-29 02:30 | 3.2895 | 0 | N/A | 0 | 0
2022-12-29 03:00 | 2.95 | 0 | N/A | 0 | 0
2022-12-29 03:30 | 2.7984 | 0 | N/A | 0 | 0
2022-12-29 04:00 | 2.6465 | 0 | N/A | 0 | 0
2022-12-29 04:30 | 2.6175 | 0 | N/A | 0 | 0
2022-12-29 05:00 | 2.5786 | 0 | N/A | 0 | 0
2022-12-29 05:30 | 2.6655 | 0 | N/A | 0 | 0
2022-12-29 06:00 | 2.7465 | 0 | N/A | 0 | 0
2022-12-29 06:30 | 2.9904 | 0 | N/A | 0 | 0
2022-12-29 07:00 | 3.1016 | 0 | N/A | 0 | 0
2022-12-29 07:30 | 3.0769 | 0 | N/A | 0 | 0
2022-12-29 08:00 | 2.9316 | 0 | N/A | 0 | 0
2022-12-29 08:30 | 2.2568 | 0 | N/A | 0 | 0
2022-12-29 09:00 | 1.9108 | 0 | N/A | 0 | 0
2022-12-29 09:30 | 1.6523 | 0 | N/A | 0 | 0
2022-12-29 10:00 | 1.3508 | 0 | N/A | 0 | 0
2022-12-29 10:30 | -0.93744 | 0 | N/A | 0 | 0
2022-12-29 11:00 | -0.95613 | 0 | N/A | 0 | 0
2022-12-29 11:30 | 0.99137 | 0 | N/A | 0 | 0
2022-12-29 12:00 | -1.0414 | 0 | N/A | 0 | 0
2022-12-29 12:30 | -1.7681 | 0 | N/A | 0 | 0
2022-12-29 13:00 | -2.0664 | 0 | N/A | 0 | 0
2022-12-29 13:30 | -1.7655 | 0 | N/A | 0 | 0
2022-12-29 14:00 | -1.6628 | 0 | N/A | 0 | 0
2022-12-29 14:30 | -1.947 | 0 | N/A | 0 | 0
2022-12-29 15:00 | -2.0236 | 0 | N/A | 0 | 0
2022-12-29 15:30 | -1.8206 | 0 | N/A | 0 | 0
2022-12-29 16:00 | -1.6208 | 0 | N/A | 0 | 0
2022-12-29 16:30 | -1.1315 | 0 | N/A | 0 | 0
2022-12-29 17:00 | 1.1887 | 0 | N/A | 0 | 0
2022-12-29 17:30 | 1.9586 | 0 | N/A | 0 | 0
2022-12-29 18:00 | 2.9159 | 0 | N/A | 0 | 0
2022-12-29 18:30 | 3.5046 | 0 | N/A | 0 | 0
2022-12-29 19:00 | 3.9529 | 0 | N/A | 0 | 0
2022-12-29 19:30 | 4.3204 | 0 | N/A | 0 | 0
2022-12-29 20:00 | 4.2196 | 0 | N/A | 0 | 0
2022-12-29 20:30 | 4.4409 | 0 | N/A | 0 | 0
2022-12-29 21:00 | 4.5847 | 0 | N/A | 0 | 0
2022-12-29 21:30 | 4.4444 | 0 | N/A | 0 | 0
2022-12-29 22:00 | 4.3091 | 0 | N/A | 0 | 0
2022-12-29 22:30 | 4.543 | 0 | N/A | 0 | 0
2022-12-29 23:00 | 4.4908 | 0 | N/A | 0 | 0
2022-12-29 23:30 | 4.1968 | 0 | N/A | 0 | 0
2022-12-30 | 4.1705 | 0 | N/A | 0 | 0
2022-12-31 00:30 | 4.1647 | 0 | N/A | 0 | 0
2022-12-31 01:00 | 4.3787 | 0 | N/A | 0 | 0
2022-12-31 01:30 | 3.7182 | 0 | N/A | 0 | 0
2022-12-31 02:00 | 3.1984 | 0 | N/A | 0 | 0
2022-12-31 02:30 | 3.1141 | 0 | N/A | 0 | 0
2022-12-31 03:00 | 2.9346 | 0 | N/A | 0 | 0
2022-12-31 03:30 | 2.6482 | 0 | N/A | 0 | 0
2022-12-31 04:00 | 2.5187 | 0 | N/A | 0 | 0
2022-12-31 04:30 | 2.438 | 0 | N/A | 0 | 0
2022-12-31 05:00 | 2.4009 | 0 | N/A | 0 | 0
2022-12-31 05:30 | 2.4251 | 0 | N/A | 0 | 0
2022-12-31 06:00 | 2.5172 | 0 | N/A | 0 | 0
2022-12-31 06:30 | 2.6509 | 0 | N/A | 0 | 0
2022-12-31 07:00 | 2.632 | 0 | N/A | 0 | 0
2022-12-31 07:30 | 2.5832 | 0 | N/A | 0 | 0
2022-12-31 08:00 | 2.5831 | 0 | N/A | 0 | 0
2022-12-31 08:30 | 2.4615 | 0 | N/A | 0 | 0
2022-12-31 09:00 | 2.3307 | 0 | N/A | 0 | 0
2022-12-31 09:30 | 2.1822 | 0 | N/A | 0 | 0
2022-12-31 10:00 | 1.9733 | 0 | N/A | 0 | 0
2022-12-31 10:30 | 1.4123 | 0 | N/A | 0 | 0
2022-12-31 11:00 | -0.8676 | 0 | N/A | 0 | 0
2022-12-31 11:30 | -1.688 | 0 | N/A | 0 | 0
2022-12-31 12:00 | -2.0834 | 0 | N/A | 0 | 0
2022-12-31 12:30 | -2.1231 | 0 | N/A | 0 | 0
2022-12-31 13:00 | -1.8797 | 0 | N/A | 0 | 0
2022-12-31 13:30 | -1.9868 | 0 | N/A | 0 | 0
2022-12-31 14:00 | -1.3093 | 0 | N/A | 0 | 0
2022-12-31 14:30 | -1.4537 | 0 | N/A | 0 | 0
2022-12-31 15:00 | -1.3984 | 0 | N/A | 0 | 0
2022-12-31 15:30 | -0.96755 | 0 | N/A | 0 | 0
2022-12-31 16:00 | -0.56191 | 0 | N/A | 0 | 0
2022-12-31 16:30 | 0.69215 | 0 | N/A | 0 | 0
2022-12-31 17:00 | 1.646 | 0 | N/A | 0 | 0
2022-12-31 17:30 | 1.9579 | 0 | N/A | 0 | 0
2022-12-31 18:00 | 3.2366 | 0 | N/A | 0 | 0
2022-12-31 18:30 | 3.6615 | 0 | N/A | 0 | 0
2022-12-31 19:00 | 4.5576 | 0 | N/A | 0 | 0
2022-12-31 19:30 | 5.1216 | 0 | N/A | 0 | 0
2022-12-31 20:00 | 5.1831 | 0 | N/A | 0 | 0
2022-12-31 20:30 | 5.0487 | 0 | N/A | 0 | 0
2022-12-31 21:00 | 4.9048 | 0 | N/A | 0 | 0
2022-12-31 21:30 | 4.6159 | 0 | N/A | 0 | 0
2022-12-31 22:00 | 4.476 | 0 | N/A | 0 | 0
2022-12-31 22:30 | 4.6765 | 0 | N/A | 0 | 0
2022-12-31 23:00 | 4.693 | 0 | N/A | 0 | 0
2022-12-31 23:30 | 4.386 | 0 | N/A | 0 | 0
2023-01-01 | 4.3172 | 0 | N/A | 0 | 0
2023-01-01 00:30 | 4.6491 | 0 | N/A | 0 | 0
2023-01-01 01:00 | 4.7378 | 0 | N/A | 0 | 0
2023-01-01 01:30 | 4.0194 | 0 | N/A | 0 | 0
2023-01-01 02:00 | 3.4587 | 0 | N/A | 0 | 0
2023-01-01 02:30 | 3.3148 | 0 | N/A | 0 | 0
2023-01-01 03:00 | 3.0463 | 0 | N/A | 0 | 0
2023-01-01 03:30 | 2.7772 | 0 | N/A | 0 | 0
2023-01-01 04:00 | 2.5827 | 0 | N/A | 0 | 0
2023-01-01 04:30 | 2.6142 | 0 | N/A | 0 | 0
2023-01-01 05:00 | 2.5514 | 0 | N/A | 0 | 0
2023-01-01 05:30 | 2.5561 | 0 | N/A | 0 | 0
2023-01-01 06:00 | 2.5463 | 0 | N/A | 0 | 0
2023-01-01 06:30 | 2.5775 | 0 | N/A | 0 | 0
2023-01-01 07:00 | 2.5737 | 0 | N/A | 0 | 0
2023-01-01 07:30 | 2.4303 | 0 | N/A | 0 | 0
2023-01-01 08:00 | 2.0607 | 0 | N/A | 0 | 0
2023-01-01 08:30 | 1.6334 | 0 | N/A | 0 | 0
2023-01-01 09:00 | 1.2215 | 0 | N/A | 0 | 0
2023-01-01 09:30 | 0.82514 | 0 | N/A | 0 | 0
2023-01-01 10:00 | -0.62229 | 0 | N/A | 0 | 0
2023-01-01 10:30 | -0.74316 | 0 | N/A | 0 | 0
2023-01-01 11:00 | -0.94988 | 0 | N/A | 0 | 0
2023-01-01 11:30 | -0.81143 | 0 | N/A | 0 | 0
2023-01-01 12:00 | -0.80874 | 0 | N/A | 0 | 0
2023-01-01 12:30 | -0.69565 | 0 | N/A | 0 | 0
2023-01-01 13:00 | -0.5099 | 0 | N/A | 0 | 0
2023-01-01 13:30 | 0.99895 | 0 | N/A | 0 | 0
2023-01-01 14:00 | 1.4078 | 0 | N/A | 0 | 0
2023-01-01 14:30 | 1.4244 | 0 | N/A | 0 | 0
2023-01-01 15:00 | 2.1003 | 0 | N/A | 0 | 0
2023-01-01 15:30 | 2.3181 | 0 | N/A | 0 | 0
2023-01-01 16:00 | 3.1676 | 0 | N/A | 0 | 0
2023-01-01 16:30 | 3.0422 | 0 | N/A | 0 | 0
2023-01-01 17:00 | 3.9463 | 0 | N/A | 0 | 0
2023-01-01 17:30 | 5.197 | 0 | N/A | 0 | 0
2023-01-01 18:00 | 6.3406 | 0 | N/A | 0 | 0
2023-01-01 18:30 | 7.326 | 0 | N/A | 0 | 0
2023-01-01 19:00 | 8.2288 | 0 | N/A | 0 | 0
2023-01-01 19:30 | 8.8789 | 0 | N/A | 0 | 0
2023-01-01 20:00 | 8.5957 | 0 | N/A | 0 | 0
2023-01-01 20:30 | 8.0982 | 0 | N/A | 0 | 0
2023-01-01 21:00 | 7.7882 | 0 | N/A | 0 | 0
2023-01-01 21:30 | 7.1737 | 0 | N/A | 0 | 0
2023-01-01 22:00 | 6.6903 | 0 | N/A | 0 | 0
2023-01-01 22:30 | 6.5344 | 0 | N/A | 0 | 0
2023-01-01 23:00 | 5.9859 | 0 | N/A | 0 | 0
2023-01-01 23:30 | 5.4131 | 0 | N/A | 0 | 0
2023-01-02 | 4.6833 | 0 | N/A | 0 | 0
2023-01-02 00:30 | 4.8962 | 0 | N/A | 0 | 0
2023-01-02 01:00 | 4.8842 | 0 | N/A | 0 | 0
2023-01-02 01:30 | 4.1329 | 0 | N/A | 0 | 0
2023-01-02 02:00 | 3.6219 | 0 | N/A | 0 | 0
2023-01-02 02:30 | 3.4694 | 0 | N/A | 0 | 0
2023-01-02 03:00 | 3.2548 | 0 | N/A | 0 | 0
2023-01-02 03:30 | 3.043 | 0 | N/A | 0 | 0
2023-01-02 04:00 | 3.0359 | 0 | N/A | 0 | 0
2023-01-02 04:30 | 2.9895 | 0 | N/A | 0 | 0
2023-01-02 05:00 | 2.9493 | 0 | N/A | 0 | 0
2023-01-02 05:30 | 2.9472 | 0 | N/A | 0 | 0
2023-01-02 06:00 | 3.0623 | 0 | N/A | 0 | 0
2023-01-02 06:30 | 3.0131 | 0 | N/A | 0 | 0
2023-01-02 07:00 | 3.0013 | 0 | N/A | 0 | 0
2023-01-02 07:30 | 2.9522 | 0 | N/A | 0 | 0
2023-01-02 08:00 | 2.7282 | 0 | N/A | 0 | 0
2023-01-02 08:30 | 2.4804 | 0 | N/A | 0 | 0
2023-01-02 09:00 | 1.834 | 0 | N/A | 0 | 0
2023-01-02 09:30 | 1.3845 | 0 | N/A | 0 | 0
2023-01-02 10:00 | 0.98793 | 0 | N/A | 0 | 0
2023-01-02 10:30 | 0.66843 | 0 | N/A | 0 | 0
2023-01-02 11:00 | 0.45977 | 0 | N/A | 0 | 0
2023-01-02 11:30 | 0.26537 | 0 | N/A | 0 | 0
2023-01-02 12:00 | 0.43868 | 0 | N/A | 0 | 0
2023-01-02 12:30 | 1.0541 | 0 | N/A | 0 | 0
2023-01-02 13:00 | 1.7193 | 0 | N/A | 0 | 0
2023-01-02 13:30 | 1.5948 | 0 | N/A | 0 | 0
2023-01-02 14:00 | 1.5117 | 0 | N/A | 0 | 0
2023-01-02 14:30 | 1.5563 | 0 | N/A | 0 | 0
2023-01-02 15:00 | 2 | 0 | N/A | 0 | 0
2023-01-02 15:30 | 3.3415 | 0 | N/A | 0 | 0
2023-01-02 16:00 | 2.4894 | 0 | N/A | 0 | 0
2023-01-02 16:30 | 2.7119 | 0 | N/A | 0 | 0
2023-01-02 17:00 | 5.188 | 0 | N/A | 0 | 0
2023-01-02 17:30 | 5.6863 | 0 | N/A | 0 | 0
2023-01-02 18:00 | 5.9149 | 0 | N/A | 0 | 0
2023-01-02 18:30 | 4.8971 | 0 | N/A | 0 | 0
2023-01-02 19:00 | 5.6336 | 0 | N/A | 0 | 0
2023-01-02 19:30 | 5.7071 | 0 | N/A | 0 | 0
2023-01-02 20:00 | 5.4757 | 0 | N/A | 0 | 0
2023-01-02 20:30 | 5.3391 | 0 | N/A | 0 | 0
2023-01-02 21:00 | 5.1804 | 0 | N/A | 0 | 0
2023-01-02 21:30 | 4.8271 | 0 | N/A | 0 | 0
2023-01-02 22:00 | 4.462 | 0 | N/A | 0 | 0
2023-01-02 22:30 | 4.555 | 0 | N/A | 0 | 0
2023-01-02 23:00 | 4.4806 | 0 | N/A | 0 | 0
2023-01-02 23:30 | 4.1445 | 0 | N/A | 0 | 0
2023-01-03 | 4.0804 | 0 | N/A | 0 | 0
2023-01-03 00:30 | 4.2886 | 0 | N/A | 0 | 0
2023-01-03 01:00 | 4.3567 | 0 | N/A | 0 | 0
2023-01-03 01:30 | 3.6779 | 0 | N/A | 0 | 0
2023-01-03 02:00 | 3.1256 | 0 | N/A | 0 | 0
2023-01-03 02:30 | 3.0594 | 0 | N/A | 0 | 0
2023-01-03 03:00 | 2.87 | 0 | N/A | 0 | 0
2023-01-03 03:30 | 2.5893 | 0 | N/A | 0 | 0
2023-01-03 04:00 | 2.539 | 0 | N/A | 0 | 0
2023-01-03 04:30 | 2.4879 | 0 | N/A | 0 | 0
2023-01-03 05:00 | 2.509 | 0 | N/A | 0 | 0
2023-01-03 05:30 | 2.6527 | 0 | N/A | 0 | 0
2023-01-03 06:00 | 2.7571 | 0 | N/A | 0 | 0
2023-01-03 06:30 | 2.8741 | 0 | N/A | 0 | 0
2023-01-03 07:00 | 2.9874 | 0 | N/A | 0 | 0
2023-01-03 07:30 | 3.1181 | 0 | N/A | 0 | 0
2023-01-03 08:00 | 3.1435 | 0 | N/A | 0 | 0
2023-01-03 08:30 | 3.0157 | 0 | N/A | 0 | 0
2023-01-03 09:00 | 2.7296 | 0 | N/A | 0 | 0
2023-01-03 09:30 | 2.7597 | 0 | N/A | 0 | 0
2023-01-03 10:00 | 2.491 | 0 | N/A | 0 | 0
2023-01-03 10:30 | 2.023 | 0 | N/A | 0 | 0
2023-01-03 11:00 | 1.5113 | 0 | N/A | 0 | 0
2023-01-03 11:30 | 1.2032 | 0 | N/A | 0 | 0
2023-01-03 12:00 | 1.5827 | 0 | N/A | 0 | 0
2023-01-03 12:30 | 1.0124 | 0 | N/A | 0 | 0
2023-01-03 13:00 | 1.1932 | 0 | N/A | 0 | 0
2023-01-03 13:30 | 1.5019 | 0 | N/A | 0 | 0
2023-01-03 14:00 | 0.92309 | 0 | N/A | 0 | 0
2023-01-03 14:30 | 1.3265 | 0 | N/A | 0 | 0
2023-01-03 15:00 | -0.77474 | 0 | N/A | 0 | 0
2023-01-03 15:30 | -1.2611 | 0 | N/A | 0 | 0
2023-01-03 16:00 | -0.99825 | 0 | N/A | 0 | 0
2023-01-03 16:30 | 1.0471 | 0 | N/A | 0 | 0
2023-01-03 17:00 | -1.0359 | 0 | N/A | 0 | 0
2023-01-03 17:30 | 1.6082 | 0 | N/A | 0 | 0
2023-01-03 18:00 | 2.1847 | 0 | N/A | 0 | 0
2023-01-03 18:30 | 3.1351 | 0 | N/A | 0 | 0
2023-01-03 19:00 | 3.9219 | 0 | N/A | 0 | 0
2023-01-03 19:30 | 4.2295 | 0 | N/A | 0 | 0
2023-01-03 20:00 | 4.4586 | 0 | N/A | 0 | 0
2023-01-03 20:30 | 4.5107 | 0 | N/A | 0 | 0
2023-01-03 21:00 | 4.5318 | 0 | N/A | 0 | 0
2023-01-03 21:30 | 4.3527 | 0 | N/A | 0 | 0
2023-01-03 22:00 | 4.1701 | 0 | N/A | 0 | 0
2023-01-03 22:30 | 4.3713 | 0 | N/A | 0 | 0
2023-01-03 23:00 | 4.3415 | 0 | N/A | 0 | 0
2023-01-03 23:30 | 4.0488 | 0 | N/A | 0 | 0
2023-01-04 | 4.0699 | 0 | N/A | 0 | 0
2023-01-04 00:30 | 4.3393 | 0 | N/A | 0 | 0
2023-01-04 01:00 | 4.5944 | 0 | N/A | 0 | 0
2023-01-04 01:30 | 3.8663 | 0 | N/A | 0 | 0
2023-01-04 02:00 | 3.3193 | 0 | N/A | 0 | 0
2023-01-04 02:30 | 3.3656 | 0 | N/A | 0 | 0
2023-01-04 03:00 | 3.0815 | 0 | N/A | 0 | 0
2023-01-04 03:30 | 2.8478 | 0 | N/A | 0 | 0
2023-01-04 04:00 | 2.6629 | 0 | N/A | 0 | 0
2023-01-04 04:30 | 2.597 | 0 | N/A | 0 | 0
2023-01-04 05:00 | 2.6069 | 0 | N/A | 0 | 0
2023-01-04 05:30 | 2.6703 | 0 | N/A | 0 | 0
2023-01-04 06:00 | 2.8795 | 0 | N/A | 0 | 0
2023-01-04 06:30 | 3.0388 | 0 | N/A | 0 | 0
2023-01-04 07:00 | 3.1763 | 0 | N/A | 0 | 0
2023-01-04 07:30 | 3.3939 | 0 | N/A | 0 | 0
2023-01-04 08:00 | 3.2969 | 0 | N/A | 0 | 0
2023-01-04 08:30 | 3.163 | 0 | N/A | 0 | 0
2023-01-04 09:00 | 2.5358 | 0 | N/A | 0 | 0
2023-01-04 09:30 | 2.5942 | 0 | N/A | 0 | 0
2023-01-04 10:00 | 2.1392 | 0 | N/A | 0 | 0
2023-01-04 10:30 | 2.3942 | 0 | N/A | 0 | 0
2023-01-04 11:00 | 1.4509 | 0 | N/A | 0 | 0
2023-01-04 11:30 | 2.1616 | 0 | N/A | 0 | 0
2023-01-04 12:00 | 1.7808 | 0 | N/A | 0 | 0
2023-01-04 12:30 | 1.6771 | 0 | N/A | 0 | 0
2023-01-04 13:00 | 1.0282 | 0 | N/A | 0 | 0
2023-01-04 13:30 | -0.86701 | 0 | N/A | 0 | 0
2023-01-04 14:00 | -1.0827 | 0 | N/A | 0 | 0
2023-01-04 14:30 | -1.2187 | 0 | N/A | 0 | 0
2023-01-04 15:00 | -0.98241 | 0 | N/A | 0 | 0
2023-01-04 15:30 | 1.0722 | 0 | N/A | 0 | 0
2023-01-04 16:00 | 1.2331 | 0 | N/A | 0 | 0
2023-01-04 16:30 | 1.5841 | 0 | N/A | 0 | 0
2023-01-04 17:00 | 2.1074 | 0 | N/A | 0 | 0
2023-01-04 17:30 | 2.5954 | 0 | N/A | 0 | 0
2023-01-04 18:00 | 3.7703 | 0 | N/A | 0 | 0
2023-01-04 18:30 | 4.3631 | 0 | N/A | 0 | 0
2023-01-04 19:00 | 4.6847 | 0 | N/A | 0 | 0
2023-01-04 19:30 | 4.7496 | 0 | N/A | 0 | 0
2023-01-04 20:00 | 4.894 | 0 | N/A | 0 | 0
2023-01-04 20:30 | 4.9723 | 0 | N/A | 0 | 0
2023-01-04 21:00 | 5.0376 | 0 | N/A | 0 | 0
2023-01-04 21:30 | 4.8788 | 0 | N/A | 0 | 0
2023-01-04 22:00 | 4.6543 | 0 | N/A | 0 | 0
2023-01-04 22:30 | 4.7504 | 0 | N/A | 0 | 0
2023-01-04 23:00 | 4.7958 | 0 | N/A | 0 | 0
2023-01-04 23:30 | 4.5239 | 0 | N/A | 0 | 0
2023-01-05 | 4.4667 | 0 | N/A | 0 | 0
2023-01-07 00:30 | 4.3129 | 0 | N/A | 0 | 0
2023-01-07 01:00 | 4.4929 | 0 | N/A | 0 | 0
2023-01-07 01:30 | 3.8596 | 0 | N/A | 0 | 0
2023-01-07 02:00 | 3.3257 | 0 | N/A | 0 | 0
2023-01-07 02:30 | 3.2255 | 0 | N/A | 0 | 0
2023-01-07 03:00 | 2.9591 | 0 | N/A | 0 | 0
2023-01-07 03:30 | 2.7699 | 0 | N/A | 0 | 0
2023-01-07 04:00 | 2.6578 | 0 | N/A | 0 | 0
2023-01-07 04:30 | 2.6049 | 0 | N/A | 0 | 0
2023-01-07 05:00 | 2.548 | 0 | N/A | 0 | 0
2023-01-07 05:30 | 2.6197 | 0 | N/A | 0 | 0
2023-01-07 06:00 | 2.6801 | 0 | N/A | 0 | 0
2023-01-07 06:30 | 2.7811 | 0 | N/A | 0 | 0
2023-01-07 07:00 | 2.8415 | 0 | N/A | 0 | 0
2023-01-07 07:30 | 2.7204 | 0 | N/A | 0 | 0
2023-01-07 08:00 | 2.3979 | 0 | N/A | 0 | 0
2023-01-07 08:30 | 1.9369 | 0 | N/A | 0 | 0
2023-01-07 09:00 | 1.4556 | 0 | N/A | 0 | 0
2023-01-07 09:30 | 0.99372 | 0 | N/A | 0 | 0
2023-01-07 10:00 | -0.94623 | 0 | N/A | 0 | 0
2023-01-07 10:30 | -1.3137 | 0 | N/A | 0 | 0
2023-01-07 11:00 | -1.7682 | 0 | N/A | 0 | 0
2023-01-07 11:30 | -2.1942 | 0 | N/A | 0 | 0
2023-01-07 12:00 | -2.3829 | 0 | N/A | 0 | 0
2023-01-07 12:30 | -2.4158 | 0 | N/A | 0 | 0
2023-01-07 13:00 | -2.4145 | 0 | N/A | 0 | 0
2023-01-07 13:30 | -2.3893 | 0 | N/A | 0 | 0
2023-01-07 14:00 | -2.3477 | 0 | N/A | 0 | 0
2023-01-07 14:30 | -2.1869 | 0 | N/A | 0 | 0
2023-01-07 15:00 | -1.9436 | 0 | N/A | 0 | 0
2023-01-07 15:30 | -1.6994 | 0 | N/A | 0 | 0
2023-01-07 16:00 | -1.2334 | 0 | N/A | 0 | 0
2023-01-07 16:30 | -0.69631 | 0 | N/A | 0 | 0
2023-01-07 17:00 | 0.73348 | 0 | N/A | 0 | 0
2023-01-07 17:30 | 1.5124 | 0 | N/A | 0 | 0
2023-01-07 18:00 | 2.5546 | 0 | N/A | 0 | 0
2023-01-07 18:30 | 3.6014 | 0 | N/A | 0 | 0
2023-01-07 19:00 | 4.5434 | 0 | N/A | 0 | 0
2023-01-07 19:30 | 5.148 | 0 | N/A | 0 | 0
2023-01-07 20:00 | 5.3208 | 0 | N/A | 0 | 0
2023-01-07 20:30 | 5.1972 | 0 | N/A | 0 | 0
2023-01-07 21:00 | 5.0237 | 0 | N/A | 0 | 0
2023-01-07 21:30 | 4.7839 | 0 | N/A | 0 | 0
2023-01-07 22:00 | 4.5705 | 0 | N/A | 0 | 0
2023-01-07 22:30 | 4.6528 | 0 | N/A | 0 | 0
2023-01-07 23:00 | 4.6224 | 0 | N/A | 0 | 0
2023-01-07 23:30 | 4.2333 | 0 | N/A | 0 | 0
2023-01-08 | 4.1996 | 0 | N/A | 0 | 0
2023-01-08 00:30 | 4.4286 | 0 | N/A | 0 | 0
2023-01-08 01:00 | 4.5084 | 0 | N/A | 0 | 0
2023-01-08 01:30 | 3.8 | 0 | N/A | 0 | 0
2023-01-08 02:00 | 3.3048 | 0 | N/A | 0 | 0
2023-01-08 02:30 | 3.311 | 0 | N/A | 0 | 0
2023-01-08 03:00 | 3.0539 | 0 | N/A | 0 | 0
2023-01-08 03:30 | 2.7942 | 0 | N/A | 0 | 0
2023-01-08 04:00 | 2.6492 | 0 | N/A | 0 | 0
2023-01-08 04:30 | 2.6385 | 0 | N/A | 0 | 0
2023-01-08 05:00 | 2.5525 | 0 | N/A | 0 | 0
2023-01-08 05:30 | 2.6377 | 0 | N/A | 0 | 0
2023-01-08 06:00 | 2.6526 | 0 | N/A | 0 | 0
2023-01-08 06:30 | 2.7422 | 0 | N/A | 0 | 0
2023-01-08 07:00 | 2.7219 | 0 | N/A | 0 | 0
2023-01-08 07:30 | 2.6535 | 0 | N/A | 0 | 0
2023-01-08 08:00 | 2.354 | 0 | N/A | 0 | 0
2023-01-08 08:30 | 1.9428 | 0 | N/A | 0 | 0
2023-01-08 09:00 | 1.5251 | 0 | N/A | 0 | 0
2023-01-08 09:30 | 1.0975 | 0 | N/A | 0 | 0
2023-01-08 10:00 | 0.82779 | 0 | N/A | 0 | 0
2023-01-08 10:30 | -0.80411 | 0 | N/A | 0 | 0
2023-01-08 11:00 | -0.9216 | 0 | N/A | 0 | 0
2023-01-08 11:30 | -0.90225 | 0 | N/A | 0 | 0
2023-01-08 12:00 | -0.864 | 0 | N/A | 0 | 0
2023-01-08 12:30 | -0.75822 | 0 | N/A | 0 | 0
2023-01-08 13:00 | -0.54416 | 0 | N/A | 0 | 0
2023-01-08 13:30 | -0.53029 | 0 | N/A | 0 | 0
2023-01-08 14:00 | 0.56041 | 0 | N/A | 0 | 0
2023-01-08 14:30 | 1.1646 | 0 | N/A | 0 | 0
2023-01-08 15:00 | 2.1351 | 0 | N/A | 0 | 0
2023-01-08 15:30 | 2.7954 | 0 | N/A | 0 | 0
2023-01-08 16:00 | 2.4737 | 0 | N/A | 0 | 0
2023-01-08 16:30 | 3.4292 | 0 | N/A | 0 | 0
2023-01-08 17:00 | 3.7378 | 0 | N/A | 0 | 0
2023-01-08 17:30 | 4.7724 | 0 | N/A | 0 | 0
2023-01-08 18:00 | 6.1991 | 0 | N/A | 0 | 0
2023-01-08 18:30 | 7.3151 | 0 | N/A | 0 | 0
2023-01-08 19:00 | 7.1337 | 0 | N/A | 0 | 0
2023-01-08 19:30 | 7.2012 | 0 | N/A | 0 | 0
2023-01-08 20:00 | 7.0914 | 0 | N/A | 0 | 0
2023-01-08 20:30 | 6.8004 | 0 | N/A | 0 | 0
2023-01-08 21:00 | 6.348 | 0 | N/A | 0 | 0
2023-01-08 21:30 | 5.9903 | 0 | N/A | 0 | 0
2023-01-08 22:00 | 5.432 | 0 | N/A | 0 | 0
2023-01-08 22:30 | 5.3184 | 0 | N/A | 0 | 0
2023-01-08 23:00 | 5.1877 | 0 | N/A | 0 | 0
2023-01-08 23:30 | 4.6746 | 0 | N/A | 0 | 0
2023-01-09 | 4.4924 | 0 | N/A | 0 | 0
2023-01-09 00:30 | 4.6832 | 0 | N/A | 0 | 0
2023-01-09 01:00 | 4.7414 | 0 | N/A | 0 | 0
2023-01-09 01:30 | 3.9923 | 0 | N/A | 0 | 0
2023-01-09 02:00 | 3.4325 | 0 | N/A | 0 | 0
2023-01-09 02:30 | 3.3544 | 0 | N/A | 0 | 0
2023-01-09 03:00 | 3.0797 | 0 | N/A | 0 | 0
2023-01-09 03:30 | 2.8225 | 0 | N/A | 0 | 0
2023-01-09 04:00 | 2.7608 | 0 | N/A | 0 | 0
2023-01-09 04:30 | 2.7489 | 0 | N/A | 0 | 0
2023-01-09 05:00 | 2.7259 | 0 | N/A | 0 | 0
2023-01-09 05:30 | 2.8652 | 0 | N/A | 0 | 0
2023-01-09 06:00 | 2.9405 | 0 | N/A | 0 | 0
2023-01-09 06:30 | 3.1626 | 0 | N/A | 0 | 0
2023-01-09 07:00 | 3.3792 | 0 | N/A | 0 | 0
2023-01-09 07:30 | 3.503 | 0 | N/A | 0 | 0
2023-01-09 08:00 | 3.406 | 0 | N/A | 0 | 0
2023-01-09 08:30 | 2.8257 | 0 | N/A | 0 | 0
2023-01-09 09:00 | 2.4579 | 0 | N/A | 0 | 0
2023-01-09 09:30 | 1.9606 | 0 | N/A | 0 | 0
2023-01-09 10:00 | 1.1541 | 0 | N/A | 0 | 0
2023-01-09 10:30 | 0.53037 | 0 | N/A | 0 | 0
2023-01-09 11:00 | -0.48831 | 0 | N/A | 0 | 0
2023-01-09 11:30 | -0.61341 | 0 | N/A | 0 | 0
2023-01-09 12:00 | -0.7994 | 0 | N/A | 0 | 0
2023-01-09 12:30 | -0.9173 | 0 | N/A | 0 | 0
2023-01-09 13:00 | -0.92124 | 0 | N/A | 0 | 0
2023-01-09 13:30 | -0.83974 | 0 | N/A | 0 | 0
2023-01-09 14:00 | -0.82006 | 0 | N/A | 0 | 0
2023-01-09 14:30 | -0.75384 | 0 | N/A | 0 | 0
2023-01-09 15:00 | -0.5385 | 0 | N/A | 0 | 0
2023-01-09 15:30 | -0.31556 | 0 | N/A | 0 | 0
2023-01-09 16:00 | 0.39868 | 0 | N/A | 0 | 0
2023-01-09 16:30 | 0.72126 | 0 | N/A | 0 | 0
2023-01-09 17:00 | 1.2647 | 0 | N/A | 0 | 0
2023-01-09 17:30 | 2.2057 | 0 | N/A | 0 | 0
2023-01-09 18:00 | 3.2316 | 0 | N/A | 0 | 0
2023-01-09 18:30 | 4.1705 | 0 | N/A | 0 | 0
2023-01-09 19:00 | 4.7863 | 0 | N/A | 0 | 0
2023-01-09 19:30 | 5.1229 | 0 | N/A | 0 | 0
2023-01-09 20:00 | 5.3393 | 0 | N/A | 0 | 0
2023-01-09 20:30 | 5.2257 | 0 | N/A | 0 | 0
2023-01-09 21:00 | 4.9861 | 0 | N/A | 0 | 0
2023-01-09 21:30 | 4.7151 | 0 | N/A | 0 | 0
2023-01-09 22:00 | 4.445 | 0 | N/A | 0 | 0
2023-01-09 22:30 | 4.572 | 0 | N/A | 0 | 0
2023-01-09 23:00 | 4.4885 | 0 | N/A | 0 | 0
2023-01-09 23:30 | 4.1662 | 0 | N/A | 0 | 0
2023-01-10 | 4.0709 | 0 | N/A | 0 | 0
2023-01-10 00:30 | 4.3017 | 0 | N/A | 0 | 0
2023-01-10 01:00 | 4.5429 | 0 | N/A | 0 | 0
2023-01-10 01:30 | 3.7781 | 0 | N/A | 0 | 0
2023-01-10 02:00 | 3.2696 | 0 | N/A | 0 | 0
2023-01-10 02:30 | 3.2071 | 0 | N/A | 0 | 0
2023-01-10 03:00 | 3.0193 | 0 | N/A | 0 | 0
2023-01-10 03:30 | 2.8103 | 0 | N/A | 0 | 0
2023-01-10 04:00 | 2.7638 | 0 | N/A | 0 | 0
2023-01-10 04:30 | 2.6924 | 0 | N/A | 0 | 0
2023-01-10 05:00 | 2.6928 | 0 | N/A | 0 | 0
2023-01-10 05:30 | 2.7776 | 0 | N/A | 0 | 0
2023-01-10 06:00 | 2.8995 | 0 | N/A | 0 | 0
2023-01-10 06:30 | 3.2194 | 0 | N/A | 0 | 0
2023-01-10 07:00 | 3.3806 | 0 | N/A | 0 | 0
2023-01-10 07:30 | 3.5692 | 0 | N/A | 0 | 0
2023-01-10 08:00 | 3.7459 | 0 | N/A | 0 | 0
2023-01-10 08:30 | 3.6262 | 0 | N/A | 0 | 0
2023-01-10 09:00 | 3.4651 | 0 | N/A | 0 | 0
2023-01-10 09:30 | 2.9336 | 0 | N/A | 0 | 0
2023-01-10 10:00 | 2.0983 | 0 | N/A | 0 | 0
2023-01-10 10:30 | 1.1224 | 0 | N/A | 0 | 0
2023-01-10 11:00 | -0.50028 | 0 | N/A | 0 | 0
2023-01-10 11:30 | -1.6085 | 0 | N/A | 0 | 0
2023-01-10 12:00 | -2.0125 | 0 | N/A | 0 | 0
2023-01-10 12:30 | -2.1384 | 0 | N/A | 0 | 0
2023-01-10 13:00 | -2.2018 | 0 | N/A | 0 | 0
2023-01-10 13:30 | -2.27 | 0 | N/A | 0 | 0
2023-01-10 14:00 | -2.2536 | 0 | N/A | 0 | 0
2023-01-10 14:30 | -2.1338 | 0 | N/A | 0 | 0
2023-01-10 15:00 | -1.9269 | 0 | N/A | 0 | 0
2023-01-10 15:30 | -1.6797 | 0 | N/A | 0 | 0
2023-01-10 16:00 | -1.484 | 0 | N/A | 0 | 0
2023-01-10 16:30 | -1.034 | 0 | N/A | 0 | 0
2023-01-10 17:00 | -0.56514 | 0 | N/A | 0 | 0
2023-01-10 17:30 | 0.99705 | 0 | N/A | 0 | 0
2023-01-10 18:00 | 2.086 | 0 | N/A | 0 | 0
2023-01-10 18:30 | 3.0289 | 0 | N/A | 0 | 0
2023-01-10 19:00 | 3.9126 | 0 | N/A | 0 | 0
2023-01-10 19:30 | 4.5198 | 0 | N/A | 0 | 0
2023-01-10 20:00 | 4.7264 | 0 | N/A | 0 | 0
2023-01-10 20:30 | 4.8574 | 0 | N/A | 0 | 0
2023-01-10 21:00 | 4.7464 | 0 | N/A | 0 | 0
2023-01-10 21:30 | 4.5557 | 0 | N/A | 0 | 0
2023-01-10 22:00 | 4.3827 | 0 | N/A | 0 | 0
2023-01-10 22:30 | 4.5444 | 0 | N/A | 0 | 0
2023-01-10 23:00 | 4.4651 | 0 | N/A | 0 | 0
2023-01-10 23:30 | 4.1021 | 0 | N/A | 0 | 0
2023-01-11 | 3.9711 | 0 | N/A | 0 | 0
2023-01-12 00:30 | 4.6244 | 0 | N/A | 0 | 0
2023-01-12 01:00 | 4.6624 | 0 | N/A | 0 | 0
2023-01-12 01:30 | 3.944 | 0 | N/A | 0 | 0
2023-01-12 02:00 | 3.3265 | 0 | N/A | 0 | 0
2023-01-12 02:30 | 3.2769 | 0 | N/A | 0 | 0
2023-01-12 03:00 | 3.0831 | 0 | N/A | 0 | 0
2023-01-12 03:30 | 2.873 | 0 | N/A | 0 | 0
2023-01-12 04:00 | 2.7954 | 0 | N/A | 0 | 0
2023-01-12 04:30 | 2.7461 | 0 | N/A | 0 | 0
2023-01-12 05:00 | 2.7723 | 0 | N/A | 0 | 0
2023-01-12 05:30 | 2.8809 | 0 | N/A | 0 | 0
2023-01-12 06:00 | 3.0308 | 0 | N/A | 0 | 0
2023-01-12 06:30 | 3.2884 | 0 | N/A | 0 | 0
2023-01-12 07:00 | 3.6632 | 0 | N/A | 0 | 0
2023-01-12 07:30 | 3.9168 | 0 | N/A | 0 | 0
2023-01-12 08:00 | 4.0617 | 0 | N/A | 0 | 0
2023-01-12 08:30 | 3.4815 | 0 | N/A | 0 | 0
2023-01-12 09:00 | 3.3369 | 0 | N/A | 0 | 0
2023-01-12 09:30 | 2.2427 | 0 | N/A | 0 | 0
2023-01-12 10:00 | 1.7214 | 0 | N/A | 0 | 0
2023-01-12 10:30 | 0.88334 | 0 | N/A | 0 | 0
2023-01-12 11:00 | -0.29548 | 0 | N/A | 0 | 0
2023-01-12 11:30 | -0.38897 | 0 | N/A | 0 | 0
2023-01-12 12:00 | -0.50581 | 0 | N/A | 0 | 0
2023-01-12 12:30 | -0.5852 | 0 | N/A | 0 | 0
2023-01-12 13:00 | -0.56668 | 0 | N/A | 0 | 0
2023-01-12 13:30 | -0.58668 | 0 | N/A | 0 | 0
2023-01-12 14:00 | -0.93005 | 0 | N/A | 0 | 0
2023-01-12 14:30 | -0.79 | 0 | N/A | 0 | 0
2023-01-12 15:00 | -0.43915 | 0 | N/A | 0 | 0
2023-01-12 15:30 | -0.15613 | 0 | N/A | 0 | 0
2023-01-12 16:00 | 0.40388 | 0 | N/A | 0 | 0
2023-01-12 16:30 | 1.0442 | 0 | N/A | 0 | 0
2023-01-12 17:00 | 1.9235 | 0 | N/A | 0 | 0
2023-01-12 17:30 | 2.9157 | 0 | N/A | 0 | 0
2023-01-12 18:00 | 4.0654 | 0 | N/A | 0 | 0
2023-01-12 18:30 | 5.1591 | 0 | N/A | 0 | 0
2023-01-12 19:00 | 5.8903 | 0 | N/A | 0 | 0
2023-01-12 19:30 | 6.2705 | 0 | N/A | 0 | 0
2023-01-12 20:00 | 6.3803 | 0 | N/A | 0 | 0
2023-01-12 20:30 | 6.3226 | 0 | N/A | 0 | 0
2023-01-12 21:00 | 5.9666 | 0 | N/A | 0 | 0
2023-01-12 21:30 | 5.4797 | 0 | N/A | 0 | 0
2023-01-12 22:00 | 5.0236 | 0 | N/A | 0 | 0
2023-01-12 22:30 | 4.9386 | 0 | N/A | 0 | 0
2023-01-12 23:00 | 4.7491 | 0 | N/A | 0 | 0
2023-01-12 23:30 | 4.3586 | 0 | N/A | 0 | 0
2023-01-13 | 4.1685 | 0 | N/A | 0 | 0
2023-01-13 00:30 | 4.4923 | 0 | N/A | 0 | 0
2023-01-13 01:00 | 4.6408 | 0 | N/A | 0 | 0
2023-01-13 01:30 | 3.834 | 0 | N/A | 0 | 0
2023-01-13 02:00 | 3.2549 | 0 | N/A | 0 | 0
2023-01-13 02:30 | 3.2009 | 0 | N/A | 0 | 0
2023-01-13 03:00 | 2.9971 | 0 | N/A | 0 | 0
2023-01-13 03:30 | 2.7975 | 0 | N/A | 0 | 0
2023-01-13 04:00 | 2.7155 | 0 | N/A | 0 | 0
2023-01-13 04:30 | 2.7234 | 0 | N/A | 0 | 0
2023-01-13 05:00 | 2.7161 | 0 | N/A | 0 | 0
2023-01-13 05:30 | 2.8474 | 0 | N/A | 0 | 0
2023-01-13 06:00 | 2.9869 | 0 | N/A | 0 | 0
2023-01-13 06:30 | 3.255 | 0 | N/A | 0 | 0
2023-01-13 07:00 | 3.5723 | 0 | N/A | 0 | 0
2023-01-13 07:30 | 4.1134 | 0 | N/A | 0 | 0
2023-01-13 08:00 | 4.2373 | 0 | N/A | 0 | 0
2023-01-13 08:30 | 4.0531 | 0 | N/A | 0 | 0
2023-01-13 09:00 | 3.3944 | 0 | N/A | 0 | 0
2023-01-13 09:30 | 2.3397 | 0 | N/A | 0 | 0
2023-01-13 10:00 | 2.3064 | 0 | N/A | 0 | 0
2023-01-13 10:30 | 1.4956 | 0 | N/A | 0 | 0
2023-01-13 11:00 | 0.84393 | 0 | N/A | 0 | 0
2023-01-13 11:30 | -0.51175 | 0 | N/A | 0 | 0
2023-01-13 12:00 | -1.0453 | 0 | N/A | 0 | 0
2023-01-13 12:30 | -0.98964 | 0 | N/A | 0 | 0
2023-01-13 13:00 | -0.92093 | 0 | N/A | 0 | 0
2023-01-13 13:30 | -0.83272 | 0 | N/A | 0 | 0
2023-01-13 14:00 | -0.39834 | 0 | N/A | 0 | 0
2023-01-13 14:30 | -0.31401 | 0 | N/A | 0 | 0
2023-01-13 15:00 | -0.31842 | 0 | N/A | 0 | 0
2023-01-13 15:30 | -0.56487 | 0 | N/A | 0 | 0
2023-01-13 16:00 | -0.43868 | 0 | N/A | 0 | 0
2023-01-13 16:30 | 0.74953 | 0 | N/A | 0 | 0
2023-01-13 17:00 | 1.6354 | 0 | N/A | 0 | 0
2023-01-13 17:30 | 2.6026 | 0 | N/A | 0 | 0
2023-01-13 18:00 | 3.7719 | 0 | N/A | 0 | 0
2023-01-13 18:30 | 4.8303 | 0 | N/A | 0 | 0
2023-01-13 19:00 | 5.5764 | 0 | N/A | 0 | 0
2023-01-13 19:30 | 6.0287 | 0 | N/A | 0 | 0
2023-01-13 20:00 | 6.0941 | 0 | N/A | 0 | 0
2023-01-13 20:30 | 5.9802 | 0 | N/A | 0 | 0
2023-01-13 21:00 | 5.7235 | 0 | N/A | 0 | 0
2023-01-13 21:30 | 5.3035 | 0 | N/A | 0 | 0
2023-01-13 22:00 | 4.9247 | 0 | N/A | 0 | 0
2023-01-13 22:30 | 4.8867 | 0 | N/A | 0 | 0
2023-01-13 23:00 | 4.8377 | 0 | N/A | 0 | 0
2023-01-13 23:30 | 4.4554 | 0 | N/A | 0 | 0
2023-01-14 | 4.3225 | 0 | N/A | 0 | 0
2023-01-14 00:30 | 4.5961 | 0 | N/A | 0 | 0
2023-01-14 01:00 | 4.5799 | 0 | N/A | 0 | 0
2023-01-14 01:30 | 3.8624 | 0 | N/A | 0 | 0
2023-01-14 02:00 | 3.3033 | 0 | N/A | 0 | 0
2023-01-14 02:30 | 3.2128 | 0 | N/A | 0 | 0
2023-01-14 03:00 | 2.968 | 0 | N/A | 0 | 0
2023-01-14 03:30 | 2.8447 | 0 | N/A | 0 | 0
2023-01-14 04:00 | 2.7261 | 0 | N/A | 0 | 0
2023-01-14 04:30 | 2.729 | 0 | N/A | 0 | 0
2023-01-14 05:00 | 2.6979 | 0 | N/A | 0 | 0
2023-01-14 05:30 | 2.7884 | 0 | N/A | 0 | 0
2023-01-14 06:00 | 2.8195 | 0 | N/A | 0 | 0
2023-01-14 06:30 | 2.8937 | 0 | N/A | 0 | 0
2023-01-14 07:00 | 2.9169 | 0 | N/A | 0 | 0
2023-01-14 07:30 | 2.8268 | 0 | N/A | 0 | 0
2023-01-14 08:00 | 2.7361 | 0 | N/A | 0 | 0
2023-01-14 08:30 | 2.3629 | 0 | N/A | 0 | 0
2023-01-14 09:00 | 2.0586 | 0 | N/A | 0 | 0
2023-01-14 09:30 | 1.619 | 0 | N/A | 0 | 0
2023-01-14 10:00 | 1.1597 | 0 | N/A | 0 | 0
2023-01-14 10:30 | 0.87849 | 0 | N/A | 0 | 0
2023-01-14 11:00 | 0.66517 | 0 | N/A | 0 | 0
2023-01-14 11:30 | 0.58494 | 0 | N/A | 0 | 0
2023-01-14 12:00 | 0.54083 | 0 | N/A | 0 | 0
2023-01-14 12:30 | 0.57629 | 0 | N/A | 0 | 0
2023-01-14 13:00 | 0.70384 | 0 | N/A | 0 | 0
2023-01-14 13:30 | 0.82314 | 0 | N/A | 0 | 0
2023-01-14 14:00 | 1.0769 | 0 | N/A | 0 | 0
2023-01-14 14:30 | 1.3175 | 0 | N/A | 0 | 0
2023-01-14 15:00 | 1.7043 | 0 | N/A | 0 | 0
2023-01-14 15:30 | 2.1351 | 0 | N/A | 0 | 0
2023-01-14 16:00 | 2.5982 | 0 | N/A | 0 | 0
2023-01-14 16:30 | 3.3105 | 0 | N/A | 0 | 0
2023-01-14 17:00 | 4.1668 | 0 | N/A | 0 | 0
2023-01-14 17:30 | 5.0726 | 0 | N/A | 0 | 0
2023-01-14 18:00 | 6.1535 | 0 | N/A | 0 | 0
2023-01-14 18:30 | 7.2554 | 0 | N/A | 0 | 0
2023-01-14 19:00 | 7.9371 | 0 | N/A | 0 | 0
2023-01-14 19:30 | 8.3103 | 0 | N/A | 0 | 0
2023-01-14 20:00 | 8.3441 | 0 | N/A | 0 | 0
2023-01-14 20:30 | 8.0099 | 0 | N/A | 0 | 0
2023-01-14 21:00 | 7.3583 | 0 | N/A | 0 | 0
2023-01-14 21:30 | 6.7707 | 0 | N/A | 0 | 0
2023-01-14 22:00 | 6.0498 | 0 | N/A | 0 | 0
2023-01-14 22:30 | 5.7966 | 0 | N/A | 0 | 0
2023-01-14 23:00 | 5.3887 | 0 | N/A | 0 | 0
2023-01-14 23:30 | 4.7754 | 0 | N/A | 0 | 0
2023-01-15 | 4.5952 | 0 | N/A | 0 | 0
2023-01-15 00:30 | 4.8446 | 0 | N/A | 0 | 0
2023-01-15 01:00 | 4.8467 | 0 | N/A | 0 | 0
2023-01-15 01:30 | 3.9303 | 0 | N/A | 0 | 0
2023-01-15 02:00 | 3.469 | 0 | N/A | 0 | 0
2023-01-15 02:30 | 3.4325 | 0 | N/A | 0 | 0
2023-01-15 03:00 | 3.1847 | 0 | N/A | 0 | 0
2023-01-15 03:30 | 2.9425 | 0 | N/A | 0 | 0
2023-01-15 04:00 | 2.8786 | 0 | N/A | 0 | 0
2023-01-15 04:30 | 2.8384 | 0 | N/A | 0 | 0
2023-01-15 05:00 | 2.8279 | 0 | N/A | 0 | 0
2023-01-15 05:30 | 2.8712 | 0 | N/A | 0 | 0
2023-01-15 06:00 | 2.8618 | 0 | N/A | 0 | 0
2023-01-15 06:30 | 2.9742 | 0 | N/A | 0 | 0
2023-01-15 07:00 | 2.9949 | 0 | N/A | 0 | 0
2023-01-15 07:30 | 2.912 | 0 | N/A | 0 | 0
2023-01-15 08:00 | 2.8385 | 0 | N/A | 0 | 0
2023-01-15 08:30 | 2.8106 | 0 | N/A | 0 | 0
2023-01-15 09:00 | 2.7973 | 0 | N/A | 0 | 0
2023-01-15 09:30 | 2.533 | 0 | N/A | 0 | 0
2023-01-15 10:00 | 2.0797 | 0 | N/A | 0 | 0
2023-01-15 10:30 | 1.6637 | 0 | N/A | 0 | 0
2023-01-15 11:00 | 1.2604 | 0 | N/A | 0 | 0
2023-01-15 11:30 | 1.1622 | 0 | N/A | 0 | 0
2023-01-15 12:00 | 0.9851 | 0 | N/A | 0 | 0
2023-01-15 12:30 | -0.83974 | 0 | N/A | 0 | 0
2023-01-15 13:00 | -1.0607 | 0 | N/A | 0 | 0
2023-01-15 13:30 | -1.5538 | 0 | N/A | 0 | 0
2023-01-15 14:00 | -1.9351 | 0 | N/A | 0 | 0
2023-01-15 14:30 | -2.2867 | 0 | N/A | 0 | 0
2023-01-15 15:00 | -2.5932 | 0 | N/A | 0 | 0
2023-01-15 15:30 | -2.5159 | 0 | N/A | 0 | 0
2023-01-15 16:00 | -2.256 | 0 | N/A | 0 | 0
2023-01-15 16:30 | -1.8343 | 0 | N/A | 0 | 0
2023-01-15 17:00 | -1.1696 | 0 | N/A | 0 | 0
2023-01-15 17:30 | -0.78772 | 0 | N/A | 0 | 0
2023-01-15 18:00 | 1.2526 | 0 | N/A | 0 | 0
2023-01-15 18:30 | 2.1409 | 0 | N/A | 0 | 0
2023-01-15 19:00 | 2.9452 | 0 | N/A | 0 | 0
2023-01-15 19:30 | 3.5345 | 0 | N/A | 0 | 0
2023-01-15 20:00 | 3.9393 | 0 | N/A | 0 | 0
2023-01-15 20:30 | 4.1057 | 0 | N/A | 0 | 0
2023-01-15 21:00 | 4.2915 | 0 | N/A | 0 | 0
2023-01-15 21:30 | 4.2324 | 0 | N/A | 0 | 0
2023-01-15 22:00 | 4.065 | 0 | N/A | 0 | 0
2023-01-15 22:30 | 4.3288 | 0 | N/A | 0 | 0
2023-01-15 23:00 | 4.3481 | 0 | N/A | 0 | 0
2023-01-15 23:30 | 4.0815 | 0 | N/A | 0 | 0
2023-01-16 | 3.9868 | 0 | N/A | 0 | 0
2023-01-16 00:30 | 4.2747 | 0 | N/A | 0 | 0
2023-01-16 01:00 | 4.4826 | 0 | N/A | 0 | 0
2023-01-16 01:30 | 3.7562 | 0 | N/A | 0 | 0
2023-01-16 02:00 | 3.2221 | 0 | N/A | 0 | 0
2023-01-16 02:30 | 3.1294 | 0 | N/A | 0 | 0
2023-01-16 03:00 | 2.8621 | 0 | N/A | 0 | 0
2023-01-16 03:30 | 2.6489 | 0 | N/A | 0 | 0
2023-01-16 04:00 | 2.5525 | 0 | N/A | 0 | 0
2023-01-16 04:30 | 2.5085 | 0 | N/A | 0 | 0
2023-01-16 05:00 | 2.5609 | 0 | N/A | 0 | 0
2023-01-16 05:30 | 2.6961 | 0 | N/A | 0 | 0
2023-01-16 06:00 | 2.9003 | 0 | N/A | 0 | 0
2023-01-16 06:30 | 3.2471 | 0 | N/A | 0 | 0
2023-01-16 07:00 | 3.8833 | 0 | N/A | 0 | 0
2023-01-16 07:30 | 4.2111 | 0 | N/A | 0 | 0
2023-01-16 08:00 | 3.3912 | 0 | N/A | 0 | 0
2023-01-16 08:30 | 3.1571 | 0 | N/A | 0 | 0
2023-01-16 09:00 | 3.1889 | 0 | N/A | 0 | 0
2023-01-16 09:30 | 2.745 | 0 | N/A | 0 | 0
2023-01-16 10:00 | 2.5946 | 0 | N/A | 0 | 0
2023-01-16 10:30 | 2.7795 | 0 | N/A | 0 | 0
2023-01-16 11:00 | 2.8046 | 0 | N/A | 0 | 0
2023-01-16 11:30 | 1.8866 | 0 | N/A | 0 | 0
2023-01-16 12:00 | 0.75854 | 0 | N/A | 0 | 0
2023-01-16 12:30 | 0.45929 | 0 | N/A | 0 | 0
2023-01-16 13:00 | 1.2053 | 0 | N/A | 0 | 0
2023-01-16 13:30 | 0.36723 | 0 | N/A | 0 | 0
2023-01-16 14:00 | -0.66622 | 0 | N/A | 0 | 0
2023-01-16 14:30 | -0.96301 | 0 | N/A | 0 | 0
2023-01-16 15:00 | -0.43529 | 0 | N/A | 0 | 0
2023-01-16 15:30 | 0.34217 | 0 | N/A | 0 | 0
2023-01-16 16:00 | 1.3908 | 0 | N/A | 0 | 0
2023-01-16 16:30 | 1.3402 | 0 | N/A | 0 | 0
2023-01-16 17:00 | 3.4644 | 0 | N/A | 0 | 0
2023-01-16 17:30 | 3.8342 | 0 | N/A | 0 | 0
2023-01-16 18:00 | 4.624 | 0 | N/A | 0 | 0
2023-01-16 18:30 | 4.5604 | 0 | N/A | 0 | 0
2023-01-16 19:00 | 5.3225 | 0 | N/A | 0 | 0
2023-01-16 19:30 | 5.8923 | 0 | N/A | 0 | 0
2023-01-16 20:00 | 6.0724 | 0 | N/A | 0 | 0
2023-01-16 20:30 | 5.9689 | 0 | N/A | 0 | 0
2023-01-16 21:00 | 5.7399 | 0 | N/A | 0 | 0
2023-01-16 21:30 | 5.4726 | 0 | N/A | 0 | 0
2023-01-16 22:00 | 5.113 | 0 | N/A | 0 | 0
2023-01-16 22:30 | 5.1382 | 0 | N/A | 0 | 0
2023-01-16 23:00 | 4.8646 | 0 | N/A | 0 | 0
2023-01-16 23:30 | 4.4394 | 0 | N/A | 0 | 0
2023-01-17 | 4.3414 | 0 | N/A | 0 | 0
2023-01-19 00:30 | 4.5957 | 0 | N/A | 0 | 0
2023-01-19 01:00 | 4.8287 | 0 | N/A | 0 | 0
2023-01-19 01:30 | 4.0272 | 0 | N/A | 0 | 0
2023-01-19 02:00 | 3.502 | 0 | N/A | 0 | 0
2023-01-19 02:30 | 3.4092 | 0 | N/A | 0 | 0
2023-01-19 03:00 | 3.1365 | 0 | N/A | 0 | 0
2023-01-19 03:30 | 2.8902 | 0 | N/A | 0 | 0
2023-01-19 04:00 | 2.815 | 0 | N/A | 0 | 0
2023-01-19 04:30 | 2.7537 | 0 | N/A | 0 | 0
2023-01-19 05:00 | 2.8268 | 0 | N/A | 0 | 0
2023-01-19 05:30 | 2.9803 | 0 | N/A | 0 | 0
2023-01-19 06:00 | 3.195 | 0 | N/A | 0 | 0
2023-01-19 06:30 | 3.5468 | 0 | N/A | 0 | 0
2023-01-19 07:00 | 3.9494 | 0 | N/A | 0 | 0
2023-01-19 07:30 | 4.4847 | 0 | N/A | 0 | 0
2023-01-19 08:00 | 4.7519 | 0 | N/A | 0 | 0
2023-01-19 08:30 | 4.7227 | 0 | N/A | 0 | 0
2023-01-19 09:00 | 4.4596 | 0 | N/A | 0 | 0
2023-01-19 09:30 | 3.993 | 0 | N/A | 0 | 0
2023-01-19 10:00 | 3.7653 | 0 | N/A | 0 | 0
2023-01-19 10:30 | 4.2695 | 0 | N/A | 0 | 0
2023-01-19 11:00 | 2.7278 | 0 | N/A | 0 | 0
2023-01-19 11:30 | 2.5275 | 0 | N/A | 0 | 0
2023-01-19 12:00 | 1.6046 | 0 | N/A | 0 | 0
2023-01-19 12:30 | 1.0517 | 0 | N/A | 0 | 0
2023-01-19 13:00 | -0.5747 | 0 | N/A | 0 | 0
2023-01-19 13:30 | -0.91727 | 0 | N/A | 0 | 0
2023-01-19 14:00 | -0.6589 | 0 | N/A | 0 | 0
2023-01-19 14:30 | 0.68803 | 0 | N/A | 0 | 0
2023-01-19 15:00 | -1.339 | 0 | N/A | 0 | 0
2023-01-19 15:30 | -1.4664 | 0 | N/A | 0 | 0
2023-01-19 16:00 | -1.5234 | 0 | N/A | 0 | 0
2023-01-19 16:30 | -1.5623 | 0 | N/A | 0 | 0
2023-01-19 17:00 | -1.4223 | 0 | N/A | 0 | 0
2023-01-19 17:30 | -0.92909 | 0 | N/A | 0 | 0
2023-01-19 18:00 | 1.2777 | 0 | N/A | 0 | 0
2023-01-19 18:30 | 2.0307 | 0 | N/A | 0 | 0
2023-01-19 19:00 | 2.9054 | 0 | N/A | 0 | 0
2023-01-19 19:30 | 3.6001 | 0 | N/A | 0 | 0
2023-01-19 20:00 | 4.0929 | 0 | N/A | 0 | 0
2023-01-19 20:30 | 4.462 | 0 | N/A | 0 | 0
2023-01-19 21:00 | 4.6872 | 0 | N/A | 0 | 0
2023-01-19 21:30 | 4.7291 | 0 | N/A | 0 | 0
2023-01-19 22:00 | 4.5353 | 0 | N/A | 0 | 0
2023-01-19 22:30 | 4.6859 | 0 | N/A | 0 | 0
2023-01-19 23:00 | 4.6396 | 0 | N/A | 0 | 0
2023-01-19 23:30 | 4.3133 | 0 | N/A | 0 | 0
2023-01-20 | 4.283 | 0 | N/A | 0 | 0
2023-01-20 00:30 | 4.5522 | 0 | N/A | 0 | 0
2023-01-20 01:00 | 4.7477 | 0 | N/A | 0 | 0
2023-01-20 01:30 | 4.0159 | 0 | N/A | 0 | 0
2023-01-20 02:00 | 3.4316 | 0 | N/A | 0 | 0
2023-01-20 02:30 | 3.3154 | 0 | N/A | 0 | 0
2023-01-20 03:00 | 3.1201 | 0 | N/A | 0 | 0
2023-01-20 03:30 | 2.909 | 0 | N/A | 0 | 0
2023-01-20 04:00 | 2.7583 | 0 | N/A | 0 | 0
2023-01-20 04:30 | 2.7005 | 0 | N/A | 0 | 0
2023-01-20 05:00 | 2.7383 | 0 | N/A | 0 | 0
2023-01-20 05:30 | 2.9496 | 0 | N/A | 0 | 0
2023-01-20 06:00 | 3.1513 | 0 | N/A | 0 | 0
2023-01-20 06:30 | 3.5089 | 0 | N/A | 0 | 0
2023-01-20 07:00 | 4.0759 | 0 | N/A | 0 | 0
2023-01-20 07:30 | 4.5242 | 0 | N/A | 0 | 0
2023-01-20 08:00 | 4.6868 | 0 | N/A | 0 | 0
2023-01-20 08:30 | 5.0167 | 0 | N/A | 0 | 0
2023-01-20 09:00 | 4.9311 | 0 | N/A | 0 | 0
2023-01-20 09:30 | 4.6317 | 0 | N/A | 0 | 0
2023-01-20 10:00 | 4.7029 | 0 | N/A | 0 | 0
2023-01-20 10:30 | 4.3493 | 0 | N/A | 0 | 0
2023-01-20 11:00 | 3.0067 | 0 | N/A | 0 | 0
2023-01-20 11:30 | 2.1164 | 0 | N/A | 0 | 0
2023-01-20 12:00 | 1.4756 | 0 | N/A | 0 | 0
2023-01-20 12:30 | 0.89677 | 0 | N/A | 0 | 0
2023-01-20 13:00 | 0.65812 | 0 | N/A | 0 | 0
2023-01-20 13:30 | -0.61464 | 0 | N/A | 0 | 0
2023-01-20 14:00 | -0.71957 | 0 | N/A | 0 | 0
2023-01-20 14:30 | -1.0375 | 0 | N/A | 0 | 0
2023-01-20 15:00 | -1.2984 | 0 | N/A | 0 | 0
2023-01-20 15:30 | -1.2327 | 0 | N/A | 0 | 0
2023-01-20 16:00 | -1.7568 | 0 | N/A | 0 | 0
2023-01-20 16:30 | -1.9313 | 0 | N/A | 0 | 0
2023-01-20 17:00 | -1.3595 | 0 | N/A | 0 | 0
2023-01-20 17:30 | -0.90002 | 0 | N/A | 0 | 0
2023-01-20 18:00 | 1.1926 | 0 | N/A | 0 | 0
2023-01-20 18:30 | 1.9378 | 0 | N/A | 0 | 0
2023-01-20 19:00 | 2.7164 | 0 | N/A | 0 | 0
2023-01-20 19:30 | 3.5573 | 0 | N/A | 0 | 0
2023-01-20 20:00 | 3.7217 | 0 | N/A | 0 | 0
2023-01-20 20:30 | 4.1111 | 0 | N/A | 0 | 0
2023-01-20 21:00 | 4.2321 | 0 | N/A | 0 | 0
2023-01-20 21:30 | 4.2374 | 0 | N/A | 0 | 0
2023-01-20 22:00 | 4.0656 | 0 | N/A | 0 | 0
2023-01-20 22:30 | 4.2652 | 0 | N/A | 0 | 0
2023-01-20 23:00 | 4.4101 | 0 | N/A | 0 | 0
2023-01-20 23:30 | 4.1342 | 0 | N/A | 0 | 0
2023-01-21 | 4.0101 | 0 | N/A | 0 | 0
2023-01-21 00:30 | 4.3504 | 0 | N/A | 0 | 0
2023-01-21 01:00 | 4.5654 | 0 | N/A | 0 | 0
2023-01-21 01:30 | 3.8242 | 0 | N/A | 0 | 0
2023-01-21 02:00 | 3.3182 | 0 | N/A | 0 | 0
2023-01-21 02:30 | 3.2414 | 0 | N/A | 0 | 0
2023-01-21 03:00 | 3.0591 | 0 | N/A | 0 | 0
2023-01-21 03:30 | 2.8061 | 0 | N/A | 0 | 0
2023-01-21 04:00 | 2.6992 | 0 | N/A | 0 | 0
2023-01-21 04:30 | 2.6154 | 0 | N/A | 0 | 0
2023-01-21 05:00 | 2.631 | 0 | N/A | 0 | 0
2023-01-21 05:30 | 2.5944 | 0 | N/A | 0 | 0
2023-01-21 06:00 | 2.6869 | 0 | N/A | 0 | 0
2023-01-21 06:30 | 2.8417 | 0 | N/A | 0 | 0
2023-01-21 07:00 | 3.0724 | 0 | N/A | 0 | 0
2023-01-21 07:30 | 3.45 | 0 | N/A | 0 | 0
2023-01-21 08:00 | 3.5841 | 0 | N/A | 0 | 0
2023-01-21 08:30 | 3.6139 | 0 | N/A | 0 | 0
2023-01-21 09:00 | 3.4849 | 0 | N/A | 0 | 0
2023-01-21 09:30 | 3.0513 | 0 | N/A | 0 | 0
2023-01-21 10:00 | 1.8746 | 0 | N/A | 0 | 0
2023-01-21 10:30 | -0.95112 | 0 | N/A | 0 | 0
2023-01-21 11:00 | -1.041 | 0 | N/A | 0 | 0
2023-01-21 11:30 | -1.3135 | 0 | N/A | 0 | 0
2023-01-21 12:00 | -0.92515 | 0 | N/A | 0 | 0
2023-01-21 12:30 | -1.2169 | 0 | N/A | 0 | 0
2023-01-21 13:00 | -2.3624 | 0 | N/A | 0 | 0
2023-01-21 13:30 | -2.1521 | 0 | N/A | 0 | 0
2023-01-21 14:00 | -1.4346 | 0 | N/A | 0 | 0
2023-01-21 14:30 | -0.92195 | 0 | N/A | 0 | 0
2023-01-21 15:00 | -1.4791 | 0 | N/A | 0 | 0
2023-01-21 15:30 | -1.4649 | 0 | N/A | 0 | 0
2023-01-21 16:00 | -1.0573 | 0 | N/A | 0 | 0
2023-01-21 16:30 | -1.0486 | 0 | N/A | 0 | 0
2023-01-21 17:00 | 0.88109 | 0 | N/A | 0 | 0
2023-01-21 17:30 | 0.84354 | 0 | N/A | 0 | 0
2023-01-21 18:00 | 1.479 | 0 | N/A | 0 | 0
2023-01-21 18:30 | 2.1719 | 0 | N/A | 0 | 0
2023-01-21 19:00 | 2.7943 | 0 | N/A | 0 | 0
2023-01-21 19:30 | 3.6936 | 0 | N/A | 0 | 0
2023-01-21 20:00 | 3.9035 | 0 | N/A | 0 | 0
2023-01-21 20:30 | 4.1594 | 0 | N/A | 0 | 0
2023-01-21 21:00 | 4.1363 | 0 | N/A | 0 | 0
2023-01-21 21:30 | 4.0909 | 0 | N/A | 0 | 0
2023-01-21 22:00 | 3.9529 | 0 | N/A | 0 | 0
2023-01-21 22:30 | 4.1775 | 0 | N/A | 0 | 0
2023-01-21 23:00 | 4.2592 | 0 | N/A | 0 | 0
2023-01-21 23:30 | 4.0751 | 0 | N/A | 0 | 0
2023-01-22 | 4.0435 | 0 | N/A | 0 | 0
2023-01-22 00:30 | 4.2763 | 0 | N/A | 0 | 0
2023-01-22 01:00 | 4.4785 | 0 | N/A | 0 | 0
2023-01-22 01:30 | 3.7243 | 0 | N/A | 0 | 0
2023-01-22 02:00 | 3.1902 | 0 | N/A | 0 | 0
2023-01-22 02:30 | 3.108 | 0 | N/A | 0 | 0
2023-01-22 03:00 | 2.9681 | 0 | N/A | 0 | 0
2023-01-22 03:30 | 2.7334 | 0 | N/A | 0 | 0
2023-01-22 04:00 | 2.572 | 0 | N/A | 0 | 0
2023-01-22 04:30 | 2.5462 | 0 | N/A | 0 | 0
2023-01-22 05:00 | 2.5257 | 0 | N/A | 0 | 0
2023-01-22 05:30 | 2.5765 | 0 | N/A | 0 | 0
2023-01-22 06:00 | 2.5869 | 0 | N/A | 0 | 0
2023-01-22 06:30 | 2.779 | 0 | N/A | 0 | 0
2023-01-22 07:00 | 2.7838 | 0 | N/A | 0 | 0
2023-01-22 07:30 | 2.8106 | 0 | N/A | 0 | 0
2023-01-22 08:00 | 2.6839 | 0 | N/A | 0 | 0
2023-01-22 08:30 | 2.4891 | 0 | N/A | 0 | 0
2023-01-22 09:00 | 2.1342 | 0 | N/A | 0 | 0
2023-01-22 09:30 | 1.8941 | 0 | N/A | 0 | 0
2023-01-22 10:00 | 1.4405 | 0 | N/A | 0 | 0
2023-01-22 10:30 | 1.1195 | 0 | N/A | 0 | 0
2023-01-22 11:00 | -1.0016 | 0 | N/A | 0 | 0
2023-01-22 11:30 | -1.2999 | 0 | N/A | 0 | 0
2023-01-22 12:00 | -1.6428 | 0 | N/A | 0 | 0
2023-01-22 12:30 | -1.8638 | 0 | N/A | 0 | 0
2023-01-22 13:00 | -1.9752 | 0 | N/A | 0 | 0
2023-01-22 13:30 | -1.99 | 0 | N/A | 0 | 0
2023-01-22 14:00 | -1.734 | 0 | N/A | 0 | 0
2023-01-22 14:30 | -1.5644 | 0 | N/A | 0 | 0
2023-01-22 15:00 | -1.5913 | 0 | N/A | 0 | 0
2023-01-22 15:30 | -1.2937 | 0 | N/A | 0 | 0
2023-01-22 16:00 | -1.1688 | 0 | N/A | 0 | 0
2023-01-22 16:30 | -0.85797 | 0 | N/A | 0 | 0
2023-01-22 17:00 | -0.72667 | 0 | N/A | 0 | 0
2023-01-22 17:30 | 1.5487 | 0 | N/A | 0 | 0
2023-01-22 18:00 | 2.3358 | 0 | N/A | 0 | 0
2023-01-22 18:30 | 2.9114 | 0 | N/A | 0 | 0
2023-01-22 19:00 | 3.5384 | 0 | N/A | 0 | 0
2023-01-22 19:30 | 4.0262 | 0 | N/A | 0 | 0
2023-01-22 20:00 | 4.4214 | 0 | N/A | 0 | 0
2023-01-22 20:30 | 4.4958 | 0 | N/A | 0 | 0
2023-01-22 21:00 | 4.4853 | 0 | N/A | 0 | 0
2023-01-22 21:30 | 4.3943 | 0 | N/A | 0 | 0
2023-01-22 22:00 | 4.1667 | 0 | N/A | 0 | 0
2023-01-22 22:30 | 4.3564 | 0 | N/A | 0 | 0
2023-01-22 23:00 | 4.3015 | 0 | N/A | 0 | 0
2023-01-22 23:30 | 4.054 | 0 | N/A | 0 | 0
2023-01-23 | 4.0888 | 0 | N/A | 0 | 0
2023-01-23 00:30 | 4.3165 | 0 | N/A | 0 | 0
2023-01-23 01:00 | 4.4402 | 0 | N/A | 0 | 0
2023-01-23 01:30 | 3.7188 | 0 | N/A | 0 | 0
2023-01-23 02:00 | 3.1791 | 0 | N/A | 0 | 0
2023-01-23 02:30 | 3.1571 | 0 | N/A | 0 | 0
2023-01-23 03:00 | 2.9755 | 0 | N/A | 0 | 0
2023-01-23 03:30 | 2.7226 | 0 | N/A | 0 | 0
2023-01-23 04:00 | 2.586 | 0 | N/A | 0 | 0
2023-01-23 04:30 | 2.5596 | 0 | N/A | 0 | 0
2023-01-23 05:00 | 2.5988 | 0 | N/A | 0 | 0
2023-01-23 05:30 | 2.796 | 0 | N/A | 0 | 0
2023-01-23 06:00 | 2.9816 | 0 | N/A | 0 | 0
2023-01-23 06:30 | 3.3066 | 0 | N/A | 0 | 0
2023-01-23 07:00 | 3.9124 | 0 | N/A | 0 | 0
2023-01-23 07:30 | 4.3771 | 0 | N/A | 0 | 0
2023-01-23 08:00 | 4.2353 | 0 | N/A | 0 | 0
2023-01-23 08:30 | 3.8143 | 0 | N/A | 0 | 0
2023-01-23 09:00 | 3.5118 | 0 | N/A | 0 | 0
2023-01-23 09:30 | 2.7503 | 0 | N/A | 0 | 0
2023-01-23 10:00 | 1.7701 | 0 | N/A | 0 | 0
2023-01-23 10:30 | 0.9255 | 0 | N/A | 0 | 0
2023-01-23 11:00 | 0.40668 | 0 | N/A | 0 | 0
2023-01-23 11:30 | -0.54659 | 0 | N/A | 0 | 0
2023-01-23 12:00 | -0.60877 | 0 | N/A | 0 | 0
2023-01-23 12:30 | -0.60631 | 0 | N/A | 0 | 0
2023-01-23 13:00 | 0.52698 | 0 | N/A | 0 | 0
2023-01-23 13:30 | 0.52069 | 0 | N/A | 0 | 0
2023-01-23 14:00 | 0.74204 | 0 | N/A | 0 | 0
2023-01-23 14:30 | 0.3746 | 0 | N/A | 0 | 0
2023-01-23 15:00 | 0.41189 | 0 | N/A | 0 | 0
2023-01-23 15:30 | 0.73424 | 0 | N/A | 0 | 0
2023-01-23 16:00 | 1.1048 | 0 | N/A | 0 | 0
2023-01-23 16:30 | 1.2131 | 0 | N/A | 0 | 0
2023-01-23 17:00 | 1.8011 | 0 | N/A | 0 | 0
2023-01-23 17:30 | 2.4046 | 0 | N/A | 0 | 0
2023-01-23 18:00 | 3.3925 | 0 | N/A | 0 | 0
2023-01-23 18:30 | 4.4755 | 0 | N/A | 0 | 0
2023-01-23 19:00 | 5.2416 | 0 | N/A | 0 | 0
2023-01-23 19:30 | 5.6045 | 0 | N/A | 0 | 0
2023-01-23 20:00 | 5.4601 | 0 | N/A | 0 | 0
2023-01-23 20:30 | 5.3205 | 0 | N/A | 0 | 0
2023-01-23 21:00 | 5.1495 | 0 | N/A | 0 | 0
2023-01-23 21:30 | 4.8885 | 0 | N/A | 0 | 0
2023-01-23 22:00 | 4.536 | 0 | N/A | 0 | 0
2023-01-23 22:30 | 4.6181 | 0 | N/A | 0 | 0
2023-01-23 23:00 | 4.4789 | 0 | N/A | 0 | 0
2023-01-23 23:30 | 4.1048 | 0 | N/A | 0 | 0
2023-01-24 | 4.0957 | 0 | N/A | 0 | 0
2023-01-24 00:30 | 4.3168 | 0 | N/A | 0 | 0
2023-01-24 01:00 | 4.4256 | 0 | N/A | 0 | 0
2023-01-24 01:30 | 3.6507 | 0 | N/A | 0 | 0
2023-01-24 02:00 | 3.1848 | 0 | N/A | 0 | 0
2023-01-24 02:30 | 3.1148 | 0 | N/A | 0 | 0
2023-01-24 03:00 | 2.9086 | 0 | N/A | 0 | 0
2023-01-24 03:30 | 2.7773 | 0 | N/A | 0 | 0
2023-01-24 04:00 | 2.6451 | 0 | N/A | 0 | 0
2023-01-24 04:30 | 2.6592 | 0 | N/A | 0 | 0
2023-01-24 05:00 | 2.6632 | 0 | N/A | 0 | 0
2023-01-24 05:30 | 2.7577 | 0 | N/A | 0 | 0
2023-01-24 06:00 | 3.0221 | 0 | N/A | 0 | 0
2023-01-24 06:30 | 3.3446 | 0 | N/A | 0 | 0
2023-01-24 07:00 | 4.0286 | 0 | N/A | 0 | 0
2023-01-24 07:30 | 4.3146 | 0 | N/A | 0 | 0
2023-01-24 08:00 | 4.2808 | 0 | N/A | 0 | 0
2023-01-24 08:30 | 4.59 | 0 | N/A | 0 | 0
2023-01-24 09:00 | 4.5013 | 0 | N/A | 0 | 0
2023-01-24 09:30 | 4.1092 | 0 | N/A | 0 | 0
2023-01-24 10:00 | 3.0339 | 0 | N/A | 0 | 0
2023-01-24 10:30 | 2.44 | 0 | N/A | 0 | 0
2023-01-24 11:00 | 0.68505 | 0 | N/A | 0 | 0
2023-01-24 11:30 | 0.90961 | 0 | N/A | 0 | 0
2023-01-24 12:00 | 0.75439 | 0 | N/A | 0 | 0
2023-01-24 12:30 | 1.7866 | 0 | N/A | 0 | 0
2023-01-24 13:00 | 1.5261 | 0 | N/A | 0 | 0
2023-01-24 13:30 | 1.3651 | 0 | N/A | 0 | 0
2023-01-24 14:00 | 0.68471 | 0 | N/A | 0 | 0
2023-01-24 14:30 | 0.90706 | 0 | N/A | 0 | 0
2023-01-24 15:00 | 3.6875 | 0 | N/A | 0 | 0
2023-01-24 15:30 | 4.4895 | 0 | N/A | 0 | 0
2023-01-24 16:00 | 3.4571 | 0 | N/A | 0 | 0
2023-01-24 16:30 | 2.3556 | 0 | N/A | 0 | 0
2023-01-24 17:00 | 1.7983 | 0 | N/A | 0 | 0
2023-01-24 17:30 | 1.6503 | 0 | N/A | 0 | 0
2023-01-24 18:00 | 2.9762 | 0 | N/A | 0 | 0
2023-01-24 18:30 | 3.5424 | 0 | N/A | 0 | 0
2023-01-24 19:00 | 3.5792 | 0 | N/A | 0 | 0
2023-01-24 19:30 | 3.9173 | 0 | N/A | 0 | 0
2023-01-24 20:00 | 4.339 | 0 | N/A | 0 | 0
2023-01-24 20:30 | 4.6616 | 0 | N/A | 0 | 0
2023-01-24 21:00 | 4.6898 | 0 | N/A | 0 | 0
2023-01-24 21:30 | 4.6665 | 0 | N/A | 0 | 0
2023-01-24 22:00 | 4.4039 | 0 | N/A | 0 | 0
2023-01-24 22:30 | 4.499 | 0 | N/A | 0 | 0
2023-01-24 23:00 | 4.4575 | 0 | N/A | 0 | 0
2023-01-24 23:30 | 4.0795 | 0 | N/A | 0 | 0
2023-01-25 | 3.9667 | 0 | N/A | 0 | 0
2023-01-25 00:30 | 4.3099 | 0 | N/A | 0 | 0
2023-01-25 01:00 | 4.4831 | 0 | N/A | 0 | 0
2023-01-25 01:30 | 3.7405 | 0 | N/A | 0 | 0
2023-01-25 02:00 | 3.2209 | 0 | N/A | 0 | 0
2023-01-25 02:30 | 3.1182 | 0 | N/A | 0 | 0
2023-01-25 03:00 | 2.9457 | 0 | N/A | 0 | 0
2023-01-25 03:30 | 2.7527 | 0 | N/A | 0 | 0
2023-01-25 04:00 | 2.6544 | 0 | N/A | 0 | 0
2023-01-25 04:30 | 2.6515 | 0 | N/A | 0 | 0
2023-01-25 05:00 | 2.6395 | 0 | N/A | 0 | 0
2023-01-25 05:30 | 2.7581 | 0 | N/A | 0 | 0
2023-01-25 06:00 | 2.9727 | 0 | N/A | 0 | 0
2023-01-25 06:30 | 3.6052 | 0 | N/A | 0 | 0
2023-01-25 07:00 | 4.1947 | 0 | N/A | 0 | 0
2023-01-25 07:30 | 4.471 | 0 | N/A | 0 | 0
2023-01-25 08:00 | 4.2855 | 0 | N/A | 0 | 0
2023-01-25 08:30 | 3.5849 | 0 | N/A | 0 | 0
2023-01-25 09:00 | 2.7905 | 0 | N/A | 0 | 0
2023-01-25 09:30 | 2.0923 | 0 | N/A | 0 | 0
2023-01-25 10:00 | 1.077 | 0 | N/A | 0 | 0
2023-01-25 10:30 | 0.48374 | 0 | N/A | 0 | 0
2023-01-25 11:00 | -0.34913 | 0 | N/A | 0 | 0
2023-01-25 11:30 | -0.43534 | 0 | N/A | 0 | 0
2023-01-25 12:00 | -0.36577 | 0 | N/A | 0 | 0
2023-01-25 12:30 | -0.41623 | 0 | N/A | 0 | 0
2023-01-25 13:00 | -0.48591 | 0 | N/A | 0 | 0
2023-01-25 13:30 | 0.48814 | 0 | N/A | 0 | 0
2023-01-25 14:00 | 0.46755 | 0 | N/A | 0 | 0
2023-01-25 14:30 | 0.49357 | 0 | N/A | 0 | 0
2023-01-25 15:00 | 0.93217 | 0 | N/A | 0 | 0
2023-01-25 15:30 | 1.4537 | 0 | N/A | 0 | 0
2023-01-25 16:00 | 1.6205 | 0 | N/A | 0 | 0
2023-01-25 16:30 | 1.6286 | 0 | N/A | 0 | 0
2023-01-25 17:00 | 1.8514 | 0 | N/A | 0 | 0
2023-01-25 17:30 | 3.1378 | 0 | N/A | 0 | 0
2023-01-25 18:00 | 3.912 | 0 | N/A | 0 | 0
2023-01-25 18:30 | 4.7754 | 0 | N/A | 0 | 0
2023-01-25 19:00 | 5.4874 | 0 | N/A | 0 | 0
2023-01-25 19:30 | 5.3575 | 0 | N/A | 0 | 0
2023-01-25 20:00 | 5.5291 | 0 | N/A | 0 | 0
2023-01-25 20:30 | 5.3892 | 0 | N/A | 0 | 0
2023-01-25 21:00 | 5.2161 | 0 | N/A | 0 | 0
2023-01-25 21:30 | 4.9005 | 0 | N/A | 0 | 0
2023-01-25 22:00 | 4.6049 | 0 | N/A | 0 | 0
2023-01-25 22:30 | 4.6777 | 0 | N/A | 0 | 0
2023-01-25 23:00 | 4.5752 | 0 | N/A | 0 | 0
2023-01-25 23:30 | 4.1173 | 0 | N/A | 0 | 0
2023-01-26 | 4.1194 | 0 | N/A | 0 | 0
2023-01-26 00:30 | 4.4091 | 0 | N/A | 0 | 0
2023-01-26 01:00 | 4.5474 | 0 | N/A | 0 | 0
2023-01-26 01:30 | 3.8273 | 0 | N/A | 0 | 0
2023-01-26 02:00 | 3.2911 | 0 | N/A | 0 | 0
2023-01-26 02:30 | 3.1782 | 0 | N/A | 0 | 0
2023-01-26 03:00 | 2.9482 | 0 | N/A | 0 | 0
2023-01-26 03:30 | 2.7841 | 0 | N/A | 0 | 0
2023-01-26 04:00 | 2.7092 | 0 | N/A | 0 | 0
2023-01-26 04:30 | 2.655 | 0 | N/A | 0 | 0
2023-01-26 05:00 | 2.6062 | 0 | N/A | 0 | 0
2023-01-26 05:30 | 2.6574 | 0 | N/A | 0 | 0
2023-01-26 06:00 | 2.7471 | 0 | N/A | 0 | 0
2023-01-26 06:30 | 2.9196 | 0 | N/A | 0 | 0
2023-01-26 07:00 | 3.1186 | 0 | N/A | 0 | 0
2023-01-26 07:30 | 3.3499 | 0 | N/A | 0 | 0
2023-01-26 08:00 | 2.9936 | 0 | N/A | 0 | 0
2023-01-26 08:30 | 2.6482 | 0 | N/A | 0 | 0
2023-01-26 09:00 | 2.4651 | 0 | N/A | 0 | 0
2023-01-26 09:30 | 2.4499 | 0 | N/A | 0 | 0
2023-01-26 10:00 | 1.6781 | 0 | N/A | 0 | 0
2023-01-26 10:30 | 0.90472 | 0 | N/A | 0 | 0
2023-01-26 11:00 | -0.83269 | 0 | N/A | 0 | 0
2023-01-26 11:30 | -0.7801 | 0 | N/A | 0 | 0
2023-01-26 12:00 | -1.0672 | 0 | N/A | 0 | 0
2023-01-26 12:30 | -0.99231 | 0 | N/A | 0 | 0
2023-01-26 13:00 | -1.0894 | 0 | N/A | 0 | 0
2023-01-26 13:30 | -1.3675 | 0 | N/A | 0 | 0
2023-01-26 14:00 | -1.7089 | 0 | N/A | 0 | 0
2023-01-26 14:30 | -1.2511 | 0 | N/A | 0 | 0
2023-01-26 15:00 | -1.4034 | 0 | N/A | 0 | 0
2023-01-26 15:30 | -1.7988 | 0 | N/A | 0 | 0
2023-01-26 16:00 | -1.85 | 0 | N/A | 0 | 0
2023-01-26 16:30 | -1.6714 | 0 | N/A | 0 | 0
2023-01-26 17:00 | -1.1361 | 0 | N/A | 0 | 0
2023-01-26 17:30 | -0.80433 | 0 | N/A | 0 | 0
2023-01-26 18:00 | 1.3506 | 0 | N/A | 0 | 0
2023-01-26 18:30 | 2.3322 | 0 | N/A | 0 | 0
2023-01-26 19:00 | 3.0985 | 0 | N/A | 0 | 0
2023-01-26 19:30 | 3.5517 | 0 | N/A | 0 | 0
2023-01-26 20:00 | 4.0435 | 0 | N/A | 0 | 0
2023-01-26 20:30 | 4.2129 | 0 | N/A | 0 | 0
2023-01-26 21:00 | 4.2987 | 0 | N/A | 0 | 0
2023-01-26 21:30 | 4.228 | 0 | N/A | 0 | 0
2023-01-26 22:00 | 4.0237 | 0 | N/A | 0 | 0
2023-01-26 22:30 | 4.2345 | 0 | N/A | 0 | 0
2023-01-26 23:00 | 4.2662 | 0 | N/A | 0 | 0
2023-01-26 23:30 | 3.9228 | 0 | N/A | 0 | 0
2023-01-27 | 3.8863 | 0 | N/A | 0 | 0
2023-01-27 00:30 | 4.2228 | 0 | N/A | 0 | 0
2023-01-27 01:00 | 4.3884 | 0 | N/A | 0 | 0
2023-01-27 01:30 | 3.6652 | 0 | N/A | 0 | 0
2023-01-27 02:00 | 3.1745 | 0 | N/A | 0 | 0
2023-01-27 02:30 | 3.1037 | 0 | N/A | 0 | 0
2023-01-27 03:00 | 2.9207 | 0 | N/A | 0 | 0
2023-01-27 03:30 | 2.743 | 0 | N/A | 0 | 0
2023-01-27 04:00 | 2.585 | 0 | N/A | 0 | 0
2023-01-27 04:30 | 2.5767 | 0 | N/A | 0 | 0
2023-01-27 05:00 | 2.5536 | 0 | N/A | 0 | 0
2023-01-27 05:30 | 2.6819 | 0 | N/A | 0 | 0
2023-01-27 06:00 | 2.7958 | 0 | N/A | 0 | 0
2023-01-27 06:30 | 3.108 | 0 | N/A | 0 | 0
2023-01-27 07:00 | 3.2964 | 0 | N/A | 0 | 0
2023-01-27 07:30 | 3.5134 | 0 | N/A | 0 | 0
2023-01-27 08:00 | 3.2094 | 0 | N/A | 0 | 0
2023-01-27 08:30 | 2.5861 | 0 | N/A | 0 | 0
2023-01-27 09:00 | 1.9832 | 0 | N/A | 0 | 0
2023-01-27 09:30 | 1.2304 | 0 | N/A | 0 | 0
2023-01-27 10:00 | 0.71917 | 0 | N/A | 0 | 0
2023-01-27 10:30 | -0.95266 | 0 | N/A | 0 | 0
2023-01-27 11:00 | -1.3371 | 0 | N/A | 0 | 0
2023-01-27 11:30 | -1.4693 | 0 | N/A | 0 | 0
2023-01-27 12:00 | -2.1694 | 0 | N/A | 0 | 0
2023-01-27 12:30 | -2.3181 | 0 | N/A | 0 | 0
2023-01-27 13:00 | -2.4247 | 0 | N/A | 0 | 0
2023-01-27 13:30 | -2.4266 | 0 | N/A | 0 | 0
2023-01-27 14:00 | -2.4019 | 0 | N/A | 0 | 0
2023-01-27 14:30 | -2.1905 | 0 | N/A | 0 | 0
2023-01-27 15:00 | -1.883 | 0 | N/A | 0 | 0
2023-01-27 15:30 | -1.4533 | 0 | N/A | 0 | 0
2023-01-27 16:00 | -0.97744 | 0 | N/A | 0 | 0
2023-01-27 16:30 | -0.60974 | 0 | N/A | 0 | 0
2023-01-27 17:00 | 0.86667 | 0 | N/A | 0 | 0
2023-01-27 17:30 | 1.8045 | 0 | N/A | 0 | 0
2023-01-27 18:00 | 3.1384 | 0 | N/A | 0 | 0
2023-01-27 18:30 | 4.0969 | 0 | N/A | 0 | 0
2023-01-27 19:00 | 5.0189 | 0 | N/A | 0 | 0
2023-01-27 19:30 | 5.5961 | 0 | N/A | 0 | 0
2023-01-27 20:00 | 5.8485 | 0 | N/A | 0 | 0
2023-01-27 20:30 | 5.6621 | 0 | N/A | 0 | 0
2023-01-27 21:00 | 5.3415 | 0 | N/A | 0 | 0
2023-01-27 21:30 | 5.0191 | 0 | N/A | 0 | 0
2023-01-27 22:00 | 4.6637 | 0 | N/A | 0 | 0
2023-01-27 22:30 | 4.6843 | 0 | N/A | 0 | 0
2023-01-27 23:00 | 4.505 | 0 | N/A | 0 | 0
2023-01-27 23:30 | 4.1103 | 0 | N/A | 0 | 0
2023-01-28 | 4.0422 | 0 | N/A | 0 | 0
2023-01-28 00:30 | 4.3141 | 0 | N/A | 0 | 0
2023-01-28 01:00 | 4.3316 | 0 | N/A | 0 | 0
2023-01-28 01:30 | 3.5812 | 0 | N/A | 0 | 0
2023-01-28 02:00 | 3.126 | 0 | N/A | 0 | 0
2023-01-28 02:30 | 3.1024 | 0 | N/A | 0 | 0
2023-01-28 03:00 | 2.9218 | 0 | N/A | 0 | 0
2023-01-28 03:30 | 2.69 | 0 | N/A | 0 | 0
2023-01-28 04:00 | 2.5786 | 0 | N/A | 0 | 0
2023-01-28 04:30 | 2.573 | 0 | N/A | 0 | 0
2023-01-28 05:00 | 2.5498 | 0 | N/A | 0 | 0
2023-01-28 05:30 | 2.6016 | 0 | N/A | 0 | 0
2023-01-28 06:00 | 2.6073 | 0 | N/A | 0 | 0
2023-01-28 06:30 | 2.6804 | 0 | N/A | 0 | 0
2023-01-28 07:00 | 2.7435 | 0 | N/A | 0 | 0
2023-01-28 07:30 | 2.7302 | 0 | N/A | 0 | 0
2023-01-28 08:00 | 2.3398 | 0 | N/A | 0 | 0
2023-01-28 08:30 | 2.2296 | 0 | N/A | 0 | 0
2023-01-28 09:00 | 2.0416 | 0 | N/A | 0 | 0
2023-01-28 09:30 | 1.8062 | 0 | N/A | 0 | 0
2023-01-28 10:00 | 1.746 | 0 | N/A | 0 | 0
2023-01-28 10:30 | 1.0033 | 0 | N/A | 0 | 0
2023-01-28 11:00 | 1.1981 | 0 | N/A | 0 | 0
2023-01-28 11:30 | -0.92418 | 0 | N/A | 0 | 0
2023-01-28 12:00 | -1.3357 | 0 | N/A | 0 | 0
2023-01-28 12:30 | 1.4452 | 0 | N/A | 0 | 0
2023-01-28 13:00 | 1.804 | 0 | N/A | 0 | 0
2023-01-28 13:30 | 1.7592 | 0 | N/A | 0 | 0
2023-01-28 14:00 | 1.2074 | 0 | N/A | 0 | 0
2023-01-28 14:30 | 1.5277 | 0 | N/A | 0 | 0
2023-01-28 15:00 | 2.2176 | 0 | N/A | 0 | 0
2023-01-28 15:30 | 3.1054 | 0 | N/A | 0 | 0
2023-01-28 16:00 | 2.7461 | 0 | N/A | 0 | 0
2023-01-28 16:30 | 3.7602 | 0 | N/A | 0 | 0
2023-01-28 17:00 | 4.4295 | 0 | N/A | 0 | 0
2023-01-28 17:30 | 4.6893 | 0 | N/A | 0 | 0
2023-01-28 18:00 | 4.9868 | 0 | N/A | 0 | 0
2023-01-28 18:30 | 5.3424 | 0 | N/A | 0 | 0
2023-01-28 19:00 | 5.3747 | 0 | N/A | 0 | 0
2023-01-28 19:30 | 5.4405 | 0 | N/A | 0 | 0
2023-01-28 20:00 | 5.303 | 0 | N/A | 0 | 0
2023-01-28 20:30 | 4.9247 | 0 | N/A | 0 | 0
2023-01-28 21:00 | 4.8163 | 0 | N/A | 0 | 0
2023-01-28 21:30 | 4.7056 | 0 | N/A | 0 | 0
2023-01-28 22:00 | 4.4174 | 0 | N/A | 0 | 0
2023-01-28 22:30 | 4.504 | 0 | N/A | 0 | 0
2023-01-28 23:00 | 4.4967 | 0 | N/A | 0 | 0
2023-01-28 23:30 | 4.2101 | 0 | N/A | 0 | 0
2023-01-29 | 4.142 | 0 | N/A | 0 | 0
2023-01-29 00:30 | 4.4704 | 0 | N/A | 0 | 0
2023-01-29 01:00 | 4.5613 | 0 | N/A | 0 | 0
2023-01-29 01:30 | 3.7895 | 0 | N/A | 0 | 0
2023-01-29 02:00 | 3.259 | 0 | N/A | 0 | 0
2023-01-29 02:30 | 3.2354 | 0 | N/A | 0 | 0
2023-01-29 03:00 | 3.0657 | 0 | N/A | 0 | 0
2023-01-29 03:30 | 2.8344 | 0 | N/A | 0 | 0
2023-01-29 04:00 | 2.6832 | 0 | N/A | 0 | 0
2023-01-29 04:30 | 2.6542 | 0 | N/A | 0 | 0
2023-01-29 05:00 | 2.6238 | 0 | N/A | 0 | 0
2023-01-29 05:30 | 2.6281 | 0 | N/A | 0 | 0
2023-01-29 06:00 | 2.7148 | 0 | N/A | 0 | 0
2023-01-29 06:30 | 2.7971 | 0 | N/A | 0 | 0
2023-01-29 07:00 | 2.8862 | 0 | N/A | 0 | 0
2023-01-29 07:30 | 3.0089 | 0 | N/A | 0 | 0
2023-01-29 08:00 | 2.7958 | 0 | N/A | 0 | 0
2023-01-29 08:30 | 3.0219 | 0 | N/A | 0 | 0
2023-01-29 09:00 | 2.7971 | 0 | N/A | 0 | 0
2023-01-29 09:30 | 3.0969 | 0 | N/A | 0 | 0
2023-01-29 10:00 | 3.4015 | 0 | N/A | 0 | 0
2023-01-29 10:30 | 3.1249 | 0 | N/A | 0 | 0
2023-01-29 11:00 | 3.0954 | 0 | N/A | 0 | 0
2023-01-29 11:30 | 3.5966 | 0 | N/A | 0 | 0
2023-01-29 12:00 | 3.3482 | 0 | N/A | 0 | 0
2023-01-29 12:30 | 3.1093 | 0 | N/A | 0 | 0
2023-01-29 13:00 | 2.9295 | 0 | N/A | 0 | 0
2023-01-29 13:30 | 2.2788 | 0 | N/A | 0 | 0
2023-01-29 14:00 | 1.2864 | 0 | N/A | 0 | 0
2023-01-29 14:30 | 2.0061 | 0 | N/A | 0 | 0
2023-01-29 15:00 | 2.3966 | 0 | N/A | 0 | 0
2023-01-29 15:30 | 3.3428 | 0 | N/A | 0 | 0
2023-01-29 16:00 | 3.5686 | 0 | N/A | 0 | 0
2023-01-29 16:30 | 3.3891 | 0 | N/A | 0 | 0
2023-01-29 17:00 | 3.1206 | 0 | N/A | 0 | 0
2023-01-29 17:30 | 3.7911 | 0 | N/A | 0 | 0
2023-01-29 18:00 | 4.5082 | 0 | N/A | 0 | 0
2023-01-29 18:30 | 4.9029 | 0 | N/A | 0 | 0
2023-01-29 19:00 | 4.7821 | 0 | N/A | 0 | 0
2023-01-29 19:30 | 4.7552 | 0 | N/A | 0 | 0
2023-01-29 20:00 | 4.7812 | 0 | N/A | 0 | 0
2023-01-29 20:30 | 4.7278 | 0 | N/A | 0 | 0
2023-01-29 21:00 | 4.6496 | 0 | N/A | 0 | 0
2023-01-29 21:30 | 4.4724 | 0 | N/A | 0 | 0
2023-01-29 22:00 | 4.224 | 0 | N/A | 0 | 0
2023-01-29 22:30 | 4.3827 | 0 | N/A | 0 | 0
2023-01-29 23:00 | 4.4079 | 0 | N/A | 0 | 0
2023-01-29 23:30 | 4.052 | 0 | N/A | 0 | 0
2023-01-30 | 4.0372 | 0 | N/A | 0 | 0
2023-01-30 00:30 | 4.3776 | 0 | N/A | 0 | 0
2023-01-30 01:00 | 4.62 | 0 | N/A | 0 | 0
2023-01-30 01:30 | 3.8777 | 0 | N/A | 0 | 0
2023-01-30 02:00 | 3.2779 | 0 | N/A | 0 | 0
2023-01-30 02:30 | 3.2376 | 0 | N/A | 0 | 0
2023-01-30 03:00 | 2.9874 | 0 | N/A | 0 | 0
2023-01-30 03:30 | 2.7388 | 0 | N/A | 0 | 0
2023-01-30 04:00 | 2.6144 | 0 | N/A | 0 | 0
2023-01-30 04:30 | 2.541 | 0 | N/A | 0 | 0
2023-01-30 05:00 | 2.6239 | 0 | N/A | 0 | 0
2023-01-30 05:30 | 2.8128 | 0 | N/A | 0 | 0
2023-01-30 06:00 | 3.0179 | 0 | N/A | 0 | 0
2023-01-30 06:30 | 3.3866 | 0 | N/A | 0 | 0
2023-01-30 07:00 | 4.0273 | 0 | N/A | 0 | 0
2023-01-30 07:30 | 4.5875 | 0 | N/A | 0 | 0
2023-01-30 08:00 | 4.3797 | 0 | N/A | 0 | 0
2023-01-30 08:30 | 4.0867 | 0 | N/A | 0 | 0
2023-01-30 09:00 | 4.2864 | 0 | N/A | 0 | 0
2023-01-30 09:30 | 4.0145 | 0 | N/A | 0 | 0
2023-01-30 10:00 | 3.6492 | 0 | N/A | 0 | 0
2023-01-30 10:30 | 3.4902 | 0 | N/A | 0 | 0
2023-01-30 11:00 | 2.9352 | 0 | N/A | 0 | 0
2023-01-30 11:30 | 2.4019 | 0 | N/A | 0 | 0
2023-01-30 12:00 | 1.2987 | 0 | N/A | 0 | 0
2023-01-30 12:30 | -0.50139 | 0 | N/A | 0 | 0
2023-01-30 13:00 | -1.1344 | 0 | N/A | 0 | 0
2023-01-30 13:30 | -1.5863 | 0 | N/A | 0 | 0
2023-01-30 14:00 | -1.511 | 0 | N/A | 0 | 0
2023-01-30 14:30 | -1.4213 | 0 | N/A | 0 | 0
2023-01-30 15:00 | -1.0466 | 0 | N/A | 0 | 0
2023-01-30 15:30 | -1.4182 | 0 | N/A | 0 | 0
2023-01-30 16:00 | -1.1318 | 0 | N/A | 0 | 0
2023-01-30 16:30 | -0.71629 | 0 | N/A | 0 | 0
2023-01-30 17:00 | -0.78749 | 0 | N/A | 0 | 0
2023-01-30 17:30 | 1.5124 | 0 | N/A | 0 | 0
2023-01-30 18:00 | 2.5487 | 0 | N/A | 0 | 0
2023-01-30 18:30 | 3.0245 | 0 | N/A | 0 | 0
2023-01-30 19:00 | 4.0938 | 0 | N/A | 0 | 0
2023-01-30 19:30 | 4.2616 | 0 | N/A | 0 | 0
2023-01-30 20:00 | 4.4056 | 0 | N/A | 0 | 0
2023-01-30 20:30 | 4.538 | 0 | N/A | 0 | 0
2023-01-30 21:00 | 4.5634 | 0 | N/A | 0 | 0
2023-01-30 21:30 | 4.5376 | 0 | N/A | 0 | 0
2023-01-30 22:00 | 4.291 | 0 | N/A | 0 | 0
2023-01-30 22:30 | 4.3396 | 0 | N/A | 0 | 0
2023-01-30 23:00 | 4.3288 | 0 | N/A | 0 | 0
2023-01-30 23:30 | 4.0119 | 0 | N/A | 0 | 0
2023-01-31 | 3.9077 | 0 | N/A | 0 | 0
2023-01-31 00:30 | 4.3549 | 0 | N/A | 0 | 0
2023-01-31 01:00 | 4.505 | 0 | N/A | 0 | 0
2023-01-31 01:30 | 3.6813 | 0 | N/A | 0 | 0
2023-01-31 02:00 | 3.2001 | 0 | N/A | 0 | 0
2023-01-31 02:30 | 3.1493 | 0 | N/A | 0 | 0
2023-01-31 03:00 | 2.921 | 0 | N/A | 0 | 0
2023-01-31 03:30 | 2.7526 | 0 | N/A | 0 | 0
2023-01-31 04:00 | 2.5954 | 0 | N/A | 0 | 0
2023-01-31 04:30 | 2.5655 | 0 | N/A | 0 | 0
2023-01-31 05:00 | 2.6327 | 0 | N/A | 0 | 0
2023-01-31 05:30 | 2.7979 | 0 | N/A | 0 | 0
2023-01-31 06:00 | 3.0487 | 0 | N/A | 0 | 0
2023-01-31 06:30 | 3.4869 | 0 | N/A | 0 | 0
2023-01-31 07:00 | 4.1391 | 0 | N/A | 0 | 0
2023-01-31 07:30 | 4.6979 | 0 | N/A | 0 | 0
2023-01-31 08:00 | 4.6341 | 0 | N/A | 0 | 0
2023-01-31 08:30 | 3.8446 | 0 | N/A | 0 | 0
2023-01-31 09:00 | 3.3278 | 0 | N/A | 0 | 0
2023-01-31 09:30 | 2.6759 | 0 | N/A | 0 | 0
2023-01-31 10:00 | 2.4623 | 0 | N/A | 0 | 0
2023-01-31 10:30 | 1.549 | 0 | N/A | 0 | 0
2023-01-31 11:00 | 0.54947 | 0 | N/A | 0 | 0
2023-01-31 11:30 | -0.94843 | 0 | N/A | 0 | 0
2023-01-31 12:00 | -1.4803 | 0 | N/A | 0 | 0
2023-01-31 12:30 | -1.7854 | 0 | N/A | 0 | 0
2023-01-31 13:00 | -1.8001 | 0 | N/A | 0 | 0
2023-01-31 13:30 | -1.9479 | 0 | N/A | 0 | 0
2023-01-31 14:00 | -2.0396 | 0 | N/A | 0 | 0
2023-01-31 14:30 | -2.0836 | 0 | N/A | 0 | 0
2023-01-31 15:00 | -1.7742 | 0 | N/A | 0 | 0
2023-01-31 15:30 | -1.7121 | 0 | N/A | 0 | 0
2023-01-31 16:00 | -1.4693 | 0 | N/A | 0 | 0
2023-01-31 16:30 | -1.1024 | 0 | N/A | 0 | 0
2023-01-31 17:00 | -0.75664 | 0 | N/A | 0 | 0
2023-01-31 17:30 | 0.79119 | 0 | N/A | 0 | 0
2023-01-31 18:00 | 1.8158 | 0 | N/A | 0 | 0
2023-01-31 18:30 | 2.8981 | 0 | N/A | 0 | 0
2023-01-31 19:00 | 3.6927 | 0 | N/A | 0 | 0
2023-01-31 19:30 | 4.3103 | 0 | N/A | 0 | 0
2023-01-31 20:00 | 4.5738 | 0 | N/A | 0 | 0
2023-01-31 20:30 | 4.7021 | 0 | N/A | 0 | 0
2023-01-31 21:00 | 4.6826 | 0 | N/A | 0 | 0
2023-01-31 21:30 | 4.5243 | 0 | N/A | 0 | 0
2023-01-31 22:00 | 4.2861 | 0 | N/A | 0 | 0
2023-01-31 22:30 | 4.3479 | 0 | N/A | 0 | 0
2023-01-31 23:00 | 4.2675 | 0 | N/A | 0 | 0
2023-01-31 23:30 | 3.9614 | 0 | N/A | 0 | 0
2023-02-01 | 3.889 | 0 | N/A | 0 | 0
2023-02-01 00:30 | 4.1955 | 0 | N/A | 0 | 0
2023-02-01 01:00 | 4.3775 | 0 | N/A | 0 | 0
2023-02-01 01:30 | 3.6533 | 0 | N/A | 0 | 0
2023-02-01 02:00 | 3.1007 | 0 | N/A | 0 | 0
2023-02-01 02:30 | 3.0754 | 0 | N/A | 0 | 0
2023-02-01 03:00 | 2.8359 | 0 | N/A | 0 | 0
2023-02-01 03:30 | 2.7201 | 0 | N/A | 0 | 0
2023-02-01 04:00 | 2.6224 | 0 | N/A | 0 | 0
2023-02-01 04:30 | 2.5772 | 0 | N/A | 0 | 0
2023-02-01 05:00 | 1.9444 | 0 | N/A | 0 | 0
2023-02-01 05:30 | 1.5919 | 0 | N/A | 0 | 0
2023-02-01 06:00 | 4.2981 | 0 | N/A | 0 | 0
2023-02-01 06:30 | 3.4831 | 0 | N/A | 0 | 0
2023-02-01 07:00 | 4.0488 | 0 | N/A | 0 | 0
2023-02-01 07:30 | 4.719 | 0 | N/A | 0 | 0
2023-02-01 08:00 | 4.5169 | 0 | N/A | 0 | 0
2023-02-01 08:30 | 3.6089 | 0 | N/A | 0 | 0
2023-02-01 09:00 | 2.7633 | 0 | N/A | 0 | 0
2023-02-01 09:30 | 2.144 | 0 | N/A | 0 | 0
2023-02-01 10:00 | 2.6062 | 0 | N/A | 0 | 0
2023-02-01 10:30 | 2.9867 | 0 | N/A | 0 | 0
2023-02-01 11:00 | 2.7701 | 0 | N/A | 0 | 0
2023-02-01 11:30 | 1.6337 | 0 | N/A | 0 | 0
2023-02-01 12:00 | 1.2962 | 0 | N/A | 0 | 0
2023-02-01 12:30 | 1.6016 | 0 | N/A | 0 | 0
2023-02-01 13:00 | 1.5366 | 0 | N/A | 0 | 0
2023-02-01 13:30 | 1.0486 | 0 | N/A | 0 | 0
2023-02-01 14:00 | 2.3881 | 0 | N/A | 0 | 0
2023-02-01 14:30 | 2.181 | 0 | N/A | 0 | 0
2023-02-01 15:00 | -0.71487 | 0 | N/A | 0 | 0
2023-02-01 15:30 | 0.69446 | 0 | N/A | 0 | 0
2023-02-01 16:00 | 0.90328 | 0 | N/A | 0 | 0
2023-02-01 16:30 | 1.1263 | 0 | N/A | 0 | 0
2023-02-01 17:00 | 1.1467 | 0 | N/A | 0 | 0
2023-02-01 17:30 | 1.8883 | 0 | N/A | 0 | 0
2023-02-01 18:00 | 2.2012 | 0 | N/A | 0 | 0
2023-02-01 18:30 | 3.1918 | 0 | N/A | 0 | 0
2023-02-01 19:00 | 3.7266 | 0 | N/A | 0 | 0
2023-02-01 19:30 | 3.9927 | 0 | N/A | 0 | 0
2023-02-01 20:00 | 4.2802 | 0 | N/A | 0 | 0
2023-02-01 20:30 | 4.5484 | 0 | N/A | 0 | 0
2023-02-01 21:00 | 4.6487 | 0 | N/A | 0 | 0
2023-02-01 21:30 | 4.575 | 0 | N/A | 0 | 0
2023-02-01 22:00 | 4.3127 | 0 | N/A | 0 | 0
2023-02-01 22:30 | 4.3842 | 0 | N/A | 0 | 0
2023-02-01 23:00 | 4.326 | 0 | N/A | 0 | 0
2023-02-01 23:30 | 3.9487 | 0 | N/A | 0 | 0
2023-02-02 | 3.9446 | 0 | N/A | 0 | 0
2023-02-02 00:30 | 4.2908 | 0 | N/A | 0 | 0
2023-02-02 01:00 | 4.4003 | 0 | N/A | 0 | 0
2023-02-02 01:30 | 3.7516 | 0 | N/A | 0 | 0
2023-02-02 02:00 | 3.1742 | 0 | N/A | 0 | 0
2023-02-02 02:30 | 3.1382 | 0 | N/A | 0 | 0
2023-02-02 03:00 | 2.8673 | 0 | N/A | 0 | 0
2023-02-02 03:30 | 2.6932 | 0 | N/A | 0 | 0
2023-02-02 04:00 | 2.6077 | 0 | N/A | 0 | 0
2023-02-02 04:30 | 2.5508 | 0 | N/A | 0 | 0
2023-02-02 05:00 | 2.5684 | 0 | N/A | 0 | 0
2023-02-02 05:30 | 2.7896 | 0 | N/A | 0 | 0
2023-02-02 06:00 | 3.1167 | 0 | N/A | 0 | 0
2023-02-02 06:30 | 3.6596 | 0 | N/A | 0 | 0
2023-02-02 07:00 | 4.4464 | 0 | N/A | 0 | 0
2023-02-02 07:30 | 5.1844 | 0 | N/A | 0 | 0
2023-02-02 08:00 | 4.8783 | 0 | N/A | 0 | 0
2023-02-02 08:30 | 3.8126 | 0 | N/A | 0 | 0
2023-02-02 09:00 | 3.7774 | 0 | N/A | 0 | 0
2023-02-02 09:30 | 3.6051 | 0 | N/A | 0 | 0
2023-02-02 10:00 | 2.8313 | 0 | N/A | 0 | 0
2023-02-02 10:30 | 2.9922 | 0 | N/A | 0 | 0
2023-02-02 11:00 | 3.3707 | 0 | N/A | 0 | 0
2023-02-02 11:30 | 3.3644 | 0 | N/A | 0 | 0
2023-02-02 12:00 | 1.6471 | 0 | N/A | 0 | 0
2023-02-02 12:30 | 1.0241 | 0 | N/A | 0 | 0
2023-02-02 13:00 | -0.78593 | 0 | N/A | 0 | 0
2023-02-02 13:30 | 2.3557 | 0 | N/A | 0 | 0
2023-02-02 14:00 | 3.7086 | 0 | N/A | 0 | 0
2023-02-02 14:30 | 3.9616 | 0 | N/A | 0 | 0
2023-02-02 15:00 | 4.6923 | 0 | N/A | 0 | 0
2023-02-02 15:30 | 5.1552 | 0 | N/A | 0 | 0
2023-02-02 16:00 | 5.0953 | 0 | N/A | 0 | 0
2023-02-02 16:30 | 5.3521 | 0 | N/A | 0 | 0
2023-02-02 17:00 | 4.8629 | 0 | N/A | 0 | 0
2023-02-02 17:30 | 4.5115 | 0 | N/A | 0 | 0
2023-02-02 18:00 | 5.4287 | 0 | N/A | 0 | 0
2023-02-02 18:30 | 5.7551 | 0 | N/A | 0 | 0
2023-02-02 19:00 | 5.2534 | 0 | N/A | 0 | 0
2023-02-02 19:30 | 5.6224 | 0 | N/A | 0 | 0
2023-02-02 20:00 | 6.3067 | 0 | N/A | 0 | 0
2023-02-02 20:30 | 6.5253 | 0 | N/A | 0 | 0
2023-02-02 21:00 | 6.4663 | 0 | N/A | 0 | 0
2023-02-02 21:30 | 6.3868 | 0 | N/A | 0 | 0
2023-02-02 22:00 | 6.0169 | 0 | N/A | 0 | 0
2023-02-02 22:30 | 5.915 | 0 | N/A | 0 | 0
2023-02-02 23:00 | 5.632 | 0 | N/A | 0 | 0
2023-02-02 23:30 | 5.1897 | 0 | N/A | 0 | 0
2023-02-03 | 5.0583 | 0 | N/A | 0 | 0
2023-02-04 00:30 | 5.0343 | 0 | N/A | 0 | 0
2023-02-04 01:00 | 5.2107 | 0 | N/A | 0 | 0
2023-02-04 01:30 | 4.5085 | 0 | N/A | 0 | 0
2023-02-04 02:00 | 3.9462 | 0 | N/A | 0 | 0
2023-02-04 02:30 | 3.8155 | 0 | N/A | 0 | 0
2023-02-04 03:00 | 3.5621 | 0 | N/A | 0 | 0
2023-02-04 03:30 | 3.2866 | 0 | N/A | 0 | 0
2023-02-04 04:00 | 3.1097 | 0 | N/A | 0 | 0
2023-02-04 04:30 | 3.039 | 0 | N/A | 0 | 0
2023-02-04 05:00 | 3.04 | 0 | N/A | 0 | 0
2023-02-04 05:30 | 3.0163 | 0 | N/A | 0 | 0
2023-02-04 06:00 | 3.1261 | 0 | N/A | 0 | 0
2023-02-04 06:30 | 3.4394 | 0 | N/A | 0 | 0
2023-02-04 07:00 | 3.7127 | 0 | N/A | 0 | 0
2023-02-04 07:30 | 4.1047 | 0 | N/A | 0 | 0
2023-02-04 08:00 | 4.4905 | 0 | N/A | 0 | 0
2023-02-04 08:30 | 4.6895 | 0 | N/A | 0 | 0
2023-02-04 09:00 | 4.7481 | 0 | N/A | 0 | 0
2023-02-04 09:30 | 4.4445 | 0 | N/A | 0 | 0
2023-02-04 10:00 | 4.3452 | 0 | N/A | 0 | 0
2023-02-04 10:30 | 3.6457 | 0 | N/A | 0 | 0
2023-02-04 11:00 | 2.6511 | 0 | N/A | 0 | 0
2023-02-04 11:30 | 2.6332 | 0 | N/A | 0 | 0
2023-02-04 12:00 | 2.9629 | 0 | N/A | 0 | 0
2023-02-04 12:30 | 3.2719 | 0 | N/A | 0 | 0
2023-02-04 13:00 | 2.4629 | 0 | N/A | 0 | 0
2023-02-04 13:30 | 1.7017 | 0 | N/A | 0 | 0
2023-02-04 14:00 | 1.1485 | 0 | N/A | 0 | 0
2023-02-04 14:30 | 1.0678 | 0 | N/A | 0 | 0
2023-02-04 15:00 | -1.0078 | 0 | N/A | 0 | 0
2023-02-04 15:30 | -0.93172 | 0 | N/A | 0 | 0
2023-02-04 16:00 | -0.90669 | 0 | N/A | 0 | 0
2023-02-04 16:30 | -0.87356 | 0 | N/A | 0 | 0
2023-02-04 17:00 | -0.95175 | 0 | N/A | 0 | 0
2023-02-04 17:30 | 1.1945 | 0 | N/A | 0 | 0
2023-02-04 18:00 | 2.649 | 0 | N/A | 0 | 0
2023-02-04 18:30 | 3.5456 | 0 | N/A | 0 | 0
2023-02-04 19:00 | 4.2639 | 0 | N/A | 0 | 0
2023-02-04 19:30 | 4.728 | 0 | N/A | 0 | 0
2023-02-04 20:00 | 5.5462 | 0 | N/A | 0 | 0
2023-02-04 20:30 | 5.5945 | 0 | N/A | 0 | 0
2023-02-04 21:00 | 5.1049 | 0 | N/A | 0 | 0
2023-02-04 21:30 | 4.5801 | 0 | N/A | 0 | 0
2023-02-04 22:00 | 4.2991 | 0 | N/A | 0 | 0
2023-02-04 22:30 | 4.5696 | 0 | N/A | 0 | 0
2023-02-04 23:00 | 4.6484 | 0 | N/A | 0 | 0
2023-02-04 23:30 | 4.3932 | 0 | N/A | 0 | 0
2023-02-05 | 4.341 | 0 | N/A | 0 | 0
2023-02-05 00:30 | 4.5344 | 0 | N/A | 0 | 0
2023-02-05 01:00 | 4.8581 | 0 | N/A | 0 | 0
2023-02-05 01:30 | 4.2343 | 0 | N/A | 0 | 0
2023-02-05 02:00 | 3.6335 | 0 | N/A | 0 | 0
2023-02-05 02:30 | 3.4938 | 0 | N/A | 0 | 0
2023-02-05 03:00 | 3.3016 | 0 | N/A | 0 | 0
2023-02-05 03:30 | 3.0443 | 0 | N/A | 0 | 0
2023-02-05 04:00 | 2.8974 | 0 | N/A | 0 | 0
2023-02-05 04:30 | 2.8107 | 0 | N/A | 0 | 0
2023-02-05 05:00 | 2.7715 | 0 | N/A | 0 | 0
2023-02-05 05:30 | 2.7888 | 0 | N/A | 0 | 0
2023-02-05 06:00 | 2.836 | 0 | N/A | 0 | 0
2023-02-05 06:30 | 2.9796 | 0 | N/A | 0 | 0
2023-02-05 07:00 | 3.1328 | 0 | N/A | 0 | 0
2023-02-05 07:30 | 3.3739 | 0 | N/A | 0 | 0
2023-02-05 08:00 | 3.4376 | 0 | N/A | 0 | 0
2023-02-05 08:30 | 3.2265 | 0 | N/A | 0 | 0
2023-02-05 09:00 | 3.103 | 0 | N/A | 0 | 0
2023-02-05 09:30 | 3.4038 | 0 | N/A | 0 | 0
2023-02-05 10:00 | 3.5405 | 0 | N/A | 0 | 0
2023-02-05 10:30 | 3.3833 | 0 | N/A | 0 | 0
2023-02-05 11:00 | 2.9224 | 0 | N/A | 0 | 0
2023-02-05 11:30 | 2.8928 | 0 | N/A | 0 | 0
2023-02-05 12:00 | 3.0375 | 0 | N/A | 0 | 0
2023-02-05 12:30 | 3.1207 | 0 | N/A | 0 | 0
2023-02-05 13:00 | 2.6792 | 0 | N/A | 0 | 0
2023-02-05 13:30 | 2.3648 | 0 | N/A | 0 | 0
2023-02-05 14:00 | 2.4985 | 0 | N/A | 0 | 0
2023-02-05 14:30 | 2.2521 | 0 | N/A | 0 | 0
2023-02-05 15:00 | 1.4236 | 0 | N/A | 0 | 0
2023-02-05 15:30 | 0.95529 | 0 | N/A | 0 | 0
2023-02-05 16:00 | 1.3038 | 0 | N/A | 0 | 0
2023-02-05 16:30 | 1.5968 | 0 | N/A | 0 | 0
2023-02-05 17:00 | 1.9418 | 0 | N/A | 0 | 0
2023-02-05 17:30 | 3.0173 | 0 | N/A | 0 | 0
2023-02-05 18:00 | 3.7996 | 0 | N/A | 0 | 0
2023-02-05 18:30 | 4.5393 | 0 | N/A | 0 | 0
2023-02-05 19:00 | 4.9658 | 0 | N/A | 0 | 0
2023-02-05 19:30 | 4.8981 | 0 | N/A | 0 | 0
2023-02-05 20:00 | 4.9522 | 0 | N/A | 0 | 0
2023-02-05 20:30 | 4.9048 | 0 | N/A | 0 | 0
2023-02-05 21:00 | 4.838 | 0 | N/A | 0 | 0
2023-02-05 21:30 | 4.7595 | 0 | N/A | 0 | 0
2023-02-05 22:00 | 4.4067 | 0 | N/A | 0 | 0
2023-02-05 22:30 | 4.5704 | 0 | N/A | 0 | 0
2023-02-05 23:00 | 4.4912 | 0 | N/A | 0 | 0
2023-02-05 23:30 | 4.2649 | 0 | N/A | 0 | 0
2023-02-06 | 4.2692 | 0 | N/A | 0 | 0
2023-02-07 00:30 | 4.3226 | 0 | N/A | 0 | 0
2023-02-07 01:00 | 4.5252 | 0 | N/A | 0 | 0
2023-02-07 01:30 | 3.8724 | 0 | N/A | 0 | 0
2023-02-07 02:00 | 3.3415 | 0 | N/A | 0 | 0
2023-02-07 02:30 | 3.2224 | 0 | N/A | 0 | 0
2023-02-07 03:00 | 2.9964 | 0 | N/A | 0 | 0
2023-02-07 03:30 | 2.7772 | 0 | N/A | 0 | 0
2023-02-07 04:00 | 2.6744 | 0 | N/A | 0 | 0
2023-02-07 04:30 | 2.5824 | 0 | N/A | 0 | 0
2023-02-07 05:00 | 2.6585 | 0 | N/A | 0 | 0
2023-02-07 05:30 | 2.8152 | 0 | N/A | 0 | 0
2023-02-07 06:00 | 3.1163 | 0 | N/A | 0 | 0
2023-02-07 06:30 | 3.4992 | 0 | N/A | 0 | 0
2023-02-07 07:00 | 4.1797 | 0 | N/A | 0 | 0
2023-02-07 07:30 | 5.0435 | 0 | N/A | 0 | 0
2023-02-07 08:00 | 5.2208 | 0 | N/A | 0 | 0
2023-02-07 08:30 | 4.6117 | 0 | N/A | 0 | 0
2023-02-07 09:00 | 4.4323 | 0 | N/A | 0 | 0
2023-02-07 09:30 | 4.1977 | 0 | N/A | 0 | 0
2023-02-07 10:00 | 4.0772 | 0 | N/A | 0 | 0
2023-02-07 10:30 | 2.6554 | 0 | N/A | 0 | 0
2023-02-07 11:00 | 1.1188 | 0 | N/A | 0 | 0
2023-02-07 11:30 | -0.41934 | 0 | N/A | 0 | 0
2023-02-07 12:00 | -0.96427 | 0 | N/A | 0 | 0
2023-02-07 12:30 | -1.1353 | 0 | N/A | 0 | 0
2023-02-07 13:00 | -0.99135 | 0 | N/A | 0 | 0
2023-02-07 13:30 | -1.683 | 0 | N/A | 0 | 0
2023-02-07 14:00 | -1.7481 | 0 | N/A | 0 | 0
2023-02-07 14:30 | -1.7045 | 0 | N/A | 0 | 0
2023-02-07 15:00 | -2.0301 | 0 | N/A | 0 | 0
2023-02-07 15:30 | -1.9664 | 0 | N/A | 0 | 0
2023-02-07 16:00 | -1.725 | 0 | N/A | 0 | 0
2023-02-07 16:30 | -1.519 | 0 | N/A | 0 | 0
2023-02-07 17:00 | -1.1577 | 0 | N/A | 0 | 0
2023-02-07 17:30 | 0.73673 | 0 | N/A | 0 | 0
2023-02-07 18:00 | 1.4927 | 0 | N/A | 0 | 0
2023-02-07 18:30 | 2.5174 | 0 | N/A | 0 | 0
2023-02-07 19:00 | 3.3206 | 0 | N/A | 0 | 0
2023-02-07 19:30 | 3.8812 | 0 | N/A | 0 | 0
2023-02-07 20:00 | 4.3825 | 0 | N/A | 0 | 0
2023-02-07 20:30 | 4.6358 | 0 | N/A | 0 | 0
2023-02-07 21:00 | 4.5729 | 0 | N/A | 0 | 0
2023-02-07 21:30 | 4.4821 | 0 | N/A | 0 | 0
2023-02-07 22:00 | 4.255 | 0 | N/A | 0 | 0
2023-02-07 22:30 | 4.3434 | 0 | N/A | 0 | 0
2023-02-07 23:00 | 4.297 | 0 | N/A | 0 | 0
2023-02-07 23:30 | 3.9395 | 0 | N/A | 0 | 0
2023-02-08 | 3.9607 | 0 | N/A | 0 | 0
2023-02-10 00:30 | 4.304 | 0 | N/A | 0 | 0
2023-02-10 01:00 | 4.4186 | 0 | N/A | 0 | 0
2023-02-10 01:30 | 3.6089 | 0 | N/A | 0 | 0
2023-02-10 02:00 | 3.1475 | 0 | N/A | 0 | 0
2023-02-10 02:30 | 3.0799 | 0 | N/A | 0 | 0
2023-02-10 03:00 | 2.9442 | 0 | N/A | 0 | 0
2023-02-10 03:30 | 2.7114 | 0 | N/A | 0 | 0
2023-02-10 04:00 | 2.5784 | 0 | N/A | 0 | 0
2023-02-10 04:30 | 2.5399 | 0 | N/A | 0 | 0
2023-02-10 05:00 | 2.6164 | 0 | N/A | 0 | 0
2023-02-10 05:30 | 2.8109 | 0 | N/A | 0 | 0
2023-02-10 06:00 | 3.003 | 0 | N/A | 0 | 0
2023-02-10 06:30 | 3.4187 | 0 | N/A | 0 | 0
2023-02-10 07:00 | 4.0803 | 0 | N/A | 0 | 0
2023-02-10 07:30 | 4.7998 | 0 | N/A | 0 | 0
2023-02-10 08:00 | 4.7826 | 0 | N/A | 0 | 0
2023-02-10 08:30 | 3.7765 | 0 | N/A | 0 | 0
2023-02-10 09:00 | 3.0245 | 0 | N/A | 0 | 0
2023-02-10 09:30 | 2.5522 | 0 | N/A | 0 | 0
2023-02-10 10:00 | 1.7746 | 0 | N/A | 0 | 0
2023-02-10 10:30 | 1.1973 | 0 | N/A | 0 | 0
2023-02-10 11:00 | 0.43748 | 0 | N/A | 0 | 0
2023-02-10 11:30 | -0.33726 | 0 | N/A | 0 | 0
2023-02-10 12:00 | -0.30921 | 0 | N/A | 0 | 0
2023-02-10 12:30 | -0.63837 | 0 | N/A | 0 | 0
2023-02-10 13:00 | -0.47709 | 0 | N/A | 0 | 0
2023-02-10 13:30 | -0.45594 | 0 | N/A | 0 | 0
2023-02-10 14:00 | -0.3173 | 0 | N/A | 0 | 0
2023-02-10 14:30 | 0.31632 | 0 | N/A | 0 | 0
2023-02-10 15:00 | -0.379 | 0 | N/A | 0 | 0
2023-02-10 15:30 | 0.36878 | 0 | N/A | 0 | 0
2023-02-10 16:00 | 0.88475 | 0 | N/A | 0 | 0
2023-02-10 16:30 | 1.6128 | 0 | N/A | 0 | 0
2023-02-10 17:00 | 2.5527 | 0 | N/A | 0 | 0
2023-02-10 17:30 | 3.5107 | 0 | N/A | 0 | 0
2023-02-10 18:00 | 4.6303 | 0 | N/A | 0 | 0
2023-02-10 18:30 | 5.5038 | 0 | N/A | 0 | 0
2023-02-10 19:00 | 6.1983 | 0 | N/A | 0 | 0
2023-02-10 19:30 | 6.3397 | 0 | N/A | 0 | 0
2023-02-10 20:00 | 6.1451 | 0 | N/A | 0 | 0
2023-02-10 20:30 | 5.7272 | 0 | N/A | 0 | 0
2023-02-10 21:00 | 5.4262 | 0 | N/A | 0 | 0
2023-02-10 21:30 | 5.0652 | 0 | N/A | 0 | 0
2023-02-10 22:00 | 4.7533 | 0 | N/A | 0 | 0
2023-02-10 22:30 | 4.6562 | 0 | N/A | 0 | 0
2023-02-10 23:00 | 4.5189 | 0 | N/A | 0 | 0
2023-02-10 23:30 | 4.1305 | 0 | N/A | 0 | 0
2023-02-11 | 4.0567 | 0 | N/A | 0 | 0
2023-02-11 00:30 | 4.3635 | 0 | N/A | 0 | 0
2023-02-11 01:00 | 4.4514 | 0 | N/A | 0 | 0
2023-02-11 01:30 | 3.6644 | 0 | N/A | 0 | 0
2023-02-11 02:00 | 3.0923 | 0 | N/A | 0 | 0
2023-02-11 02:30 | 3.0504 | 0 | N/A | 0 | 0
2023-02-11 03:00 | 2.8028 | 0 | N/A | 0 | 0
2023-02-11 03:30 | 2.6957 | 0 | N/A | 0 | 0
2023-02-11 04:00 | 2.5841 | 0 | N/A | 0 | 0
2023-02-11 04:30 | 2.5279 | 0 | N/A | 0 | 0
2023-02-11 05:00 | 2.5576 | 0 | N/A | 0 | 0
2023-02-11 05:30 | 2.6401 | 0 | N/A | 0 | 0
2023-02-11 06:00 | 2.7106 | 0 | N/A | 0 | 0
2023-02-11 06:30 | 2.8801 | 0 | N/A | 0 | 0
2023-02-11 07:00 | 2.9787 | 0 | N/A | 0 | 0
2023-02-11 07:30 | 3.1772 | 0 | N/A | 0 | 0
2023-02-11 08:00 | 3.0702 | 0 | N/A | 0 | 0
2023-02-11 08:30 | 2.6167 | 0 | N/A | 0 | 0
2023-02-11 09:00 | 2.3097 | 0 | N/A | 0 | 0
2023-02-11 09:30 | 1.8834 | 0 | N/A | 0 | 0
2023-02-11 10:00 | 1.4084 | 0 | N/A | 0 | 0
2023-02-11 10:30 | 1.277 | 0 | N/A | 0 | 0
2023-02-11 11:00 | 1.4144 | 0 | N/A | 0 | 0
2023-02-11 11:30 | 2.0826 | 0 | N/A | 0 | 0
2023-02-11 12:00 | 1.646 | 0 | N/A | 0 | 0
2023-02-11 12:30 | -0.62414 | 0 | N/A | 0 | 0
2023-02-11 13:00 | -1.4343 | 0 | N/A | 0 | 0
2023-02-11 13:30 | -1.9753 | 0 | N/A | 0 | 0
2023-02-11 14:00 | -1.908 | 0 | N/A | 0 | 0
2023-02-11 14:30 | -1.8256 | 0 | N/A | 0 | 0
2023-02-11 15:00 | -1.9165 | 0 | N/A | 0 | 0
2023-02-11 15:30 | -1.6525 | 0 | N/A | 0 | 0
2023-02-11 16:00 | -1.3231 | 0 | N/A | 0 | 0
2023-02-11 16:30 | -0.79903 | 0 | N/A | 0 | 0
2023-02-11 17:00 | 0.64668 | 0 | N/A | 0 | 0
2023-02-11 17:30 | 1.3563 | 0 | N/A | 0 | 0
2023-02-11 18:00 | 2.3826 | 0 | N/A | 0 | 0
2023-02-11 18:30 | 3.3778 | 0 | N/A | 0 | 0
2023-02-11 19:00 | 4.1925 | 0 | N/A | 0 | 0
2023-02-11 19:30 | 4.5919 | 0 | N/A | 0 | 0
2023-02-11 20:00 | 4.6525 | 0 | N/A | 0 | 0
2023-02-11 20:30 | 4.6011 | 0 | N/A | 0 | 0
2023-02-11 21:00 | 4.5461 | 0 | N/A | 0 | 0
2023-02-11 21:30 | 4.3463 | 0 | N/A | 0 | 0
2023-02-11 22:00 | 4.0485 | 0 | N/A | 0 | 0
2023-02-11 22:30 | 4.2624 | 0 | N/A | 0 | 0
2023-02-11 23:00 | 4.3283 | 0 | N/A | 0 | 0
2023-02-11 23:30 | 3.9447 | 0 | N/A | 0 | 0
2023-02-12 | 3.9049 | 0 | N/A | 0 | 0
2023-02-12 00:30 | 4.2906 | 0 | N/A | 0 | 0
2023-02-12 01:00 | 4.4944 | 0 | N/A | 0 | 0
2023-02-12 01:30 | 3.7356 | 0 | N/A | 0 | 0
2023-02-12 02:00 | 3.1869 | 0 | N/A | 0 | 0
2023-02-12 02:30 | 3.1386 | 0 | N/A | 0 | 0
2023-02-12 03:00 | 2.9099 | 0 | N/A | 0 | 0
2023-02-12 03:30 | 2.6812 | 0 | N/A | 0 | 0
2023-02-12 04:00 | 2.5891 | 0 | N/A | 0 | 0
2023-02-12 04:30 | 2.562 | 0 | N/A | 0 | 0
2023-02-12 05:00 | 2.5464 | 0 | N/A | 0 | 0
2023-02-12 05:30 | 2.5323 | 0 | N/A | 0 | 0
2023-02-12 06:00 | 2.539 | 0 | N/A | 0 | 0
2023-02-12 06:30 | 0.34106 | 0 | N/A | 0 | 0
2023-02-12 07:00 | 0 | 0 | N/A | 0 | 0
2023-02-12 07:30 | 0 | 0 | N/A | 0 | 0
2023-02-12 08:00 | 0 | 0 | N/A | 0 | 0
2023-02-12 08:30 | 0 | 0 | N/A | 0 | 0
2023-02-12 09:00 | 0 | 0 | N/A | 0 | 0
2023-02-12 09:30 | 0 | 0 | N/A | 0 | 0
2023-02-12 10:00 | 0 | 0 | N/A | 0 | 0
2023-02-12 10:30 | 0 | 0 | N/A | 0 | 0
2023-02-12 11:00 | 1.9649 | 0 | N/A | 0 | 0
2023-02-12 11:30 | 1.6532 | 0 | N/A | 0 | 0
2023-02-12 12:00 | 1.6017 | 0 | N/A | 0 | 0
2023-02-12 12:30 | 0.95297 | 0 | N/A | 0 | 0
2023-02-12 13:00 | -0.98903 | 0 | N/A | 0 | 0
2023-02-12 13:30 | -1.1048 | 0 | N/A | 0 | 0
2023-02-12 14:00 | -1.4641 | 0 | N/A | 0 | 0
2023-02-12 14:30 | -1.946 | 0 | N/A | 0 | 0
2023-02-12 15:00 | -1.6461 | 0 | N/A | 0 | 0
2023-02-12 15:30 | -1.033 | 0 | N/A | 0 | 0
2023-02-12 16:00 | 1.031 | 0 | N/A | 0 | 0
2023-02-12 16:30 | 1.1583 | 0 | N/A | 0 | 0
2023-02-12 17:00 | -0.95815 | 0 | N/A | 0 | 0
2023-02-12 17:30 | 1.6284 | 0 | N/A | 0 | 0
2023-02-12 18:00 | 2.7474 | 0 | N/A | 0 | 0
2023-02-12 18:30 | 3.9955 | 0 | N/A | 0 | 0
2023-02-12 19:00 | 4.3926 | 0 | N/A | 0 | 0
2023-02-12 19:30 | 4.6458 | 0 | N/A | 0 | 0
2023-02-12 20:00 | 4.7096 | 0 | N/A | 0 | 0
2023-02-12 20:30 | 4.7948 | 0 | N/A | 0 | 0
2023-02-12 21:00 | 4.8571 | 0 | N/A | 0 | 0
2023-02-12 21:30 | 4.7344 | 0 | N/A | 0 | 0
2023-02-12 22:00 | 4.4562 | 0 | N/A | 0 | 0
2023-02-12 22:30 | 4.5254 | 0 | N/A | 0 | 0
2023-02-12 23:00 | 4.4753 | 0 | N/A | 0 | 0
2023-02-12 23:30 | 4.2218 | 0 | N/A | 0 | 0
2023-02-13 | 4.2617 | 0 | N/A | 0 | 0
2023-02-13 00:30 | 4.5191 | 0 | N/A | 0 | 0
2023-02-13 01:00 | 4.7056 | 0 | N/A | 0 | 0
2023-02-13 01:30 | 4.0455 | 0 | N/A | 0 | 0
2023-02-13 02:00 | 3.569 | 0 | N/A | 0 | 0
2023-02-13 02:30 | 3.4526 | 0 | N/A | 0 | 0
2023-02-13 03:00 | 3.3124 | 0 | N/A | 0 | 0
2023-02-13 03:30 | 3.0325 | 0 | N/A | 0 | 0
2023-02-13 04:00 | 2.8437 | 0 | N/A | 0 | 0
2023-02-13 04:30 | 2.791 | 0 | N/A | 0 | 0
2023-02-13 05:00 | 2.831 | 0 | N/A | 0 | 0
2023-02-13 05:30 | 2.9941 | 0 | N/A | 0 | 0
2023-02-13 06:00 | 3.2451 | 0 | N/A | 0 | 0
2023-02-13 06:30 | 3.6951 | 0 | N/A | 0 | 0
2023-02-13 07:00 | 4.2345 | 0 | N/A | 0 | 0
2023-02-13 07:30 | 4.9053 | 0 | N/A | 0 | 0
2023-02-13 08:00 | 5.0502 | 0 | N/A | 0 | 0
2023-02-13 08:30 | 4.6942 | 0 | N/A | 0 | 0
2023-02-13 09:00 | 4.1558 | 0 | N/A | 0 | 0
2023-02-13 09:30 | 3.3641 | 0 | N/A | 0 | 0
2023-02-13 10:00 | 2.1214 | 0 | N/A | 0 | 0
2023-02-13 10:30 | 1.9889 | 0 | N/A | 0 | 0
2023-02-13 11:00 | 2.0557 | 0 | N/A | 0 | 0
2023-02-13 11:30 | 1.6294 | 0 | N/A | 0 | 0
2023-02-13 12:00 | 0.86866 | 0 | N/A | 0 | 0
2023-02-13 12:30 | -0.58421 | 0 | N/A | 0 | 0
2023-02-13 13:00 | -1.1954 | 0 | N/A | 0 | 0
2023-02-13 13:30 | -1.151 | 0 | N/A | 0 | 0
2023-02-13 14:00 | -0.81822 | 0 | N/A | 0 | 0
2023-02-13 14:30 | 0.82462 | 0 | N/A | 0 | 0
2023-02-13 15:00 | 0.98829 | 0 | N/A | 0 | 0
2023-02-13 15:30 | 1.4974 | 0 | N/A | 0 | 0
2023-02-13 16:00 | 1.1715 | 0 | N/A | 0 | 0
2023-02-13 16:30 | 1.5685 | 0 | N/A | 0 | 0
2023-02-13 17:00 | 1.8056 | 0 | N/A | 0 | 0
2023-02-13 17:30 | 2.2309 | 0 | N/A | 0 | 0
2023-02-13 18:00 | 2.7998 | 0 | N/A | 0 | 0
2023-02-13 18:30 | 3.6326 | 0 | N/A | 0 | 0
2023-02-13 19:00 | 4.1521 | 0 | N/A | 0 | 0
2023-02-13 19:30 | 4.4047 | 0 | N/A | 0 | 0
2023-02-13 20:00 | 4.5711 | 0 | N/A | 0 | 0
2023-02-13 20:30 | 4.8227 | 0 | N/A | 0 | 0
2023-02-13 21:00 | 4.8595 | 0 | N/A | 0 | 0
2023-02-13 21:30 | 4.7747 | 0 | N/A | 0 | 0
2023-02-13 22:00 | 4.5303 | 0 | N/A | 0 | 0
2023-02-13 22:30 | 4.4807 | 0 | N/A | 0 | 0
2023-02-13 23:00 | 4.4641 | 0 | N/A | 0 | 0
2023-02-13 23:30 | 4.204 | 0 | N/A | 0 | 0
2023-02-14 | 4.1954 | 0 | N/A | 0 | 0
2023-02-14 00:30 | 4.4971 | 0 | N/A | 0 | 0
2023-02-14 01:00 | 4.5278 | 0 | N/A | 0 | 0
2023-02-14 01:30 | 3.8975 | 0 | N/A | 0 | 0
2023-02-14 02:00 | 3.3659 | 0 | N/A | 0 | 0
2023-02-14 02:30 | 3.3863 | 0 | N/A | 0 | 0
2023-02-14 03:00 | 3.0859 | 0 | N/A | 0 | 0
2023-02-14 03:30 | 2.909 | 0 | N/A | 0 | 0
2023-02-14 04:00 | 2.7985 | 0 | N/A | 0 | 0
2023-02-14 04:30 | 2.7583 | 0 | N/A | 0 | 0
2023-02-14 05:00 | 2.8157 | 0 | N/A | 0 | 0
2023-02-14 05:30 | 3.0118 | 0 | N/A | 0 | 0
2023-02-14 06:00 | 3.3794 | 0 | N/A | 0 | 0
2023-02-14 06:30 | 3.906 | 0 | N/A | 0 | 0
2023-02-14 07:00 | 4.8227 | 0 | N/A | 0 | 0
2023-02-14 07:30 | 5.6416 | 0 | N/A | 0 | 0
2023-02-14 08:00 | 5.5293 | 0 | N/A | 0 | 0
2023-02-14 08:30 | 4.4455 | 0 | N/A | 0 | 0
2023-02-14 09:00 | 3.4004 | 0 | N/A | 0 | 0
2023-02-14 09:30 | 2.7609 | 0 | N/A | 0 | 0
2023-02-14 10:00 | 2.1386 | 0 | N/A | 0 | 0
2023-02-14 10:30 | 1.5951 | 0 | N/A | 0 | 0
2023-02-14 11:00 | 0.76158 | 0 | N/A | 0 | 0
2023-02-14 11:30 | -0.82344 | 0 | N/A | 0 | 0
2023-02-14 12:00 | -1.4355 | 0 | N/A | 0 | 0
2023-02-14 12:30 | -1.605 | 0 | N/A | 0 | 0
2023-02-14 13:00 | -1.8501 | 0 | N/A | 0 | 0
2023-02-14 13:30 | -2.0652 | 0 | N/A | 0 | 0
2023-02-14 14:00 | -2.0614 | 0 | N/A | 0 | 0
2023-02-14 14:30 | -2.0448 | 0 | N/A | 0 | 0
2023-02-14 15:00 | -1.9737 | 0 | N/A | 0 | 0
2023-02-14 15:30 | -1.9021 | 0 | N/A | 0 | 0
2023-02-14 16:00 | -1.82 | 0 | N/A | 0 | 0
2023-02-14 16:30 | -1.3569 | 0 | N/A | 0 | 0
2023-02-14 17:00 | -0.97824 | 0 | N/A | 0 | 0
2023-02-14 17:30 | 0.89085 | 0 | N/A | 0 | 0
2023-02-14 18:00 | 1.8497 | 0 | N/A | 0 | 0
2023-02-14 18:30 | 2.8538 | 0 | N/A | 0 | 0
2023-02-14 19:00 | 3.6473 | 0 | N/A | 0 | 0
2023-02-14 19:30 | 4.1781 | 0 | N/A | 0 | 0
2023-02-14 20:00 | 4.609 | 0 | N/A | 0 | 0
2023-02-14 20:30 | 4.6749 | 0 | N/A | 0 | 0
2023-02-14 21:00 | 4.6338 | 0 | N/A | 0 | 0
2023-02-14 21:30 | 4.5125 | 0 | N/A | 0 | 0
2023-02-14 22:00 | 4.224 | 0 | N/A | 0 | 0
2023-02-14 22:30 | 4.3614 | 0 | N/A | 0 | 0
2023-02-14 23:00 | 4.3012 | 0 | N/A | 0 | 0
2023-02-14 23:30 | 3.9375 | 0 | N/A | 0 | 0
2023-02-15 | 3.9116 | 0 | N/A | 0 | 0
2023-02-15 00:30 | 4.2481 | 0 | N/A | 0 | 0
2023-02-15 01:00 | 4.4454 | 0 | N/A | 0 | 0
2023-02-15 01:30 | 3.7328 | 0 | N/A | 0 | 0
2023-02-15 02:00 | 3.2191 | 0 | N/A | 0 | 0
2023-02-15 02:30 | 3.1307 | 0 | N/A | 0 | 0
2023-02-15 03:00 | 2.9479 | 0 | N/A | 0 | 0
2023-02-15 03:30 | 2.8239 | 0 | N/A | 0 | 0
2023-02-15 04:00 | 2.6808 | 0 | N/A | 0 | 0
2023-02-15 04:30 | 2.6479 | 0 | N/A | 0 | 0
2023-02-15 05:00 | 2.7617 | 0 | N/A | 0 | 0
2023-02-15 05:30 | 2.8918 | 0 | N/A | 0 | 0
2023-02-15 06:00 | 3.2068 | 0 | N/A | 0 | 0
2023-02-15 06:30 | 3.8897 | 0 | N/A | 0 | 0
2023-02-15 07:00 | 4.3384 | 0 | N/A | 0 | 0
2023-02-15 07:30 | 5.1552 | 0 | N/A | 0 | 0
2023-02-15 08:00 | 5.0951 | 0 | N/A | 0 | 0
2023-02-15 08:30 | 4.2306 | 0 | N/A | 0 | 0
2023-02-15 09:00 | 3.2852 | 0 | N/A | 0 | 0
2023-02-15 09:30 | 2.5728 | 0 | N/A | 0 | 0
2023-02-15 10:00 | 1.5805 | 0 | N/A | 0 | 0
2023-02-15 10:30 | 0.90057 | 0 | N/A | 0 | 0
2023-02-15 11:00 | 0.58789 | 0 | N/A | 0 | 0
2023-02-15 11:30 | -0.55733 | 0 | N/A | 0 | 0
2023-02-15 12:00 | -0.70821 | 0 | N/A | 0 | 0
2023-02-15 12:30 | -0.73506 | 0 | N/A | 0 | 0
2023-02-15 13:00 | -0.73704 | 0 | N/A | 0 | 0
2023-02-15 13:30 | -1.163 | 0 | N/A | 0 | 0
2023-02-15 14:00 | -0.93145 | 0 | N/A | 0 | 0
2023-02-15 14:30 | -0.6902 | 0 | N/A | 0 | 0
2023-02-15 15:00 | -0.42555 | 0 | N/A | 0 | 0
2023-02-15 15:30 | 0.48955 | 0 | N/A | 0 | 0
2023-02-15 16:00 | 1.0147 | 0 | N/A | 0 | 0
2023-02-15 16:30 | 1.5387 | 0 | N/A | 0 | 0
2023-02-15 17:00 | 2.5385 | 0 | N/A | 0 | 0
2023-02-15 17:30 | 3.1209 | 0 | N/A | 0 | 0
2023-02-15 18:00 | 4.6261 | 0 | N/A | 0 | 0
2023-02-15 18:30 | 5.5181 | 0 | N/A | 0 | 0
2023-02-15 19:00 | 6.0621 | 0 | N/A | 0 | 0
2023-02-15 19:30 | 6.1909 | 0 | N/A | 0 | 0
2023-02-15 20:00 | 6.172 | 0 | N/A | 0 | 0
2023-02-15 20:30 | 5.9028 | 0 | N/A | 0 | 0
2023-02-15 21:00 | 5.6701 | 0 | N/A | 0 | 0
2023-02-15 21:30 | 5.2005 | 0 | N/A | 0 | 0
2023-02-15 22:00 | 4.7748 | 0 | N/A | 0 | 0
2023-02-15 22:30 | 4.7716 | 0 | N/A | 0 | 0
2023-02-15 23:00 | 4.505 | 0 | N/A | 0 | 0
2023-02-15 23:30 | 4.1241 | 0 | N/A | 0 | 0
2023-02-16 | 4.0349 | 0 | N/A | 0 | 0
2023-02-16 00:30 | 4.3168 | 0 | N/A | 0 | 0
2023-02-16 01:00 | 4.3809 | 0 | N/A | 0 | 0
2023-02-16 01:30 | 3.679 | 0 | N/A | 0 | 0
2023-02-16 02:00 | 3.2438 | 0 | N/A | 0 | 0
2023-02-16 02:30 | 3.1273 | 0 | N/A | 0 | 0
2023-02-16 03:00 | 2.9786 | 0 | N/A | 0 | 0
2023-02-16 03:30 | 2.7926 | 0 | N/A | 0 | 0
2023-02-16 04:00 | 2.6743 | 0 | N/A | 0 | 0
2023-02-16 04:30 | 2.642 | 0 | N/A | 0 | 0
2023-02-16 05:00 | 2.7122 | 0 | N/A | 0 | 0
2023-02-16 05:30 | 2.8727 | 0 | N/A | 0 | 0
2023-02-16 06:00 | 3.101 | 0 | N/A | 0 | 0
2023-02-16 06:30 | 3.5659 | 0 | N/A | 0 | 0
2023-02-16 07:00 | 4.1219 | 0 | N/A | 0 | 0
2023-02-16 07:30 | 4.6828 | 0 | N/A | 0 | 0
2023-02-16 08:00 | 4.8001 | 0 | N/A | 0 | 0
2023-02-16 08:30 | 4.0697 | 0 | N/A | 0 | 0
2023-02-16 09:00 | 3.7343 | 0 | N/A | 0 | 0
2023-02-16 09:30 | 2.9494 | 0 | N/A | 0 | 0
2023-02-16 10:00 | 2.1398 | 0 | N/A | 0 | 0
2023-02-16 10:30 | 1.7323 | 0 | N/A | 0 | 0
2023-02-16 11:00 | 1.675 | 0 | N/A | 0 | 0
2023-02-16 11:30 | 1.3291 | 0 | N/A | 0 | 0
2023-02-16 12:00 | 0.73082 | 0 | N/A | 0 | 0
2023-02-16 12:30 | 0.58085 | 0 | N/A | 0 | 0
2023-02-16 13:00 | 0.44086 | 0 | N/A | 0 | 0
2023-02-16 13:30 | 0.69389 | 0 | N/A | 0 | 0
2023-02-16 14:00 | 0.68003 | 0 | N/A | 0 | 0
2023-02-16 14:30 | 0.87677 | 0 | N/A | 0 | 0
2023-02-16 15:00 | 2.6612 | 0 | N/A | 0 | 0
2023-02-16 15:30 | 2.9742 | 0 | N/A | 0 | 0
2023-02-16 16:00 | 3.627 | 0 | N/A | 0 | 0
2023-02-16 16:30 | 2.9964 | 0 | N/A | 0 | 0
2023-02-16 17:00 | 4.7342 | 0 | N/A | 0 | 0
2023-02-16 17:30 | 6.3481 | 0 | N/A | 0 | 0
2023-02-16 18:00 | 6.5848 | 0 | N/A | 0 | 0
2023-02-16 18:30 | 7.9 | 0 | N/A | 0 | 0
2023-02-16 19:00 | 8.9435 | 0 | N/A | 0 | 0
2023-02-16 19:30 | 8.7306 | 0 | N/A | 0 | 0
2023-02-16 20:00 | 8.3608 | 0 | N/A | 0 | 0
2023-02-16 20:30 | 7.7432 | 0 | N/A | 0 | 0
2023-02-16 21:00 | 6.9745 | 0 | N/A | 0 | 0
2023-02-16 21:30 | 6.3944 | 0 | N/A | 0 | 0
2023-02-16 22:00 | 5.7785 | 0 | N/A | 0 | 0
2023-02-16 22:30 | 5.4873 | 0 | N/A | 0 | 0
2023-02-16 23:00 | 5.1493 | 0 | N/A | 0 | 0
2023-02-16 23:30 | 4.7225 | 0 | N/A | 0 | 0
2023-02-17 | 4.475 | 0 | N/A | 0 | 0
2023-02-17 00:30 | 4.8592 | 0 | N/A | 0 | 0
2023-02-17 01:00 | 4.8036 | 0 | N/A | 0 | 0
2023-02-17 01:30 | 3.9795 | 0 | N/A | 0 | 0
2023-02-17 02:00 | 3.4743 | 0 | N/A | 0 | 0
2023-02-17 02:30 | 3.4975 | 0 | N/A | 0 | 0
2023-02-17 03:00 | 3.2873 | 0 | N/A | 0 | 0
2023-02-17 03:30 | 3.1105 | 0 | N/A | 0 | 0
2023-02-17 04:00 | 3.0627 | 0 | N/A | 0 | 0
2023-02-17 04:30 | 3.0564 | 0 | N/A | 0 | 0
2023-02-17 05:00 | 3.1 | 0 | N/A | 0 | 0
2023-02-17 05:30 | 3.1962 | 0 | N/A | 0 | 0
2023-02-17 06:00 | 3.4604 | 0 | N/A | 0 | 0
2023-02-17 06:30 | 4.0378 | 0 | N/A | 0 | 0
2023-02-17 07:00 | 4.5208 | 0 | N/A | 0 | 0
2023-02-17 07:30 | 5.1855 | 0 | N/A | 0 | 0
2023-02-17 08:00 | 5.1606 | 0 | N/A | 0 | 0
2023-02-17 08:30 | 4.9808 | 0 | N/A | 0 | 0
2023-02-17 09:00 | 4.4186 | 0 | N/A | 0 | 0
2023-02-17 09:30 | 3.9497 | 0 | N/A | 0 | 0
2023-02-17 10:00 | 3.2969 | 0 | N/A | 0 | 0
2023-02-17 10:30 | 2.7284 | 0 | N/A | 0 | 0
2023-02-17 11:00 | 2.4349 | 0 | N/A | 0 | 0
2023-02-17 11:30 | 2.3424 | 0 | N/A | 0 | 0
2023-02-17 12:00 | 2.3283 | 0 | N/A | 0 | 0
2023-02-17 12:30 | 2.1649 | 0 | N/A | 0 | 0
2023-02-17 13:00 | 2.39 | 0 | N/A | 0 | 0
2023-02-17 13:30 | 2.5667 | 0 | N/A | 0 | 0
2023-02-17 14:00 | 2.8033 | 0 | N/A | 0 | 0
2023-02-17 14:30 | 3.1767 | 0 | N/A | 0 | 0
2023-02-17 15:00 | 3.5467 | 0 | N/A | 0 | 0
2023-02-17 15:30 | 3.9302 | 0 | N/A | 0 | 0
2023-02-17 16:00 | 4.7834 | 0 | N/A | 0 | 0
2023-02-17 16:30 | 5.26 | 0 | N/A | 0 | 0
2023-02-17 17:00 | 5.7934 | 0 | N/A | 0 | 0
2023-02-17 17:30 | 6.4305 | 0 | N/A | 0 | 0
2023-02-17 18:00 | 7.12 | 0 | N/A | 0 | 0
2023-02-17 18:30 | 7.4474 | 0 | N/A | 0 | 0
2023-02-17 19:00 | 7.6476 | 0 | N/A | 0 | 0
2023-02-17 19:30 | 7.5961 | 0 | N/A | 0 | 0
2023-02-17 20:00 | 7.1792 | 0 | N/A | 0 | 0
2023-02-17 20:30 | 6.4766 | 0 | N/A | 0 | 0
2023-02-17 21:00 | 5.9711 | 0 | N/A | 0 | 0
2023-02-17 21:30 | 5.4307 | 0 | N/A | 0 | 0
2023-02-17 22:00 | 4.8872 | 0 | N/A | 0 | 0
2023-02-17 22:30 | 4.7615 | 0 | N/A | 0 | 0
2023-02-17 23:00 | 4.6412 | 0 | N/A | 0 | 0
2023-02-17 23:30 | 4.045 | 0 | N/A | 0 | 0
2023-02-18 | 3.9962 | 0 | N/A | 0 | 0
2023-02-18 00:30 | 4.3531 | 0 | N/A | 0 | 0
2023-02-18 01:00 | 4.4235 | 0 | N/A | 0 | 0
2023-02-18 01:30 | 3.6094 | 0 | N/A | 0 | 0
2023-02-18 02:00 | 3.1121 | 0 | N/A | 0 | 0
2023-02-18 02:30 | 3.0691 | 0 | N/A | 0 | 0
2023-02-18 03:00 | 2.8713 | 0 | N/A | 0 | 0
2023-02-18 03:30 | 2.7236 | 0 | N/A | 0 | 0
2023-02-18 04:00 | 2.6771 | 0 | N/A | 0 | 0
2023-02-18 04:30 | 2.6759 | 0 | N/A | 0 | 0
2023-02-18 05:00 | 2.6514 | 0 | N/A | 0 | 0
2023-02-18 05:30 | 2.6105 | 0 | N/A | 0 | 0
2023-02-18 06:00 | 2.692 | 0 | N/A | 0 | 0
2023-02-18 06:30 | 2.8574 | 0 | N/A | 0 | 0
2023-02-18 07:00 | 3.0149 | 0 | N/A | 0 | 0
2023-02-18 07:30 | 3.2617 | 0 | N/A | 0 | 0
2023-02-18 08:00 | 3.3243 | 0 | N/A | 0 | 0
2023-02-18 08:30 | 3.4456 | 0 | N/A | 0 | 0
2023-02-18 09:00 | 3.2319 | 0 | N/A | 0 | 0
2023-02-18 09:30 | 2.4661 | 0 | N/A | 0 | 0
2023-02-18 10:00 | 1.3611 | 0 | N/A | 0 | 0
2023-02-18 10:30 | 1.3741 | 0 | N/A | 0 | 0
2023-02-18 11:00 | -0.92895 | 0 | N/A | 0 | 0
2023-02-18 11:30 | -1.4655 | 0 | N/A | 0 | 0
2023-02-18 12:00 | -1.851 | 0 | N/A | 0 | 0
2023-02-18 12:30 | -2.2224 | 0 | N/A | 0 | 0
2023-02-18 13:00 | -2.3385 | 0 | N/A | 0 | 0
2023-02-18 13:30 | -2.4777 | 0 | N/A | 0 | 0
2023-02-18 14:00 | -2.5465 | 0 | N/A | 0 | 0
2023-02-18 14:30 | -2.4759 | 0 | N/A | 0 | 0
2023-02-18 15:00 | -2.2974 | 0 | N/A | 0 | 0
2023-02-18 15:30 | -2.0874 | 0 | N/A | 0 | 0
2023-02-18 16:00 | -1.7563 | 0 | N/A | 0 | 0
2023-02-18 16:30 | -1.1839 | 0 | N/A | 0 | 0
2023-02-18 17:00 | -0.74109 | 0 | N/A | 0 | 0
2023-02-18 17:30 | 1.0908 | 0 | N/A | 0 | 0
2023-02-18 18:00 | 2.0288 | 0 | N/A | 0 | 0
2023-02-18 18:30 | 3.0619 | 0 | N/A | 0 | 0
2023-02-18 19:00 | 3.8891 | 0 | N/A | 0 | 0
2023-02-18 19:30 | 4.3511 | 0 | N/A | 0 | 0
2023-02-18 20:00 | 4.441 | 0 | N/A | 0 | 0
2023-02-18 20:30 | 4.4967 | 0 | N/A | 0 | 0
2023-02-18 21:00 | 4.3814 | 0 | N/A | 0 | 0
2023-02-18 21:30 | 4.1932 | 0 | N/A | 0 | 0
2023-02-18 22:00 | 3.9667 | 0 | N/A | 0 | 0
2023-02-18 22:30 | 4.2197 | 0 | N/A | 0 | 0
2023-02-18 23:00 | 4.2422 | 0 | N/A | 0 | 0
2023-02-18 23:30 | 4.0146 | 0 | N/A | 0 | 0
2023-02-19 | 4.0278 | 0 | N/A | 0 | 0
2023-02-19 00:30 | 4.2769 | 0 | N/A | 0 | 0
2023-02-19 01:00 | 4.3365 | 0 | N/A | 0 | 0
2023-02-19 01:30 | 3.6963 | 0 | N/A | 0 | 0
2023-02-19 02:00 | 3.1454 | 0 | N/A | 0 | 0
2023-02-19 02:30 | 3.0666 | 0 | N/A | 0 | 0
2023-02-19 03:00 | 2.8698 | 0 | N/A | 0 | 0
2023-02-19 03:30 | 2.6972 | 0 | N/A | 0 | 0
2023-02-19 04:00 | 2.5738 | 0 | N/A | 0 | 0
2023-02-19 04:30 | 2.5347 | 0 | N/A | 0 | 0
2023-02-19 05:00 | 2.5083 | 0 | N/A | 0 | 0
2023-02-19 05:30 | 2.5315 | 0 | N/A | 0 | 0
2023-02-19 06:00 | 2.5795 | 0 | N/A | 0 | 0
2023-02-19 06:30 | 2.7885 | 0 | N/A | 0 | 0
2023-02-19 07:00 | 2.8858 | 0 | N/A | 0 | 0
2023-02-19 07:30 | 3.0654 | 0 | N/A | 0 | 0
2023-02-19 08:00 | 3.0858 | 0 | N/A | 0 | 0
2023-02-19 08:30 | 2.8429 | 0 | N/A | 0 | 0
2023-02-19 09:00 | 2.535 | 0 | N/A | 0 | 0
2023-02-19 09:30 | 1.8149 | 0 | N/A | 0 | 0
2023-02-19 10:00 | 1.1681 | 0 | N/A | 0 | 0
2023-02-19 10:30 | -0.96375 | 0 | N/A | 0 | 0
2023-02-19 11:00 | -1.1197 | 0 | N/A | 0 | 0
2023-02-19 11:30 | -1.4881 | 0 | N/A | 0 | 0
2023-02-19 12:00 | -1.7432 | 0 | N/A | 0 | 0
2023-02-19 12:30 | -1.9201 | 0 | N/A | 0 | 0
2023-02-19 13:00 | -1.964 | 0 | N/A | 0 | 0
2023-02-19 13:30 | -2.009 | 0 | N/A | 0 | 0
2023-02-19 14:00 | -1.9719 | 0 | N/A | 0 | 0
2023-02-19 14:30 | -1.7416 | 0 | N/A | 0 | 0
2023-02-19 15:00 | -1.4948 | 0 | N/A | 0 | 0
2023-02-19 15:30 | -1.0383 | 0 | N/A | 0 | 0
2023-02-19 16:00 | -0.63641 | 0 | N/A | 0 | 0
2023-02-19 16:30 | 0.77029 | 0 | N/A | 0 | 0
2023-02-19 17:00 | 1.6518 | 0 | N/A | 0 | 0
2023-02-19 17:30 | 2.7407 | 0 | N/A | 0 | 0
2023-02-19 18:00 | 3.9065 | 0 | N/A | 0 | 0
2023-02-19 18:30 | 5.0619 | 0 | N/A | 0 | 0
2023-02-19 19:00 | 5.9087 | 0 | N/A | 0 | 0
2023-02-19 19:30 | 6.1799 | 0 | N/A | 0 | 0
2023-02-19 20:00 | 6.161 | 0 | N/A | 0 | 0
2023-02-19 20:30 | 5.7108 | 0 | N/A | 0 | 0
2023-02-19 21:00 | 5.3271 | 0 | N/A | 0 | 0
2023-02-19 21:30 | 5.0135 | 0 | N/A | 0 | 0
2023-02-19 22:00 | 4.6123 | 0 | N/A | 0 | 0
2023-02-19 22:30 | 4.5863 | 0 | N/A | 0 | 0
2023-02-19 23:00 | 4.4382 | 0 | N/A | 0 | 0
2023-02-19 23:30 | 4.0327 | 0 | N/A | 0 | 0
2023-02-20 | 3.9818 | 0 | N/A | 0 | 0
2023-02-20 00:30 | 4.2617 | 0 | N/A | 0 | 0
2023-02-20 01:00 | 4.4162 | 0 | N/A | 0 | 0
2023-02-20 01:30 | 3.756 | 0 | N/A | 0 | 0
2023-02-20 02:00 | 3.2361 | 0 | N/A | 0 | 0
2023-02-20 02:30 | 3.155 | 0 | N/A | 0 | 0
2023-02-20 03:00 | 2.9692 | 0 | N/A | 0 | 0
2023-02-20 03:30 | 2.7858 | 0 | N/A | 0 | 0
2023-02-20 04:00 | 2.5979 | 0 | N/A | 0 | 0
2023-02-20 04:30 | 2.5611 | 0 | N/A | 0 | 0
2023-02-20 05:00 | 2.5831 | 0 | N/A | 0 | 0
2023-02-20 05:30 | 2.8375 | 0 | N/A | 0 | 0
2023-02-20 06:00 | 3.0846 | 0 | N/A | 0 | 0
2023-02-20 06:30 | 3.4329 | 0 | N/A | 0 | 0
2023-02-20 07:00 | 4.1628 | 0 | N/A | 0 | 0
2023-02-20 07:30 | 4.9817 | 0 | N/A | 0 | 0
2023-02-20 08:00 | 4.9484 | 0 | N/A | 0 | 0
2023-02-20 08:30 | 4.0213 | 0 | N/A | 0 | 0
2023-02-20 09:00 | 3.4405 | 0 | N/A | 0 | 0
2023-02-20 09:30 | 2.5842 | 0 | N/A | 0 | 0
2023-02-20 10:00 | 1.7477 | 0 | N/A | 0 | 0
2023-02-20 10:30 | 1.0127 | 0 | N/A | 0 | 0
2023-02-20 11:00 | 0.45338 | 0 | N/A | 0 | 0
2023-02-20 11:30 | -0.35229 | 0 | N/A | 0 | 0
2023-02-20 12:00 | -0.57299 | 0 | N/A | 0 | 0
2023-02-20 12:30 | -0.8183 | 0 | N/A | 0 | 0
2023-02-20 13:00 | -0.98456 | 0 | N/A | 0 | 0
2023-02-20 13:30 | -1.0456 | 0 | N/A | 0 | 0
2023-02-20 14:00 | -0.86457 | 0 | N/A | 0 | 0
2023-02-20 14:30 | -0.83155 | 0 | N/A | 0 | 0
2023-02-20 15:00 | -0.53333 | 0 | N/A | 0 | 0
2023-02-20 15:30 | -0.14881 | 0 | N/A | 0 | 0
2023-02-20 16:00 | 0.34533 | 0 | N/A | 0 | 0
2023-02-20 16:30 | 0.89657 | 0 | N/A | 0 | 0
2023-02-20 17:00 | 1.7043 | 0 | N/A | 0 | 0
2023-02-20 17:30 | 2.8512 | 0 | N/A | 0 | 0
2023-02-20 18:00 | 3.7879 | 0 | N/A | 0 | 0
2023-02-20 18:30 | 4.8649 | 0 | N/A | 0 | 0
2023-02-20 19:00 | 5.1548 | 0 | N/A | 0 | 0
2023-02-20 19:30 | 5.7201 | 0 | N/A | 0 | 0
2023-02-20 20:00 | 5.6314 | 0 | N/A | 0 | 0
2023-02-20 20:30 | 5.4292 | 0 | N/A | 0 | 0
2023-02-20 21:00 | 5.2192 | 0 | N/A | 0 | 0
2023-02-20 21:30 | 4.8867 | 0 | N/A | 0 | 0
2023-02-20 22:00 | 4.5295 | 0 | N/A | 0 | 0
2023-02-20 22:30 | 4.4352 | 0 | N/A | 0 | 0
2023-02-20 23:00 | 4.4069 | 0 | N/A | 0 | 0
2023-02-20 23:30 | 4.0685 | 0 | N/A | 0 | 0
2023-02-21 | 3.9683 | 0 | N/A | 0 | 0
2023-02-22 00:30 | 4.307 | 0 | N/A | 0 | 0
2023-02-22 01:00 | 4.5905 | 0 | N/A | 0 | 0
2023-02-22 01:30 | 3.8711 | 0 | N/A | 0 | 0
2023-02-22 02:00 | 3.3609 | 0 | N/A | 0 | 0
2023-02-22 02:30 | 3.2866 | 0 | N/A | 0 | 0
2023-02-22 03:00 | 3.04 | 0 | N/A | 0 | 0
2023-02-22 03:30 | 2.8214 | 0 | N/A | 0 | 0
2023-02-22 04:00 | 2.7214 | 0 | N/A | 0 | 0
2023-02-22 04:30 | 2.6526 | 0 | N/A | 0 | 0
2023-02-22 05:00 | 2.7217 | 0 | N/A | 0 | 0
2023-02-22 05:30 | 2.8851 | 0 | N/A | 0 | 0
2023-02-22 06:00 | 3.0769 | 0 | N/A | 0 | 0
2023-02-22 06:30 | 3.5433 | 0 | N/A | 0 | 0
2023-02-22 07:00 | 4.3145 | 0 | N/A | 0 | 0
2023-02-22 07:30 | 5.0252 | 0 | N/A | 0 | 0
2023-02-22 08:00 | 4.956 | 0 | N/A | 0 | 0
2023-02-22 08:30 | 4.0895 | 0 | N/A | 0 | 0
2023-02-22 09:00 | 3.3936 | 0 | N/A | 0 | 0
2023-02-22 09:30 | 2.454 | 0 | N/A | 0 | 0
2023-02-22 10:00 | 1.5047 | 0 | N/A | 0 | 0
2023-02-22 10:30 | 0.857 | 0 | N/A | 0 | 0
2023-02-22 11:00 | 0.47629 | 0 | N/A | 0 | 0
2023-02-22 11:30 | 0.41145 | 0 | N/A | 0 | 0
2023-02-22 12:00 | -0.45412 | 0 | N/A | 0 | 0
2023-02-22 12:30 | -0.89563 | 0 | N/A | 0 | 0
2023-02-22 13:00 | -1.2358 | 0 | N/A | 0 | 0
2023-02-22 13:30 | -1.2276 | 0 | N/A | 0 | 0
2023-02-22 14:00 | -0.96832 | 0 | N/A | 0 | 0
2023-02-22 14:30 | -0.84897 | 0 | N/A | 0 | 0
2023-02-22 15:00 | -0.5039 | 0 | N/A | 0 | 0
2023-02-22 15:30 | -0.2415 | 0 | N/A | 0 | 0
2023-02-22 16:00 | 0.52345 | 0 | N/A | 0 | 0
2023-02-22 16:30 | 1.2109 | 0 | N/A | 0 | 0
2023-02-22 17:00 | 2.4973 | 0 | N/A | 0 | 0
2023-02-22 17:30 | 3.8994 | 0 | N/A | 0 | 0
2023-02-22 18:00 | 5.1165 | 0 | N/A | 0 | 0
2023-02-22 18:30 | 5.2417 | 0 | N/A | 0 | 0
2023-02-22 19:00 | 5.7943 | 0 | N/A | 0 | 0
2023-02-22 19:30 | 6.416 | 0 | N/A | 0 | 0
2023-02-22 20:00 | 6.282 | 0 | N/A | 0 | 0
2023-02-22 20:30 | 6.0602 | 0 | N/A | 0 | 0
2023-02-22 21:00 | 5.7077 | 0 | N/A | 0 | 0
2023-02-22 21:30 | 5.2967 | 0 | N/A | 0 | 0
2023-02-22 22:00 | 4.8646 | 0 | N/A | 0 | 0
2023-02-22 22:30 | 4.8258 | 0 | N/A | 0 | 0
2023-02-22 23:00 | 4.572 | 0 | N/A | 0 | 0
2023-02-22 23:30 | 4.1816 | 0 | N/A | 0 | 0
2023-02-23 | 4.1309 | 0 | N/A | 0 | 0
2023-02-25 00:30 | 4.6545 | 0 | N/A | 0 | 0
2023-02-25 01:00 | 4.644 | 0 | N/A | 0 | 0
2023-02-25 01:30 | 3.8605 | 0 | N/A | 0 | 0
2023-02-25 02:00 | 3.3924 | 0 | N/A | 0 | 0
2023-02-25 02:30 | 3.3022 | 0 | N/A | 0 | 0
2023-02-25 03:00 | 3.1178 | 0 | N/A | 0 | 0
2023-02-25 03:30 | 2.9413 | 0 | N/A | 0 | 0
2023-02-25 04:00 | 2.8475 | 0 | N/A | 0 | 0
2023-02-25 04:30 | 2.8124 | 0 | N/A | 0 | 0
2023-02-25 05:00 | 2.7937 | 0 | N/A | 0 | 0
2023-02-25 05:30 | 2.7582 | 0 | N/A | 0 | 0
2023-02-25 06:00 | 2.8862 | 0 | N/A | 0 | 0
2023-02-25 06:30 | 3.0775 | 0 | N/A | 0 | 0
2023-02-25 07:00 | 3.1567 | 0 | N/A | 0 | 0
2023-02-25 07:30 | 3.4007 | 0 | N/A | 0 | 0
2023-02-25 08:00 | 3.6292 | 0 | N/A | 0 | 0
2023-02-25 08:30 | 3.7578 | 0 | N/A | 0 | 0
2023-02-25 09:00 | 3.9643 | 0 | N/A | 0 | 0
2023-02-25 09:30 | 3.5186 | 0 | N/A | 0 | 0
2023-02-25 10:00 | 3.3636 | 0 | N/A | 0 | 0
2023-02-25 10:30 | 3.6717 | 0 | N/A | 0 | 0
2023-02-25 11:00 | 3.6962 | 0 | N/A | 0 | 0
2023-02-25 11:30 | 2.8525 | 0 | N/A | 0 | 0
2023-02-25 12:00 | 3.4697 | 0 | N/A | 0 | 0
2023-02-25 12:30 | 3.8815 | 0 | N/A | 0 | 0
2023-02-25 13:00 | 3.9884 | 0 | N/A | 0 | 0
2023-02-25 13:30 | 3.9676 | 0 | N/A | 0 | 0
2023-02-25 14:00 | 3.8708 | 0 | N/A | 0 | 0
2023-02-25 14:30 | 3.3874 | 0 | N/A | 0 | 0
2023-02-25 15:00 | 3.4168 | 0 | N/A | 0 | 0
2023-02-25 15:30 | 3.7972 | 0 | N/A | 0 | 0
2023-02-25 16:00 | 3.9392 | 0 | N/A | 0 | 0
2023-02-25 16:30 | 3.3279 | 0 | N/A | 0 | 0
2023-02-25 17:00 | 3.1523 | 0 | N/A | 0 | 0
2023-02-25 17:30 | 2.8128 | 0 | N/A | 0 | 0
2023-02-25 18:00 | 3.8283 | 0 | N/A | 0 | 0
2023-02-25 18:30 | 4.6858 | 0 | N/A | 0 | 0
2023-02-25 19:00 | 4.9582 | 0 | N/A | 0 | 0
2023-02-25 19:30 | 4.8589 | 0 | N/A | 0 | 0
2023-02-25 20:00 | 4.666 | 0 | N/A | 0 | 0
2023-02-25 20:30 | 4.4113 | 0 | N/A | 0 | 0
2023-02-25 21:00 | 4.2812 | 0 | N/A | 0 | 0
2023-02-25 21:30 | 4.0995 | 0 | N/A | 0 | 0
2023-02-25 22:00 | 3.9276 | 0 | N/A | 0 | 0
2023-02-25 22:30 | 4.1701 | 0 | N/A | 0 | 0
2023-02-25 23:00 | 4.1834 | 0 | N/A | 0 | 0
2023-02-25 23:30 | 3.9455 | 0 | N/A | 0 | 0
2023-02-26 | 3.8807 | 0 | N/A | 0 | 0
2023-02-26 00:30 | 4.2525 | 0 | N/A | 0 | 0
2023-02-26 01:00 | 4.468 | 0 | N/A | 0 | 0
2023-02-26 01:30 | 3.7013 | 0 | N/A | 0 | 0
2023-02-26 02:00 | 3.2308 | 0 | N/A | 0 | 0
2023-02-26 02:30 | 3.132 | 0 | N/A | 0 | 0
2023-02-26 03:00 | 2.9032 | 0 | N/A | 0 | 0
2023-02-26 03:30 | 2.6886 | 0 | N/A | 0 | 0
2023-02-26 04:00 | 2.5721 | 0 | N/A | 0 | 0
2023-02-26 04:30 | 2.4908 | 0 | N/A | 0 | 0
2023-02-26 05:00 | 2.4746 | 0 | N/A | 0 | 0
2023-02-26 05:30 | 2.5368 | 0 | N/A | 0 | 0
2023-02-26 06:00 | 2.573 | 0 | N/A | 0 | 0
2023-02-26 06:30 | 2.7258 | 0 | N/A | 0 | 0
2023-02-26 07:00 | 2.9019 | 0 | N/A | 0 | 0
2023-02-26 07:30 | 3.1218 | 0 | N/A | 0 | 0
2023-02-26 08:00 | 3.3452 | 0 | N/A | 0 | 0
2023-02-26 08:30 | 2.9096 | 0 | N/A | 0 | 0
2023-02-26 09:00 | 2.8045 | 0 | N/A | 0 | 0
2023-02-26 09:30 | 2.9223 | 0 | N/A | 0 | 0
2023-02-26 10:00 | 2.9322 | 0 | N/A | 0 | 0
2023-02-26 10:30 | 2.8552 | 0 | N/A | 0 | 0
2023-02-26 11:00 | 2.0701 | 0 | N/A | 0 | 0
2023-02-26 11:30 | 1.5156 | 0 | N/A | 0 | 0
2023-02-26 12:00 | 0.99394 | 0 | N/A | 0 | 0
2023-02-26 12:30 | -0.9443 | 0 | N/A | 0 | 0
2023-02-26 13:00 | -0.93719 | 0 | N/A | 0 | 0
2023-02-26 13:30 | -0.99242 | 0 | N/A | 0 | 0
2023-02-26 14:00 | -0.95574 | 0 | N/A | 0 | 0
2023-02-26 14:30 | 1.4029 | 0 | N/A | 0 | 0
2023-02-26 15:00 | 1.3967 | 0 | N/A | 0 | 0
2023-02-26 15:30 | 1.6668 | 0 | N/A | 0 | 0
2023-02-26 16:00 | 1.2086 | 0 | N/A | 0 | 0
2023-02-26 16:30 | 1.2455 | 0 | N/A | 0 | 0
2023-02-26 17:00 | 2.0514 | 0 | N/A | 0 | 0
2023-02-26 17:30 | 2.4766 | 0 | N/A | 0 | 0
2023-02-26 18:00 | 3.7274 | 0 | N/A | 0 | 0
2023-02-26 18:30 | 4.262 | 0 | N/A | 0 | 0
2023-02-26 19:00 | 4.2598 | 0 | N/A | 0 | 0
2023-02-26 19:30 | 4.5677 | 0 | N/A | 0 | 0
2023-02-26 20:00 | 4.8026 | 0 | N/A | 0 | 0
2023-02-26 20:30 | 4.7154 | 0 | N/A | 0 | 0
2023-02-26 21:00 | 4.6579 | 0 | N/A | 0 | 0
2023-02-26 21:30 | 4.5264 | 0 | N/A | 0 | 0
2023-02-26 22:00 | 4.1753 | 0 | N/A | 0 | 0
2023-02-26 22:30 | 4.2609 | 0 | N/A | 0 | 0
2023-02-26 23:00 | 4.2419 | 0 | N/A | 0 | 0
2023-02-26 23:30 | 3.9524 | 0 | N/A | 0 | 0
2023-02-27 | 4.0238 | 0 | N/A | 0 | 0
2023-02-28 00:30 | 4.3766 | 0 | N/A | 0 | 0
2023-02-28 01:00 | 4.605 | 0 | N/A | 0 | 0
2023-02-28 01:30 | 3.9775 | 0 | N/A | 0 | 0
2023-02-28 02:00 | 3.3785 | 0 | N/A | 0 | 0
2023-02-28 02:30 | 3.3372 | 0 | N/A | 0 | 0
2023-02-28 03:00 | 3.1231 | 0 | N/A | 0 | 0
2023-02-28 03:30 | 2.8621 | 0 | N/A | 0 | 0
2023-02-28 04:00 | 2.7628 | 0 | N/A | 0 | 0
2023-02-28 04:30 | 2.6931 | 0 | N/A | 0 | 0
2023-02-28 05:00 | 2.7527 | 0 | N/A | 0 | 0
2023-02-28 05:30 | 2.9071 | 0 | N/A | 0 | 0
2023-02-28 06:00 | 3.1738 | 0 | N/A | 0 | 0
2023-02-28 06:30 | 3.7216 | 0 | N/A | 0 | 0
2023-02-28 07:00 | 4.4686 | 0 | N/A | 0 | 0
2023-02-28 07:30 | 5.3731 | 0 | N/A | 0 | 0
2023-02-28 08:00 | 5.657 | 0 | N/A | 0 | 0
2023-02-28 08:30 | 5.3034 | 0 | N/A | 0 | 0
2023-02-28 09:00 | 5.0461 | 0 | N/A | 0 | 0
2023-02-28 09:30 | 4.8598 | 0 | N/A | 0 | 0
2023-02-28 10:00 | 4.3025 | 0 | N/A | 0 | 0
2023-02-28 10:30 | 5.4296 | 0 | N/A | 0 | 0
2023-02-28 11:00 | 5.7427 | 0 | N/A | 0 | 0
2023-02-28 11:30 | 4.6699 | 0 | N/A | 0 | 0
2023-02-28 12:00 | 4.4818 | 0 | N/A | 0 | 0
2023-02-28 12:30 | 4.5368 | 0 | N/A | 0 | 0
2023-02-28 13:00 | 4.2868 | 0 | N/A | 0 | 0
2023-02-28 13:30 | 3.5079 | 0 | N/A | 0 | 0
2023-02-28 14:00 | 2.9497 | 0 | N/A | 0 | 0
2023-02-28 14:30 | 3.3172 | 0 | N/A | 0 | 0
2023-02-28 15:00 | 3.4837 | 0 | N/A | 0 | 0
2023-02-28 15:30 | 3.2861 | 0 | N/A | 0 | 0
2023-02-28 16:00 | 3.3463 | 0 | N/A | 0 | 0
2023-02-28 16:30 | 3.3194 | 0 | N/A | 0 | 0
2023-02-28 17:00 | 3.6704 | 0 | N/A | 0 | 0
2023-02-28 17:30 | 4.3093 | 0 | N/A | 0 | 0
2023-02-28 18:00 | 5.3019 | 0 | N/A | 0 | 0
2023-02-28 18:30 | 5.6346 | 0 | N/A | 0 | 0
2023-02-28 19:00 | 5.8645 | 0 | N/A | 0 | 0
2023-02-28 19:30 | 5.8883 | 0 | N/A | 0 | 0
2023-02-28 20:00 | 5.8282 | 0 | N/A | 0 | 0
2023-02-28 20:30 | 5.7681 | 0 | N/A | 0 | 0
2023-02-28 21:00 | 5.5863 | 0 | N/A | 0 | 0
2023-02-28 21:30 | 5.2712 | 0 | N/A | 0 | 0
2023-02-28 22:00 | 4.8677 | 0 | N/A | 0 | 0
2023-02-28 22:30 | 4.8829 | 0 | N/A | 0 | 0
2023-02-28 23:00 | 4.7038 | 0 | N/A | 0 | 0
2023-02-28 23:30 | 4.2694 | 0 | N/A | 0 | 0
2023-03-01 | 4.1107 | 0 | N/A | 0 | 0
2023-03-02 00:30 | 4.3019 | 0 | N/A | 0 | 0
2023-03-02 01:00 | 4.6197 | 0 | N/A | 0 | 0
2023-03-02 01:30 | 4.0033 | 0 | N/A | 0 | 0
2023-03-02 02:00 | 3.3946 | 0 | N/A | 0 | 0
2023-03-02 02:30 | 3.2735 | 0 | N/A | 0 | 0
2023-03-02 03:00 | 3.0903 | 0 | N/A | 0 | 0
2023-03-02 03:30 | 2.8624 | 0 | N/A | 0 | 0
2023-03-02 04:00 | 2.7588 | 0 | N/A | 0 | 0
2023-03-02 04:30 | 2.6839 | 0 | N/A | 0 | 0
2023-03-02 05:00 | 2.7531 | 0 | N/A | 0 | 0
2023-03-02 05:30 | 2.8957 | 0 | N/A | 0 | 0
2023-03-02 06:00 | 3.1509 | 0 | N/A | 0 | 0
2023-03-02 06:30 | 3.6518 | 0 | N/A | 0 | 0
2023-03-02 07:00 | 4.6754 | 0 | N/A | 0 | 0
2023-03-02 07:30 | 5.6647 | 0 | N/A | 0 | 0
2023-03-02 08:00 | 5.8309 | 0 | N/A | 0 | 0
2023-03-02 08:30 | 5.3128 | 0 | N/A | 0 | 0
2023-03-02 09:00 | 4.6409 | 0 | N/A | 0 | 0
2023-03-02 09:30 | 4.2264 | 0 | N/A | 0 | 0
2023-03-02 10:00 | 2.6738 | 0 | N/A | 0 | 0
2023-03-02 10:30 | 0 | 0 | N/A | 0 | 0
2023-03-02 11:00 | 0 | 0 | N/A | 0 | 0
2023-03-02 11:30 | 0 | 0 | N/A | 0 | 0
2023-03-02 12:00 | 0 | 0 | N/A | 0 | 0
2023-03-02 12:30 | 0 | 0 | N/A | 0 | 0
2023-03-02 13:00 | 0 | 0 | N/A | 0 | 0
2023-03-02 13:30 | 0 | 0 | N/A | 0 | 0
2023-03-02 14:00 | 0 | 0 | N/A | 0 | 0
2023-03-02 14:30 | 0 | 0 | N/A | 0 | 0
2023-03-02 15:00 | 0 | 0 | N/A | 0 | 0
2023-03-02 15:30 | 0 | 0 | N/A | 0 | 0
2023-03-02 16:00 | -0.55747 | 0 | N/A | 0 | 0
2023-03-02 16:30 | -1.0121 | 0 | N/A | 0 | 0
2023-03-02 17:00 | 1.0174 | 0 | N/A | 0 | 0
2023-03-02 17:30 | 1.6217 | 0 | N/A | 0 | 0
2023-03-02 18:00 | 2.415 | 0 | N/A | 0 | 0
2023-03-02 18:30 | 3.3317 | 0 | N/A | 0 | 0
2023-03-02 19:00 | 4.0619 | 0 | N/A | 0 | 0
2023-03-02 19:30 | 4.429 | 0 | N/A | 0 | 0
2023-03-02 20:00 | 4.9267 | 0 | N/A | 0 | 0
2023-03-02 20:30 | 5.0656 | 0 | N/A | 0 | 0
2023-03-02 21:00 | 4.9624 | 0 | N/A | 0 | 0
2023-03-02 21:30 | 4.7975 | 0 | N/A | 0 | 0
2023-03-02 22:00 | 4.4869 | 0 | N/A | 0 | 0
2023-03-02 22:30 | 4.6338 | 0 | N/A | 0 | 0
2023-03-02 23:00 | 4.5172 | 0 | N/A | 0 | 0
2023-03-02 23:30 | 4.1845 | 0 | N/A | 0 | 0
2023-03-03 | 4.1865 | 0 | N/A | 0 | 0
2023-03-03 00:30 | 4.3819 | 0 | N/A | 0 | 0
2023-03-03 01:00 | 4.6579 | 0 | N/A | 0 | 0
2023-03-03 01:30 | 4.011 | 0 | N/A | 0 | 0
2023-03-03 02:00 | 3.5396 | 0 | N/A | 0 | 0
2023-03-03 02:30 | 3.4471 | 0 | N/A | 0 | 0
2023-03-03 03:00 | 3.1814 | 0 | N/A | 0 | 0
2023-03-03 03:30 | 2.9175 | 0 | N/A | 0 | 0
2023-03-03 04:00 | 2.8227 | 0 | N/A | 0 | 0
2023-03-03 04:30 | 2.768 | 0 | N/A | 0 | 0
2023-03-03 05:00 | 2.8023 | 0 | N/A | 0 | 0
2023-03-03 05:30 | 2.9612 | 0 | N/A | 0 | 0
2023-03-03 06:00 | 3.2524 | 0 | N/A | 0 | 0
2023-03-03 06:30 | 3.7846 | 0 | N/A | 0 | 0
2023-03-03 07:00 | 4.5888 | 0 | N/A | 0 | 0
2023-03-03 07:30 | 5.3242 | 0 | N/A | 0 | 0
2023-03-03 08:00 | 5.6455 | 0 | N/A | 0 | 0
2023-03-03 08:30 | 5.3344 | 0 | N/A | 0 | 0
2023-03-03 09:00 | 4.9164 | 0 | N/A | 0 | 0
2023-03-03 09:30 | 4.7643 | 0 | N/A | 0 | 0
2023-03-03 10:00 | 3.7867 | 0 | N/A | 0 | 0
2023-03-03 10:30 | 3.0361 | 0 | N/A | 0 | 0
2023-03-03 11:00 | 2.6494 | 0 | N/A | 0 | 0
2023-03-03 11:30 | 2.0632 | 0 | N/A | 0 | 0
2023-03-03 12:00 | 1.5265 | 0 | N/A | 0 | 0
2023-03-03 12:30 | 0.6926 | 0 | N/A | 0 | 0
2023-03-03 13:00 | -1.3562 | 0 | N/A | 0 | 0
2023-03-03 13:30 | -1.925 | 0 | N/A | 0 | 0
2023-03-03 14:00 | -2.2567 | 0 | N/A | 0 | 0
2023-03-03 14:30 | -2.301 | 0 | N/A | 0 | 0
2023-03-03 15:00 | -2.0797 | 0 | N/A | 0 | 0
2023-03-03 15:30 | -2.2776 | 0 | N/A | 0 | 0
2023-03-03 16:00 | -2.1886 | 0 | N/A | 0 | 0
2023-03-03 16:30 | -1.6595 | 0 | N/A | 0 | 0
2023-03-03 17:00 | -1.1046 | 0 | N/A | 0 | 0
2023-03-03 17:30 | 0.89237 | 0 | N/A | 0 | 0
2023-03-03 18:00 | 1.5845 | 0 | N/A | 0 | 0
2023-03-03 18:30 | 2.6133 | 0 | N/A | 0 | 0
2023-03-03 19:00 | 3.5344 | 0 | N/A | 0 | 0
2023-03-03 19:30 | 4.1343 | 0 | N/A | 0 | 0
2023-03-03 20:00 | 4.4968 | 0 | N/A | 0 | 0
2023-03-03 20:30 | 4.7277 | 0 | N/A | 0 | 0
2023-03-03 21:00 | 4.7887 | 0 | N/A | 0 | 0
2023-03-03 21:30 | 4.6222 | 0 | N/A | 0 | 0
2023-03-03 22:00 | 4.3395 | 0 | N/A | 0 | 0
2023-03-03 22:30 | 4.5206 | 0 | N/A | 0 | 0
2023-03-03 23:00 | 4.4412 | 0 | N/A | 0 | 0
2023-03-03 23:30 | 4.1944 | 0 | N/A | 0 | 0
2023-03-04 | 4.1605 | 0 | N/A | 0 | 0
2023-03-04 00:30 | 4.3425 | 0 | N/A | 0 | 0
2023-03-04 01:00 | 4.5752 | 0 | N/A | 0 | 0
2023-03-04 01:30 | 3.8881 | 0 | N/A | 0 | 0
2023-03-04 02:00 | 3.3663 | 0 | N/A | 0 | 0
2023-03-04 02:30 | 3.2075 | 0 | N/A | 0 | 0
2023-03-04 03:00 | 2.9783 | 0 | N/A | 0 | 0
2023-03-04 03:30 | 2.8072 | 0 | N/A | 0 | 0
2023-03-04 04:00 | 2.721 | 0 | N/A | 0 | 0
2023-03-04 04:30 | 2.6857 | 0 | N/A | 0 | 0
2023-03-04 05:00 | 2.6526 | 0 | N/A | 0 | 0
2023-03-04 05:30 | 2.6414 | 0 | N/A | 0 | 0
2023-03-04 06:00 | 2.7362 | 0 | N/A | 0 | 0
2023-03-04 06:30 | 2.9859 | 0 | N/A | 0 | 0
2023-03-04 07:00 | 3.1872 | 0 | N/A | 0 | 0
2023-03-04 07:30 | 3.366 | 0 | N/A | 0 | 0
2023-03-04 08:00 | 3.3795 | 0 | N/A | 0 | 0
2023-03-04 08:30 | 3.3273 | 0 | N/A | 0 | 0
2023-03-04 09:00 | 3.1469 | 0 | N/A | 0 | 0
2023-03-04 09:30 | 2.1712 | 0 | N/A | 0 | 0
2023-03-04 10:00 | 1.3373 | 0 | N/A | 0 | 0
2023-03-04 10:30 | 0.8542 | 0 | N/A | 0 | 0
2023-03-04 11:00 | -0.74441 | 0 | N/A | 0 | 0
2023-03-04 11:30 | 1.6457 | 0 | N/A | 0 | 0
2023-03-04 12:00 | 1.4644 | 0 | N/A | 0 | 0
2023-03-04 12:30 | -1.02 | 0 | N/A | 0 | 0
2023-03-04 13:00 | 1.0886 | 0 | N/A | 0 | 0
2023-03-04 13:30 | -1.0594 | 0 | N/A | 0 | 0
2023-03-04 14:00 | -1.3463 | 0 | N/A | 0 | 0
2023-03-04 14:30 | -1.7967 | 0 | N/A | 0 | 0
2023-03-04 15:00 | -1.1947 | 0 | N/A | 0 | 0
2023-03-04 15:30 | 1.0514 | 0 | N/A | 0 | 0
2023-03-04 16:00 | 1.3082 | 0 | N/A | 0 | 0
2023-03-04 16:30 | 0.98611 | 0 | N/A | 0 | 0
2023-03-04 17:00 | 1.402 | 0 | N/A | 0 | 0
2023-03-04 17:30 | 2.2892 | 0 | N/A | 0 | 0
2023-03-04 18:00 | 2.1198 | 0 | N/A | 0 | 0
2023-03-04 18:30 | 3.1687 | 0 | N/A | 0 | 0
2023-03-04 19:00 | 3.8741 | 0 | N/A | 0 | 0
2023-03-04 19:30 | 4.3163 | 0 | N/A | 0 | 0
2023-03-04 20:00 | 4.5527 | 0 | N/A | 0 | 0
2023-03-04 20:30 | 4.5277 | 0 | N/A | 0 | 0
2023-03-04 21:00 | 4.3599 | 0 | N/A | 0 | 0
2023-03-04 21:30 | 4.1491 | 0 | N/A | 0 | 0
2023-03-04 22:00 | 3.8477 | 0 | N/A | 0 | 0
2023-03-04 22:30 | 4.1301 | 0 | N/A | 0 | 0
2023-03-04 23:00 | 4.1564 | 0 | N/A | 0 | 0
2023-03-04 23:30 | 3.8107 | 0 | N/A | 0 | 0
2023-03-05 | 3.8957 | 0 | N/A | 0 | 0
2023-03-05 00:30 | 4.2144 | 0 | N/A | 0 | 0
2023-03-05 01:00 | 4.3236 | 0 | N/A | 0 | 0
2023-03-05 01:30 | 3.6661 | 0 | N/A | 0 | 0
2023-03-05 02:00 | 3.2159 | 0 | N/A | 0 | 0
2023-03-05 02:30 | 3.0996 | 0 | N/A | 0 | 0
2023-03-05 03:00 | 2.9389 | 0 | N/A | 0 | 0
2023-03-05 03:30 | 2.6434 | 0 | N/A | 0 | 0
2023-03-05 04:00 | 2.5055 | 0 | N/A | 0 | 0
2023-03-05 04:30 | 2.5005 | 0 | N/A | 0 | 0
2023-03-05 05:00 | 2.4707 | 0 | N/A | 0 | 0
2023-03-05 05:30 | 2.4995 | 0 | N/A | 0 | 0
2023-03-05 06:00 | 2.4886 | 0 | N/A | 0 | 0
2023-03-05 06:30 | 2.6885 | 0 | N/A | 0 | 0
2023-03-05 07:00 | 2.8217 | 0 | N/A | 0 | 0
2023-03-05 07:30 | 2.9602 | 0 | N/A | 0 | 0
2023-03-05 08:00 | 3.0795 | 0 | N/A | 0 | 0
2023-03-05 08:30 | 2.7467 | 0 | N/A | 0 | 0
2023-03-05 09:00 | 2.3324 | 0 | N/A | 0 | 0
2023-03-05 09:30 | 1.8551 | 0 | N/A | 0 | 0
2023-03-05 10:00 | 1.368 | 0 | N/A | 0 | 0
2023-03-05 10:30 | 1.017 | 0 | N/A | 0 | 0
2023-03-05 11:00 | -0.9294 | 0 | N/A | 0 | 0
2023-03-05 11:30 | -0.89756 | 0 | N/A | 0 | 0
2023-03-05 12:00 | -1.3474 | 0 | N/A | 0 | 0
2023-03-05 12:30 | -0.91171 | 0 | N/A | 0 | 0
2023-03-05 13:00 | -1.802 | 0 | N/A | 0 | 0
2023-03-05 13:30 | -0.97402 | 0 | N/A | 0 | 0
2023-03-05 14:00 | -0.88391 | 0 | N/A | 0 | 0
2023-03-05 14:30 | -0.79533 | 0 | N/A | 0 | 0
2023-03-05 15:00 | 0.73086 | 0 | N/A | 0 | 0
2023-03-05 15:30 | 2.0378 | 0 | N/A | 0 | 0
2023-03-05 16:00 | 3.6664 | 0 | N/A | 0 | 0
2023-03-05 16:30 | 4.7494 | 0 | N/A | 0 | 0
2023-03-05 17:00 | 5.2909 | 0 | N/A | 0 | 0
2023-03-05 17:30 | 5.1019 | 0 | N/A | 0 | 0
2023-03-05 18:00 | 5.6621 | 0 | N/A | 0 | 0
2023-03-05 18:30 | 5.3463 | 0 | N/A | 0 | 0
2023-03-05 19:00 | 5.302 | 0 | N/A | 0 | 0
2023-03-05 19:30 | 5.2612 | 0 | N/A | 0 | 0
2023-03-05 20:00 | 5.0784 | 0 | N/A | 0 | 0
2023-03-05 20:30 | 4.7658 | 0 | N/A | 0 | 0
2023-03-05 21:00 | 4.5292 | 0 | N/A | 0 | 0
2023-03-05 21:30 | 4.3333 | 0 | N/A | 0 | 0
2023-03-05 22:00 | 4.0323 | 0 | N/A | 0 | 0
2023-03-05 22:30 | 4.1862 | 0 | N/A | 0 | 0
2023-03-05 23:00 | 4.1173 | 0 | N/A | 0 | 0
2023-03-05 23:30 | 3.8872 | 0 | N/A | 0 | 0
2023-03-06 | 3.904 | 0 | N/A | 0 | 0
2023-03-06 00:30 | 4.242 | 0 | N/A | 0 | 0
2023-03-06 01:00 | 4.3824 | 0 | N/A | 0 | 0
2023-03-06 01:30 | 3.7086 | 0 | N/A | 0 | 0
2023-03-06 02:00 | 3.239 | 0 | N/A | 0 | 0
2023-03-06 02:30 | 3.1565 | 0 | N/A | 0 | 0
2023-03-06 03:00 | 2.9307 | 0 | N/A | 0 | 0
2023-03-06 03:30 | 2.7209 | 0 | N/A | 0 | 0
2023-03-06 04:00 | 2.6394 | 0 | N/A | 0 | 0
2023-03-06 04:30 | 2.603 | 0 | N/A | 0 | 0
2023-03-06 05:00 | 2.6167 | 0 | N/A | 0 | 0
2023-03-06 05:30 | 2.8378 | 0 | N/A | 0 | 0
2023-03-06 06:00 | 3.1397 | 0 | N/A | 0 | 0
2023-03-06 06:30 | 3.5602 | 0 | N/A | 0 | 0
2023-03-06 07:00 | 4.2327 | 0 | N/A | 0 | 0
2023-03-06 07:30 | 5.1453 | 0 | N/A | 0 | 0
2023-03-06 08:00 | 5.3738 | 0 | N/A | 0 | 0
2023-03-06 08:30 | 4.3997 | 0 | N/A | 0 | 0
2023-03-06 09:00 | 3.5654 | 0 | N/A | 0 | 0
2023-03-06 09:30 | 2.7995 | 0 | N/A | 0 | 0
2023-03-06 10:00 | 2.7164 | 0 | N/A | 0 | 0
2023-03-06 10:30 | 1.7307 | 0 | N/A | 0 | 0
2023-03-06 11:00 | 1.3012 | 0 | N/A | 0 | 0
2023-03-06 11:30 | 0.9548 | 0 | N/A | 0 | 0
2023-03-06 12:00 | 0.72078 | 0 | N/A | 0 | 0
2023-03-06 12:30 | -0.82206 | 0 | N/A | 0 | 0
2023-03-06 13:00 | 0.91381 | 0 | N/A | 0 | 0
2023-03-06 13:30 | -0.70286 | 0 | N/A | 0 | 0
2023-03-06 14:00 | 0.69208 | 0 | N/A | 0 | 0
2023-03-06 14:30 | 0.76164 | 0 | N/A | 0 | 0
2023-03-06 15:00 | 0.80236 | 0 | N/A | 0 | 0
2023-03-06 15:30 | 1.0469 | 0 | N/A | 0 | 0
2023-03-06 16:00 | 1.2054 | 0 | N/A | 0 | 0
2023-03-06 16:30 | 0.88757 | 0 | N/A | 0 | 0
2023-03-06 17:00 | 1.1614 | 0 | N/A | 0 | 0
2023-03-06 17:30 | 1.9557 | 0 | N/A | 0 | 0
2023-03-06 18:00 | 2.6536 | 0 | N/A | 0 | 0
2023-03-06 18:30 | 3.4559 | 0 | N/A | 0 | 0
2023-03-06 19:00 | 4.3503 | 0 | N/A | 0 | 0
2023-03-06 19:30 | 4.7844 | 0 | N/A | 0 | 0
2023-03-06 20:00 | 4.905 | 0 | N/A | 0 | 0
2023-03-06 20:30 | 4.9492 | 0 | N/A | 0 | 0
2023-03-06 21:00 | 4.7881 | 0 | N/A | 0 | 0
2023-03-06 21:30 | 4.4762 | 0 | N/A | 0 | 0
2023-03-06 22:00 | 4.2065 | 0 | N/A | 0 | 0
2023-03-06 22:30 | 4.2883 | 0 | N/A | 0 | 0
2023-03-06 23:00 | 4.2048 | 0 | N/A | 0 | 0
2023-03-06 23:30 | 3.8999 | 0 | N/A | 0 | 0
2023-03-07 | 3.8304 | 0 | N/A | 0 | 0
2023-03-07 00:30 | 4.2175 | 0 | N/A | 0 | 0
2023-03-07 01:00 | 4.4405 | 0 | N/A | 0 | 0
2023-03-07 01:30 | 3.7689 | 0 | N/A | 0 | 0
2023-03-07 02:00 | 3.3212 | 0 | N/A | 0 | 0
2023-03-07 02:30 | 3.2494 | 0 | N/A | 0 | 0
2023-03-07 03:00 | 3.0148 | 0 | N/A | 0 | 0
2023-03-07 03:30 | 2.8107 | 0 | N/A | 0 | 0
2023-03-07 04:00 | 2.6939 | 0 | N/A | 0 | 0
2023-03-07 04:30 | 2.6486 | 0 | N/A | 0 | 0
2023-03-07 05:00 | 2.704 | 0 | N/A | 0 | 0
2023-03-07 05:30 | 2.9133 | 0 | N/A | 0 | 0
2023-03-07 06:00 | 3.1665 | 0 | N/A | 0 | 0
2023-03-07 06:30 | 3.6726 | 0 | N/A | 0 | 0
2023-03-07 07:00 | 4.1599 | 0 | N/A | 0 | 0
2023-03-07 07:30 | 5.0856 | 0 | N/A | 0 | 0
2023-03-07 08:00 | 5.3394 | 0 | N/A | 0 | 0
2023-03-07 08:30 | 4.8016 | 0 | N/A | 0 | 0
2023-03-07 09:00 | 4.0455 | 0 | N/A | 0 | 0
2023-03-07 09:30 | 3.2056 | 0 | N/A | 0 | 0
2023-03-07 10:00 | 2.6923 | 0 | N/A | 0 | 0
2023-03-07 10:30 | 2.0525 | 0 | N/A | 0 | 0
2023-03-07 11:00 | 0.90806 | 0 | N/A | 0 | 0
2023-03-07 11:30 | 0.60898 | 0 | N/A | 0 | 0
2023-03-07 12:00 | 0.82568 | 0 | N/A | 0 | 0
2023-03-07 12:30 | 0.91389 | 0 | N/A | 0 | 0
2023-03-07 13:00 | 0.92947 | 0 | N/A | 0 | 0
2023-03-07 13:30 | 0.97609 | 0 | N/A | 0 | 0
2023-03-07 14:00 | -0.90349 | 0 | N/A | 0 | 0
2023-03-07 14:30 | 1.0282 | 0 | N/A | 0 | 0
2023-03-07 15:00 | 0.93212 | 0 | N/A | 0 | 0
2023-03-07 15:30 | 1.6428 | 0 | N/A | 0 | 0
2023-03-07 16:00 | 1.5085 | 0 | N/A | 0 | 0
2023-03-07 16:30 | 1.9354 | 0 | N/A | 0 | 0
2023-03-07 17:00 | 2.4303 | 0 | N/A | 0 | 0
2023-03-07 17:30 | 2.781 | 0 | N/A | 0 | 0
2023-03-07 18:00 | 4.216 | 0 | N/A | 0 | 0
2023-03-07 18:30 | 4.83 | 0 | N/A | 0 | 0
2023-03-07 19:00 | 5.176 | 0 | N/A | 0 | 0
2023-03-07 19:30 | 5.3498 | 0 | N/A | 0 | 0
2023-03-07 20:00 | 5.3582 | 0 | N/A | 0 | 0
2023-03-07 20:30 | 5.4196 | 0 | N/A | 0 | 0
2023-03-07 21:00 | 5.3141 | 0 | N/A | 0 | 0
2023-03-07 21:30 | 5.0586 | 0 | N/A | 0 | 0
2023-03-07 22:00 | 4.6771 | 0 | N/A | 0 | 0
2023-03-07 22:30 | 4.6295 | 0 | N/A | 0 | 0
2023-03-07 23:00 | 4.4964 | 0 | N/A | 0 | 0
2023-03-07 23:30 | 4.1416 | 0 | N/A | 0 | 0
2023-03-08 | 4.2154 | 0 | N/A | 0 | 0
2023-03-08 00:30 | 4.5108 | 0 | N/A | 0 | 0
2023-03-08 01:00 | 4.7116 | 0 | N/A | 0 | 0
2023-03-08 01:30 | 4.052 | 0 | N/A | 0 | 0
2023-03-08 02:00 | 3.502 | 0 | N/A | 0 | 0
2023-03-08 02:30 | 3.4457 | 0 | N/A | 0 | 0
2023-03-08 03:00 | 3.2401 | 0 | N/A | 0 | 0
2023-03-08 03:30 | 3.0698 | 0 | N/A | 0 | 0
2023-03-08 04:00 | 2.879 | 0 | N/A | 0 | 0
2023-03-08 04:30 | 2.8555 | 0 | N/A | 0 | 0
2023-03-08 05:00 | 2.8863 | 0 | N/A | 0 | 0
2023-03-08 05:30 | 3.0817 | 0 | N/A | 0 | 0
2023-03-08 06:00 | 3.419 | 0 | N/A | 0 | 0
2023-03-08 06:30 | 3.9868 | 0 | N/A | 0 | 0
2023-03-08 07:00 | 4.6777 | 0 | N/A | 0 | 0
2023-03-08 07:30 | 5.4841 | 0 | N/A | 0 | 0
2023-03-08 08:00 | 5.7425 | 0 | N/A | 0 | 0
2023-03-08 08:30 | 4.8773 | 0 | N/A | 0 | 0
2023-03-08 09:00 | 3.989 | 0 | N/A | 0 | 0
2023-03-08 09:30 | 3.1214 | 0 | N/A | 0 | 0
2023-03-08 10:00 | 2.349 | 0 | N/A | 0 | 0
2023-03-08 10:30 | 2.037 | 0 | N/A | 0 | 0
2023-03-08 11:00 | 1.701 | 0 | N/A | 0 | 0
2023-03-08 11:30 | 2.5708 | 0 | N/A | 0 | 0
2023-03-08 12:00 | 1.8455 | 0 | N/A | 0 | 0
2023-03-08 12:30 | 2.1686 | 0 | N/A | 0 | 0
2023-03-08 13:00 | 1.4783 | 0 | N/A | 0 | 0
2023-03-08 13:30 | 1.0923 | 0 | N/A | 0 | 0
2023-03-08 14:00 | 1.3489 | 0 | N/A | 0 | 0
2023-03-08 14:30 | 0.92535 | 0 | N/A | 0 | 0
2023-03-08 15:00 | 1.5544 | 0 | N/A | 0 | 0
2023-03-08 15:30 | 1.1018 | 0 | N/A | 0 | 0
2023-03-08 16:00 | 1.6136 | 0 | N/A | 0 | 0
2023-03-08 16:30 | 1.4907 | 0 | N/A | 0 | 0
2023-03-08 17:00 | 2.3235 | 0 | N/A | 0 | 0
2023-03-08 17:30 | 2.7893 | 0 | N/A | 0 | 0
2023-03-08 18:00 | 4.2915 | 0 | N/A | 0 | 0
2023-03-08 18:30 | 4.8388 | 0 | N/A | 0 | 0
2023-03-08 19:00 | 4.9674 | 0 | N/A | 0 | 0
2023-03-08 19:30 | 5.4055 | 0 | N/A | 0 | 0
2023-03-08 20:00 | 5.7101 | 0 | N/A | 0 | 0
2023-03-08 20:30 | 5.7957 | 0 | N/A | 0 | 0
2023-03-08 21:00 | 5.6608 | 0 | N/A | 0 | 0
2023-03-08 21:30 | 5.377 | 0 | N/A | 0 | 0
2023-03-08 22:00 | 4.9615 | 0 | N/A | 0 | 0
2023-03-08 22:30 | 4.9033 | 0 | N/A | 0 | 0
2023-03-08 23:00 | 4.851 | 0 | N/A | 0 | 0
2023-03-08 23:30 | 4.4501 | 0 | N/A | 0 | 0
2023-03-09 | 4.3534 | 0 | N/A | 0 | 0
2023-03-09 00:30 | 4.6475 | 0 | N/A | 0 | 0
2023-03-09 01:00 | 4.8672 | 0 | N/A | 0 | 0
2023-03-09 01:30 | 4.1414 | 0 | N/A | 0 | 0
2023-03-09 02:00 | 3.6572 | 0 | N/A | 0 | 0
2023-03-09 02:30 | 3.6049 | 0 | N/A | 0 | 0
2023-03-09 03:00 | 3.3962 | 0 | N/A | 0 | 0
2023-03-09 03:30 | 3.1738 | 0 | N/A | 0 | 0
2023-03-09 04:00 | 3.0211 | 0 | N/A | 0 | 0
2023-03-09 04:30 | 2.9744 | 0 | N/A | 0 | 0
2023-03-09 05:00 | 2.9946 | 0 | N/A | 0 | 0
2023-03-09 05:30 | 3.217 | 0 | N/A | 0 | 0
2023-03-09 06:00 | 3.5252 | 0 | N/A | 0 | 0
2023-03-09 06:30 | 4.0499 | 0 | N/A | 0 | 0
2023-03-09 07:00 | 4.7955 | 0 | N/A | 0 | 0
2023-03-09 07:30 | 5.6619 | 0 | N/A | 0 | 0
2023-03-09 08:00 | 5.9143 | 0 | N/A | 0 | 0
2023-03-09 08:30 | 5.2197 | 0 | N/A | 0 | 0
2023-03-09 09:00 | 4.7289 | 0 | N/A | 0 | 0
2023-03-09 09:30 | 4.3277 | 0 | N/A | 0 | 0
2023-03-09 10:00 | 3.6115 | 0 | N/A | 0 | 0
2023-03-09 10:30 | 3.6011 | 0 | N/A | 0 | 0
2023-03-09 11:00 | 2.7787 | 0 | N/A | 0 | 0
2023-03-09 11:30 | 1.9294 | 0 | N/A | 0 | 0
2023-03-09 12:00 | 2.1544 | 0 | N/A | 0 | 0
2023-03-09 12:30 | 0.87594 | 0 | N/A | 0 | 0
2023-03-09 13:00 | 1.6096 | 0 | N/A | 0 | 0
2023-03-09 13:30 | 1.5337 | 0 | N/A | 0 | 0
2023-03-09 14:00 | 1.2493 | 0 | N/A | 0 | 0
2023-03-09 14:30 | 1.0123 | 0 | N/A | 0 | 0
2023-03-09 15:00 | 0.9366 | 0 | N/A | 0 | 0
2023-03-09 15:30 | 0.85222 | 0 | N/A | 0 | 0
2023-03-09 16:00 | -0.88717 | 0 | N/A | 0 | 0
2023-03-09 16:30 | 1.8784 | 0 | N/A | 0 | 0
2023-03-09 17:00 | 2.4684 | 0 | N/A | 0 | 0
2023-03-09 17:30 | 2.9773 | 0 | N/A | 0 | 0
2023-03-09 18:00 | 2.732 | 0 | N/A | 0 | 0
2023-03-09 18:30 | 3.3936 | 0 | N/A | 0 | 0
2023-03-09 19:00 | 4.076 | 0 | N/A | 0 | 0
2023-03-09 19:30 | 4.6753 | 0 | N/A | 0 | 0
2023-03-09 20:00 | 5.0405 | 0 | N/A | 0 | 0
2023-03-09 20:30 | 5.3107 | 0 | N/A | 0 | 0
2023-03-09 21:00 | 5.1953 | 0 | N/A | 0 | 0
2023-03-09 21:30 | 5.0285 | 0 | N/A | 0 | 0
2023-03-09 22:00 | 4.7238 | 0 | N/A | 0 | 0
2023-03-09 22:30 | 4.7412 | 0 | N/A | 0 | 0
2023-03-09 23:00 | 4.6485 | 0 | N/A | 0 | 0
2023-03-09 23:30 | 4.2271 | 0 | N/A | 0 | 0
2023-03-10 | 4.2694 | 0 | N/A | 0 | 0
2023-03-10 00:30 | 4.5022 | 0 | N/A | 0 | 0
2023-03-10 01:00 | 4.793 | 0 | N/A | 0 | 0
2023-03-10 01:30 | 4.1109 | 0 | N/A | 0 | 0
2023-03-10 02:00 | 3.5619 | 0 | N/A | 0 | 0
2023-03-10 02:30 | 3.4576 | 0 | N/A | 0 | 0
2023-03-10 03:00 | 3.2006 | 0 | N/A | 0 | 0
2023-03-10 03:30 | 2.9971 | 0 | N/A | 0 | 0
2023-03-10 04:00 | 2.8735 | 0 | N/A | 0 | 0
2023-03-10 04:30 | 2.78 | 0 | N/A | 0 | 0
2023-03-10 05:00 | 2.8091 | 0 | N/A | 0 | 0
2023-03-10 05:30 | 3.0016 | 0 | N/A | 0 | 0
2023-03-10 06:00 | 3.2969 | 0 | N/A | 0 | 0
2023-03-10 06:30 | 3.9782 | 0 | N/A | 0 | 0
2023-03-10 07:00 | 4.6336 | 0 | N/A | 0 | 0
2023-03-10 07:30 | 5.3547 | 0 | N/A | 0 | 0
2023-03-10 08:00 | 5.6093 | 0 | N/A | 0 | 0
2023-03-10 08:30 | 5.1617 | 0 | N/A | 0 | 0
2023-03-10 09:00 | 4.8904 | 0 | N/A | 0 | 0
2023-03-10 09:30 | 4.3337 | 0 | N/A | 0 | 0
2023-03-10 10:00 | 3.8105 | 0 | N/A | 0 | 0
2023-03-10 10:30 | 3.1817 | 0 | N/A | 0 | 0
2023-03-10 11:00 | 2.8345 | 0 | N/A | 0 | 0
2023-03-10 11:30 | 2.1462 | 0 | N/A | 0 | 0
2023-03-10 12:00 | 1.3431 | 0 | N/A | 0 | 0
2023-03-10 12:30 | 0.75828 | 0 | N/A | 0 | 0
2023-03-10 13:00 | -0.85512 | 0 | N/A | 0 | 0
2023-03-10 13:30 | -1.1749 | 0 | N/A | 0 | 0
2023-03-10 14:00 | -1.3844 | 0 | N/A | 0 | 0
2023-03-10 14:30 | -1.7212 | 0 | N/A | 0 | 0
2023-03-10 15:00 | -1.7051 | 0 | N/A | 0 | 0
2023-03-10 15:30 | -1.8807 | 0 | N/A | 0 | 0
2023-03-10 16:00 | -1.4483 | 0 | N/A | 0 | 0
2023-03-10 16:30 | -0.82517 | 0 | N/A | 0 | 0
2023-03-10 17:00 | 0.90628 | 0 | N/A | 0 | 0
2023-03-10 17:30 | 2.3216 | 0 | N/A | 0 | 0
2023-03-10 18:00 | 2.804 | 0 | N/A | 0 | 0
2023-03-10 18:30 | 3.549 | 0 | N/A | 0 | 0
2023-03-10 19:00 | 4.2679 | 0 | N/A | 0 | 0
2023-03-10 19:30 | 4.5069 | 0 | N/A | 0 | 0
2023-03-10 20:00 | 4.5636 | 0 | N/A | 0 | 0
2023-03-10 20:30 | 4.5797 | 0 | N/A | 0 | 0
2023-03-10 21:00 | 4.4786 | 0 | N/A | 0 | 0
2023-03-10 21:30 | 4.326 | 0 | N/A | 0 | 0
2023-03-10 22:00 | 4.0921 | 0 | N/A | 0 | 0
2023-03-10 22:30 | 4.2378 | 0 | N/A | 0 | 0
2023-03-10 23:00 | 4.2471 | 0 | N/A | 0 | 0
2023-03-10 23:30 | 3.9596 | 0 | N/A | 0 | 0
2023-03-11 | 3.9568 | 0 | N/A | 0 | 0
2023-03-11 00:30 | 4.385 | 0 | N/A | 0 | 0
2023-03-11 01:00 | 4.4507 | 0 | N/A | 0 | 0
2023-03-11 01:30 | 3.7363 | 0 | N/A | 0 | 0
2023-03-11 02:00 | 3.2762 | 0 | N/A | 0 | 0
2023-03-11 02:30 | 3.2142 | 0 | N/A | 0 | 0
2023-03-11 03:00 | 3.0442 | 0 | N/A | 0 | 0
2023-03-11 03:30 | 2.7697 | 0 | N/A | 0 | 0
2023-03-11 04:00 | 2.6675 | 0 | N/A | 0 | 0
2023-03-11 04:30 | 2.6155 | 0 | N/A | 0 | 0
2023-03-11 05:00 | 2.5389 | 0 | N/A | 0 | 0
2023-03-11 05:30 | 2.6448 | 0 | N/A | 0 | 0
2023-03-11 06:00 | 2.7549 | 0 | N/A | 0 | 0
2023-03-11 06:30 | 3.0248 | 0 | N/A | 0 | 0
2023-03-11 07:00 | 3.1933 | 0 | N/A | 0 | 0
2023-03-11 07:30 | 3.4997 | 0 | N/A | 0 | 0
2023-03-11 08:00 | 3.7217 | 0 | N/A | 0 | 0
2023-03-11 08:30 | 3.4173 | 0 | N/A | 0 | 0
2023-03-11 09:00 | 2.9711 | 0 | N/A | 0 | 0
2023-03-11 09:30 | 2.381 | 0 | N/A | 0 | 0
2023-03-11 10:00 | 1.6062 | 0 | N/A | 0 | 0
2023-03-11 10:30 | 1.0942 | 0 | N/A | 0 | 0
2023-03-11 11:00 | -0.9173 | 0 | N/A | 0 | 0
2023-03-11 11:30 | -1.3417 | 0 | N/A | 0 | 0
2023-03-11 12:00 | -1.1344 | 0 | N/A | 0 | 0
2023-03-11 12:30 | -1.7524 | 0 | N/A | 0 | 0
2023-03-11 13:00 | -1.8181 | 0 | N/A | 0 | 0
2023-03-11 13:30 | -2.0794 | 0 | N/A | 0 | 0
2023-03-11 14:00 | -1.9619 | 0 | N/A | 0 | 0
2023-03-11 14:30 | -1.8837 | 0 | N/A | 0 | 0
2023-03-11 15:00 | -1.7892 | 0 | N/A | 0 | 0
2023-03-11 15:30 | -1.1035 | 0 | N/A | 0 | 0
2023-03-11 16:00 | -0.8852 | 0 | N/A | 0 | 0
2023-03-11 16:30 | -0.87831 | 0 | N/A | 0 | 0
2023-03-11 17:00 | 1.5354 | 0 | N/A | 0 | 0
2023-03-11 17:30 | 2.3688 | 0 | N/A | 0 | 0
2023-03-11 18:00 | 2.5917 | 0 | N/A | 0 | 0
2023-03-11 18:30 | 3.3121 | 0 | N/A | 0 | 0
2023-03-11 19:00 | 3.8152 | 0 | N/A | 0 | 0
2023-03-11 19:30 | 4.177 | 0 | N/A | 0 | 0
2023-03-11 20:00 | 4.3489 | 0 | N/A | 0 | 0
2023-03-11 20:30 | 4.3754 | 0 | N/A | 0 | 0
2023-03-11 21:00 | 4.1547 | 0 | N/A | 0 | 0
2023-03-11 21:30 | 4.0142 | 0 | N/A | 0 | 0
2023-03-11 22:00 | 3.784 | 0 | N/A | 0 | 0
2023-03-11 22:30 | 3.9941 | 0 | N/A | 0 | 0
2023-03-11 23:00 | 4.0763 | 0 | N/A | 0 | 0
2023-03-11 23:30 | 3.8477 | 0 | N/A | 0 | 0
2023-03-12 | 3.7882 | 0 | N/A | 0 | 0
2023-03-12 00:30 | 4.1141 | 0 | N/A | 0 | 0
2023-03-12 01:00 | 4.3578 | 0 | N/A | 0 | 0
2023-03-12 01:30 | 3.6973 | 0 | N/A | 0 | 0
2023-03-12 02:00 | 3.171 | 0 | N/A | 0 | 0
2023-03-12 02:30 | 3.0888 | 0 | N/A | 0 | 0
2023-03-12 03:00 | 2.8928 | 0 | N/A | 0 | 0
2023-03-12 03:30 | 2.7308 | 0 | N/A | 0 | 0
2023-03-12 04:00 | 2.5914 | 0 | N/A | 0 | 0
2023-03-12 04:30 | 2.5461 | 0 | N/A | 0 | 0
2023-03-12 05:00 | 2.5001 | 0 | N/A | 0 | 0
2023-03-12 05:30 | 2.5511 | 0 | N/A | 0 | 0
2023-03-12 06:00 | 2.6182 | 0 | N/A | 0 | 0
2023-03-12 06:30 | 2.7247 | 0 | N/A | 0 | 0
2023-03-12 07:00 | 2.8396 | 0 | N/A | 0 | 0
2023-03-12 07:30 | 3.0769 | 0 | N/A | 0 | 0
2023-03-12 08:00 | 3.2939 | 0 | N/A | 0 | 0
2023-03-12 08:30 | 3.3327 | 0 | N/A | 0 | 0
2023-03-12 09:00 | 3.4135 | 0 | N/A | 0 | 0
2023-03-12 09:30 | 3.3016 | 0 | N/A | 0 | 0
2023-03-12 10:00 | 2.9238 | 0 | N/A | 0 | 0
2023-03-12 10:30 | 2.4078 | 0 | N/A | 0 | 0
2023-03-12 11:00 | 1.6432 | 0 | N/A | 0 | 0
2023-03-12 11:30 | 1.7128 | 0 | N/A | 0 | 0
2023-03-12 12:00 | 1.9259 | 0 | N/A | 0 | 0
2023-03-12 12:30 | 1.4734 | 0 | N/A | 0 | 0
2023-03-12 13:00 | 1.6504 | 0 | N/A | 0 | 0
2023-03-12 13:30 | 1.0449 | 0 | N/A | 0 | 0
2023-03-12 14:00 | 1.3223 | 0 | N/A | 0 | 0
2023-03-12 14:30 | 1.1476 | 0 | N/A | 0 | 0
2023-03-12 15:00 | 1.1493 | 0 | N/A | 0 | 0
2023-03-12 15:30 | 1.6645 | 0 | N/A | 0 | 0
2023-03-12 16:00 | 2.3119 | 0 | N/A | 0 | 0
2023-03-12 16:30 | 2.5333 | 0 | N/A | 0 | 0
2023-03-12 17:00 | 3.2606 | 0 | N/A | 0 | 0
2023-03-12 17:30 | 4.1484 | 0 | N/A | 0 | 0
2023-03-12 18:00 | 4.3302 | 0 | N/A | 0 | 0
2023-03-12 18:30 | 4.7278 | 0 | N/A | 0 | 0
2023-03-12 19:00 | 4.4252 | 0 | N/A | 0 | 0
2023-03-12 19:30 | 4.5912 | 0 | N/A | 0 | 0
2023-03-12 20:00 | 4.8535 | 0 | N/A | 0 | 0
2023-03-12 20:30 | 4.8397 | 0 | N/A | 0 | 0
2023-03-12 21:00 | 4.62 | 0 | N/A | 0 | 0
2023-03-12 21:30 | 4.4885 | 0 | N/A | 0 | 0
2023-03-12 22:00 | 4.1816 | 0 | N/A | 0 | 0
2023-03-12 22:30 | 4.3765 | 0 | N/A | 0 | 0
2023-03-12 23:00 | 4.3791 | 0 | N/A | 0 | 0
2023-03-12 23:30 | 4.1479 | 0 | N/A | 0 | 0
2023-03-13 | 4.159 | 0 | N/A | 0 | 0
2023-03-13 00:30 | 4.3882 | 0 | N/A | 0 | 0
2023-03-13 01:00 | 4.6676 | 0 | N/A | 0 | 0
2023-03-13 01:30 | 3.997 | 0 | N/A | 0 | 0
2023-03-13 02:00 | 3.4814 | 0 | N/A | 0 | 0
2023-03-13 02:30 | 3.3863 | 0 | N/A | 0 | 0
2023-03-13 03:00 | 3.1678 | 0 | N/A | 0 | 0
2023-03-13 03:30 | 2.934 | 0 | N/A | 0 | 0
2023-03-13 04:00 | 2.7405 | 0 | N/A | 0 | 0
2023-03-13 04:30 | 2.7236 | 0 | N/A | 0 | 0
2023-03-13 05:00 | 2.6325 | 0 | N/A | 0 | 0
2023-03-13 05:30 | 2.7199 | 0 | N/A | 0 | 0
2023-03-13 06:00 | 2.7713 | 0 | N/A | 0 | 0
2023-03-13 06:30 | 2.9539 | 0 | N/A | 0 | 0
2023-03-13 07:00 | 3.1126 | 0 | N/A | 0 | 0
2023-03-13 07:30 | 3.2782 | 0 | N/A | 0 | 0
2023-03-13 08:00 | 3.4633 | 0 | N/A | 0 | 0
2023-03-13 08:30 | 3.1508 | 0 | N/A | 0 | 0
2023-03-13 09:00 | 2.8559 | 0 | N/A | 0 | 0
2023-03-13 09:30 | 2.4685 | 0 | N/A | 0 | 0
2023-03-13 10:00 | 1.617 | 0 | N/A | 0 | 0
2023-03-13 10:30 | 0.98478 | 0 | N/A | 0 | 0
2023-03-13 11:00 | -1.0833 | 0 | N/A | 0 | 0
2023-03-13 11:30 | -1.6042 | 0 | N/A | 0 | 0
2023-03-13 12:00 | -1.966 | 0 | N/A | 0 | 0
2023-03-13 12:30 | -2.1725 | 0 | N/A | 0 | 0
2023-03-13 13:00 | -2.331 | 0 | N/A | 0 | 0
2023-03-13 13:30 | -2.4246 | 0 | N/A | 0 | 0
2023-03-13 14:00 | -2.4927 | 0 | N/A | 0 | 0
2023-03-13 14:30 | -2.3712 | 0 | N/A | 0 | 0
2023-03-13 15:00 | -2.1579 | 0 | N/A | 0 | 0
2023-03-13 15:30 | -1.797 | 0 | N/A | 0 | 0
2023-03-13 16:00 | -1.3159 | 0 | N/A | 0 | 0
2023-03-13 16:30 | -0.89312 | 0 | N/A | 0 | 0
2023-03-13 17:00 | 0.99452 | 0 | N/A | 0 | 0
2023-03-13 17:30 | 1.8836 | 0 | N/A | 0 | 0
2023-03-13 18:00 | 3.1145 | 0 | N/A | 0 | 0
2023-03-13 18:30 | 4.2227 | 0 | N/A | 0 | 0
2023-03-13 19:00 | 5.108 | 0 | N/A | 0 | 0
2023-03-13 19:30 | 5.2497 | 0 | N/A | 0 | 0
2023-03-13 20:00 | 5.2564 | 0 | N/A | 0 | 0
2023-03-13 20:30 | 5.1782 | 0 | N/A | 0 | 0
2023-03-13 21:00 | 4.8967 | 0 | N/A | 0 | 0
2023-03-13 21:30 | 4.6051 | 0 | N/A | 0 | 0
2023-03-13 22:00 | 4.2176 | 0 | N/A | 0 | 0
2023-03-13 22:30 | 4.2202 | 0 | N/A | 0 | 0
2023-03-13 23:00 | 4.1737 | 0 | N/A | 0 | 0
2023-03-13 23:30 | 3.9269 | 0 | N/A | 0 | 0
2023-03-14 | 3.9339 | 0 | N/A | 0 | 0
2023-03-15 00:30 | 4.2033 | 0 | N/A | 0 | 0
2023-03-15 01:00 | 4.3284 | 0 | N/A | 0 | 0
2023-03-15 01:30 | 3.6958 | 0 | N/A | 0 | 0
2023-03-15 02:00 | 3.239 | 0 | N/A | 0 | 0
2023-03-15 02:30 | 3.1064 | 0 | N/A | 0 | 0
2023-03-15 03:00 | 2.9606 | 0 | N/A | 0 | 0
2023-03-15 03:30 | 2.6967 | 0 | N/A | 0 | 0
2023-03-15 04:00 | 2.6218 | 0 | N/A | 0 | 0
2023-03-15 04:30 | 2.6159 | 0 | N/A | 0 | 0
2023-03-15 05:00 | 2.5926 | 0 | N/A | 0 | 0
2023-03-15 05:30 | 2.7641 | 0 | N/A | 0 | 0
2023-03-15 06:00 | 2.9583 | 0 | N/A | 0 | 0
2023-03-15 06:30 | 3.3974 | 0 | N/A | 0 | 0
2023-03-15 07:00 | 3.9614 | 0 | N/A | 0 | 0
2023-03-15 07:30 | 4.6738 | 0 | N/A | 0 | 0
2023-03-15 08:00 | 5.0918 | 0 | N/A | 0 | 0
2023-03-15 08:30 | 4.4251 | 0 | N/A | 0 | 0
2023-03-15 09:00 | 3.7799 | 0 | N/A | 0 | 0
2023-03-15 09:30 | 2.9455 | 0 | N/A | 0 | 0
2023-03-15 10:00 | 2.0537 | 0 | N/A | 0 | 0
2023-03-15 10:30 | 1.1273 | 0 | N/A | 0 | 0
2023-03-15 11:00 | 0.55467 | 0 | N/A | 0 | 0
2023-03-15 11:30 | -0.2953 | 0 | N/A | 0 | 0
2023-03-15 12:00 | -0.46421 | 0 | N/A | 0 | 0
2023-03-15 12:30 | -1.0033 | 0 | N/A | 0 | 0
2023-03-15 13:00 | -1.0467 | 0 | N/A | 0 | 0
2023-03-15 13:30 | -1.1333 | 0 | N/A | 0 | 0
2023-03-15 14:00 | -0.79085 | 0 | N/A | 0 | 0
2023-03-15 14:30 | -0.38426 | 0 | N/A | 0 | 0
2023-03-15 15:00 | -0.16826 | 0 | N/A | 0 | 0
2023-03-15 15:30 | 1.091 | 0 | N/A | 0 | 0
2023-03-15 16:00 | 2.1875 | 0 | N/A | 0 | 0
2023-03-15 16:30 | 1.5716 | 0 | N/A | 0 | 0
2023-03-15 17:00 | 2.6417 | 0 | N/A | 0 | 0
2023-03-15 17:30 | 4.121 | 0 | N/A | 0 | 0
2023-03-15 18:00 | 4.9363 | 0 | N/A | 0 | 0
2023-03-15 18:30 | 5.3119 | 0 | N/A | 0 | 0
2023-03-15 19:00 | 5.4822 | 0 | N/A | 0 | 0
2023-03-15 19:30 | 5.5164 | 0 | N/A | 0 | 0
2023-03-15 20:00 | 5.3699 | 0 | N/A | 0 | 0
2023-03-15 20:30 | 5.2844 | 0 | N/A | 0 | 0
2023-03-15 21:00 | 5.1151 | 0 | N/A | 0 | 0
2023-03-15 21:30 | 4.8038 | 0 | N/A | 0 | 0
2023-03-15 22:00 | 4.4191 | 0 | N/A | 0 | 0
2023-03-15 22:30 | 4.4423 | 0 | N/A | 0 | 0
2023-03-15 23:00 | 4.2632 | 0 | N/A | 0 | 0
2023-03-15 23:30 | 3.9365 | 0 | N/A | 0 | 0
2023-03-16 | 3.8685 | 0 | N/A | 0 | 0
2023-03-16 00:30 | 4.2132 | 0 | N/A | 0 | 0
2023-03-16 01:00 | 4.3077 | 0 | N/A | 0 | 0
2023-03-16 01:30 | 3.6312 | 0 | N/A | 0 | 0
2023-03-16 02:00 | 3.1872 | 0 | N/A | 0 | 0
2023-03-16 02:30 | 3.1116 | 0 | N/A | 0 | 0
2023-03-16 03:00 | 2.901 | 0 | N/A | 0 | 0
2023-03-16 03:30 | 2.7217 | 0 | N/A | 0 | 0
2023-03-16 04:00 | 2.6476 | 0 | N/A | 0 | 0
2023-03-16 04:30 | 2.5839 | 0 | N/A | 0 | 0
2023-03-16 05:00 | 2.6133 | 0 | N/A | 0 | 0
2023-03-16 05:30 | 2.7446 | 0 | N/A | 0 | 0
2023-03-16 06:00 | 2.9979 | 0 | N/A | 0 | 0
2023-03-16 06:30 | 3.3934 | 0 | N/A | 0 | 0
2023-03-16 07:00 | 3.8909 | 0 | N/A | 0 | 0
2023-03-16 07:30 | 4.6418 | 0 | N/A | 0 | 0
2023-03-16 08:00 | 4.8637 | 0 | N/A | 0 | 0
2023-03-16 08:30 | 4.4113 | 0 | N/A | 0 | 0
2023-03-16 09:00 | 4.2476 | 0 | N/A | 0 | 0
2023-03-16 09:30 | 4.0772 | 0 | N/A | 0 | 0
2023-03-16 10:00 | 3.625 | 0 | N/A | 0 | 0
2023-03-16 10:30 | 3.0484 | 0 | N/A | 0 | 0
2023-03-16 11:00 | 2.1508 | 0 | N/A | 0 | 0
2023-03-16 11:30 | 0.75487 | 0 | N/A | 0 | 0
2023-03-16 12:00 | -0.58622 | 0 | N/A | 0 | 0
2023-03-16 12:30 | -0.70836 | 0 | N/A | 0 | 0
2023-03-16 13:00 | 0.72076 | 0 | N/A | 0 | 0
2023-03-16 13:30 | 0.92413 | 0 | N/A | 0 | 0
2023-03-16 14:00 | 1.3861 | 0 | N/A | 0 | 0
2023-03-16 14:30 | -0.6751 | 0 | N/A | 0 | 0
2023-03-16 15:00 | 0.93444 | 0 | N/A | 0 | 0
2023-03-16 15:30 | 2.4562 | 0 | N/A | 0 | 0
2023-03-16 16:00 | 2.4679 | 0 | N/A | 0 | 0
2023-03-16 16:30 | 3.0364 | 0 | N/A | 0 | 0
2023-03-16 17:00 | 3.2351 | 0 | N/A | 0 | 0
2023-03-16 17:30 | 3.2762 | 0 | N/A | 0 | 0
2023-03-16 18:00 | 4.2614 | 0 | N/A | 0 | 0
2023-03-16 18:30 | 4.4894 | 0 | N/A | 0 | 0
2023-03-16 19:00 | 4.9008 | 0 | N/A | 0 | 0
2023-03-16 19:30 | 5.0416 | 0 | N/A | 0 | 0
2023-03-16 20:00 | 5.1358 | 0 | N/A | 0 | 0
2023-03-16 20:30 | 5.1193 | 0 | N/A | 0 | 0
2023-03-16 21:00 | 4.8871 | 0 | N/A | 0 | 0
2023-03-16 21:30 | 4.6315 | 0 | N/A | 0 | 0
2023-03-16 22:00 | 4.3511 | 0 | N/A | 0 | 0
2023-03-16 22:30 | 4.4404 | 0 | N/A | 0 | 0
2023-03-16 23:00 | 4.2892 | 0 | N/A | 0 | 0
2023-03-16 23:30 | 3.9929 | 0 | N/A | 0 | 0
2023-03-17 | 3.9668 | 0 | N/A | 0 | 0
2023-03-18 00:30 | 4.1954 | 0 | N/A | 0 | 0
2023-03-18 01:00 | 4.3197 | 0 | N/A | 0 | 0
2023-03-18 01:30 | 3.6528 | 0 | N/A | 0 | 0
2023-03-18 02:00 | 3.1424 | 0 | N/A | 0 | 0
2023-03-18 02:30 | 3.0702 | 0 | N/A | 0 | 0
2023-03-18 03:00 | 2.8806 | 0 | N/A | 0 | 0
2023-03-18 03:30 | 2.7194 | 0 | N/A | 0 | 0
2023-03-18 04:00 | 2.5914 | 0 | N/A | 0 | 0
2023-03-18 04:30 | 2.4651 | 0 | N/A | 0 | 0
2023-03-18 05:00 | 2.4378 | 0 | N/A | 0 | 0
2023-03-18 05:30 | 2.4735 | 0 | N/A | 0 | 0
2023-03-18 06:00 | 2.608 | 0 | N/A | 0 | 0
2023-03-18 06:30 | 2.8299 | 0 | N/A | 0 | 0
2023-03-18 07:00 | 3.0367 | 0 | N/A | 0 | 0
2023-03-18 07:30 | 3.4416 | 0 | N/A | 0 | 0
2023-03-18 08:00 | 3.6735 | 0 | N/A | 0 | 0
2023-03-18 08:30 | 3.564 | 0 | N/A | 0 | 0
2023-03-18 09:00 | 3.2878 | 0 | N/A | 0 | 0
2023-03-18 09:30 | 2.6016 | 0 | N/A | 0 | 0
2023-03-18 10:00 | 1.9106 | 0 | N/A | 0 | 0
2023-03-18 10:30 | 1.079 | 0 | N/A | 0 | 0
2023-03-18 11:00 | 0.59228 | 0 | N/A | 0 | 0
2023-03-18 11:30 | -0.84762 | 0 | N/A | 0 | 0
2023-03-18 12:00 | -1.1838 | 0 | N/A | 0 | 0
2023-03-18 12:30 | -0.60848 | 0 | N/A | 0 | 0
2023-03-18 13:00 | 1.2174 | 0 | N/A | 0 | 0
2023-03-18 13:30 | 1.9769 | 0 | N/A | 0 | 0
2023-03-18 14:00 | 2.0469 | 0 | N/A | 0 | 0
2023-03-18 14:30 | 2.8125 | 0 | N/A | 0 | 0
2023-03-18 15:00 | 3.0516 | 0 | N/A | 0 | 0
2023-03-18 15:30 | 2.4679 | 0 | N/A | 0 | 0
2023-03-18 16:00 | 1.8292 | 0 | N/A | 0 | 0
2023-03-18 16:30 | 3.098 | 0 | N/A | 0 | 0
2023-03-18 17:00 | 3.1497 | 0 | N/A | 0 | 0
2023-03-18 17:30 | 4.5025 | 0 | N/A | 0 | 0
2023-03-18 18:00 | 4.6596 | 0 | N/A | 0 | 0
2023-03-18 18:30 | 4.8311 | 0 | N/A | 0 | 0
2023-03-18 19:00 | 4.9342 | 0 | N/A | 0 | 0
2023-03-18 19:30 | 5.0192 | 0 | N/A | 0 | 0
2023-03-18 20:00 | 5.0012 | 0 | N/A | 0 | 0
2023-03-18 20:30 | 4.7755 | 0 | N/A | 0 | 0
2023-03-18 21:00 | 4.4905 | 0 | N/A | 0 | 0
2023-03-18 21:30 | 4.2532 | 0 | N/A | 0 | 0
2023-03-18 22:00 | 4.0069 | 0 | N/A | 0 | 0
2023-03-18 22:30 | 4.1839 | 0 | N/A | 0 | 0
2023-03-18 23:00 | 4.2071 | 0 | N/A | 0 | 0
2023-03-18 23:30 | 3.8881 | 0 | N/A | 0 | 0
2023-03-19 | 3.9154 | 0 | N/A | 0 | 0
2023-03-19 00:30 | 4.2271 | 0 | N/A | 0 | 0
2023-03-19 01:00 | 4.3679 | 0 | N/A | 0 | 0
2023-03-19 01:30 | 3.6101 | 0 | N/A | 0 | 0
2023-03-19 02:00 | 3.1369 | 0 | N/A | 0 | 0
2023-03-19 02:30 | 3.0963 | 0 | N/A | 0 | 0
2023-03-19 03:00 | 2.8764 | 0 | N/A | 0 | 0
2023-03-19 03:30 | 2.6906 | 0 | N/A | 0 | 0
2023-03-19 04:00 | 2.5933 | 0 | N/A | 0 | 0
2023-03-19 04:30 | 2.4987 | 0 | N/A | 0 | 0
2023-03-19 05:00 | 2.4774 | 0 | N/A | 0 | 0
2023-03-19 05:30 | 2.4957 | 0 | N/A | 0 | 0
2023-03-19 06:00 | 2.6163 | 0 | N/A | 0 | 0
2023-03-19 06:30 | 2.7267 | 0 | N/A | 0 | 0
2023-03-19 07:00 | 2.8921 | 0 | N/A | 0 | 0
2023-03-19 07:30 | 3.132 | 0 | N/A | 0 | 0
2023-03-19 08:00 | 3.2428 | 0 | N/A | 0 | 0
2023-03-19 08:30 | 3.329 | 0 | N/A | 0 | 0
2023-03-19 09:00 | 3.5041 | 0 | N/A | 0 | 0
2023-03-19 09:30 | 3.7532 | 0 | N/A | 0 | 0
2023-03-19 10:00 | 3.4867 | 0 | N/A | 0 | 0
2023-03-19 10:30 | 3.3548 | 0 | N/A | 0 | 0
2023-03-19 11:00 | 3.4355 | 0 | N/A | 0 | 0
2023-03-19 11:30 | 3.2785 | 0 | N/A | 0 | 0
2023-03-19 12:00 | 3.2877 | 0 | N/A | 0 | 0
2023-03-19 12:30 | 2.6779 | 0 | N/A | 0 | 0
2023-03-19 13:00 | 2.2826 | 0 | N/A | 0 | 0
2023-03-19 13:30 | 2.0274 | 0 | N/A | 0 | 0
2023-03-19 14:00 | 1.3236 | 0 | N/A | 0 | 0
2023-03-19 14:30 | 1.1922 | 0 | N/A | 0 | 0
2023-03-19 15:00 | 1.2133 | 0 | N/A | 0 | 0
2023-03-19 15:30 | 1.1797 | 0 | N/A | 0 | 0
2023-03-19 16:00 | 1.07 | 0 | N/A | 0 | 0
2023-03-19 16:30 | 1.0778 | 0 | N/A | 0 | 0
2023-03-19 17:00 | 1.6593 | 0 | N/A | 0 | 0
2023-03-19 17:30 | 2.1388 | 0 | N/A | 0 | 0
2023-03-19 18:00 | 3.0214 | 0 | N/A | 0 | 0
2023-03-19 18:30 | 3.9097 | 0 | N/A | 0 | 0
2023-03-19 19:00 | 4.4167 | 0 | N/A | 0 | 0
2023-03-19 19:30 | 4.8247 | 0 | N/A | 0 | 0
2023-03-19 20:00 | 5.1538 | 0 | N/A | 0 | 0
2023-03-19 20:30 | 5.1196 | 0 | N/A | 0 | 0
2023-03-19 21:00 | 4.8718 | 0 | N/A | 0 | 0
2023-03-19 21:30 | 4.5771 | 0 | N/A | 0 | 0
2023-03-19 22:00 | 4.2091 | 0 | N/A | 0 | 0
2023-03-19 22:30 | 4.326 | 0 | N/A | 0 | 0
2023-03-19 23:00 | 4.3788 | 0 | N/A | 0 | 0
2023-03-19 23:30 | 4.0702 | 0 | N/A | 0 | 0
2023-03-20 | 4.0769 | 0 | N/A | 0 | 0
2023-03-20 00:30 | 4.379 | 0 | N/A | 0 | 0
2023-03-20 01:00 | 4.676 | 0 | N/A | 0 | 0
2023-03-20 01:30 | 4.0642 | 0 | N/A | 0 | 0
2023-03-20 02:00 | 3.5414 | 0 | N/A | 0 | 0
2023-03-20 02:30 | 3.4623 | 0 | N/A | 0 | 0
2023-03-20 03:00 | 3.2066 | 0 | N/A | 0 | 0
2023-03-20 03:30 | 2.8913 | 0 | N/A | 0 | 0
2023-03-20 04:00 | 2.7734 | 0 | N/A | 0 | 0
2023-03-20 04:30 | 2.7059 | 0 | N/A | 0 | 0
2023-03-20 05:00 | 2.7297 | 0 | N/A | 0 | 0
2023-03-20 05:30 | 2.9501 | 0 | N/A | 0 | 0
2023-03-20 06:00 | 3.2129 | 0 | N/A | 0 | 0
2023-03-20 06:30 | 3.6164 | 0 | N/A | 0 | 0
2023-03-20 07:00 | 4.2672 | 0 | N/A | 0 | 0
2023-03-20 07:30 | 5.1689 | 0 | N/A | 0 | 0
2023-03-20 08:00 | 5.5496 | 0 | N/A | 0 | 0
2023-03-20 08:30 | 4.7025 | 0 | N/A | 0 | 0
2023-03-20 09:00 | 3.7679 | 0 | N/A | 0 | 0
2023-03-20 09:30 | 2.9177 | 0 | N/A | 0 | 0
2023-03-20 10:00 | 2.1641 | 0 | N/A | 0 | 0
2023-03-20 10:30 | 1.4415 | 0 | N/A | 0 | 0
2023-03-20 11:00 | 0.80117 | 0 | N/A | 0 | 0
2023-03-20 11:30 | -0.95733 | 0 | N/A | 0 | 0
2023-03-20 12:00 | -1.3189 | 0 | N/A | 0 | 0
2023-03-20 12:30 | -1.6496 | 0 | N/A | 0 | 0
2023-03-20 13:00 | -2.0448 | 0 | N/A | 0 | 0
2023-03-20 13:30 | -2.1667 | 0 | N/A | 0 | 0
2023-03-20 14:00 | -2.3903 | 0 | N/A | 0 | 0
2023-03-20 14:30 | -2.3396 | 0 | N/A | 0 | 0
2023-03-20 15:00 | -2.2666 | 0 | N/A | 0 | 0
2023-03-20 15:30 | -2.1378 | 0 | N/A | 0 | 0
2023-03-20 16:00 | -1.8784 | 0 | N/A | 0 | 0
2023-03-20 16:30 | 1.137 | 0 | N/A | 0 | 0
2023-03-20 17:00 | 1.653 | 0 | N/A | 0 | 0
2023-03-20 17:30 | 2.7097 | 0 | N/A | 0 | 0
2023-03-20 18:00 | 3.4278 | 0 | N/A | 0 | 0
2023-03-20 18:30 | 4.3841 | 0 | N/A | 0 | 0
2023-03-20 19:00 | 4.8809 | 0 | N/A | 0 | 0
2023-03-20 19:30 | 5.3557 | 0 | N/A | 0 | 0
2023-03-20 20:00 | 5.6484 | 0 | N/A | 0 | 0
2023-03-20 20:30 | 5.6252 | 0 | N/A | 0 | 0
2023-03-20 21:00 | 5.4951 | 0 | N/A | 0 | 0
2023-03-20 21:30 | 5.1325 | 0 | N/A | 0 | 0
2023-03-20 22:00 | 4.6929 | 0 | N/A | 0 | 0
2023-03-20 22:30 | 4.6576 | 0 | N/A | 0 | 0
2023-03-20 23:00 | 4.5642 | 0 | N/A | 0 | 0
2023-03-20 23:30 | 4.1728 | 0 | N/A | 0 | 0
2023-03-21 | 4.1627 | 0 | N/A | 0 | 0
2023-03-23 00:30 | 4.1904 | 0 | N/A | 0 | 0
2023-03-23 01:00 | 4.3471 | 0 | N/A | 0 | 0
2023-03-23 01:30 | 3.722 | 0 | N/A | 0 | 0
2023-03-23 02:00 | 3.2043 | 0 | N/A | 0 | 0
2023-03-23 02:30 | 3.1156 | 0 | N/A | 0 | 0
2023-03-23 03:00 | 2.9673 | 0 | N/A | 0 | 0
2023-03-23 03:30 | 2.7326 | 0 | N/A | 0 | 0
2023-03-23 04:00 | 2.6233 | 0 | N/A | 0 | 0
2023-03-23 04:30 | 2.5806 | 0 | N/A | 0 | 0
2023-03-23 05:00 | 2.6077 | 0 | N/A | 0 | 0
2023-03-23 05:30 | 2.8016 | 0 | N/A | 0 | 0
2023-03-23 06:00 | 3.0412 | 0 | N/A | 0 | 0
2023-03-23 06:30 | 3.4985 | 0 | N/A | 0 | 0
2023-03-23 07:00 | 4.1219 | 0 | N/A | 0 | 0
2023-03-23 07:30 | 4.8657 | 0 | N/A | 0 | 0
2023-03-23 08:00 | 5.2438 | 0 | N/A | 0 | 0
2023-03-23 08:30 | 4.801 | 0 | N/A | 0 | 0
2023-03-23 09:00 | 4.1081 | 0 | N/A | 0 | 0
2023-03-23 09:30 | 3.0325 | 0 | N/A | 0 | 0
2023-03-23 10:00 | 1.8574 | 0 | N/A | 0 | 0
2023-03-23 10:30 | 3.7132 | 0 | N/A | 0 | 0
2023-03-23 11:00 | 4.6441 | 0 | N/A | 0 | 0
2023-03-23 11:30 | 3.3068 | 0 | N/A | 0 | 0
2023-03-23 12:00 | 3.5891 | 0 | N/A | 0 | 0
2023-03-23 12:30 | 5.29 | 0 | N/A | 0 | 0
2023-03-23 13:00 | 3.4163 | 0 | N/A | 0 | 0
2023-03-23 13:30 | 1.3406 | 0 | N/A | 0 | 0
2023-03-23 14:00 | 2.1198 | 0 | N/A | 0 | 0
2023-03-23 14:30 | -0.58471 | 0 | N/A | 0 | 0
2023-03-23 15:00 | -1.5211 | 0 | N/A | 0 | 0
2023-03-23 15:30 | -1.4255 | 0 | N/A | 0 | 0
2023-03-23 16:00 | -1.0018 | 0 | N/A | 0 | 0
2023-03-23 16:30 | -0.84294 | 0 | N/A | 0 | 0
2023-03-23 17:00 | 1.1538 | 0 | N/A | 0 | 0
2023-03-23 17:30 | 2.01 | 0 | N/A | 0 | 0
2023-03-23 18:00 | 2.9017 | 0 | N/A | 0 | 0
2023-03-23 18:30 | 3.7983 | 0 | N/A | 0 | 0
2023-03-23 19:00 | 4.4546 | 0 | N/A | 0 | 0
2023-03-23 19:30 | 4.8921 | 0 | N/A | 0 | 0
2023-03-23 20:00 | 4.9648 | 0 | N/A | 0 | 0
2023-03-23 20:30 | 4.93 | 0 | N/A | 0 | 0
2023-03-23 21:00 | 4.7058 | 0 | N/A | 0 | 0
2023-03-23 21:30 | 4.9007 | 0 | N/A | 0 | 0
2023-03-23 22:00 | 4.3971 | 0 | N/A | 0 | 0
2023-03-23 22:30 | 4.0468 | 0 | N/A | 0 | 0
2023-03-23 23:00 | 4.0383 | 0 | N/A | 0 | 0
2023-03-23 23:30 | 3.7959 | 0 | N/A | 0 | 0
2023-03-24 | 3.8629 | 0 | N/A | 0 | 0
2023-03-24 00:30 | 4.1458 | 0 | N/A | 0 | 0
2023-03-24 01:00 | 4.3064 | 0 | N/A | 0 | 0
2023-03-24 01:30 | 3.6331 | 0 | N/A | 0 | 0
2023-03-24 02:00 | 3.0943 | 0 | N/A | 0 | 0
2023-03-24 02:30 | 3.0068 | 0 | N/A | 0 | 0
2023-03-24 03:00 | 2.846 | 0 | N/A | 0 | 0
2023-03-24 03:30 | 2.6845 | 0 | N/A | 0 | 0
2023-03-24 04:00 | 2.5954 | 0 | N/A | 0 | 0
2023-03-24 04:30 | 2.5406 | 0 | N/A | 0 | 0
2023-03-24 05:00 | 2.5472 | 0 | N/A | 0 | 0
2023-03-24 05:30 | 2.6954 | 0 | N/A | 0 | 0
2023-03-24 06:00 | 2.9088 | 0 | N/A | 0 | 0
2023-03-24 06:30 | 3.3784 | 0 | N/A | 0 | 0
2023-03-24 07:00 | 3.9535 | 0 | N/A | 0 | 0
2023-03-24 07:30 | 4.8994 | 0 | N/A | 0 | 0
2023-03-24 08:00 | 5.213 | 0 | N/A | 0 | 0
2023-03-24 08:30 | 4.9144 | 0 | N/A | 0 | 0
2023-03-24 09:00 | 4.7026 | 0 | N/A | 0 | 0
2023-03-24 09:30 | 4.5233 | 0 | N/A | 0 | 0
2023-03-24 10:00 | 4.2887 | 0 | N/A | 0 | 0
2023-03-24 10:30 | 3.8082 | 0 | N/A | 0 | 0
2023-03-24 11:00 | 3.5418 | 0 | N/A | 0 | 0
2023-03-24 11:30 | 3.8026 | 0 | N/A | 0 | 0
2023-03-24 12:00 | 3.382 | 0 | N/A | 0 | 0
2023-03-24 12:30 | 3.3247 | 0 | N/A | 0 | 0
2023-03-24 13:00 | 3.5989 | 0 | N/A | 0 | 0
2023-03-24 13:30 | 3.2541 | 0 | N/A | 0 | 0
2023-03-24 14:00 | 2.7116 | 0 | N/A | 0 | 0
2023-03-24 14:30 | 2.1963 | 0 | N/A | 0 | 0
2023-03-24 15:00 | 0.89429 | 0 | N/A | 0 | 0
2023-03-24 15:30 | -0.9985 | 0 | N/A | 0 | 0
2023-03-24 16:00 | -1.4017 | 0 | N/A | 0 | 0
2023-03-24 16:30 | -1.1027 | 0 | N/A | 0 | 0
2023-03-24 17:00 | 1.1378 | 0 | N/A | 0 | 0
2023-03-24 17:30 | 1.7062 | 0 | N/A | 0 | 0
2023-03-24 18:00 | 2.6469 | 0 | N/A | 0 | 0
2023-03-24 18:30 | 3.6718 | 0 | N/A | 0 | 0
2023-03-24 19:00 | 4.4449 | 0 | N/A | 0 | 0
2023-03-24 19:30 | 4.9586 | 0 | N/A | 0 | 0
2023-03-24 20:00 | 5.1888 | 0 | N/A | 0 | 0
2023-03-24 20:30 | 5.1874 | 0 | N/A | 0 | 0
2023-03-24 21:00 | 5.0156 | 0 | N/A | 0 | 0
2023-03-24 21:30 | 4.7928 | 0 | N/A | 0 | 0
2023-03-24 22:00 | 4.5334 | 0 | N/A | 0 | 0
2023-03-24 22:30 | 4.6872 | 0 | N/A | 0 | 0
2023-03-24 23:00 | 4.6607 | 0 | N/A | 0 | 0
2023-03-24 23:30 | 4.3097 | 0 | N/A | 0 | 0
2023-03-25 | 4.2629 | 0 | N/A | 0 | 0
2023-03-25 00:30 | 4.5324 | 0 | N/A | 0 | 0
2023-03-25 01:00 | 4.7417 | 0 | N/A | 0 | 0
2023-03-25 01:30 | 3.9585 | 0 | N/A | 0 | 0
2023-03-25 02:00 | 3.4454 | 0 | N/A | 0 | 0
2023-03-25 02:30 | 3.3711 | 0 | N/A | 0 | 0
2023-03-25 03:00 | 3.1499 | 0 | N/A | 0 | 0
2023-03-25 03:30 | 2.9123 | 0 | N/A | 0 | 0
2023-03-25 04:00 | 2.8332 | 0 | N/A | 0 | 0
2023-03-25 04:30 | 2.6535 | 0 | N/A | 0 | 0
2023-03-25 05:00 | 2.6834 | 0 | N/A | 0 | 0
2023-03-25 05:30 | 2.7542 | 0 | N/A | 0 | 0
2023-03-25 06:00 | 2.8767 | 0 | N/A | 0 | 0
2023-03-25 06:30 | 3.1728 | 0 | N/A | 0 | 0
2023-03-25 07:00 | 3.4423 | 0 | N/A | 0 | 0
2023-03-25 07:30 | 3.7865 | 0 | N/A | 0 | 0
2023-03-25 08:00 | 4.2305 | 0 | N/A | 0 | 0
2023-03-25 08:30 | 4.1743 | 0 | N/A | 0 | 0
2023-03-25 09:00 | 3.9529 | 0 | N/A | 0 | 0
2023-03-25 09:30 | 2.9663 | 0 | N/A | 0 | 0
2023-03-25 10:00 | 2.2849 | 0 | N/A | 0 | 0
2023-03-25 10:30 | 2.2975 | 0 | N/A | 0 | 0
2023-03-25 11:00 | 3.0046 | 0 | N/A | 0 | 0
2023-03-25 11:30 | 2.7508 | 0 | N/A | 0 | 0
2023-03-25 12:00 | 1.9093 | 0 | N/A | 0 | 0
2023-03-25 12:30 | 1.3983 | 0 | N/A | 0 | 0
2023-03-25 13:00 | 1.2071 | 0 | N/A | 0 | 0
2023-03-25 13:30 | 0.88969 | 0 | N/A | 0 | 0
2023-03-25 14:00 | -1.2361 | 0 | N/A | 0 | 0
2023-03-25 14:30 | -1.2073 | 0 | N/A | 0 | 0
2023-03-25 15:00 | -1.6767 | 0 | N/A | 0 | 0
2023-03-25 15:30 | -1.8056 | 0 | N/A | 0 | 0
2023-03-25 16:00 | -1.2526 | 0 | N/A | 0 | 0
2023-03-25 16:30 | -1.1285 | 0 | N/A | 0 | 0
2023-03-25 17:00 | 1.2108 | 0 | N/A | 0 | 0
2023-03-25 17:30 | 3.2826 | 0 | N/A | 0 | 0
2023-03-25 18:00 | 3.7603 | 0 | N/A | 0 | 0
2023-03-25 18:30 | 3.916 | 0 | N/A | 0 | 0
2023-03-25 19:00 | 4.3508 | 0 | N/A | 0 | 0
2023-03-25 19:30 | 5.0491 | 0 | N/A | 0 | 0
2023-03-25 20:00 | 5.2595 | 0 | N/A | 0 | 0
2023-03-25 20:30 | 5.129 | 0 | N/A | 0 | 0
2023-03-25 21:00 | 4.925 | 0 | N/A | 0 | 0
2023-03-25 21:30 | 4.8195 | 0 | N/A | 0 | 0
2023-03-25 22:00 | 4.5305 | 0 | N/A | 0 | 0
2023-03-25 22:30 | 4.7689 | 0 | N/A | 0 | 0
2023-03-25 23:00 | 4.7887 | 0 | N/A | 0 | 0
2023-03-25 23:30 | 4.4721 | 0 | N/A | 0 | 0
2023-03-26 | 4.5152 | 0 | N/A | 0 | 0
2023-03-26 00:30 | 4.7156 | 0 | N/A | 0 | 0
2023-03-26 01:00 | 4.9142 | 0 | N/A | 0 | 0
2023-03-26 01:30 | 4.2241 | 0 | N/A | 0 | 0
2023-03-26 02:00 | 3.7035 | 0 | N/A | 0 | 0
2023-03-26 02:30 | 3.52 | 0 | N/A | 0 | 0
2023-03-26 03:00 | 3.3142 | 0 | N/A | 0 | 0
2023-03-26 03:30 | 2.9814 | 0 | N/A | 0 | 0
2023-03-26 04:00 | 2.8801 | 0 | N/A | 0 | 0
2023-03-26 04:30 | 2.7738 | 0 | N/A | 0 | 0
2023-03-26 05:00 | 2.7659 | 0 | N/A | 0 | 0
2023-03-26 05:30 | 2.7963 | 0 | N/A | 0 | 0
2023-03-26 06:00 | 2.8983 | 0 | N/A | 0 | 0
2023-03-26 06:30 | 3.1063 | 0 | N/A | 0 | 0
2023-03-26 07:00 | 3.3483 | 0 | N/A | 0 | 0
2023-03-26 07:30 | 3.7108 | 0 | N/A | 0 | 0
2023-03-26 08:00 | 3.9373 | 0 | N/A | 0 | 0
2023-03-26 08:30 | 3.6903 | 0 | N/A | 0 | 0
2023-03-26 09:00 | 3.7468 | 0 | N/A | 0 | 0
2023-03-26 09:30 | 3.8738 | 0 | N/A | 0 | 0
2023-03-26 10:00 | 3.0127 | 0 | N/A | 0 | 0
2023-03-26 10:30 | 2.5482 | 0 | N/A | 0 | 0
2023-03-26 11:00 | 2.2496 | 0 | N/A | 0 | 0
2023-03-26 11:30 | 1.5477 | 0 | N/A | 0 | 0
2023-03-26 12:00 | 1.2548 | 0 | N/A | 0 | 0
2023-03-26 12:30 | 1.0488 | 0 | N/A | 0 | 0
2023-03-26 13:00 | 1.167 | 0 | N/A | 0 | 0
2023-03-26 13:30 | -0.95973 | 0 | N/A | 0 | 0
2023-03-26 14:00 | -1.1265 | 0 | N/A | 0 | 0
2023-03-26 14:30 | 1.5674 | 0 | N/A | 0 | 0
2023-03-26 15:00 | 1.6814 | 0 | N/A | 0 | 0
2023-03-26 15:30 | 1.9797 | 0 | N/A | 0 | 0
2023-03-26 16:00 | 3.3751 | 0 | N/A | 0 | 0
2023-03-26 16:30 | 3.6781 | 0 | N/A | 0 | 0
2023-03-26 17:00 | 4.3161 | 0 | N/A | 0 | 0
2023-03-26 17:30 | 4.7285 | 0 | N/A | 0 | 0
2023-03-26 18:00 | 5.2897 | 0 | N/A | 0 | 0
2023-03-26 18:30 | 5.4436 | 0 | N/A | 0 | 0
2023-03-26 19:00 | 5.7469 | 0 | N/A | 0 | 0
2023-03-26 19:30 | 5.7898 | 0 | N/A | 0 | 0
2023-03-26 20:00 | 5.7201 | 0 | N/A | 0 | 0
2023-03-26 20:30 | 5.4175 | 0 | N/A | 0 | 0
2023-03-26 21:00 | 5.1286 | 0 | N/A | 0 | 0
2023-03-26 21:30 | 4.7573 | 0 | N/A | 0 | 0
2023-03-26 22:00 | 4.4488 | 0 | N/A | 0 | 0
2023-03-26 22:30 | 4.5395 | 0 | N/A | 0 | 0
2023-03-26 23:00 | 4.4358 | 0 | N/A | 0 | 0
2023-03-26 23:30 | 4.0827 | 0 | N/A | 0 | 0
2023-03-27 | 4.0964 | 0 | N/A | 0 | 0
2023-03-27 00:30 | 4.3344 | 0 | N/A | 0 | 0
2023-03-27 01:00 | 4.6697 | 0 | N/A | 0 | 0
2023-03-27 01:30 | 4.0991 | 0 | N/A | 0 | 0
2023-03-27 02:00 | 3.5118 | 0 | N/A | 0 | 0
2023-03-27 02:30 | 3.4603 | 0 | N/A | 0 | 0
2023-03-27 03:00 | 3.2975 | 0 | N/A | 0 | 0
2023-03-27 03:30 | 2.9661 | 0 | N/A | 0 | 0
2023-03-27 04:00 | 2.7655 | 0 | N/A | 0 | 0
2023-03-27 04:30 | 2.7199 | 0 | N/A | 0 | 0
2023-03-27 05:00 | 2.7328 | 0 | N/A | 0 | 0
2023-03-27 05:30 | 2.9498 | 0 | N/A | 0 | 0
2023-03-27 06:00 | 3.2782 | 0 | N/A | 0 | 0
2023-03-27 06:30 | 3.7593 | 0 | N/A | 0 | 0
2023-03-27 07:00 | 4.351 | 0 | N/A | 0 | 0
2023-03-27 07:30 | 5.2708 | 0 | N/A | 0 | 0
2023-03-27 08:00 | 5.827 | 0 | N/A | 0 | 0
2023-03-27 08:30 | 5.5356 | 0 | N/A | 0 | 0
2023-03-27 09:00 | 5.3385 | 0 | N/A | 0 | 0
2023-03-27 09:30 | 5.1994 | 0 | N/A | 0 | 0
2023-03-27 10:00 | 4.748 | 0 | N/A | 0 | 0
2023-03-27 10:30 | 4.7677 | 0 | N/A | 0 | 0
2023-03-27 11:00 | 5.2466 | 0 | N/A | 0 | 0
2023-03-27 11:30 | 5.0071 | 0 | N/A | 0 | 0
2023-03-27 12:00 | 4.8313 | 0 | N/A | 0 | 0
2023-03-27 12:30 | 5.1962 | 0 | N/A | 0 | 0
2023-03-27 13:00 | 4.8734 | 0 | N/A | 0 | 0
2023-03-27 13:30 | 4.6501 | 0 | N/A | 0 | 0
2023-03-27 14:00 | 5.098 | 0 | N/A | 0 | 0
2023-03-27 14:30 | 5.0613 | 0 | N/A | 0 | 0
2023-03-27 15:00 | 5.357 | 0 | N/A | 0 | 0
2023-03-27 15:30 | 5.2444 | 0 | N/A | 0 | 0
2023-03-27 16:00 | 5.232 | 0 | N/A | 0 | 0
2023-03-27 16:30 | 4.8725 | 0 | N/A | 0 | 0
2023-03-27 17:00 | 5.1829 | 0 | N/A | 0 | 0
2023-03-27 17:30 | 5.8721 | 0 | N/A | 0 | 0
2023-03-27 18:00 | 6.4726 | 0 | N/A | 0 | 0
2023-03-27 18:30 | 6.9574 | 0 | N/A | 0 | 0
2023-03-27 19:00 | 6.9486 | 0 | N/A | 0 | 0
2023-03-27 19:30 | 6.862 | 0 | N/A | 0 | 0
2023-03-27 20:00 | 6.6452 | 0 | N/A | 0 | 0
2023-03-27 20:30 | 6.3233 | 0 | N/A | 0 | 0
2023-03-27 21:00 | 5.9787 | 0 | N/A | 0 | 0
2023-03-27 21:30 | 5.4971 | 0 | N/A | 0 | 0
2023-03-27 22:00 | 4.9776 | 0 | N/A | 0 | 0
2023-03-27 22:30 | 4.9284 | 0 | N/A | 0 | 0
2023-03-27 23:00 | 4.6926 | 0 | N/A | 0 | 0
2023-03-27 23:30 | 4.2468 | 0 | N/A | 0 | 0
2023-03-28 | 4.2685 | 0 | N/A | 0 | 0
2023-03-28 00:30 | 4.618 | 0 | N/A | 0 | 0
2023-03-28 01:00 | 4.9131 | 0 | N/A | 0 | 0
2023-03-28 01:30 | 4.3439 | 0 | N/A | 0 | 0
2023-03-28 02:00 | 3.7164 | 0 | N/A | 0 | 0
2023-03-28 02:30 | 3.6246 | 0 | N/A | 0 | 0
2023-03-28 03:00 | 3.3197 | 0 | N/A | 0 | 0
2023-03-28 03:30 | 3.0473 | 0 | N/A | 0 | 0
2023-03-28 04:00 | 2.9033 | 0 | N/A | 0 | 0
2023-03-28 04:30 | 2.8611 | 0 | N/A | 0 | 0
2023-03-28 05:00 | 2.8718 | 0 | N/A | 0 | 0
2023-03-28 05:30 | 3.0078 | 0 | N/A | 0 | 0
2023-03-28 06:00 | 3.2866 | 0 | N/A | 0 | 0
2023-03-28 06:30 | 3.858 | 0 | N/A | 0 | 0
2023-03-28 07:00 | 4.5842 | 0 | N/A | 0 | 0
2023-03-28 07:30 | 5.6459 | 0 | N/A | 0 | 0
2023-03-28 08:00 | 6.0455 | 0 | N/A | 0 | 0
2023-03-28 08:30 | 5.7814 | 0 | N/A | 0 | 0
2023-03-28 09:00 | 5.6 | 0 | N/A | 0 | 0
2023-03-28 09:30 | 4.8965 | 0 | N/A | 0 | 0
2023-03-28 10:00 | 4.4539 | 0 | N/A | 0 | 0
2023-03-28 10:30 | 3.9018 | 0 | N/A | 0 | 0
2023-03-28 11:00 | 2.8304 | 0 | N/A | 0 | 0
2023-03-28 11:30 | 2.4853 | 0 | N/A | 0 | 0
2023-03-28 12:00 | 2.6264 | 0 | N/A | 0 | 0
2023-03-28 12:30 | 2.8499 | 0 | N/A | 0 | 0
2023-03-28 13:00 | 1.1099 | 0 | N/A | 0 | 0
2023-03-28 13:30 | 1.1291 | 0 | N/A | 0 | 0
2023-03-28 14:00 | 1.3996 | 0 | N/A | 0 | 0
2023-03-28 14:30 | 1.2128 | 0 | N/A | 0 | 0
2023-03-28 15:00 | 0.86023 | 0 | N/A | 0 | 0
2023-03-31 11:00 | 4.2253 | 0 | N/A | 0 | 0
2023-03-31 11:30 | 4.4289 | 0 | N/A | 0 | 0
2023-03-31 12:00 | 3.5841 | 0 | N/A | 0 | 0
2023-03-31 12:30 | 2.2609 | 0 | N/A | 0 | 0
2023-03-31 13:00 | 1.8144 | 0 | N/A | 0 | 0
2023-03-31 13:30 | 2.0873 | 0 | N/A | 0 | 0
2023-03-31 14:00 | 0.7781 | 0 | N/A | 0 | 0
2023-03-31 14:30 | 1.0328 | 0 | N/A | 0 | 0
2023-03-31 15:00 | 3.2279 | 0 | N/A | 0 | 0
2023-03-31 15:30 | 3.0842 | 0 | N/A | 0 | 0
2023-03-31 16:00 | 2.7685 | 0 | N/A | 0 | 0
2023-03-31 16:30 | 4.1573 | 0 | N/A | 0 | 0
2023-03-31 17:00 | 4.7869 | 0 | N/A | 0 | 0
2023-03-31 17:30 | 5.1023 | 0 | N/A | 0 | 0
2023-03-31 18:00 | 5.81 | 0 | N/A | 0 | 0
2023-03-31 18:30 | 6.1346 | 0 | N/A | 0 | 0
2023-03-31 19:00 | 6.3483 | 0 | N/A | 0 | 0
2023-03-31 19:30 | 6.5892 | 0 | N/A | 0 | 0
2023-03-31 20:00 | 6.6394 | 0 | N/A | 0 | 0
2023-03-31 20:30 | 6.4845 | 0 | N/A | 0 | 0
2023-03-31 21:00 | 6.255 | 0 | N/A | 0 | 0
2023-03-31 21:30 | 5.998 | 0 | N/A | 0 | 0
2023-03-31 22:00 | 5.6043 | 0 | N/A | 0 | 0
2023-03-31 22:30 | 5.6468 | 0 | N/A | 0 | 0
2023-03-31 23:00 | 5.5354 | 0 | N/A | 0 | 0
2023-03-31 23:30 | 5.0678 | 0 | N/A | 0 | 0