## Intro
Powercor 2025 Distribution System Limitation Template
This Distribution Systems Limitations template is intended to make the Distribution Annual Planning Report (DAPR) limitation data more accessible and usable. Any information provided in this System Limitations template should be read in conjunction with the Powercor 2025 DAPR. It should also be noted that the information in this template and the DAPR are based on high-level risk assessments produced for the DAPR. As such the numbers are indicative and subject to change. Therefore the information in this template should not be used to make investment decisions, and should only be used to assist in discussions with Powercor. Finalised data will be produced in a detailed risk assessment conducted at the RIT-D or business case stage. However Powercor invites interested parties to submit their proposals or to engage in joint planning with Powercor as early as possible in order to defer or avoid the proposed augmentation. Powercor also publishes its own Network Limitation maps in order to assist with the visualisation of the limitation data presented within this template and the DAPR. The data in this template will be updated annually and will be published along with the DAPR. We welcome any feedback to improve the content or usability of this template.

## Powercor Limitations
Owner | Asset Code | Asset Name | Project Name | Network Element | Voltage level (kV) | Rating | [5 empty] | Nameplate Rating | Location |  |  |  | Residential customers affected |  | Business Case | [7 empty] | Demand Reduction required to defer investment by 1 year |  | Emergency Generation |  | Load Transfer capability (MVA) | Power Factor | 10% POE | [14 empty] | 50% POE | [14 empty] | Weighted Expected Energy at Risk (MWh)
[6 empty] | Summer |  |  | Winter |  |  |  | Start |  | End |  |  |  | Constraint Primary Driver | Investment Description | Preferred network investment |  |  |  | Proposed Timing | Annual Deferral Value | [6 empty] | Forecast Maximum Demand (MVA) |  |  |  |  | Maximum Load at risk (MVA) (N-1) |  |  |  |  | Maximum Load at risk (MVA) (N-2) |  |  |  |  | Forecast Maximum Demand (MVA) |  |  |  |  | Maximum Load at risk (MVA) (N-1) |  |  |  |  | Maximum Load at risk (MVA) (N-2)
[6 empty] | N Rating (MVA) | N-1 Rating (MVA) | N-2 Rating (MVA) | N Rating (MVA) | N-1 Rating (MVA) | N-2 Rating (MVA) |  | Longitude | Latitude | Longitude | Latitude | Count | Percent |  |  | capital cost ($) | cost accuracy plus | cost accuracy minus | Operating cost ($) |  |  | (MW) | (MVA) | (MW) | (MVA) |  |  | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030
Powercor | WMN | Wemen | WMN 66kV bus augmentation | zss | 66/22 | 33 | 17.2 | - | 33 | 20.2 | - | 46.5 | 142.6833 | -34.7539 | 142.6833 | -34.7539 | 148 | 42.17% | capacity | Powercor’s preferred network option is to augment WMN line to WETS - BSP sub-transmission line. See the DAPR report for more details. | 839365 | 30% | 30% | 8393.65 | 2026/27 | 35785.2436 | 8.7306 | 9.453 | 0 | 0 | 5.3347 | 0.92358 | 28.12 | 28.48 | 28.62 | 28.61 | 28.3 | 10.92 | 11.28 | 11.42 | 11.41 | 11.1 | - | - | - | - | - | 25.56 | 25.87 | 26.01 | 26 | 25.71 | 8.36 | 8.67 | 8.81 | 8.8 | 8.51 | - | - | - | - | - | 59.6974 | 60.1514 | 60.2598 | 59.8677 | 59.3887
Powercor | DDL | Drysdale | Drysdale supply area | zss | 66/22 | 79.4 | 39.7 | - | 94.4 | 47.2 | - | 66 | 144.5643 | -38.1827 | 144.5643 | -38.1827 | 35019 | 94.12% | capacity | Powercor’s preferred network option is to install a new transformer at DDL. See the DAPR report for more details. | 8457675 | 30% | 30% | 84576.75 | 2027/28 | 360582.0596 | 45.6418 | 46.291 | 0 | 0 | 4.5726 | 0.98598 | 89.21 | 92.08 | 94.16 | 95.69 | 97.32 | 49.51 | 52.38 | 54.46 | 55.99 | 57.62 | - | - | - | - | - | 78.66 | 80.77 | 82.49 | 83.92 | 85.06 | 38.96 | 41.07 | 42.79 | 44.22 | 45.36 | - | - | - | - | - | 40.6888 | 52.3983 | 69.092 | 85.5479 | 102.4416
Powercor | BMH | Bacchus Marsh zone substation | Rebuild Bacchus Marsh zone substation | zss | 66/22 | 38.2 | 19.1 | - | 40.4 | 20.2 | - | 27 | 144.4085 | -37.6996 | 144.4085 | -37.6996 | 11955 | 91.57% | capacity | Powercor’s preferred network option is to rebuild BMH ZSS to address BMH constraints and provide additional capacity to support MLN. See the DAPR report for more details. | 29995330 | 30% | 30% | 299953.3 | 2027/28 | 1278812.1876 | 17.819 | 18.164 | 0 | 0 | 3.0484 | 0.981 | 37.34 | 38.56 | 39.7 | 40.77 | 41.62 | 18.24 | 19.46 | 20.6 | 21.67 | 22.52 | - | - | - | - | - | 34 | 35.12 | 36.22 | 37.08 | 37.78 | 14.9 | 16.02 | 17.12 | 17.98 | 18.68 | - | - | - | - | - | 9.3508 | 13.0419 | 17.6997 | 22.7838 | 29.3177
Powercor | MLN | Melton zone substation | Rebuild Bacchus Marsh zone substation | zss | 66/22 | 119.7 | 79.8 | - | 131.4 | 83.4 | - | 99 | 144.5859 | -37.6872 | 144.5859 | -37.6872 | 46682 | 95.81% | capacity | Powercor’s preferred network option is to rebuild BMH ZSS to address BMH constraints and provide additional capacity to support MLN. See the DAPR report for more details. | 29995330 | 30% | 30% | 299953.3 | 202728 | 1278812.1876 | 53.6572 | 53.713 | 0 | 0 | 10.7837 | 0.99896 | 132.2 | 136.59 | 145.14 | 152.04 | 156.88 | 52.4 | 56.79 | 65.34 | 72.24 | 77.08 | - | - | - | - | - | 116.7 | 120.69 | 128.53 | 134.91 | 139.32 | 36.9 | 40.89 | 48.73 | 55.11 | 59.52 | - | - | - | - | - | 25.1007 | 60.8378 | 142.788 | 245.6737 | 399.4819
Powercor | LV | Laverton zone substation | New zone substation PCK | zss | 66/22 | 119.7 | 79.8 | - | 143.1 | 95.4 | - | 99 | 144.7276 | -37.8519 | 144.7276 | -37.8519 | 41574 | 93.62% | capacity | Powercor’s preferred network option is to establish a neww ZSS at Point Cook (PCK). See the DAPR report for more details. | 57481291 | 30% | 30% | 574812.91 | 2030/31 | 2450640.666 | 47.7555 | 47.889 | 0 | 0 | 14.2513 | 0.99721 | 131.47 | 130.36 | 132.62 | 135.34 | 137.16 | 51.67 | 50.56 | 52.82 | 55.54 | 57.36 | - | - | - | - | - | 117.2 | 116.99 | 119.62 | 121.9 | 123.63 | 37.4 | 37.19 | 39.82 | 42.1 | 43.83 | - | - | - | - | - | 8.8033 | 10.1821 | 14.128 | 18.5879 | 24.4063
Powercor | WBE | Werribee zone substation | New zone substation RBE | zss | 66/22 | 123.7 | 82.8 | - | 137.3 | 92.2 | - | 99 | 144.6628 | -37.8905 | 144.6628 | -37.8905 | 50721 | 95.15% | capacity | Powercor’s preferred network option is to establish a neww ZSS at Rockbank East (RBE). See the DAPR report for more details. | 29995330 | 30% | 30% | 299953.3 | 2029/30 | 1278812.1876 | 47.248 | 47.452 | 0 | 0 | 8.7642 | 0.9957 | 144.96 | 133.5 | 139.16 | 144.49 | 149.97 | 62.16 | 50.7 | 56.36 | 61.69 | 67.17 | - | - | - | - | - | 132.11 | 120 | 122.05 | 124.15 | 126.06 | 49.31 | 37.2 | 39.25 | 41.35 | 43.26 | - | - | - | - | - | 32.7896 | 24.9245 | 39.516 | 75.0373 | 171.944
Powercor | DDL023 | Drysdale feeder 23 | DDL023 feeder exit cable | feeder | 22 | 12.0031 | 12.0031 | - | 12.0031 | 12.0031 | - | - | 144.5049 | -38.2655 | 144.5049 | -38.2655 | 3391 | 93.8% | capacity | Powercor’s preferred network option is to uprate 8.1km of conductor and replaces 130m of feeder exit cable on DDL023. See the DAPR report for more details. | 1625981 | 30% | 30% | 16259.81 | 2027/28 | 69321.6017 | 0.8296 | 0.83138 | 0 | 0 | - | 0.99786 | 12.824 | 13.3271 | 13.7572 | 14.1027 | 14.4336 | 0.82093 | 1.324 | 1.7541 | 2.0996 | 2.4305 | - | - | - | - | - | 11.603 | 12.0605 | 12.4391 | 12.8301 | 13.126 | 0 | 0.057402 | 0.43594 | 0.82699 | 1.1229 | - | - | - | - | - | 0.57838 | 1.1202 | 2.0176 | 2.9836 | 4.3062
Powercor | GLE013 | Geelong East feeder 13 | Geelong East new feeder | feeder | 22 | 14.4799 | 14.4799 | - | 14.6705 | 14.6705 | - | - | 144.3679 | -38.2225 | 144.3679 | -38.2225 | 9195 | 98.5% | capacity | Powercor's preferred network option is to construct a new feeder from GLE and offload GLE013. See the DAPR report for more details. | 3927787 | 30% | 30% | 39277.87 | 2026/27 | 167456.1302 | 2.176 | 2.176 | 0 | 0 | - | 0.99727 | 17.8979 | 19.1509 | 20.6871 | 22.175 | 23.5292 | 3.4179 | 4.6709 | 6.2071 | 7.6951 | 9.0492 | - | - | - | - | - | 14.3674 | 15.5867 | 16.9312 | 18.2371 | 19.5168 | 0 | 1.1067 | 2.4512 | 3.7572 | 5.0368 | - | - | - | - | - | 32.6625 | 98.0476 | 226.3385 | 433.8932 | 767.0025
Powercor | MLN021 | Melton feeder 21 | MTC009 - New 22kV Feeder | feeder | 22 | 16.0042 | 16.0042 | - | 16.0042 | 16.0042 | - | - | 144.6738 | -37.7155 | 144.6738 | -37.7155 | 5710 | 94.82% | capacity | Powercor's preferred network option is to construct a new feeder MTC009 from MTC and offload MLN021 and MLN031. See the DAPR report for more details. | 1812298 | 30% | 30% | 18122.98 | 2026/27 | 77264.9866 | 6.4275 | 6.4275 | 0 | 0 | - | 0.99994 | 22.4797 | 24 | 25.3294 | 26.6905 | 28.1433 | 6.4756 | 7.9959 | 9.3252 | 10.6863 | 12.1391 | - | - | - | - | - | 20.3869 | 21.7595 | 22.9548 | 24.0855 | 25.0838 | 4.3827 | 5.7553 | 6.9507 | 8.0813 | 9.0796 | - | - | - | - | - | 141.3153 | 281.4342 | 522.5463 | 869.3938 | 1383.7945
Powercor | MLN031 | Melton feeder 31 | MTC009 - New 22kV Feeder | feeder | 22 | 19.3 | 19.3 | - | 19.3 | 19.3 | - | - | 144.5911 | -37.7186 | 144.5911 | -37.7186 | 3542 | 97.68% | capacity | Powercor's preferred network option is to construct a new feeder MTC009 from MTC and offload MLN021 and MLN031. See the DAPR report for more details. | 1812298 | 30% | 30% | 18122.98 | 2026/27 | 77264.9866 | 0 | 0 | 0 | 0 | - | 0.979 | 14.6226 | 16.4714 | 21.5016 | 23.3953 | 24.3777 | 0 | 0 | 2.2016 | 4.0953 | 5.0777 | - | - | - | - | - | 13.3772 | 15.2494 | 19.9678 | 21.8099 | 22.7189 | 0 | 0 | 0.66776 | 2.5099 | 3.4189 | - | - | - | - | - | 0 | 3.0038 | 35.8921 | 83.8986 | 174.0715
Powercor | TNA023 | Truganina feeder 23 | MTC010 - New 22kV Feeder | feeder | 22 | 19.2431 | 19.2431 | - | 19.2431 | 19.2431 | - | - | 144.6995 | -37.8213 | 144.6995 | -37.8213 | 6733 | 95.87% | capacity | Powercor's preferred network option is to construct a new feeder MTC010 from MTC and offload TNA023. See the DAPR report for more detail. | 4400507 | 30% | 30% | 44005.07 | 2027/28 | 187609.9374 | 1.9329 | 1.9329 | 0 | 0 | - | 0.99998 | 22.5628 | 22.5387 | 24.2829 | 26.3722 | 28.3141 | 3.3197 | 3.2956 | 5.0399 | 7.1291 | 9.071 | - | - | - | - | - | 18.3507 | 18.1419 | 19.8444 | 21.5328 | 23.1636 | 0 | 0 | 0.60132 | 2.2897 | 3.9205 | - | - | - | - | - | 3.7742 | 8.8274 | 25.0175 | 70.2233 | 171.4118
Powercor | MLN011 | Melton feeder 11 | MTC011 - New 22kV Feeder | feeder | 22 | 12.0031 | 12.0031 | - | 12.3461 | 12.3461 | - | - | 144.5736 | -37.7136 | 144.5736 | -37.7136 | 6076 | 97.26% | capacity | Powercor's preferred network option is to construct a new feeder MTC011 from MTC and offload MLN011 and MLN013. See the DAPR report for more details. | 3895194 | 30% | 30% | 38951.94 | 2027/28 | 166066.5697 | 1.8763 | 1.8763 | 0 | 0 | - | 0.99946 | 13.4538 | 14.3673 | 15.383 | 16.3228 | 17.2514 | 1.4507 | 2.3641 | 3.3799 | 4.3197 | 5.2482 | - | - | - | - | - | 11.7819 | 12.3478 | 13.235 | 14.1226 | 14.974 | 0 | 0.34468 | 1.2319 | 2.1195 | 2.9709 | - | - | - | - | - | 1.1249 | 3.264 | 9.6051 | 25.0203 | 57.759
Powercor | MLN013 | Melton feeder 13 | MTC011 - New 22kV Feeder | feeder | 22 | 13.7178 | 13.7178 | - | 13.7178 | 13.7178 | - | - | 144.5575 | -37.7027 | 144.5575 | -37.7027 | 4972 | 92.38% | capacity | Powercor's preferred network option is to construct a new feeder MTC011 from MTC and offload MLN011 and MLN013. See the DAPR report for more details. | 3895194 | 30% | 30% | 38951.94 | 2027/28 | 166066.5697 | 0.8534 | 0.8534 | 0 | 0 | - | 0.99825 | 14.49 | 15.0061 | 15.465 | 15.9048 | 16.2586 | 0.77219 | 1.2882 | 1.7472 | 2.187 | 2.5408 | - | - | - | - | - | 13.282 | 13.7588 | 14.1882 | 14.584 | 14.9143 | 0 | 0.040928 | 0.47035 | 0.86616 | 1.1965 | - | - | - | - | - | 1.2682 | 3.6369 | 10.2969 | 25.8377 | 57.529
Powercor | TNA011 | Truganina feeder 11 | MTC012 - New 22kV Feeder | feeder | 22 | 19.2431 | 19.2431 | - | 19.2431 | 19.2431 | - | - | 144.7154 | -37.74 | 144.7154 | -37.74 | 6230 | 94.35% | capacity | Powercor's preferred network option is to construct a new feeder MTC012 from MTC and offload TNA011, TNA013, and TNA024. See the DAPR report for more details. | 1952212 | 30% | 30% | 19522.12 | 2026/27 | 83230.0394 | 0 | 0 | 0 | 0 | - | 0.99914 | 25.8172 | 16.4638 | 17.2487 | 17.9942 | 18.623 | 6.5741 | 0 | 0 | 0 | 0 | - | - | - | - | - | 22.6076 | 14.4265 | 15.1181 | 15.7393 | 16.2901 | 3.3645 | 0 | 0 | 0 | 0 | - | - | - | - | - | 0 | 0 | 0 | 0 | 0.01661
Powercor | TNA013 | Truganina feeder 13 | MTC012 - New 22kV Feeder | feeder | 22 | 12.9557 | 12.9557 | - | 12.9557 | 12.9557 | - | - | 144.7432 | -37.8045 | 144.7432 | -37.8045 | 19 | 7.197% | capacity | Powercor's preferred network option is to construct a new feeder MTC012 from MTC and offload TNA011, TNA013, and TNA024. See the DAPR report for more details. | 1952212 | 30% | 30% | 19522.12 | 2026/27 | 83230.0394 | 0.40549 | 0.40549 | 0 | 0 | - | 0.99769 | 13.7642 | 14.3074 | 14.885 | 15.3129 | 15.6711 | 0.80845 | 1.3516 | 1.9292 | 2.3572 | 2.7153 | - | - | - | - | - | 10.5153 | 11.115 | 11.6163 | 12.0483 | 12.3779 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | 0.56238 | 1.4593 | 2.8945 | 4.4397 | 6.3232
Powercor | TNA024 | Truganina feeder 24 | MTC012 - New 22kV Feeder | feeder | 22 | 16.3852 | 16.3852 | - | 16.3852 | 16.3852 | - | - | 144.7548 | -37.8077 | 144.7548 | -37.8077 | 28 | 5.263% | capacity | Powercor's preferred network option is to construct a new feeder MTC012 from MTC and offload TNA011, TNA013, and TNA024. See the DAPR report for more details. | 1952212 | 30% | 30% | 19522.12 | 2026/27 | 83230.0394 | 0.38585 | 0.38585 | 0 | 0 | - | 0.9828 | 17.0229 | 17.5093 | 17.8614 | 18.1494 | 18.4832 | 0.63774 | 1.1241 | 1.4762 | 1.7642 | 2.098 | - | - | - | - | - | 16.0267 | 16.4547 | 16.9684 | 17.369 | 17.7005 | 0 | 0.069469 | 0.58322 | 0.98384 | 1.3153 | - | - | - | - | - | 0.66489 | 1.8583 | 4.3579 | 7.5605 | 13.0056
Powercor | CHA | Cohuna #2 Transformer | Cohuna #2 Transformer Replacement | transformer | 66/22 | 31 | 15.5 | 0 | 31 | 15.5 | 0 | 13.5 | 144.2195 | -35.8803 | 144.2195 | -35.8803 | 2728 | 62.18% | asset condition | Powercor’s preferred network option is to replace the #2 transformer at CHA. See the DAPR report for more details. | 6755419.9014 | 30% | 30% | 67554.199 | 2027 | 288008.6101 | 2.6 | 2.6403 | 0 | 0 | 0 | 0.98472 | 17.62 | 17.78 | 17.83 | 17.75 | 17.6 | 2.12 | 2.28 | 2.33 | 2.25 | 2.1 | 17.62 | 17.78 | 17.83 | 17.75 | 17.6 | 16.18 | 16.29 | 16.34 | 16.31 | 16.1 | 0.68 | 0.79 | 0.84 | 0.81 | 0.6 | 16.18 | 16.29 | 16.34 | 16.31 | 16.1 | 10.8819 | 11.2671 | 11.6048 | 11.8642 | 12.0314
Powercor | STL | Stawell #3 Transformer | Stawell #3 Transformer Replacement | transformer | 66/22 | 35.9 | 17.9 | 0 | 35.9 | 17.9 | 0 | 13.5 | 142.7524 | -37.0592 | 142.7524 | -37.0592 | 5222 | 78.8% | asset condition | Powercor’s preferred network option is to replace the #3 transformer at STL. See the DAPR report for more details. | 6996395.5915 | 30% | 30% | 69963.9559 | 2030 | 298282.2977 | 5.1 | 5.3071 | 0 | 0 | 4.1 | 0.96098 | 27.91 | 29.02 | 28.78 | 28.51 | 28.15 | 5.91 | 7.02 | 6.78 | 6.51 | 6.15 | 23.81 | 24.92 | 24.68 | 24.41 | 24.05 | 26.19 | 27.24 | 26.98 | 26.73 | 26.39 | 4.19 | 5.24 | 4.98 | 4.73 | 4.39 | 22.09 | 23.14 | 22.88 | 22.63 | 22.29 | 10.8819 | 11.2671 | 11.6048 | 11.8642 | 12.0314
Powercor | WBL | Warrnambool 22kV switchgear, relay and building | Warrnambool 22kV switchgear, relay and building replacement | switchgear | 22 | 89.6 | 69.9 | 29.9 | 89.6 | 69.9 | 29.9 | N/A | 142.4911 | -38.3739 | 142.4911 | -38.3739 | 15986 | 87.21% | asset condition | Powercor’s preferred network option is to replace the 22kV switchgear, relays and building at WBL. See the DAPR report for more details. | 14000000 | 30% | 30% | 140000 | 2027 | 596871.9339 | N/A | N/A | 0 | 0 | 8.8 | 0.98679 | 57.18 | 57.09 | 56.5 | 55.97 | 55.57 | 0 | 0 | 0 | 0 | 0 | 18.48 | 18.39 | 17.8 | 17.27 | 16.87 | 51.25 | 51.29 | 51.14 | 50.87 | 50.46 | 0 | 0 | 0 | 0 | 0 | 12.55 | 12.59 | 12.44 | 12.17 | 11.76 | 5.0863 | 5.109 | 5.1385 | 5.1946 | 5.2409
Powercor | KYM | Kyabram 22kV switchgear, relay and building replacement | Kyabram 22kV switchgear, relay and building replacement | switchgear | 22 | 45.7 | 30.5 | 15.2 | 45.7 | 30.5 | 15.2 | N/A | 145.0327 | -36.3131 | 145.0327 | -36.3131 | 5026 | 72.63% | asset condition | Powercor’s preferred network option is to replace the 22kV switchgear, relays and building at KYM. See the DAPR report for more details. | 9377558 | 30% | 30% | 93775.58 | 2029 | 399800.0842 | N/A | N/A | 0 | 0 | 0 | 0.97861 | 30.36 | 30.48 | 30.36 | 30.19 | 29.82 | 0 | 0 | 0 | 0 | 0 | 15.16 | 15.28 | 15.16 | 14.99 | 14.62 | 27.69 | 27.81 | 27.72 | 27.51 | 27.19 | 0 | 0 | 0 | 0 | 0 | 12.49 | 12.61 | 12.52 | 12.31 | 11.99 | 2.1368 | 2.1458 | 2.1384 | 2.1236 | 2.0984
Powercor | PLD | Portland 22kV switchgear, relay and building replacement | Portland 22kV switchgear, relay and building replacement | switchgear | 22 | 46.1 | 23 | 0 | 46.1 | 23 | 0 | N/A | 141.5881 | -38.3324 | 141.5881 | -38.3324 | 8062 | 83.47% | asset condition | Powercor’s preferred network option is to replace the 22kV switchgear, relays and building at PLD. See the DAPR report for more details. | 8957836 | 30% | 30% | 89578.36 | 2030 | 381905.7784 | N/A | N/A | 0 | 0 | 0 | 0.99707 | 17.22 | 17.19 | 17.08 | 16.93 | 16.71 | 0 | 0 | 0 | 0 | 0 | 17.22 | 17.19 | 17.08 | 16.93 | 16.71 | 15.28 | 15.27 | 15.16 | 15.07 | 14.9 | 0 | 0 | 0 | 0 | 0 | 15.28 | 15.27 | 15.16 | 15.07 | 14.9 | 1.1013 | 1.1015 | 1.1073 | 1.1084 | 1.1062
Powercor | WBE | Werribee CB C 66kV Circuit Breaker | Werribee CB C 66kV Circuit Breaker replacement | circuit breaker | 66 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 144.6628 | -37.8905 | 144.6628 | -37.8905 | 50721 | 95.15% | asset condition | Powercor’s preferred network option is to replace the 66kV Bus tie circuit breaker C at WBE. See the DAPR report for more details. | 498000 | 30% | 30% | 4980 | 2026 | 21231.5874 | N/A | N/A | 0 | 0 | N/A | 0.9957 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A

## Sub-T Aug Sum
Sub transmission line | Season | Line N Import Rating (MVA) | Line Power Factor at Maximum Demand | Embedded Generation Capacity (MVA) | Load Transfer Capability (MVA) | Hours load is > 95% of Maximum Demand (Hrs) | Actual Maximum Demand (MVA) | 50% POE |  |  |  |  | 50% POE load above N Import Rating (%) | 50% POE load above N Import Rating (MVA) | 50% POE
[8 empty] | Forecast Maximum Demand (MVA) | [6 empty] | Energy at Risk (MWh) |  |  |  |  | Hours at Risk (Hrs)
|  |  | 2025 | 2025 | 2026 | 2025 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2026 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030
ATS-ATD | S | 102.3 | 0.99502 | 0 | - | - | 73.43 | 29.6 | 61.5 | 80 | 83.3 | 86.7361 | - | - | - | - | - | - | - | - | - | - | - | -
ATS-ATD | W | 130.3 | 0.99502 | 0 | - | - | 73.4 | 44.9 | 73.2 | 82.7 | 83.3 | 83.9044 | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-NRB | S | 52.6 | 0.85944 | 0 | - | - | 16.4791 | 26.5 | 26.5 | 26.5 | 26.5 | 26.5 | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-NRB | W | 52.6 | 0.85944 | 0 | - | - | 24.09 | 36.7 | 36.9 | 37.6 | 37.5 | 37.4003 | - | - | - | - | - | - | - | - | - | - | - | -
GTS-GHP | S | 74.3 | 0.98936 | 20.6932 | - | - | 41.4427 | 68.2 | 69.6 | 71.3 | 72.7 | 74.1275 | - | - | - | - | - | - | - | - | - | - | - | -
GTS-GHP | W | 87.5 | 0.98936 | 20.6932 | - | - | 37.32 | 62.3 | 64 | 65.5 | 66.5 | 67.5153 | - | - | - | - | - | - | - | - | - | - | - | -
BETS-MRO | S | 76.6 | 0.93529 | 20.4915 | - | - | 17.52 | 59.6 | 60.7 | 61.6 | 62 | 62.4026 | - | - | - | - | - | - | - | - | - | - | - | -
BETS-MRO | W | 89.2 | 0.93529 | 20.4915 | - | - | 17.6 | 57.1 | 57.4 | 58.5 | 59.7 | 60.9246 | - | - | - | - | - | - | - | - | - | - | - | -
HOTS-CHM | S | 26.2 | 0.91304 | 1.583 | - | - | 2.5 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | - | - | - | - | - | - | - | - | - | - | - | -
HOTS-CHM | W | 35.4 | 0.91304 | 1.583 | - | - | 2.51 | 2.2 | 2.1 | 2.1 | 2.1 | 2.1 | - | - | - | - | - | - | - | - | - | - | - | -
KTS-SA1 | S | 116.6 | 0.97635 | 44.6584 | - | - | 47.9 | 92.9 | 95 | 97.5 | 99.3 | 101.1332 | - | - | - | - | - | - | - | - | - | - | - | -
KTS-SA1 | W | 122.3 | 0.97635 | 44.6584 | - | - | 47.93 | 72.1 | 74 | 76.2 | 77.6 | 79.0257 | - | - | - | - | - | - | - | - | - | - | - | -
BGR-ART | S | 45.7 | 0.99342 | 15.7105 | - | - | 46.0085 | 12.4 | 12.4 | 12.5 | 12.5 | 12.5 | - | - | - | - | - | - | - | - | - | - | - | -
BGR-ART | W | 47.4 | 0.99342 | 15.7105 | - | - | 48.1085 | 13.7 | 13.7 | 13.8 | 13.8 | 13.8 | - | - | - | - | - | - | - | - | - | - | - | -
MBN-DTN | S | 74.3 | 0.94521 | 25.4432 | - | - | 11.8069 | 24 | 24 | 24.1 | 24.2 | 24.3004 | - | - | - | - | - | - | - | - | - | - | - | -
MBN-DTN | W | 86.9 | 0.94521 | 25.4432 | - | - | 13.2069 | 25.7 | 25.7 | 25.9 | 25.9 | 25.9 | - | - | - | - | - | - | - | - | - | - | - | -
BETS-CMN | S | 64 | 0.99652 | 33.3596 | - | - | 48 | 54.8 | 55.2 | 55.6 | 56.3 | 57.0088 | - | - | - | - | - | - | - | - | - | - | - | -
BETS-CMN | W | 65.2 | 0.99652 | 33.3596 | - | - | 48.07 | 51 | 51.6 | 52.3 | 52.8 | 53.3048 | - | - | - | - | - | - | - | - | - | - | - | -
CMN-MRO | S | 26.3 | 0.98252 | 53.8511 | - | - | 18.2 | 27.8 | 27.9 | 27.8 | 28.5 | 29.2176 | - | - | - | - | - | - | - | - | - | - | - | -
CMN-MRO | W | 35.4 | 0.98252 | 53.8511 | - | - | 19.22 | 28.9 | 28.6 | 29.2 | 29.4 | 29.6014 | - | - | - | - | - | - | - | - | - | - | - | -
HOTS-STL2 | S | 25.7 | 0.99685 | 17.53 | 4.0772 | 0.5 | 18.9 | 30.5 | 29.4 | 29.7 | 29.6 | 29.5003 | 18.68% | 4.8 | 4.2563 | 2.5503 | 2.9684 | 2.8292 | 2.8292 | 3 | 1.5 | 1.5 | 1.5 | 1.5
HOTS-STL2 | W | 34.9 | 0.99685 | 17.53 | - | - | 18 | 29.9 | 30.2 | 30.2 | 30.2 | 30.2 | - | - | - | - | - | - | - | - | - | - | - | -
BPA-HTH | S | 17.7 | 0.97297 | 0 | - | - | 8 | 3.7 | 3.8 | 3.8 | 3.8 | 3.8 | - | - | - | - | - | - | - | - | - | - | - | -
BPA-HTH | W | 35.4 | 0.97297 | 0 | - | - | 8.6 | 4.5 | 4.5 | 4.6 | 4.6 | 4.6 | - | - | - | - | - | - | - | - | - | - | - | -
HOTS-STL1 | S | 49.2 | 0.99099 | 17.53 | - | - | 22.87 | 32 | 31 | 31.2 | 31.1 | 31.0003 | - | - | - | - | - | - | - | - | - | - | - | -
HOTS-STL1 | W | 57.2 | 0.99099 | 17.53 | - | - | 34.1494 | 31.7 | 31.9 | 31.9 | 32 | 32.1003 | - | - | - | - | - | - | - | - | - | - | - | -
AL-BLTS | S | 91.4 | 0.87942 | 9.8576 | - | - | 27.12 | 78.2 | 78.6 | 78.9 | 79.3 | 79.702 | - | - | - | - | - | - | - | - | - | - | - | -
AL-BLTS | W | 91.4 | 0.87942 | 9.8576 | - | - | 39.52 | 85.8 | 86.1 | 86.8 | 87 | 87.2005 | - | - | - | - | - | - | - | - | - | - | - | -
BETS-BGO | S | 109.7 | 0.96507 | 21.6087 | - | - | 50.9 | 94.6 | 95.7 | 97.3 | 99.4 | 101.5453 | - | - | - | - | - | - | - | - | - | - | - | -
BETS-BGO | W | 114.3 | 0.96507 | 21.6087 | - | - | 51.4 | 83.1 | 84.3 | 86.1 | 87.1 | 88.1116 | - | - | - | - | - | - | - | - | - | - | - | -
RCTS-MDA2 | S | 104 | 0.9247 | 25.4014 | - | - | 52.03 | 110.6 | 111.1 | 111.5 | 112.9 | 114.3176 | - | - | - | - | - | - | - | - | - | - | - | -
RCTS-MDA2 | W | 114.3 | 0.9247 | 25.4014 | - | - | 50.03 | 83.1 | 83.5 | 84.4 | 85 | 85.6043 | - | - | - | - | - | - | - | - | - | - | - | -
RCTS-MDA1 | S | 104 | 0.91566 | 25.4014 | - | - | 35.42 | 101.7 | 102 | 103 | 104.2 | 105.414 | - | - | - | - | - | - | - | - | - | - | - | -
RCTS-MDA1 | W | 114.3 | 0.91566 | 25.4014 | - | - | 34.22 | 75.9 | 76.3 | 77.1 | 77.4 | 77.7012 | - | - | - | - | - | - | - | - | - | - | - | -
HKT-LV | S | 135.5 | 0.97816 | 82.3784 | - | - | 73.06 | 111 | 108.8 | 115.5 | 120.7 | 126.1341 | - | - | - | - | - | - | - | - | - | - | - | -
HKT-LV | W | 142.3 | 0.97816 | 82.3784 | - | - | 73.26 | 89.3 | 89.7 | 95.9 | 99.5 | 103.2351 | - | - | - | - | - | - | - | - | - | - | - | -
GTS-FDN | S | 102.9 | 0.95495 | 0 | - | - | 28.0987 | 36.2 | 36.5 | 37.4 | 37.7 | 38.0024 | - | - | - | - | - | - | - | - | - | - | - | -
GTS-FDN | W | 134.9 | 0.95495 | 0 | - | - | 19.46 | 37.5 | 37.8 | 38.4 | 38.5 | 38.6003 | - | - | - | - | - | - | - | - | - | - | - | -
WETS-WSF | S | 84.6 | 0.99548 | 0 | - | - | 86.9563 | 21.9 | 22.1 | 22.5 | 22.8 | 23.104 | - | - | - | - | - | - | - | - | - | - | - | -
WETS-WSF | W | 106.3 | 0.99548 | 0 | - | - | 89.9563 | 18.4 | 18.6 | 19 | 19.1 | 19.2005 | - | - | - | - | - | - | - | - | - | - | - | -
WSF-WMN | S | 31.4 | 0.99548 | 7.2348 | - | - | 25.2408 | 21.9 | 22.1 | 22.5 | 22.8 | 23.104 | - | - | - | - | - | - | - | - | - | - | - | -
WSF-WMN | W | 43.4 | 0.99548 | 7.2348 | - | - | 28.1408 | 18.4 | 18.6 | 19 | 19.1 | 19.2005 | - | - | - | - | - | - | - | - | - | - | - | -
ATS-AC | S | 102.3 | 0.88904 | 1.1938 | - | - | 14.82 | 76.2 | 76.7 | 77.1 | 77.9 | 78.7083 | - | - | - | - | - | - | - | - | - | - | - | -
ATS-AC | W | 108 | 0.88904 | 1.1938 | - | - | 26.22 | 83.5 | 84.3 | 85.2 | 85.3 | 85.4001 | - | - | - | - | - | - | - | - | - | - | - | -
GB-GL | S | 89.7 | 0.94674 | 19.7238 | - | - | 42.6854 | 91.5 | 92.6 | 93.7 | 94.9 | 96.1154 | - | - | - | - | - | - | - | - | - | - | - | -
GB-GL | W | 100.6 | 0.94674 | 19.7238 | - | - | 41.2854 | 73.7 | 74.7 | 75.8 | 76.5 | 77.2065 | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-SHN2 | S | 88 | 0.99085 | 27.206 | - | - | 20.3 | 35.6 | 35.7 | 36.8 | 37.4 | 38.0098 | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-SHN2 | W | 112 | 0.99085 | 27.206 | - | - | 20.45 | 29.2 | 29.6 | 30 | 30.2 | 30.4013 | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-HTN | S | 47.4 | 0.84921 | 12.7404 | - | - | 20.2 | 26.8 | 26.3 | 26.8 | 26.7 | 26.6004 | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-HTN | W | 48 | 0.84921 | 12.7404 | - | - | 25.52 | 35.3 | 35 | 35.9 | 36 | 36.1003 | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-SHN1 | S | 88 | 0.99085 | 27.206 | - | - | 16.22 | 35.6 | 35.7 | 36.8 | 37.4 | 38.0098 | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-SHN1 | W | 112 | 0.99085 | 27.206 | - | - | 16.3 | 29.2 | 29.6 | 30 | 30.2 | 30.4013 | - | - | - | - | - | - | - | - | - | - | - | -
KWF-NHL | S | 44 | 1 | 12.4066 | - | - | 11.1 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | - | - | - | - | - | - | - | - | - | - | - | -
KWF-NHL | W | 43.4 | 1 | 12.4066 | - | - | 11.3709 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | - | - | - | - | - | - | - | - | - | - | - | -
WETS-BPA | S | 31.4 | 1 | 0 | - | - | 11.94 | 6.7 | 6.7 | 6.8 | 6.8 | 6.8 | - | - | - | - | - | - | - | - | - | - | - | -
WETS-BPA | W | 43.4 | 1 | 0 | - | - | 12.3 | 7 | 7.1 | 7.1 | 7.1 | 7.1 | - | - | - | - | - | - | - | - | - | - | - | -
KRT-PLD1/CWF | S | 40 | 0.9878 | 74.8312 | - | - | 23.3581 | 14 | 13.9 | 13.8 | 13.8 | 13.8 | - | - | - | - | - | - | - | - | - | - | - | -
KRT-PLD1/CWF | W | 45.7 | 0.9878 | 74.8312 | - | - | 23.8 | 17.3 | 17.3 | 17.4 | 17.3 | 17.2006 | - | - | - | - | - | - | - | - | - | - | - | -
NKA-CME | S | 74.3 | 0.98714 | 78.7932 | - | - | 43.6685 | 35.8 | 36 | 36.3 | 36.6 | 36.9025 | - | - | - | - | - | - | - | - | - | - | - | -
NKA-CME | W | 86.9 | 0.98714 | 78.7932 | - | - | 45.1 | 30.8 | 31.1 | 31.4 | 31.6 | 31.8013 | - | - | - | - | - | - | - | - | - | - | - | -
ATS-WBE | S | 109.7 | 0.95228 | 103.2202 | 15.242 | 1 | 70.5 | 138.5 | 122.6 | 127.2 | 131.4 | 135.7387 | 26.25% | 28.8 | 235.5231 | 50.2246 | 88.5744 | 133.5867 | 133.5867 | 20.5 | 7.75 | 11 | 14.25 | 14.25
ATS-WBE | W | 134.9 | 0.95228 | 103.2202 | - | - | 71.27 | 102 | 91.2 | 94.6 | 97.4 | 100.2829 | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-CDN | S | 76.6 | 0.99598 | 19.982 | - | - | 44.2 | 54.2 | 55.5 | 56.1 | 56.6 | 57.1045 | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-CDN | W | 85.7 | 0.99598 | 19.982 | - | - | 42.46 | 53.6 | 54.2 | 54.9 | 55 | 55.1002 | - | - | - | - | - | - | - | - | - | - | - | -
NSF-NKA | S | 102.9 | 0.97582 | 36.7147 | - | - | 50.2839 | 65.2 | 66.8 | 67.6 | 68.4 | 69.2095 | - | - | - | - | - | - | - | - | - | - | - | -
NSF-NKA | W | 114.3 | 0.97582 | 36.7147 | - | - | 53.1 | 55.6 | 56.4 | 57.2 | 57.5 | 57.8016 | - | - | - | - | - | - | - | - | - | - | - | -
MDA-MBN | S | 74.3 | 0.94171 | 50.8447 | - | - | 27.9467 | 62.4 | 62.9 | 63.6 | 64.2 | 64.8057 | - | - | - | - | - | - | - | - | - | - | - | -
MDA-MBN | W | 86.9 | 0.94171 | 50.8447 | - | - | 28.7 | 42.8 | 43.2 | 43.7 | 44.1 | 44.5037 | - | - | - | - | - | - | - | - | - | - | - | -
BAN-BGR | S | 46.3 | 0.98758 | 63.7025 | - | - | 46.8 | 13 | 12.9 | 13 | 13.1 | 13.2008 | - | - | - | - | - | - | - | - | - | - | - | -
BAN-BGR | W | 49.7 | 0.98758 | 63.7025 | - | - | 51.2967 | 14.4 | 14.4 | 14.4 | 14.4 | 14.4 | - | - | - | - | - | - | - | - | - | - | - | -
ATS-TYA | S | 102.3 | 0.70039 | 0 | - | - | 19.2 | 35.3 | 34 | 33.9 | 34.4 | 34.9074 | - | - | - | - | - | - | - | - | - | - | - | -
ATS-TYA | W | 130.3 | 0.70039 | 0 | - | - | 19.83 | 39.1 | 39.3 | 37.7 | 36.7 | 35.7265 | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-TNA2 | S | 109.7 | 0.97842 | 111.7199 | 57.3101 | 1.5 | 106.2 | 144.6 | 112.7 | 118.1 | 122.6 | 127.2715 | 31.81% | 34.9 | 299.7399 | 3.5186 | 13.4073 | 30.9607 | 30.9607 | 25.75 | 1 | 2.75 | 4.75 | 4.75
DPTS-TNA2 | W | 134.9 | 0.97842 | 111.7199 | - | - | 106.2298 | 139 | 97.1 | 101 | 104.4 | 107.9145 | - | - | - | - | - | - | - | - | - | - | - | -
KGTS-SHL | S | 40 | 0.9902 | 32.6326 | - | - | 22.39 | 21.5 | 21.4 | 21.4 | 21.4 | 21.4 | - | - | - | - | - | - | - | - | - | - | - | -
KGTS-SHL | W | 49.7 | 0.9902 | 32.6326 | - | - | 20.1 | 26.1 | 26.1 | 26.2 | 26.1 | 26.0004 | - | - | - | - | - | - | - | - | - | - | - | -
BETS-EHK | S | 111.4 | 0.9587 | 40.6491 | - | - | 52.5 | 95.5 | 96.6 | 98.2 | 100.1 | 102.0368 | - | - | - | - | - | - | - | - | - | - | - | -
BETS-EHK | W | 111.4 | 0.9587 | 40.6491 | - | - | 52.96 | 83.3 | 84.6 | 86.3 | 87.3 | 88.3116 | - | - | - | - | - | - | - | - | - | - | - | -
GHP-BCG | S | 109.7 | 0.97101 | 20.6932 | - | - | 20 | 34.2 | 34.8 | 35.8 | 36.6 | 37.4179 | - | - | - | - | - | - | - | - | - | - | - | -
GHP-BCG | W | 134.9 | 0.97101 | 20.6932 | - | - | 19.9595 | 33.1 | 34 | 34.6 | 35.1 | 35.6072 | - | - | - | - | - | - | - | - | - | - | - | -
TRG-WBL1 | S | 47.4 | 0.94256 | 39.6682 | - | - | 28.2 | 36.8 | 36.7 | 36.7 | 37.3 | 37.9098 | - | - | - | - | - | - | - | - | - | - | - | -
TRG-WBL1 | W | 49.7 | 0.94256 | 39.6682 | - | - | 29.2647 | 40.9 | 41.2 | 41.6 | 41.8 | 42.001 | - | - | - | - | - | - | - | - | - | - | - | -
TRG-WBL2 | S | 45.7 | 0.98251 | 39.6682 | - | - | 31 | 32.7 | 32.6 | 32.6 | 33.1 | 33.6077 | - | - | - | - | - | - | - | - | - | - | - | -
TRG-WBL2 | W | 46.3 | 0.98251 | 39.6682 | - | - | 31.3373 | 36.1 | 36.3 | 36.9 | 37 | 37.1003 | - | - | - | - | - | - | - | - | - | - | - | -
AWT-LV | S | 109.7 | 0.97896 | 82.3784 | - | - | 69.1 | 115.1 | 120 | 131.8 | 144.1 | 157.5479 | - | - | - | - | - | - | - | - | - | - | - | -
AWT-LV | W | 134.9 | 0.97896 | 82.3784 | - | - | 68.6 | 91.2 | 93.6 | 100.6 | 109.2 | 118.5352 | - | - | - | - | - | - | - | - | - | - | - | -
GTS-GCY | S | 90.3 | 0.94011 | 19.6486 | 36.1566 | 1 | 51.4 | 109.2 | 110.3 | 111.8 | 113 | 114.2129 | 20.93% | 18.9 | 109.8862 | 124.2 | 144.9026 | 162.7709 | 162.7709 | 15.5 | 17 | 19 | 20 | 20
GTS-GCY | W | 96.6 | 0.94011 | 19.6486 | - | - | 52.14 | 86.5 | 87.6 | 89 | 89.7 | 90.4055 | - | - | - | - | - | - | - | - | - | - | - | -
FDN-CRO | S | 109.7 | 0.95706 | 6.7197 | - | - | 27.4734 | 34.5 | 34.8 | 35.7 | 36.1 | 36.5045 | - | - | - | - | - | - | - | - | - | - | - | -
FDN-CRO | W | 134.9 | 0.95706 | 6.7197 | - | - | 27.5 | 35.2 | 35.6 | 36.1 | 36.2 | 36.3003 | - | - | - | - | - | - | - | - | - | - | - | -
BATS-BAN2 | S | 96 | 0.91163 | 63.7025 | - | - | 83 | 94.9 | 74.6 | 75.6 | 76.7 | 77.816 | - | - | - | - | - | - | - | - | - | - | - | -
BATS-BAN2 | W | 114.3 | 0.91163 | 63.7025 | - | - | 83.39 | 73.7 | 74.5 | 76 | 76.7 | 77.4064 | - | - | - | - | - | - | - | - | - | - | - | -
BATS-BAN1 | S | 96 | 0.91704 | 63.7025 | - | - | 48.2 | 94.7 | 74.7 | 75.6 | 76.7 | 77.816 | - | - | - | - | - | - | - | - | - | - | - | -
BATS-BAN1 | W | 114.3 | 0.91704 | 63.7025 | - | - | 48.87 | 73.7 | 74.6 | 76 | 76.7 | 77.4064 | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-SHP | S | 101.7 | 1 | 39.3347 | - | - | 24.25 | 40.2 | 40.3 | 40.8 | 41 | 41.201 | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-SHP | W | 116 | 1 | 39.3347 | - | - | 24.2 | 30.3 | 30.6 | 30.9 | 31 | 31.1003 | - | - | - | - | - | - | - | - | - | - | - | -
BLTS-ATD | S | 97.2 | 1 | 0 | - | - | 59.3 | 29.5 | 61.3 | 79.6 | 82.8 | 86.1286 | - | - | - | - | - | - | - | - | - | - | - | -
BLTS-ATD | W | 125.7 | 1 | 0 | - | - | 59.1 | 44.8 | 72.8 | 82.3 | 82.8 | 83.303 | - | - | - | - | - | - | - | - | - | - | - | -
STL-ART | S | 38.3 | 0.96313 | 33.2405 | - | - | 41.74 | 19.8 | 18.4 | 18.7 | 18.7 | 18.7 | - | - | - | - | - | - | - | - | - | - | - | -
STL-ART | W | 43.4 | 0.96313 | 33.2405 | - | - | 42.45 | 21.6 | 21.9 | 22 | 22.1 | 22.2005 | - | - | - | - | - | - | - | - | - | - | - | -
BETS-CTN | S | 26.3 | 0.99163 | 19.1698 | - | - | 25.57 | 23.5 | 23.5 | 23.7 | 23.9 | 24.1017 | - | - | - | - | - | - | - | - | - | - | - | -
BETS-CTN | W | 30.3 | 0.99163 | 19.1698 | - | - | 25.05 | 20.5 | 20.6 | 20.8 | 20.9 | 21.0005 | - | - | - | - | - | - | - | - | - | - | - | -
HOTS-HSM2 | S | 49.2 | 0.99007 | 24.5257 | - | - | 24.336 | 42.5 | 42.6 | 42.8 | 42.9 | 43.0002 | - | - | - | - | - | - | - | - | - | - | - | -
HOTS-HSM2 | W | 52.6 | 0.99007 | 24.5257 | - | - | 24.3 | 35.4 | 35.6 | 35.9 | 35.8 | 35.7003 | - | - | - | - | - | - | - | - | - | - | - | -
HOTS-HSM1 | S | 49.2 | 0.99012 | 24.5257 | - | - | 24.686 | 42.7 | 42.8 | 43 | 43.2 | 43.4009 | - | - | - | - | - | - | - | - | - | - | - | -
HOTS-HSM1 | W | 52.6 | 0.99012 | 24.5257 | - | - | 24.7 | 35.6 | 35.7 | 36 | 36 | 36 | - | - | - | - | - | - | - | - | - | - | - | -
HTH-OYN | S | 17.7 | 0.94118 | 4.0186 | - | - | 8.0592 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | - | - | - | - | - | - | - | - | - | - | - | -
HTH-OYN | W | 35.4 | 0.94118 | 4.0186 | - | - | 7.9 | 6.6 | 6.6 | 6.7 | 6.6 | 6.5015 | - | - | - | - | - | - | - | - | - | - | - | -
GTS-CRO | S | 91.4 | 0.95732 | 6.7197 | - | - | 32.4347 | 36.2 | 36.4 | 37.4 | 37.7 | 38.0024 | - | - | - | - | - | - | - | - | - | - | - | -
GTS-CRO | W | 91.4 | 0.95732 | 6.7197 | - | - | 28.23 | 37.5 | 37.8 | 38.4 | 38.5 | 38.6003 | - | - | - | - | - | - | - | - | - | - | - | -
SHP-KYM | S | 84.6 | 0.88584 | 72.0915 | - | - | 94.1353 | 26.7 | 26.6 | 26.7 | 26.8 | 26.9004 | - | - | - | - | - | - | - | - | - | - | - | -
SHP-KYM | W | 106.3 | 0.88584 | 72.0915 | - | - | 94 | 22.4 | 22.3 | 22.5 | 22.5 | 22.5 | - | - | - | - | - | - | - | - | - | - | - | -
HCP-WBE | S | 109.7 | 0.98159 | 103.2202 | 15.242 | 0.5 | 62.94 | 126.7 | 113.4 | 117.1 | 120.5 | 123.9987 | 15.5% | 17 | 13.8092 | 1.4621 | 3.2663 | 5.4788 | 5.4788 | 2.25 | 0.5 | 0.75 | 1 | 1
HCP-WBE | W | 134.9 | 0.98159 | 103.2202 | - | - | 62.8 | 94.5 | 84.7 | 87.9 | 90.4 | 92.9711 | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-KYM1 | S | 79.4 | 0.998 | 32.7567 | - | - | 27.8 | 53.3 | 53.5 | 54.1 | 54.5 | 54.903 | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-KYM1 | W | 90.3 | 0.998 | 32.7567 | - | - | 27.19 | 39.6 | 40 | 40.5 | 40.6 | 40.7002 | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-KYM2 | S | 79.4 | 0.99802 | 32.7567 | - | - | 28 | 53.9 | 54.1 | 54.7 | 55.1 | 55.5029 | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-KYM2 | W | 90.3 | 0.99802 | 32.7567 | - | - | 28.16 | 40.1 | 40.5 | 40.9 | 41.1 | 41.301 | - | - | - | - | - | - | - | - | - | - | - | -
YSW-BMH | S | 36.6 | 0.95469 | 19.1573 | - | - | 42.9 | 33 | 34.2 | 35.2 | 36.3 | 37.4344 | - | - | - | - | - | - | - | - | - | - | - | -
YSW-BMH | W | 37.2 | 0.95469 | 19.1573 | - | - | 42.986 | 28.2 | 29.5 | 30.4 | 31.5 | 32.6398 | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-TNA1 | S | 109.7 | 0.98005 | 111.7199 | 57.3101 | 1.25 | 93.1 | 144.6 | 112.5 | 117.9 | 122.4 | 127.0718 | 31.81% | 34.9 | 295.8615 | 3.1093 | 12.4643 | 29.6572 | 29.6572 | 22.25 | 1 | 2.5 | 4.5 | 4.5
DPTS-TNA1 | W | 134.9 | 0.98005 | 111.7199 | - | - | 93.199 | 138.9 | 97 | 100.9 | 104.3 | 107.8146 | - | - | - | - | - | - | - | - | - | - | - | -
WPD-TQY1 | S | 107 | 0.99171 | 68.3733 | - | - | 20.8 | 35 | 35.4 | 36.1 | 37.6 | 39.1623 | - | - | - | - | - | - | - | - | - | - | - | -
WPD-TQY1 | W | 108.6 | 0.99171 | 68.3733 | - | - | 20.9048 | 36.7 | 37.4 | 39 | 39.7 | 40.4126 | - | - | - | - | - | - | - | - | - | - | - | -
KYM-ECA2 | S | 45.7 | 0.9975 | 71.0766 | - | - | 39.36 | 43.6 | 44 | 44.5 | 45.1 | 45.7081 | - | - | - | - | - | - | - | - | - | - | - | -
KYM-ECA2 | W | 53.2 | 0.9975 | 71.0766 | - | - | 39.3 | 32.2 | 32.5 | 32.9 | 33.1 | 33.3012 | - | - | - | - | - | - | - | - | - | - | - | -
ATS-AWT | S | 109.7 | 0.97527 | 0 | - | - | 69.23 | 120.4 | 128 | 143.5 | 158.3 | 174.6264 | - | - | - | - | - | - | - | - | - | - | - | -
ATS-AWT | W | 134.9 | 0.97527 | 0 | - | - | 67.8 | 97.2 | 103 | 113.4 | 123.6 | 134.7175 | - | - | - | - | - | - | - | - | - | - | - | -
KYM-ECA1 | S | 45.7 | 0.99496 | 71.0766 | - | - | 39.16 | 43 | 43.4 | 43.9 | 44.1 | 44.3009 | - | - | - | - | - | - | - | - | - | - | - | -
KYM-ECA1 | W | 52.6 | 0.99496 | 71.0766 | - | - | 39.1 | 31.9 | 32.2 | 32.6 | 32.8 | 33.0012 | - | - | - | - | - | - | - | - | - | - | - | -
KGTS-GSF | S | 48.6 | 0.99485 | 0 | - | - | 47.1128 | 20.5 | 20.3 | 20.3 | 20.3 | 20.3 | - | - | - | - | - | - | - | - | - | - | - | -
KGTS-GSF | W | 52.6 | 0.99485 | 0 | - | - | 32.81 | 24.4 | 24.4 | 24.5 | 24.4 | 24.3004 | - | - | - | - | - | - | - | - | - | - | - | -
GLE-DDL1 | S | 74.3 | 0.98191 | 84.6323 | - | - | 37.7389 | 72.6 | 74.8 | 78.1 | 81 | 84.0077 | - | - | - | - | - | - | - | - | - | - | - | -
GLE-DDL1 | W | 86.9 | 0.98191 | 84.6323 | - | - | 37.7 | 55 | 57.2 | 59.6 | 61.4 | 63.2544 | - | - | - | - | - | - | - | - | - | - | - | -
GLE-DDL2 | S | 74.3 | 0.98084 | 84.6323 | - | - | 45.3 | 73.2 | 75.8 | 79.1 | 82.1 | 85.2138 | - | - | - | - | - | - | - | - | - | - | - | -
GLE-DDL2 | W | 86.9 | 0.98084 | 84.6323 | - | - | 45.2997 | 55.5 | 57.6 | 60.1 | 61.9 | 63.7539 | - | - | - | - | - | - | - | - | - | - | - | -
GCY-GL | S | 109.7 | 0.96341 | 37.076 | - | - | 36.6 | 57.6 | 58.5 | 59.5 | 60.1 | 60.7061 | - | - | - | - | - | - | - | - | - | - | - | -
GCY-GL | W | 134.9 | 0.96341 | 37.076 | - | - | 36.4895 | 49.6 | 50.4 | 51.3 | 51.8 | 52.3049 | - | - | - | - | - | - | - | - | - | - | - | -
GSF-SHL | S | 76.6 | 0.99474 | 32.6326 | - | - | 24.7001 | 20 | 19.9 | 19.9 | 19.9 | 19.9 | - | - | - | - | - | - | - | - | - | - | - | -
GSF-SHL | W | 89.2 | 0.99474 | 32.6326 | - | - | 24.2 | 23.9 | 23.9 | 24 | 23.9 | 23.8004 | - | - | - | - | - | - | - | - | - | - | - | -
YSF-HTH | S | 17.7 | 0.9434 | 0 | - | - | 6.8 | 10.5 | 10.2 | 10.6 | 10.6 | 10.6 | - | - | - | - | - | - | - | - | - | - | - | -
YSF-HTH | W | 35.4 | 0.9434 | 0 | - | - | 6.9046 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | - | - | - | - | - | - | - | - | - | - | - | -
KRT-PLD2/YWF | S | 29.7 | 0.99422 | 74.8312 | - | - | 24.8602 | 15.1 | 15 | 14.9 | 14.9 | 14.9 | - | - | - | - | - | - | - | - | - | - | - | -
KRT-PLD2/YWF | W | 29.7 | 0.99422 | 74.8312 | - | - | 24.1 | 18.3 | 18.4 | 18.4 | 18.4 | 18.4 | - | - | - | - | - | - | - | - | - | - | - | -
CTN-CBW | S | 98.9 | 0 | 19.1698 | - | - | 39.2868 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | - | - | - | - | - | - | - | - | - | - | - | -
CTN-CBW | W | 106.3 | 0 | 19.1698 | - | - | 39.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | - | - | - | - | - | - | - | - | - | - | - | -
ATS-HCP | S | 109.7 | 0.95364 | 0 | 15.242 | 0.5 | 62.55 | 138.2 | 122.7 | 126.9 | 131 | 135.2325 | 25.98% | 28.5 | 93.1858 | 12.5903 | 23.2021 | 41.3486 | 41.3486 | 11 | 2 | 4.25 | 6.5 | 6.5
ATS-HCP | W | 134.9 | 0.95364 | 0 | - | - | 62.4 | 101.8 | 91 | 94.5 | 97.2 | 99.9771 | - | - | - | - | - | - | - | - | - | - | - | -
KRT-WBL | S | 46.9 | 0.861 | 82.5978 | - | - | 25.7 | 23.9 | 23.8 | 23.8 | 24.4 | 25.0151 | - | - | - | - | - | - | - | - | - | - | - | -
KRT-WBL | W | 47.4 | 0.861 | 82.5978 | - | - | 25.7587 | 20 | 20.3 | 20.6 | 20.7 | 20.8005 | - | - | - | - | - | - | - | - | - | - | - | -
ATS-SCI | S | 90.8 | 0.78218 | 0 | - | - | 25.1 | 41.1 | 41.2 | 41.4 | 41.5 | 41.6002 | - | - | - | - | - | - | - | - | - | - | - | -
ATS-SCI | W | 116 | 0.78218 | 0 | - | - | 25.62 | 41.2 | 41.3 | 41.6 | 41.5 | 41.4002 | - | - | - | - | - | - | - | - | - | - | - | -
SBY-GSB2 | S | 76.6 | 0.99273 | 22.7913 | - | - | 40 | 49.8 | 51 | 52.4 | 53.8 | 55.2374 | - | - | - | - | - | - | - | - | - | - | - | -
SBY-GSB2 | W | 89.2 | 0.99273 | 22.7913 | - | - | 40.22 | 58.4 | 60 | 61.8 | 63.1 | 64.4273 | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-WNS | S | 91.4 | 0.94373 | 0 | - | - | 95.7814 | 69.5 | 71.3 | 72.9 | 73.7 | 74.5088 | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-WNS | W | 91.4 | 0.94373 | 0 | - | - | 95.1 | 58.6 | 59.6 | 60.5 | 60.8 | 61.1015 | - | - | - | - | - | - | - | - | - | - | - | -
RCTS-YSF | S | 84.6 | 0.92661 | 0 | - | - | 5.7 | 10.8 | 10.5 | 11 | 10.9 | 10.8009 | - | - | - | - | - | - | - | - | - | - | - | -
RCTS-YSF | W | 106.3 | 0.92661 | 0 | - | - | 5.97 | 9.6 | 9.5 | 9.6 | 9.6 | 9.6 | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-SU1 | S | 109.7 | 0.96474 | 41.8716 | - | - | 75 | 97.4 | 102.2 | 105 | 107.2 | 109.4461 | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-SU1 | W | 133.7 | 0.96474 | 41.8716 | - | - | 75.1235 | 83 | 87.5 | 89.7 | 91.3 | 92.9285 | - | - | - | - | - | - | - | - | - | - | - | -
GTS-BCG | S | 109.7 | 0.98296 | 0 | - | - | 44.2 | 80.5 | 82.2 | 84 | 85.6 | 87.2305 | - | - | - | - | - | - | - | - | - | - | - | -
GTS-BCG | W | 134.9 | 0.98296 | 0 | - | - | 44.58 | 76.3 | 78.4 | 80.1 | 81.3 | 82.518 | - | - | - | - | - | - | - | - | - | - | - | -
WPD-TQY2 | S | 107 | 0.99171 | 68.3733 | - | - | 17.9246 | 35 | 35.4 | 36.7 | 37.6 | 38.5221 | - | - | - | - | - | - | - | - | - | - | - | -
WPD-TQY2 | W | 108.6 | 0.99171 | 68.3733 | - | - | 17.8 | 36.7 | 37.5 | 39 | 39.7 | 40.4126 | - | - | - | - | - | - | - | - | - | - | - | -
ATS-LVN | S | 109.7 | 0.97111 | 19.9175 | - | - | 75 | 93.3 | 93.9 | 95 | 95.8 | 96.6067 | - | - | - | - | - | - | - | - | - | - | - | -
ATS-LVN | W | 134.9 | 0.97111 | 19.9175 | - | - | 75.24 | 95.3 | 96.3 | 97.7 | 98.5 | 99.3066 | - | - | - | - | - | - | - | - | - | - | - | -
GTS-GB | S | 135.5 | 0.92883 | 2.2964 | - | - | 41.9 | 110 | 111.1 | 112.5 | 113.9 | 115.3174 | - | - | - | - | - | - | - | - | - | - | - | -
GTS-GB | W | 142.3 | 0.92883 | 2.2964 | - | - | 42.68 | 86.6 | 87.7 | 89 | 89.8 | 90.6072 | - | - | - | - | - | - | - | - | - | - | - | -
COB-CDN | S | 49.2 | 1 | 28.5118 | - | - | 32.2 | 32.9 | 34.1 | 34.6 | 35.1 | 35.6072 | - | - | - | - | - | - | - | - | - | - | - | -
COB-CDN | W | 57.2 | 1 | 28.5118 | - | - | 32.7776 | 33.6 | 34 | 34.5 | 34.8 | 35.1026 | - | - | - | - | - | - | - | - | - | - | - | -
KSF-RVL | S | 84.6 | 0.97382 | 14.5489 | - | - | 41.3136 | 20.1 | 22.2 | 22.7 | 23.1 | 23.507 | - | - | - | - | - | - | - | - | - | - | - | -
KSF-RVL | W | 106.3 | 0.97382 | 14.5489 | - | - | 40 | 13.5 | 14.7 | 15 | 15.2 | 15.4027 | - | - | - | - | - | - | - | - | - | - | - | -
BCG-WIN | S | 91.4 | 0.97877 | 12.7618 | - | - | 73 | 45.2 | 46.9 | 47.6 | 48 | 48.4034 | - | - | - | - | - | - | - | - | - | - | - | -
BCG-WIN | W | 91.4 | 0.97877 | 12.7618 | - | - | 77.4681 | 50.3 | 51.1 | 52 | 52.3 | 52.6017 | - | - | - | - | - | - | - | - | - | - | - | -
CPL-AL | S | 91.4 | 0.8864 | 9.8576 | - | - | 27.9 | 69.2 | 69.5 | 69.7 | 69.9 | 70.1006 | - | - | - | - | - | - | - | - | - | - | - | -
CPL-AL | W | 91.4 | 0.8864 | 9.8576 | - | - | 28.828 | 69.8 | 69.9 | 70.4 | 70.2 | 70.0006 | - | - | - | - | - | - | - | - | - | - | - | -
SBY-GSB1 | S | 51.4 | 0.99638 | 22.7913 | - | - | 53.9 | 50.2 | 51.3 | 52.7 | 54.1 | 55.5372 | - | - | - | - | - | - | - | - | - | - | - | -
SBY-GSB1 | W | 69.7 | 0.99638 | 22.7913 | - | - | 56 | 58.7 | 60.3 | 62.2 | 63.5 | 64.8272 | - | - | - | - | - | - | - | - | - | - | - | -
GTS-SRC | S | 109.7 | 0.95731 | 0 | - | - | 56.84 | 96 | 98.4 | 102 | 103 | 104.0098 | - | - | - | - | - | - | - | - | - | - | - | -
GTS-SRC | W | 134.9 | 0.95731 | 0 | - | - | 54.8 | 87.4 | 90.3 | 92.8 | 93.5 | 94.2053 | - | - | - | - | - | - | - | - | - | - | - | -
BLTS-TYA | S | 88 | 0.7305 | 0 | - | - | 30.83 | 37.8 | 36.6 | 36.5 | 37 | 37.5068 | - | - | - | - | - | - | - | - | - | - | - | -
BLTS-TYA | W | 112 | 0.7305 | 0 | - | - | 41.1764 | 41.7 | 42.1 | 40.5 | 39.4 | 38.3299 | - | - | - | - | - | - | - | - | - | - | - | -
BCG-WPD | S | 91.4 | 0.99036 | 40.8707 | - | - | 65.8 | 99 | 101.3 | 103.9 | 106.1 | 108.3466 | - | - | - | - | - | - | - | - | - | - | - | -
BCG-WPD | W | 91.4 | 0.99036 | 40.8707 | - | - | 65.8536 | 89.9 | 92.6 | 94.7 | 96.5 | 98.3342 | - | - | - | - | - | - | - | - | - | - | - | -
BATS-YSW/BGL | S | 36.6 | 0.9973 | 0 | 3.0484 | 0.5 | 35.9 | 40.4 | 41.9 | 43.5 | 45 | 46.5517 | 10.38% | 3.8 | 4.9984 | 5.1469 | 10.7109 | 3.4313 | 21.4219 | 0.57188 | 3.5703 | 1.1438 | 2.1422 | 2.5734
BATS-YSW/BGL | W | 37.1 | 0.9973 | 0 | - | - | 36.5 | 32.2 | 33.6 | 34.8 | 36 | 37.2414 | - | - | - | - | - | - | - | - | - | - | - | -
BATS-BAS1 | S | 83.5 | 0.97587 | 116.0329 | - | - | 56.33 | 86 | 76.6 | 82.5 | 80.1 | 77.7698 | - | - | - | - | - | - | - | - | - | - | - | -
BATS-BAS1 | W | 102.9 | 0.97587 | 116.0329 | - | - | 56.3 | 76.2 | 85.9 | 85.1 | 86.5 | 87.923 | - | - | - | - | - | - | - | - | - | - | - | -
ATS-HKT1 | S | 135.5 | 0.9711 | 0 | - | - | 81.56 | 121.3 | 128.6 | 144.4 | 159 | 175.0762 | - | - | - | - | - | - | - | - | - | - | - | -
ATS-HKT1 | W | 142.3 | 0.9711 | 0 | - | - | 85.37 | 97.7 | 103.5 | 114.1 | 124.2 | 135.194 | - | - | - | - | - | - | - | - | - | - | - | -
KTS-SSE1 | S | 89.7 | 0.93416 | 26.4458 | - | - | 34.66 | 74.1 | 74.8 | 75.9 | 76.7 | 77.5084 | - | - | - | - | - | - | - | - | - | - | - | -
KTS-SSE1 | W | 94.3 | 0.93416 | 26.4458 | - | - | 34.8 | 66.9 | 67.9 | 69.2 | 69.9 | 70.6071 | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-NSF | S | 98.3 | 0.95254 | 0 | - | - | 104.9872 | 68.7 | 70.6 | 71.6 | 72.4 | 73.2089 | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-NSF | W | 114.3 | 0.95254 | 0 | - | - | 48.4 | 57.9 | 58.9 | 59.6 | 60 | 60.4027 | - | - | - | - | - | - | - | - | - | - | - | -
HOTS-KWF | S | 44 | 0.69173 | 0 | - | - | 10.41 | 19.3 | 19.3 | 19.3 | 19.3 | 19.3 | - | - | - | - | - | - | - | - | - | - | - | -
HOTS-KWF | W | 43.4 | 0.69173 | 0 | - | - | 38.6923 | 20.3 | 20.2 | 20.3 | 20.2 | 20.1005 | - | - | - | - | - | - | - | - | - | - | - | -
KTS-SA2 | S | 108 | 0.97525 | 44.6584 | - | - | 52.3 | 93.2 | 95.2 | 97.5 | 99.5 | 101.541 | - | - | - | - | - | - | - | - | - | - | - | -
KTS-SA2 | W | 122.3 | 0.97525 | 44.6584 | - | - | 52.36 | 72.2 | 74 | 76.4 | 77.7 | 79.0221 | - | - | - | - | - | - | - | - | - | - | - | -
NRB-HTN | S | 52.6 | 0.84651 | 12.7404 | - | - | 32.5 | 23.1 | 23 | 23 | 23 | 23 | - | - | - | - | - | - | - | - | - | - | - | -
NRB-HTN | W | 53.2 | 0.84651 | 12.7404 | - | - | 39.8355 | 30.7 | 30.6 | 31.1 | 31.1 | 31.1 | - | - | - | - | - | - | - | - | - | - | - | -
GSB-WND2 | S | 46.3 | 1 | 47.3687 | - | - | 27.9 | 19.9 | 20.5 | 21.1 | 21.6 | 22.1118 | - | - | - | - | - | - | - | - | - | - | - | -
GSB-WND2 | W | 49.7 | 1 | 47.3687 | - | - | 28.12 | 26 | 26.8 | 27.6 | 28.2 | 28.813 | - | - | - | - | - | - | - | - | - | - | - | -
KGTS-CHA | S | 31.4 | 0.94771 | 36.5961 | - | - | 13.05 | 19.3 | 19.2 | 19.3 | 19.3 | 19.3 | - | - | - | - | - | - | - | - | - | - | - | -
KGTS-CHA | W | 43.4 | 0.94771 | 36.5961 | - | - | 13 | 15.6 | 15.6 | 15.8 | 15.8 | 15.8 | - | - | - | - | - | - | - | - | - | - | - | -
GSB-WND1 | S | 109.7 | 1 | 47.3687 | - | - | 24.5 | 19.7 | 20.2 | 20.8 | 21.3 | 21.812 | - | - | - | - | - | - | - | - | - | - | - | -
GSB-WND1 | W | 114.3 | 1 | 47.3687 | - | - | 24.74 | 25.6 | 26.3 | 27.1 | 27.7 | 28.3133 | - | - | - | - | - | - | - | - | - | - | - | -
KTS-SSE2 | S | 89.4 | 0.93544 | 26.4458 | - | - | 52.6 | 74.1 | 74.7 | 75.8 | 76.6 | 77.4084 | - | - | - | - | - | - | - | - | - | - | - | -
KTS-SSE2 | W | 100.6 | 0.93544 | 26.4458 | - | - | 53.81 | 66.8 | 67.9 | 69.2 | 69.8 | 70.4052 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-DLF1 | S | 87.5 | 0.88448 | 0 | - | - | 8.33 | 27.6 | 27.6 | 27.7 | 27.6 | 27.5004 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-DLF1 | W | 87.5 | 0.88448 | 0 | - | - | 8.3 | 27.7 | 27.7 | 27.6 | 27.6 | 27.6 | - | - | - | - | - | - | - | - | - | - | - | -
MDA-BNG | S | 104 | 0.93779 | 25.4014 | - | - | 30.3313 | 52.2 | 52.7 | 53 | 53.7 | 54.4092 | - | - | - | - | - | - | - | - | - | - | - | -
MDA-BNG | W | 114.3 | 0.93779 | 25.4014 | - | - | 29.7 | 37 | 37.2 | 37.7 | 37.8 | 37.9003 | - | - | - | - | - | - | - | - | - | - | - | -
GTS-GLE2 | S | 109.7 | 0.92421 | 32.1632 | 12.9557 | 1 | 76.8 | 149.2 | 152.9 | 159.9 | 166.7 | 173.7892 | 36.01% | 39.5 | 160.0868 | 196.1285 | 281.1967 | 384.8405 | 384.8405 | 12 | 14 | 17.5 | 23.5 | 23.5
GTS-GLE2 | W | 133.7 | 0.92421 | 32.1632 | - | - | 79.85 | 119.8 | 123.9 | 129.1 | 132.3 | 135.5793 | - | - | - | - | - | - | - | - | - | - | - | -
GTS-GLE1 | S | 109.7 | 0.9539 | 32.1632 | 12.9557 | 2 | 86.6 | 139.3 | 143.2 | 148.6 | 152.4 | 156.2972 | 26.98% | 29.6 | 259.4687 | 331.7117 | 448.0652 | 544.2772 | 544.2772 | 16 | 20.5 | 24 | 28 | 28
GTS-GLE1 | W | 133.7 | 0.9539 | 32.1632 | - | - | 88.53 | 115.3 | 118.9 | 122.7 | 125.5 | 128.3639 | - | - | - | - | - | - | - | - | - | - | - | -
MGW-CLC | S | 74.3 | 0.9912 | 16.06 | - | - | 66.4126 | 36.7 | 38.2 | 38.4 | 38.6 | 38.801 | - | - | - | - | - | - | - | - | - | - | - | -
MGW-CLC | W | 86.9 | 0.9912 | 16.06 | - | - | 64.8 | 38.5 | 39 | 39.5 | 39.6 | 39.7003 | - | - | - | - | - | - | - | - | - | - | - | -
BATS-BAS2/BGF | S | 93.2 | 0.9727 | 116.0329 | - | - | 57.5 | 91.1 | 81.5 | 87.7 | 85.1 | 82.5771 | - | - | - | - | - | - | - | - | - | - | - | -
BATS-BAS2/BGF | W | 94.9 | 0.9727 | 116.0329 | - | - | 58.77 | 80.3 | 90.2 | 89.4 | 90.8 | 92.2219 | - | - | - | - | - | - | - | - | - | - | - | -
STN-MNA | S | 48.6 | 0.95758 | 65.6095 | 9.3739 | 0.25 | 39.9 | 54.8 | 55.1 | 55.7 | 56.3 | 56.9065 | 12.76% | 6.2 | 2.9364 | 3.5254 | 4.0446 | 4.662 | 4.662 | 0.35642 | 0.40734 | 0.45098 | 0.53099 | 0.53099
STN-MNA | W | 52.6 | 0.95758 | 65.6095 | - | - | 40.0412 | 43.3 | 43.6 | 44.1 | 44.5 | 44.9036 | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-KRT2 | S | 97.2 | 0.85901 | 64.1676 | - | - | 31.5 | 37 | 36.8 | 36.8 | 37.3 | 37.8068 | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-KRT2 | W | 116 | 0.85901 | 64.1676 | - | - | 32.15 | 41.9 | 42.2 | 42.8 | 43 | 43.2009 | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-KRT1 | S | 44 | 0.97879 | 64.1676 | - | - | 29.9 | 32.2 | 32 | 32.1 | 32.5 | 32.905 | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-KRT1 | W | 44.6 | 0.97879 | 64.1676 | - | - | 29.99 | 36.8 | 37.1 | 37.5 | 37.6 | 37.7003 | - | - | - | - | - | - | - | - | - | - | - | -
GTS-WPD | S | 108 | 0.97242 | 40.8707 | - | - | 49 | 103 | 105.6 | 109.3 | 111.9 | 114.5618 | - | - | - | - | - | - | - | - | - | - | - | -
GTS-WPD | W | 135.5 | 0.97242 | 40.8707 | - | - | 49.19 | 93.7 | 95.9 | 98.3 | 101.1 | 103.9798 | - | - | - | - | - | - | - | - | - | - | - | -
BGO-EHK | S | 48.6 | 0.96325 | 62.2578 | 10.4027 | 0.5 | 29.6 | 53.9 | 54.9 | 56.1 | 57.2 | 58.3216 | 10.91% | 5.3 | 32.5034 | 129.9124 | 76.0876 | 139.3721 | 115.2394 | 21.4419 | 12.5581 | 21.4419 | 12.5581 | 22.0725
BGO-EHK | W | 49.2 | 0.96325 | 62.2578 | - | - | 29.66 | 47.5 | 48.5 | 49.6 | 50.5 | 51.4163 | - | - | - | - | - | - | - | - | - | - | - | -
WNS-NKA | S | 91.4 | 0.97094 | 36.7147 | - | - | 45.4061 | 65.6 | 67 | 68.3 | 69.1 | 69.9094 | - | - | - | - | - | - | - | - | - | - | - | -
WNS-NKA | W | 91.4 | 0.97094 | 36.7147 | - | - | 45.2 | 56.1 | 57 | 57.8 | 58 | 58.2007 | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-STN | S | 91.4 | 0.94565 | 36.8208 | 9.3739 | 0.25 | 52.03 | 104.1 | 104.9 | 106.1 | 107.3 | 108.5136 | 13.89% | 12.7 | 35.8605 | 43.0537 | 49.3948 | 56.9341 | 56.9341 | 4.3528 | 4.9746 | 5.5076 | 6.4848 | 6.4848
SHTS-STN | W | 91.4 | 0.94565 | 36.8208 | - | - | 51 | 77.4 | 78.2 | 78.8 | 79.9 | 81.0154 | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-SU2 | S | 109.7 | 0.96182 | 41.8716 | - | - | 67.2 | 98.9 | 104 | 106.9 | 109 | 111.1413 | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-SU2 | W | 133.7 | 0.96182 | 41.8716 | - | - | 68.3663 | 83.8 | 88.4 | 90.7 | 92.3 | 93.9282 | - | - | - | - | - | - | - | - | - | - | - | -
RVL-BSP | S | 84.6 | 0.99451 | 14.5489 | - | - | 28.08 | 19.4 | 21.2 | 21.6 | 22 | 22.4074 | - | - | - | - | - | - | - | - | - | - | - | -
RVL-BSP | W | 106.3 | 0.99451 | 14.5489 | - | - | 26.5 | 12.8 | 13.9 | 14.2 | 14.4 | 14.6028 | - | - | - | - | - | - | - | - | - | - | - | -
WIN-MGW | S | 98.3 | 0.96369 | 12.7618 | - | - | 79.7 | 38.8 | 40.6 | 41.1 | 41.6 | 42.1061 | - | - | - | - | - | - | - | - | - | - | - | -
WIN-MGW | W | 99.5 | 0.96369 | 12.7618 | - | - | 82.9369 | 40.8 | 41.5 | 42.4 | 42.8 | 43.2038 | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-MNA | S | 88 | 0.93277 | 28.7887 | 9.3739 | 0.5 | 66.9 | 107.7 | 109.4 | 110.7 | 112.1 | 113.5177 | 22.39% | 19.7 | 100.9218 | 121.1653 | 139.011 | 160.2289 | 160.2289 | 12.25 | 14 | 15.5 | 18.25 | 18.25
SHTS-MNA | W | 114.4 | 0.93277 | 28.7887 | - | - | 67.53 | 79.6 | 80.4 | 81 | 82.2 | 83.4178 | - | - | - | - | - | - | - | - | - | - | - | -
BLTS-SCI | S | 97.2 | 0.99738 | 0 | - | - | 83.6 | 92.3 | 92.6 | 93.4 | 93.7 | 94.001 | - | - | - | - | - | - | - | - | - | - | - | -
BLTS-SCI | W | 125.7 | 0.99738 | 0 | - | - | 84.7385 | 92.4 | 92.9 | 93.7 | 93.7 | 93.7 | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-MLN2 | S | 109.7 | 0.95473 | 83.4903 | - | - | 82 | 120.2 | 120.4 | 135.1 | 146 | 157.7794 | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-MLN2 | W | 134.9 | 0.95473 | 83.4903 | - | - | 82.1127 | 86 | 86.6 | 101.4 | 105 | 108.7278 | - | - | - | - | - | - | - | - | - | - | - | -
CDN-CLC | S | 74.3 | 0.99274 | 36.042 | - | - | 50.6 | 43.8 | 45.3 | 45.8 | 46.1 | 46.402 | - | - | - | - | - | - | - | - | - | - | - | -
CDN-CLC | W | 86.9 | 0.99274 | 36.042 | - | - | 51.0532 | 49.3 | 50 | 50.5 | 50.7 | 50.9008 | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-COB | S | 109.7 | 0.98614 | 8.5298 | - | - | 21.5 | 47.4 | 48.5 | 49 | 49.4 | 49.8033 | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-COB | W | 116 | 0.98614 | 8.5298 | - | - | 22.21 | 46.7 | 47.1 | 47.6 | 47.8 | 48.0008 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-DLF3 | S | 87.5 | 0.88448 | 0 | - | - | 9.69 | 27.6 | 27.6 | 27.8 | 27.6 | 27.4014 | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-DLF3 | W | 87.5 | 0.88448 | 0 | - | - | 9.7 | 27.7 | 27.7 | 27.7 | 27.6 | 27.5004 | - | - | - | - | - | - | - | - | - | - | - | -
BSP-BBD | S | 65.2 | 0.95804 | 1.0882 | - | - | 33.2349 | 33.8 | 34 | 34.2 | 34.3 | 34.4003 | - | - | - | - | - | - | - | - | - | - | - | -
BSP-BBD | W | 67.4 | 0.95804 | 1.0882 | - | - | 30 | 18 | 18.1 | 18.2 | 18.2 | 18.2 | - | - | - | - | - | - | - | - | - | - | - | -
BLTS-LVN | S | 109.7 | 0.97121 | 19.9175 | - | - | 65.97 | 93.8 | 94.5 | 95.6 | 96.6 | 97.6105 | - | - | - | - | - | - | - | - | - | - | - | -
BLTS-LVN | W | 122.3 | 0.97121 | 19.9175 | - | - | 65 | 95.8 | 97 | 98.4 | 99.3 | 100.2082 | - | - | - | - | - | - | - | - | - | - | - | -
GTS-FNS | S | 88 | 0.96039 | 41.0865 | - | - | 55.9 | 95.6 | 98 | 100.8 | 102.6 | 104.4321 | - | - | - | - | - | - | - | - | - | - | - | -
GTS-FNS | W | 112 | 0.96039 | 41.0865 | - | - | 56.43 | 87.1 | 89.9 | 91.8 | 93.2 | 94.6214 | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-TRG2 | S | 91.5 | 0.98752 | 21.2381 | - | - | 29.8 | 64.1 | 64 | 64.4 | 64.8 | 65.2025 | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-TRG2 | W | 91.5 | 0.98752 | 21.2381 | - | - | 30.76 | 69 | 70.2 | 71.1 | 71.4 | 71.7013 | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-TRG1 | S | 91.5 | 0.98752 | 21.2381 | - | - | 36.57 | 64.1 | 64 | 64.4 | 64.7 | 65.0014 | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-TRG1 | W | 91.5 | 0.98752 | 21.2381 | - | - | 34.8 | 68.9 | 70.2 | 71.1 | 71.4 | 71.7013 | - | - | - | - | - | - | - | - | - | - | - | -
RCTS-MBN | S | 97.2 | 0.91562 | 25.4432 | - | - | 26.9 | 62.4 | 62.6 | 63.2 | 64.1 | 65.0128 | - | - | - | - | - | - | - | - | - | - | - | -
RCTS-MBN | W | 114.3 | 0.91562 | 25.4432 | - | - | 26.8 | 45.4 | 45.7 | 46.2 | 46.4 | 46.6009 | - | - | - | - | - | - | - | - | - | - | - | -
RCTS-KSF | S | 84.6 | 0.97423 | 0 | - | - | 22.73 | 20.6 | 22.7 | 23.2 | 23.6 | 24.0069 | - | - | - | - | - | - | - | - | - | - | - | -
RCTS-KSF | W | 106.3 | 0.97423 | 0 | - | - | 19.8 | 13.7 | 14.9 | 15.3 | 15.5 | 15.7026 | - | - | - | - | - | - | - | - | - | - | - | -
AC-CPL | S | 102.9 | 0.89246 | 1.1938 | - | - | 28 | 73 | 73.4 | 73.8 | 74.6 | 75.4087 | - | - | - | - | - | - | - | - | - | - | - | -
AC-CPL | W | 108 | 0.89246 | 1.1938 | - | - | 28.5022 | 79.5 | 80.3 | 81.1 | 81.2 | 81.3001 | - | - | - | - | - | - | - | - | - | - | - | -
FNS-SRC | S | 109.7 | 0.94715 | 41.0865 | - | - | 38.9 | 48.5 | 48.7 | 51.1 | 51.9 | 52.7125 | - | - | - | - | - | - | - | - | - | - | - | -
FNS-SRC | W | 125.7 | 0.94715 | 41.0865 | - | - | 39.6137 | 45.9 | 46.1 | 46.4 | 47 | 47.6078 | - | - | - | - | - | - | - | - | - | - | - | -
WETS-BSP | S | 84.6 | 0.94235 | 0 | - | - | 67.0654 | 57.9 | 60.8 | 61.3 | 61.8 | 62.3041 | - | - | - | - | - | - | - | - | - | - | - | -
WETS-BSP | W | 106.3 | 0.94235 | 0 | - | - | 66 | 32.1 | 33.3 | 33.8 | 34 | 34.2012 | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-BMH | S | 32.6 | 0.94985 | 19.1573 | - | - | 22.6 | 34 | 35.12 | 36.22 | 37.08 | 37.78 | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-BMH | W | 37.7 | 0.94985 | 19.1573 | - | - | 26.34 | 27.66 | 28.84 | 30.22 | 31.44 | 32.61 | - | - | - | - | - | - | - | - | - | - | - | -
ATS-HKT2 | S | 135.4637 | 0.9711 | 0 | - | - | 25.74 | 121.3 | 128.6 | 144.4 | 159 | 175.0762 | - | - | - | - | - | - | - | - | - | - | - | -
ATS-HKT2 | W | 142.3226 | 0.9711 | 0 | - | - | 24.5 | 97.7 | 103.5 | 114.1 | 124.2 | 135.194 | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-MTC1 | S | 135.3494 | 0.95473 | 0 | - | - | 86 | 58.35 | 101.05 | 108.08 | 112.695 | 117.5071 | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-MTC1 | W | 142.3226 | 0.95473 | 0 | - | - | 87.0614 | 82.055 | 91.55 | 99.97 | 106.36 | 113.1584 | - | - | - | - | - | - | - | - | - | - | - | -
LSF-KYM | S | 79.4492 | 0.99802 | 112.7567 | - | - | 47.1 | 53.9 | 54.1 | 54.7 | 55.1 | 55.5029 | - | - | - | - | - | - | - | - | - | - | - | -
LSF-KYM | W | 90.3091 | 0.99802 | 112.7567 | - | - | 44 | 40.1 | 40.5 | 40.9 | 41.1 | 41.301 | - | - | - | - | - | - | - | - | - | - | - | -
MTC-MLN | S | 135.3494 | 0.95473 | 83.4903 | - | - | 84.8 | 43.7625 | 75.7875 | 81.06 | 84.5213 | 88.1303 | - | - | - | - | - | - | - | - | - | - | - | -
MTC-MLN | W | 142.3226 | 0.95473 | 83.4903 | - | - | 83.7 | 61.5412 | 68.6625 | 74.9775 | 79.77 | 84.8688 | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-LSF | S | 79.4492 | 0.99802 | 80 | - | - | 29.308 | 53.9 | 54.1 | 54.7 | 55.1 | 55.5029 | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-LSF | W | 90.3091 | 0.99802 | 80 | - | - | 29.1 | 40.1 | 40.5 | 40.9 | 41.1 | 41.301 | - | - | - | - | - | - | - | - | - | - | - | -

## ZSS Aug Sum
Zone Substation | Season | Station N Import Rating (MVA) | Station N-1 Import Rating (MVA) | Station Nameplate Rating (MVA) | Station Power Factor at Maximum Demand | Embedded Generation Capacity (MVA) | Load Transfer Capability (MVA) | Hours load is > 95% of Maximum Demand (Hrs) | Actual Maximum Demand (MVA) | 10% POE |  |  |  |  | 50% POE |  |  |  |  | 50% POE load above N-1 Import Rating (%) | 50% POE load above N-1 Import Rating (MVA) | 10% POE | [14 empty] | 50% POE | [14 empty] | Weighted POE
[10 empty] | Forecast Maximum Demand (MVA) |  |  |  |  | Forecast Maximum Demand (MVA) | [6 empty] | Energy at Risk (MWh) |  |  |  |  | Expected Energy at Risk (MWh) |  |  |  |  | Hours at Risk (Hrs) |  |  |  |  | Energy at Risk (MWh) |  |  |  |  | Expected Energy at Risk (MWh) |  |  |  |  | Hours at Risk (Hrs) |  |  |  |  | Energy at Risk (MWh) |  |  |  |  | Expected Energy at Risk (MWh)
[5 empty] | 2025 | 2025 | 2026 | 2025 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2026 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030
AC | summer | 60 | 30 | 40 | 0.93447 | 1.1938 | 0 | 1.3115 | 5.6342 | 9.51 | 9.7 | 9.83 | 9.9 | 9.86 | 7.82 | 7.99 | 8.11 | 8.19 | 8.16 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AC | winter | 60 | 30 | 40 | 2025: 0.93245; 2025: 1.1938; 2026: 0; 2025: 1.7598; 2025: 5.7569; Forecast Maximum Demand (MVA) 2026: 9.41; Forecast Maximum Demand (MVA) 2027: 9.52; Forecast Maximum Demand (MVA) 2028: 9.66; Forecast Maximum Demand (MVA) 2029: 9.76; Forecast Maximum Demand (MVA) 2030: 9.62; Forecast Maximum Demand (MVA) 2026: 7.85; Forecast Maximum Demand (MVA) 2027: 7.93; Forecast Maximum Demand (MVA) 2028: 8.05; Forecast Maximum Demand (MVA) 2029: 8.08; Forecast Maximum Demand (MVA) 2030: 8; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
AL | summer | 34.2 | 0 | 30 | 0.96818 | 9.8576 | 0 | 2.6352 | 21.7908 | 24.66 | 25.42 | 25.59 | 25.7 | 25.77 | 22.67 | 23.33 | 23.46 | 23.62 | 23.74 | 100% | 22.67 | 88138.3281 | 89394.4922 | 88797.7734 | 89356.4766 | 90404.3281 | 82.47 | 83.64 | 83.08 | 83.61 | 84.59 | 8760 | 8760 | 8760 | 8760 | 8760 | 71037.9609 | 71750.6016 | 69861.0625 | 70874.1797 | 71816.4922 | 66.47 | 67.13 | 65.37 | 66.31 | 67.2 | 8754.5 | 8754 | 8744.5 | 8745 | 8746 | 76168.0711 | 77043.7687 | 75542.0758 | 76418.8687 | 77392.843 | 71.27 | 72.083 | 70.683 | 71.5 | 72.417
AL | winter | 38.6 | 0 | 30 | 2025: 0.98911; 2025: 9.8576; 2026: 0; 2025: 1.4211; 2025: 17.5759; Forecast Maximum Demand (MVA) 2026: 21; Forecast Maximum Demand (MVA) 2027: 21.47; Forecast Maximum Demand (MVA) 2028: 22.01; Forecast Maximum Demand (MVA) 2029: 22.54; Forecast Maximum Demand (MVA) 2030: 23.01; Forecast Maximum Demand (MVA) 2026: 20.01; Forecast Maximum Demand (MVA) 2027: 20.44; Forecast Maximum Demand (MVA) 2028: 20.94; Forecast Maximum Demand (MVA) 2029: 21.42; Forecast Maximum Demand (MVA) 2030: 21.89; Forecast Maximum Demand (MVA) 2026: 1; Forecast Maximum Demand (MVA) 2026: 20.01
ART | summer | 28.2 | 13.6 | 20 | 0.99234 | 15.7105 | 1.1432 | 1.1153 | 14.978 | 17.27 | 17.37 | 17.19 | 17.06 | 16.92 | 15.04 | 15.04 | 14.97 | 14.91 | 14.77 | 10.59% | 1.44 | 29.99 | 36.27 | 34.4 | 32.36 | 31.74 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 32 | 36 | 36 | 33.5 | 35 | 2.07 | 2.15 | 2.01 | 1.92 | 1.62 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 3 | 2.5 | 2.5 | 10.446 | 12.386 | 11.727 | 11.052 | 10.656 | 0.009 | 0.009 | 0.009 | 0.009 | 0.009
ART | winter | 31.4 | 15.2 | 20 | 2025: 0.99585; 2025: 15.7105; 2026: 1.1432; 2025: 1.1771; 2025: 14.4728; Forecast Maximum Demand (MVA) 2026: 16; Forecast Maximum Demand (MVA) 2027: 15.9; Forecast Maximum Demand (MVA) 2028: 15.86; Forecast Maximum Demand (MVA) 2029: 15.74; Forecast Maximum Demand (MVA) 2030: 15.66; Forecast Maximum Demand (MVA) 2026: 14.98; Forecast Maximum Demand (MVA) 2027: 14.9; Forecast Maximum Demand (MVA) 2028: 14.88; Forecast Maximum Demand (MVA) 2029: 14.82; Forecast Maximum Demand (MVA) 2030: 14.73; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
BAN | summer | 145.4 | 96.4 | 120 | 0.99975 | 63.7025 | 12.9557 | 3.0269 | 90.4455 | 107.42 | 99.74 | 99.69 | 87.8 | 87.8 | 97.7 | 91.47 | 92.21 | 81.15 | 81.37 | 0.013485 | 1.3 | 53.71 | 3.73 | 2.99 | 0 | 0 | 0.08 | 0.01 | 0 | 0 | 0 | 15 | 2 | 1.5 | 0 | 0 | 0.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 16.631 | 1.119 | 0.897 | 0 | 0 | 0.024 | 0.003 | 0 | 0 | 0
BAN | winter | 157.5 | 104.4 | 120 | 2025: 0.99811; 2025: 63.7025; 2026: 12.9557; 2025: 1.3947; 2025: 87.5758; Forecast Maximum Demand (MVA) 2026: 103.49; Forecast Maximum Demand (MVA) 2027: 105.94; Forecast Maximum Demand (MVA) 2028: 95.84; Forecast Maximum Demand (MVA) 2029: 97.64; Forecast Maximum Demand (MVA) 2030: 99.37; Forecast Maximum Demand (MVA) 2026: 96.55; Forecast Maximum Demand (MVA) 2027: 98.61; Forecast Maximum Demand (MVA) 2028: 88.78; Forecast Maximum Demand (MVA) 2029: 90.45; Forecast Maximum Demand (MVA) 2030: 92.09; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
BAS | summer | 116.8 | 76 | 99 | 0.99822 | 116.0329 | 12.7652 | 3.1689 | 89.0786 | 97.3 | 80.87 | 81.9 | 79.15 | 79.86 | 83.65 | 68.76 | 69.31 | 66.43 | 66.6 | 10.07% | 7.65 | 556.04 | 9.26 | 16.72 | 3.55 | 5.7 | 0.4 | 0.01 | 0.01 | 0 | 0 | 81.5 | 4.5 | 9 | 2.5 | 3 | 32.21 | 0 | 0 | 0 | 0 | 0.02 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 189.359 | 2.778 | 5.016 | 1.065 | 1.71 | 0.134 | 0.003 | 0.003 | 0 | 0
BAS | winter | 130.1 | 84.6 | 99 | 2025: 0.99983; 2025: 116.0329; 2026: 12.7652; 2025: 0.96018; 2025: 79.5432; Forecast Maximum Demand (MVA) 2026: 76.89; Forecast Maximum Demand (MVA) 2027: 79.47; Forecast Maximum Demand (MVA) 2028: 78.95; Forecast Maximum Demand (MVA) 2029: 81.66; Forecast Maximum Demand (MVA) 2030: 84.06; Forecast Maximum Demand (MVA) 2026: 73.73; Forecast Maximum Demand (MVA) 2027: 76.31; Forecast Maximum Demand (MVA) 2028: 75.76; Forecast Maximum Demand (MVA) 2029: 78.54; Forecast Maximum Demand (MVA) 2030: 80.91; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
BBD | summer | 92.4 | 45.2 | 66 | 0.954 | 1.0882 | 0 | 4.4502 | 30.2095 | 42.43 | 43.7 | 43.8 | 43.68 | 43.09 | 35.14 | 36.33 | 36.42 | 36.28 | 35.78 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BBD | winter | 99.5 | 49.5 | 66 | 2025: 0.9061; 2025: 1.0882; 2026: 0; 2025: 2.259; 2025: 20.5718; Forecast Maximum Demand (MVA) 2026: 26.61; Forecast Maximum Demand (MVA) 2027: 27.3; Forecast Maximum Demand (MVA) 2028: 27.4; Forecast Maximum Demand (MVA) 2029: 27.21; Forecast Maximum Demand (MVA) 2030: 26.81; Forecast Maximum Demand (MVA) 2026: 22.89; Forecast Maximum Demand (MVA) 2027: 23.54; Forecast Maximum Demand (MVA) 2028: 23.6; Forecast Maximum Demand (MVA) 2029: 23.45; Forecast Maximum Demand (MVA) 2030: 23.07; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
BGO | summer | 77 | 38.5 | 66 | 0.98678 | 21.6087 | 12.4985 | 3.1785 | 44.0086 | 52.85 | 53.53 | 53.62 | 53.81 | 53.69 | 45.29 | 45.37 | 45.17 | 45.02 | 44.69 | 17.64% | 6.79 | 499.14 | 636.58 | 732.66 | 778.13 | 886.98 | 0.24 | 0.31 | 0.35 | 0.37 | 0.43 | 122 | 156.5 | 189.5 | 209 | 247.5 | 60.34 | 67.05 | 65.78 | 61.01 | 58.35 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 27 | 31 | 32 | 30 | 31 | 191.98 | 237.909 | 265.844 | 276.146 | 306.939 | 0.093 | 0.114 | 0.126 | 0.132 | 0.15
BGO | winter | 90.8 | 45.4 | 66 | 2025: 0.99608; 2025: 21.6087; 2026: 12.4985; 2025: 1.2402; 2025: 35.9443; Forecast Maximum Demand (MVA) 2026: 43.25; Forecast Maximum Demand (MVA) 2027: 43.56; Forecast Maximum Demand (MVA) 2028: 43.89; Forecast Maximum Demand (MVA) 2029: 44.09; Forecast Maximum Demand (MVA) 2030: 44.37; Forecast Maximum Demand (MVA) 2026: 40.36; Forecast Maximum Demand (MVA) 2027: 40.61; Forecast Maximum Demand (MVA) 2028: 41.13; Forecast Maximum Demand (MVA) 2029: 41.58; Forecast Maximum Demand (MVA) 2030: 41.99; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
BMH | summer | 38.2 | 19.1 | 27 | 0.981 | 19.1573 | 3.0484 | 2.3438 | 33.1293 | 37.34 | 38.56 | 39.7 | 40.77 | 41.62 | 34 | 35.12 | 36.22 | 37.08 | 37.78 | 78.01% | 14.9 | 5869.0898 | 8002.0498 | 10405.4697 | 12446.04 | 14607.3604 | 9.14 | 12.46 | 16.75 | 22.06 | 30.95 | 1634 | 2046.5 | 2393.5 | 2641.5 | 2846.5 | 2202.6399 | 3154.55 | 4417.8398 | 5438.3799 | 6719.8101 | 3.43 | 4.91 | 6.88 | 8.47 | 10.46 | 726.5 | 978.5 | 1272.5 | 1482.5 | 1717.5 | 3302.5749 | 4608.8 | 6214.1288 | 7540.6779 | 9086.0751 | 5.143 | 7.175 | 9.841 | 12.547 | 16.607
BMH | winter | 40.4 | 20.2 | 27 | 2025: 0.99849; 2025: 19.1573; 2026: 3.0484; 2025: 1.2503; 2025: 24.8175; Forecast Maximum Demand (MVA) 2026: 29.36; Forecast Maximum Demand (MVA) 2027: 30.61; Forecast Maximum Demand (MVA) 2028: 32.05; Forecast Maximum Demand (MVA) 2029: 33.35; Forecast Maximum Demand (MVA) 2030: 34.55; Forecast Maximum Demand (MVA) 2026: 27.66; Forecast Maximum Demand (MVA) 2027: 28.84; Forecast Maximum Demand (MVA) 2028: 30.22; Forecast Maximum Demand (MVA) 2029: 31.44; Forecast Maximum Demand (MVA) 2030: 32.61; Forecast Maximum Demand (MVA) 2026: 0.36931; Forecast Maximum Demand (MVA) 2026: 7.46
CDN | summer | 34.4 | 17.2 | 20 | 0.98482 | 19.982 | 0 | 1.2678 | 12.7875 | 15.61 | 15.74 | 15.74 | 15.74 | 15.6 | 13.88 | 14.01 | 14 | 13.96 | 13.84 | - | - | 0.27 | 0.27 | 0.3 | 0.25 | 0.17 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.081 | 0.081 | 0.09 | 0.075 | 0.051 | 0 | 0 | 0 | 0 | 0
CDN | winter | 36.4 | 18.2 | 20 | 2025: 0.99995; 2025: 19.982; 2026: 0; 2025: 0.22531; 2025: 12.764; Forecast Maximum Demand (MVA) 2026: 18.74; Forecast Maximum Demand (MVA) 2027: 18.75; Forecast Maximum Demand (MVA) 2028: 18.8; Forecast Maximum Demand (MVA) 2029: 18.7; Forecast Maximum Demand (MVA) 2030: 18.55; Forecast Maximum Demand (MVA) 2026: 16.19; Forecast Maximum Demand (MVA) 2027: 16.18; Forecast Maximum Demand (MVA) 2028: 16.25; Forecast Maximum Demand (MVA) 2029: 16.18; Forecast Maximum Demand (MVA) 2030: 16.06; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
CHA | summer | 38.6 | 15.2 | 27 | 0.98472 | 36.5961 | 1.9053 | 13.1927 | 15.6781 | 17.63 | 17.79 | 17.84 | 17.76 | 17.61 | 16.18 | 16.3 | 16.35 | 16.31 | 16.11 | 6.447% | 0.98 | 186.38 | 203.58 | 197.25 | 162.41 | 137.12 | 0.24 | 0.26 | 0.26 | 0.21 | 0.18 | 164.5 | 183 | 182 | 155 | 143 | 71.33 | 67.78 | 59.2 | 48.14 | 33.98 | 0.09 | 0.09 | 0.08 | 0.06 | 0.04 | 34.5 | 34.5 | 33.5 | 30.5 | 24 | 105.845 | 108.52 | 100.615 | 82.421 | 64.922 | 0.135 | 0.141 | 0.134 | 0.105 | 0.082
CHA | winter | 39 | 15.2 | 27 | 2025: 0.99955; 2025: 36.5961; 2026: 1.9053; 2025: 0.54581; 2025: 12.2199; Forecast Maximum Demand (MVA) 2026: 14.23; Forecast Maximum Demand (MVA) 2027: 14.26; Forecast Maximum Demand (MVA) 2028: 14.36; Forecast Maximum Demand (MVA) 2029: 14.3; Forecast Maximum Demand (MVA) 2030: 14.13; Forecast Maximum Demand (MVA) 2026: 13.72; Forecast Maximum Demand (MVA) 2027: 13.74; Forecast Maximum Demand (MVA) 2028: 13.84; Forecast Maximum Demand (MVA) 2029: 13.77; Forecast Maximum Demand (MVA) 2030: 13.61; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
CHM | summer | 36.9 | 0 | 33 | 0.99918 | 1.583 | 0 | 1.3474 | 2.1588 | 2.55 | 2.43 | 2.39 | 2.35 | 2.32 | 2.18 | 2.17 | 2.17 | 2.15 | 2.12 | 100% | 2.18 | 8844.2197 | 8833.0098 | 8739.7803 | 8526.6797 | 8217.1201 | 2.13 | 2.12 | 2.1 | 2.05 | 1.98 | 8746.5 | 8724.5 | 8677.5 | 8594 | 8493.5 | 6721.1001 | 6861.9702 | 6810.8398 | 6628.6499 | 6362.7998 | 1.62 | 1.65 | 1.64 | 1.59 | 1.53 | 8677.5 | 8610 | 8498 | 8350.5 | 8157 | 7358.036 | 7453.2821 | 7389.522 | 7198.0588 | 6919.0959 | 1.773 | 1.791 | 1.778 | 1.728 | 1.665
CHM | winter | 44.1 | 0 | 33 | 2025: 0.95863; 2025: 1.583; 2026: 0; 2025: 1.0956; 2025: 1.9607; Forecast Maximum Demand (MVA) 2026: 2.31; Forecast Maximum Demand (MVA) 2027: 2.28; Forecast Maximum Demand (MVA) 2028: 2.28; Forecast Maximum Demand (MVA) 2029: 2.25; Forecast Maximum Demand (MVA) 2030: 2.21; Forecast Maximum Demand (MVA) 2026: 2.01; Forecast Maximum Demand (MVA) 2027: 1.97; Forecast Maximum Demand (MVA) 2028: 1.97; Forecast Maximum Demand (MVA) 2029: 1.93; Forecast Maximum Demand (MVA) 2030: 1.9; Forecast Maximum Demand (MVA) 2026: 1; Forecast Maximum Demand (MVA) 2026: 2.01
CLC | summer | 101.2 | 49.2 | 79 | 0.99908 | 16.06 | 0 | 2.2307 | 37.8983 | 45.52 | 47.08 | 46.91 | 46.63 | 46.21 | 41.16 | 42.95 | 42.78 | 42.53 | 42.22 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CLC | winter | 112.3 | 54.8 | 79 | 2025: 1; 2025: 16.06; 2026: 0; 2025: 1.4749; 2025: 38.3468; Forecast Maximum Demand (MVA) 2026: 45.68; Forecast Maximum Demand (MVA) 2027: 45.9; Forecast Maximum Demand (MVA) 2028: 45.95; Forecast Maximum Demand (MVA) 2029: 45.94; Forecast Maximum Demand (MVA) 2030: 45.82; Forecast Maximum Demand (MVA) 2026: 43.42; Forecast Maximum Demand (MVA) 2027: 43.69; Forecast Maximum Demand (MVA) 2028: 43.82; Forecast Maximum Demand (MVA) 2029: 43.8; Forecast Maximum Demand (MVA) 2030: 43.69; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
CME | summer | 50.4 | 32.3 | 40.5 | 0.99956 | 42.0785 | 0.53347 | 1.6626 | 39.3138 | 48.31 | 48.74 | 48.71 | 48.57 | 48.28 | 40.99 | 41.32 | 41.34 | 41.27 | 41 | 26.9% | 8.69 | 778.43 | 890.78 | 934.47 | 882.02 | 933.51 | 0.87 | 1 | 1.04 | 0.99 | 1.04 | 198 | 219.5 | 231.5 | 220.5 | 231.5 | 107.7 | 124.61 | 131.32 | 124.62 | 124.37 | 0.12 | 0.14 | 0.15 | 0.14 | 0.14 | 41.5 | 47.5 | 51.5 | 49 | 50.5 | 308.919 | 354.461 | 372.265 | 351.84 | 367.112 | 0.345 | 0.398 | 0.417 | 0.395 | 0.41
CME | winter | 59.4 | 37.3 | 40.5 | 2025: 0.9902; 2025: 42.0785; 2026: 0.53347; 2025: 1.6939; 2025: 27.5197; Forecast Maximum Demand (MVA) 2026: 33.66; Forecast Maximum Demand (MVA) 2027: 33.65; Forecast Maximum Demand (MVA) 2028: 33.81; Forecast Maximum Demand (MVA) 2029: 33.8; Forecast Maximum Demand (MVA) 2030: 33.73; Forecast Maximum Demand (MVA) 2026: 29.95; Forecast Maximum Demand (MVA) 2027: 30.01; Forecast Maximum Demand (MVA) 2028: 30.18; Forecast Maximum Demand (MVA) 2029: 30.24; Forecast Maximum Demand (MVA) 2030: 30.23; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
CMN | summer | 86 | 43 | 66 | 0.99977 | 33.3596 | 0 | 5.9574 | 28.3232 | 31.49 | 31.66 | 31.85 | 31.92 | 31.92 | 28.59 | 28.9 | 29.02 | 29.15 | 29.15 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CMN | winter | 99 | 49.5 | 66 | 2025: 0.99969; 2025: 33.3596; 2026: 0; 2025: 1.1804; 2025: 30.0179; Forecast Maximum Demand (MVA) 2026: 32.2; Forecast Maximum Demand (MVA) 2027: 32.5; Forecast Maximum Demand (MVA) 2028: 32.91; Forecast Maximum Demand (MVA) 2029: 33.25; Forecast Maximum Demand (MVA) 2030: 33.56; Forecast Maximum Demand (MVA) 2026: 30.15; Forecast Maximum Demand (MVA) 2027: 30.34; Forecast Maximum Demand (MVA) 2028: 30.79; Forecast Maximum Demand (MVA) 2029: 31.15; Forecast Maximum Demand (MVA) 2030: 31.43; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
COB | summer | 38.5 | 15 | 26 | 0.89665 | 8.5298 | 1.7147 | 0.41496 | 13.1229 | 16.33 | 16.28 | 16.05 | 15.77 | 15.48 | 14.94 | 14.89 | 14.68 | 14.44 | 14.18 | - | - | 0.83 | 0.67 | 0.43 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.249 | 0.201 | 0.129 | 0.045 | 0 | 0 | 0 | 0 | 0 | 0
COB | winter | 39 | 15 | 26 | 2025: 0.92035; 2025: 8.5298; 2026: 1.7147; 2025: 0.28742; 2025: 12.6401; Forecast Maximum Demand (MVA) 2026: 16.59; Forecast Maximum Demand (MVA) 2027: 16.33; Forecast Maximum Demand (MVA) 2028: 16.1; Forecast Maximum Demand (MVA) 2029: 15.83; Forecast Maximum Demand (MVA) 2030: 15.53; Forecast Maximum Demand (MVA) 2026: 14.38; Forecast Maximum Demand (MVA) 2027: 14.17; Forecast Maximum Demand (MVA) 2028: 13.97; Forecast Maximum Demand (MVA) 2029: 13.74; Forecast Maximum Demand (MVA) 2030: 13.48; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
CRO | summer | 74.7 | 34.3 | 60 | 0.9669 | 6.7197 | 11.4315 | 1.5482 | 34.0587 | 41.94 | 42.56 | 42.67 | 42.8 | 42.49 | 36.5 | 36.95 | 37.15 | 37.25 | 37.01 | 6.414% | 2.2 | 57.47 | 72.96 | 76.37 | 79.67 | 74.94 | 0.04 | 0.05 | 0.05 | 0.05 | 0.05 | 30 | 33.5 | 33.5 | 34 | 35 | 1.43 | 2.11 | 2.42 | 2.73 | 2.29 | 0 | 0 | 0 | 0 | 0 | 1.5 | 1.5 | 1.5 | 2 | 2 | 18.242 | 23.365 | 24.605 | 25.812 | 24.085 | 0.012 | 0.015 | 0.015 | 0.015 | 0.015
CRO | winter | 82.4 | 38 | 60 | 2025: 0.97573; 2025: 6.7197; 2026: 11.4315; 2025: 2.6092; 2025: 31.7537; Forecast Maximum Demand (MVA) 2026: 42.48; Forecast Maximum Demand (MVA) 2027: 42.65; Forecast Maximum Demand (MVA) 2028: 42.94; Forecast Maximum Demand (MVA) 2029: 42.88; Forecast Maximum Demand (MVA) 2030: 42.64; Forecast Maximum Demand (MVA) 2026: 38.19; Forecast Maximum Demand (MVA) 2027: 38.35; Forecast Maximum Demand (MVA) 2028: 38.74; Forecast Maximum Demand (MVA) 2029: 38.74; Forecast Maximum Demand (MVA) 2030: 38.55; Forecast Maximum Demand (MVA) 2026: 0.005; Forecast Maximum Demand (MVA) 2026: 0.19
CTN | summer | 55 | 33.7 | 39.5 | 0.93382 | 19.1698 | 0 | 0.89686 | 21.4306 | 21.37 | 23.98 | 23.97 | 23.86 | 23.6 | 19.99 | 22.53 | 22.53 | 22.43 | 22.18 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CTN | winter | 59.1 | 38.4 | 39.5 | 2025: 0.96239; 2025: 19.1698; 2026: 0; 2025: 0.83154; 2025: 18.1122; Forecast Maximum Demand (MVA) 2026: 23.32; Forecast Maximum Demand (MVA) 2027: 24.17; Forecast Maximum Demand (MVA) 2028: 24.16; Forecast Maximum Demand (MVA) 2029: 23.96; Forecast Maximum Demand (MVA) 2030: 23.66; Forecast Maximum Demand (MVA) 2026: 21.9; Forecast Maximum Demand (MVA) 2027: 22.86; Forecast Maximum Demand (MVA) 2028: 22.82; Forecast Maximum Demand (MVA) 2029: 22.62; Forecast Maximum Demand (MVA) 2030: 22.33; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
DDL | summer | 79.4 | 39.7 | 66 | 0.98598 | 52.4691 | 4.5726 | 6.1468 | 67.3697 | 89.21 | 92.08 | 94.16 | 95.69 | 97.32 | 78.66 | 80.77 | 82.49 | 83.92 | 85.06 | 98.14% | 38.96 | 39477.9219 | 47348.0312 | 54083.3711 | 58510.4219 | 63110.1289 | 114.45 | 229.77 | 356.24 | 456.84 | 652.32 | 2904 | 3080.5 | 3165.5 | 3191.5 | 3225 | 18068.5898 | 22437.6992 | 26472.2305 | 29785.8594 | 32750.1895 | 8.68 | 12.14 | 17.17 | 26.22 | 38.81 | 1947 | 2196.5 | 2390 | 2526.5 | 2617 | 24491.3895 | 29910.7988 | 34755.5727 | 38403.2281 | 41858.1713 | 40.411 | 77.429 | 118.891 | 155.406 | 222.863
DDL | winter | 94.4 | 47.2 | 66 | 2025: 0.99949; 2025: 52.4691; 2026: 4.5726; 2025: 0.87438; 2025: 55.9896; Forecast Maximum Demand (MVA) 2026: 64.79; Forecast Maximum Demand (MVA) 2027: 68.21; Forecast Maximum Demand (MVA) 2028: 72.23; Forecast Maximum Demand (MVA) 2029: 76.25; Forecast Maximum Demand (MVA) 2030: 80.21; Forecast Maximum Demand (MVA) 2026: 62.28; Forecast Maximum Demand (MVA) 2027: 65.56; Forecast Maximum Demand (MVA) 2028: 69.47; Forecast Maximum Demand (MVA) 2029: 73.29; Forecast Maximum Demand (MVA) 2030: 77.04; Forecast Maximum Demand (MVA) 2026: 0.31949; Forecast Maximum Demand (MVA) 2026: 15.08
ECA | summer | 52.8 | 34.6 | 40.5 | 0.98113 | 38.3199 | 4.9537 | 2.2047 | 36.8386 | 39.08 | 39.34 | 39.5 | 39.52 | 39.22 | 35.52 | 35.79 | 35.93 | 35.94 | 35.74 | 2.659% | 0.92 | 16.82 | 20.21 | 23.03 | 23.65 | 20.49 | 0.02 | 0.03 | 0.03 | 0.03 | 0.03 | 11.5 | 14 | 16 | 16 | 14.5 | 0.32 | 0.62 | 0.77 | 0.8 | 0.61 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 5.27 | 6.497 | 7.448 | 7.655 | 6.574 | 0.006 | 0.009 | 0.009 | 0.009 | 0.009
ECA | winter | 60.6 | 40.4 | 40.5 | 2025: 0.98754; 2025: 38.3199; 2026: 4.9537; 2025: 1.3741; 2025: 30.1894; Forecast Maximum Demand (MVA) 2026: 32.83; Forecast Maximum Demand (MVA) 2027: 33.03; Forecast Maximum Demand (MVA) 2028: 33.37; Forecast Maximum Demand (MVA) 2029: 33.63; Forecast Maximum Demand (MVA) 2030: 33.88; Forecast Maximum Demand (MVA) 2026: 30.92; Forecast Maximum Demand (MVA) 2027: 31.12; Forecast Maximum Demand (MVA) 2028: 31.56; Forecast Maximum Demand (MVA) 2029: 31.83; Forecast Maximum Demand (MVA) 2030: 32.02; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
EHK | summer | 72.8 | 36.4 | 54 | 0.99526 | 40.6491 | 17.4521 | 2.5697 | 52.2287 | 63.44 | 66.15 | 66.66 | 67.37 | 67.63 | 57.84 | 60.62 | 61.18 | 61.64 | 61.91 | 58.9% | 21.44 | 4624.48 | 6877.1001 | 8123.79 | 9209.5 | 10272.8398 | 4.85 | 7.21 | 8.51 | 9.65 | 10.77 | 905.5 | 1232 | 1426 | 1595 | 1710 | 1694.11 | 2800.8999 | 3426.3601 | 3841.3601 | 4429.3101 | 1.78 | 2.94 | 3.59 | 4.03 | 4.64 | 366.5 | 578.5 | 692 | 771 | 859 | 2573.221 | 4023.76 | 4835.5891 | 5451.8021 | 6182.369 | 2.701 | 4.221 | 5.066 | 5.716 | 6.479
EHK | winter | 82 | 41 | 54 | 2025: 0.99617; 2025: 40.6491; 2026: 17.4521; 2025: 1.2251; 2025: 45.338; Forecast Maximum Demand (MVA) 2026: 57.18; Forecast Maximum Demand (MVA) 2027: 59.07; Forecast Maximum Demand (MVA) 2028: 60.61; Forecast Maximum Demand (MVA) 2029: 61.98; Forecast Maximum Demand (MVA) 2030: 63.31; Forecast Maximum Demand (MVA) 2026: 55.25; Forecast Maximum Demand (MVA) 2027: 57.27; Forecast Maximum Demand (MVA) 2028: 58.81; Forecast Maximum Demand (MVA) 2029: 60.21; Forecast Maximum Demand (MVA) 2030: 61.51; Forecast Maximum Demand (MVA) 2026: 0.34756; Forecast Maximum Demand (MVA) 2026: 14.25
FNS | summer | 130.8 | 87.2 | 99 | 0.99479 | 41.0865 | 0 | 2.7633 | 44.1871 | 59.54 | 63.21 | 63.87 | 64.18 | 64.34 | 53.47 | 57.12 | 57.66 | 58.09 | 58.23 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FNS | winter | 147.9 | 98.6 | 99 | 2025: 0.99907; 2025: 41.0865; 2026: 0; 2025: 1.3851; 2025: 37.3181; Forecast Maximum Demand (MVA) 2026: 54.6; Forecast Maximum Demand (MVA) 2027: 56.01; Forecast Maximum Demand (MVA) 2028: 57.25; Forecast Maximum Demand (MVA) 2029: 58.11; Forecast Maximum Demand (MVA) 2030: 58.98; Forecast Maximum Demand (MVA) 2026: 52.23; Forecast Maximum Demand (MVA) 2027: 53.69; Forecast Maximum Demand (MVA) 2028: 54.84; Forecast Maximum Demand (MVA) 2029: 55.8; Forecast Maximum Demand (MVA) 2030: 56.67; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
GB | summer | 56.4 | 37.6 | 37.5 | 0.93977 | 2.2964 | 0 | 9.0197 | 15.6137 | 17.39 | 17.42 | 17.32 | 17.22 | 17.1 | 16.28 | 16.29 | 16.16 | 16.05 | 15.94 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GB | winter | 56.4 | 37.6 | 37.5 | 2025: 0.95764; 2025: 2.2964; 2026: 0; 2025: 2.8682; 2025: 13.589; Forecast Maximum Demand (MVA) 2026: 16.93; Forecast Maximum Demand (MVA) 2027: 17.06; Forecast Maximum Demand (MVA) 2028: 17.1; Forecast Maximum Demand (MVA) 2029: 17.09; Forecast Maximum Demand (MVA) 2030: 17.06; Forecast Maximum Demand (MVA) 2026: 15.32; Forecast Maximum Demand (MVA) 2027: 15.31; Forecast Maximum Demand (MVA) 2028: 15.34; Forecast Maximum Demand (MVA) 2029: 15.37; Forecast Maximum Demand (MVA) 2030: 15.39; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
GCY | summer | 75.6 | 37.8 | 66 | 0.98834 | 19.6486 | 16.7663 | 3.3221 | 52.2345 | 56.7 | 56.48 | 55.88 | 55.62 | 54.93 | 49.91 | 49.85 | 49.27 | 48.68 | 48.02 | 32.04% | 12.11 | 1947.49 | 1492.96 | 1071.28 | 920.8 | 889.21 | 0.94 | 0.72 | 0.51 | 0.44 | 0.43 | 383 | 337.5 | 248 | 211.5 | 207.5 | 490.54 | 320.78 | 247.21 | 201.07 | 185.83 | 0.24 | 0.15 | 0.12 | 0.1 | 0.09 | 164 | 99.5 | 73.5 | 61 | 59 | 927.625 | 672.434 | 494.431 | 416.989 | 396.844 | 0.45 | 0.321 | 0.237 | 0.202 | 0.192
GCY | winter | 87.8 | 43.9 | 66 | 2025: 0.99843; 2025: 19.6486; 2026: 16.7663; 2025: 1.9582; 2025: 37.0716; Forecast Maximum Demand (MVA) 2026: 44.18; Forecast Maximum Demand (MVA) 2027: 44.5; Forecast Maximum Demand (MVA) 2028: 44.96; Forecast Maximum Demand (MVA) 2029: 45.39; Forecast Maximum Demand (MVA) 2030: 45.7; Forecast Maximum Demand (MVA) 2026: 40.73; Forecast Maximum Demand (MVA) 2027: 41.1; Forecast Maximum Demand (MVA) 2028: 41.59; Forecast Maximum Demand (MVA) 2029: 42.01; Forecast Maximum Demand (MVA) 2030: 42.44; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
GHP | summer | 99 | 49.5 | 66 | 0.99667 | 20.6932 | 0 | 6.2508 | 34.0033 | 36.05 | 36.77 | 37.4 | 37.96 | 38.26 | 33.45 | 34.17 | 34.79 | 35.29 | 35.58 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GHP | winter | 99 | 49.5 | 66 | 2025: 0.99995; 2025: 20.6932; 2026: 0; 2025: 1.0886; 2025: 26.2146; Forecast Maximum Demand (MVA) 2026: 30.46; Forecast Maximum Demand (MVA) 2027: 31.63; Forecast Maximum Demand (MVA) 2028: 33.04; Forecast Maximum Demand (MVA) 2029: 34.32; Forecast Maximum Demand (MVA) 2030: 35.56; Forecast Maximum Demand (MVA) 2026: 29.59; Forecast Maximum Demand (MVA) 2027: 30.73; Forecast Maximum Demand (MVA) 2028: 32.08; Forecast Maximum Demand (MVA) 2029: 33.35; Forecast Maximum Demand (MVA) 2030: 34.56; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
GL | summer | 102.1 | 47.6 | 80 | 0.99483 | 17.4274 | 17.4522 | 2.8195 | 44.3827 | 49.17 | 50.75 | 50.89 | 51.18 | 51.27 | 45.04 | 46.55 | 46.83 | 46.95 | 46.98 | - | - | 1.6 | 6.5 | 8.09 | 13.25 | 16.41 | 0 | 0.01 | 0.01 | 0.02 | 0.02 | 1.5 | 6 | 7 | 12 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.48 | 1.95 | 2.427 | 3.975 | 4.923 | 0 | 0.003 | 0.003 | 0.006 | 0.006
GL | winter | 116.3 | 47.6 | 80 | 2025: 0.99975; 2025: 17.4274; 2026: 17.4522; 2025: 1.0709; 2025: 34.9254; Forecast Maximum Demand (MVA) 2026: 45.43; Forecast Maximum Demand (MVA) 2027: 46.33; Forecast Maximum Demand (MVA) 2028: 47.53; Forecast Maximum Demand (MVA) 2029: 48.7; Forecast Maximum Demand (MVA) 2030: 49.77; Forecast Maximum Demand (MVA) 2026: 42.71; Forecast Maximum Demand (MVA) 2027: 43.82; Forecast Maximum Demand (MVA) 2028: 45.1; Forecast Maximum Demand (MVA) 2029: 46.32; Forecast Maximum Demand (MVA) 2030: 47.46; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
GLE | summer | 84.3 | 53.3 | 79.5 | 0.9959 | 32.1632 | 6.0968 | 2.1904 | 62.9583 | 68.48 | 71.77 | 73.05 | 74.66 | 76.25 | 62.6 | 65.76 | 66.74 | 67.55 | 68.11 | 17.45% | 9.3 | 432.39 | 816.36 | 976.38 | 1275.04 | 1814.4301 | 0.43 | 0.81 | 0.97 | 1.26 | 1.8 | 94.5 | 150 | 180 | 227.5 | 323.5 | 91.45 | 251.09 | 305.14 | 369.08 | 466.91 | 0.09 | 0.25 | 0.3 | 0.37 | 0.46 | 33 | 67 | 75 | 82 | 103 | 193.732 | 420.671 | 506.512 | 640.868 | 871.166 | 0.192 | 0.418 | 0.501 | 0.637 | 0.862
GLE | winter | 99.1 | 59.1 | 79.5 | 2025: 0.99807; 2025: 32.1632; 2026: 6.0968; 2025: 1.4662; 2025: 50.0902; Forecast Maximum Demand (MVA) 2026: 70.95; Forecast Maximum Demand (MVA) 2027: 71.98; Forecast Maximum Demand (MVA) 2028: 74.43; Forecast Maximum Demand (MVA) 2029: 76.73; Forecast Maximum Demand (MVA) 2030: 79.08; Forecast Maximum Demand (MVA) 2026: 63.97; Forecast Maximum Demand (MVA) 2027: 66.15; Forecast Maximum Demand (MVA) 2028: 68.61; Forecast Maximum Demand (MVA) 2029: 70.74; Forecast Maximum Demand (MVA) 2030: 72.94; Forecast Maximum Demand (MVA) 2026: 0.082403; Forecast Maximum Demand (MVA) 2026: 4.87
GSB | summer | 99 | 49.5 | 66 | 0.99763 | 22.7913 | 0 | 5.4902 | 30.6968 | 33.25 | 33.92 | 34.39 | 34.8 | 35.06 | 29.42 | 30.04 | 30.46 | 30.91 | 31.16 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GSB | winter | 99 | 49.5 | 66 | 2025: 0.99999; 2025: 22.7913; 2026: 0; 2025: 0.90923; 2025: 28.4963; Forecast Maximum Demand (MVA) 2026: 33.37; Forecast Maximum Demand (MVA) 2027: 34.22; Forecast Maximum Demand (MVA) 2028: 35.3; Forecast Maximum Demand (MVA) 2029: 36.25; Forecast Maximum Demand (MVA) 2030: 37.13; Forecast Maximum Demand (MVA) 2026: 31.77; Forecast Maximum Demand (MVA) 2027: 32.6; Forecast Maximum Demand (MVA) 2028: 33.62; Forecast Maximum Demand (MVA) 2029: 34.51; Forecast Maximum Demand (MVA) 2030: 35.34; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
HSM | summer | 59.6 | 39.7 | 40.5 | 0.9923 | 24.5257 | 6.6303 | 3.3033 | 47.667 | 49.52 | 49.73 | 49.28 | 48.9 | 48.2 | 46.34 | 46.47 | 46.22 | 45.87 | 45.26 | 0.16725 | 6.64 | 322.83 | 372.15 | 354.89 | 313.69 | 282.04 | 0.5 | 0.58 | 0.55 | 0.49 | 0.44 | 108 | 127.5 | 125 | 114.5 | 107.5 | 92.64 | 104.67 | 101.25 | 86.36 | 69.89 | 0.14 | 0.16 | 0.16 | 0.13 | 0.11 | 44.5 | 50.5 | 51 | 47 | 42 | 161.697 | 184.914 | 177.342 | 154.559 | 133.535 | 0.248 | 0.286 | 0.277 | 0.238 | 0.209
HSM | winter | 60.6 | 40.4 | 40.5 | 2025: 0.99986; 2025: 24.5257; 2026: 6.6303; 2025: 2.4798; 2025: 36.6219; Forecast Maximum Demand (MVA) 2026: 42.13; Forecast Maximum Demand (MVA) 2027: 42.09; Forecast Maximum Demand (MVA) 2028: 42.27; Forecast Maximum Demand (MVA) 2029: 42.2; Forecast Maximum Demand (MVA) 2030: 42.04; Forecast Maximum Demand (MVA) 2026: 40.3; Forecast Maximum Demand (MVA) 2027: 40.18; Forecast Maximum Demand (MVA) 2028: 40.33; Forecast Maximum Demand (MVA) 2029: 40.3; Forecast Maximum Demand (MVA) 2030: 40.18; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
HTN | summer | 51.7 | 34.2 | 39.5 | 0.99526 | 12.7404 | 0 | 5.0925 | 26.8439 | 27.4 | 27.34 | 27.24 | 27.03 | 26.64 | 25.59 | 25.54 | 25.38 | 25.22 | 24.88 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HTN | winter | 58.1 | 38.4 | 39.5 | 2025: 0.99999; 2025: 12.7404; 2026: 0; 2025: 0.30467; 2025: 22.6635; Forecast Maximum Demand (MVA) 2026: 25.53; Forecast Maximum Demand (MVA) 2027: 25.57; Forecast Maximum Demand (MVA) 2028: 25.73; Forecast Maximum Demand (MVA) 2029: 25.72; Forecast Maximum Demand (MVA) 2030: 25.65; Forecast Maximum Demand (MVA) 2026: 24.71; Forecast Maximum Demand (MVA) 2027: 24.73; Forecast Maximum Demand (MVA) 2028: 24.87; Forecast Maximum Demand (MVA) 2029: 24.85; Forecast Maximum Demand (MVA) 2030: 24.78; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
KRT | summer | 52.5 | 33.4 | 40.5 | 0.99648 | 64.1676 | 3.1627 | 2.88 | 25.7743 | 34.78 | 35.3 | 35.15 | 35.2 | 35.15 | 28.01 | 28.27 | 28.27 | 28.27 | 28.14 | - | - | 1.33 | 2.45 | 1.83 | 1.85 | 1.69 | 0 | 0 | 0 | 0 | 0 | 2 | 3.5 | 2.5 | 3 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.399 | 0.735 | 0.549 | 0.555 | 0.507 | 0 | 0 | 0 | 0 | 0
KRT | winter | 57.8 | 37.6 | 40.5 | 2025: 0.99913; 2025: 64.1676; 2026: 3.1627; 2025: 1.5054; 2025: 25.2621; Forecast Maximum Demand (MVA) 2026: 31.05; Forecast Maximum Demand (MVA) 2027: 31.08; Forecast Maximum Demand (MVA) 2028: 31.29; Forecast Maximum Demand (MVA) 2029: 31.46; Forecast Maximum Demand (MVA) 2030: 31.65; Forecast Maximum Demand (MVA) 2026: 29.16; Forecast Maximum Demand (MVA) 2027: 29.29; Forecast Maximum Demand (MVA) 2028: 29.56; Forecast Maximum Demand (MVA) 2029: 29.72; Forecast Maximum Demand (MVA) 2030: 29.89; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
KYM | summer | 52.6 | 33.8 | 40.5 | 0.97861 | 32.7567 | 0 | 5.9715 | 28.5833 | 30.9 | 31.02 | 30.89 | 30.72 | 30.34 | 28.16 | 28.28 | 28.19 | 27.98 | 27.65 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KYM | winter | 59 | 38.8 | 40.5 | 2025: 0.99299; 2025: 32.7567; 2026: 0; 2025: 1.9682; 2025: 20.7442; Forecast Maximum Demand (MVA) 2026: 22.79; Forecast Maximum Demand (MVA) 2027: 22.91; Forecast Maximum Demand (MVA) 2028: 23.2; Forecast Maximum Demand (MVA) 2029: 23.36; Forecast Maximum Demand (MVA) 2030: 23.5; Forecast Maximum Demand (MVA) 2026: 21.45; Forecast Maximum Demand (MVA) 2027: 21.58; Forecast Maximum Demand (MVA) 2028: 21.84; Forecast Maximum Demand (MVA) 2029: 22.04; Forecast Maximum Demand (MVA) 2030: 22.17; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
LV | summer | 119.7 | 79.8 | 99 | 0.99721 | 82.3784 | 14.2513 | 7.257 | 106.4033 | 131.47 | 130.36 | 132.62 | 135.34 | 137.16 | 117.2 | 116.99 | 119.62 | 121.9 | 123.63 | 46.87% | 37.4 | 16312.9404 | 18613.7305 | 22972.8594 | 26940.9492 | 30293.4707 | 80.77 | 68.88 | 122.16 | 203.66 | 295.65 | 1410.5 | 1643.5 | 1895 | 2067 | 2177 | 2857.76 | 3190.99 | 4448.6001 | 5350.96 | 6593.7002 | 2.06 | 2.3 | 3.21 | 4.85 | 7.97 | 332 | 389 | 517 | 598.5 | 688 | 6894.3141 | 7817.8121 | 10005.8779 | 11827.9567 | 13703.6313 | 25.673 | 22.274 | 38.895 | 64.493 | 94.274
LV | winter | 143.1 | 95.4 | 99 | 2025: 0.99834; 2025: 82.3784; 2026: 14.2513; 2025: 1.7831; 2025: 78.7338; Forecast Maximum Demand (MVA) 2026: 100.94; Forecast Maximum Demand (MVA) 2027: 100.22; Forecast Maximum Demand (MVA) 2028: 105.73; Forecast Maximum Demand (MVA) 2029: 111.12; Forecast Maximum Demand (MVA) 2030: 116.37; Forecast Maximum Demand (MVA) 2026: 96.94; Forecast Maximum Demand (MVA) 2027: 96.64; Forecast Maximum Demand (MVA) 2028: 101.96; Forecast Maximum Demand (MVA) 2029: 107.15; Forecast Maximum Demand (MVA) 2030: 112.32; Forecast Maximum Demand (MVA) 2026: 0.016143; Forecast Maximum Demand (MVA) 2026: 1.54
LVN | summer | 155.7 | 79.7 | 129 | 0.97128 | 19.9175 | 4.9537 | 2.8106 | 68.3553 | 85.44 | 86.61 | 86.34 | 86.01 | 85.43 | 81.21 | 82.58 | 82.35 | 82 | 81.48 | 0.018946 | 1.51 | 11.11 | 17.95 | 16.33 | 13.71 | 10.82 | 0.02 | 0.04 | 0.04 | 0.03 | 0.02 | 6.5 | 9.5 | 9 | 7.5 | 5.5 | 0.33 | 1.67 | 1.46 | 1.1 | 0.75 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 3.564 | 6.554 | 5.921 | 4.883 | 3.771 | 0.006 | 0.012 | 0.012 | 0.009 | 0.006
LVN | winter | 127.7 | 82.5 | 129 | 2025: 0.97715; 2025: 19.9175; 2026: 4.9537; 2025: 2.4473; 2025: 65.8978; Forecast Maximum Demand (MVA) 2026: 85.67; Forecast Maximum Demand (MVA) 2027: 85.64; Forecast Maximum Demand (MVA) 2028: 85.89; Forecast Maximum Demand (MVA) 2029: 85.8; Forecast Maximum Demand (MVA) 2030: 85.46; Forecast Maximum Demand (MVA) 2026: 82.73; Forecast Maximum Demand (MVA) 2027: 82.71; Forecast Maximum Demand (MVA) 2028: 82.89; Forecast Maximum Demand (MVA) 2029: 82.82; Forecast Maximum Demand (MVA) 2030: 82.58; Forecast Maximum Demand (MVA) 2026: 0.0027879; Forecast Maximum Demand (MVA) 2026: 0.23
MBN | summer | 83.2 | 37.6 | 59 | 0.99429 | 25.4432 | 13.7178 | 1.8247 | 48.6133 | 51.29 | 51.8 | 52.03 | 52.1 | 51.87 | 48.66 | 49.18 | 49.44 | 49.59 | 49.4 | 29.41% | 11.06 | 257.15 | 304.24 | 336.2 | 330.42 | 352.03 | 0.23 | 0.27 | 0.3 | 0.3 | 0.32 | 63 | 72 | 80.5 | 80 | 87.5 | 127.37 | 154.07 | 171.99 | 172.42 | 182.07 | 0.11 | 0.14 | 0.15 | 0.15 | 0.16 | 40 | 43.5 | 46.5 | 46 | 50.5 | 166.304 | 199.121 | 221.253 | 219.82 | 233.058 | 0.146 | 0.179 | 0.195 | 0.195 | 0.208
MBN | winter | 80.8 | 40.4 | 59 | 2025: 0.99822; 2025: 25.4432; 2026: 13.7178; 2025: 1.3996; 2025: 28.6302; Forecast Maximum Demand (MVA) 2026: 33.62; Forecast Maximum Demand (MVA) 2027: 33.9; Forecast Maximum Demand (MVA) 2028: 34.2; Forecast Maximum Demand (MVA) 2029: 34.29; Forecast Maximum Demand (MVA) 2030: 34.2; Forecast Maximum Demand (MVA) 2026: 29.62; Forecast Maximum Demand (MVA) 2027: 29.73; Forecast Maximum Demand (MVA) 2028: 29.98; Forecast Maximum Demand (MVA) 2029: 30; Forecast Maximum Demand (MVA) 2030: 29.89; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
MDA | summer | 79.4 | 39.7 | 66 | 0.99996 | 25.4014 | 16.7663 | 2.1046 | 51.3089 | 59.59 | 60.71 | 60.44 | 60.3 | 59.89 | 53.41 | 54.1 | 53.99 | 53.81 | 53.45 | 34.53% | 13.71 | 1016.1 | 1314.1899 | 1471.47 | 1565.3101 | 1739.4399 | 0.49 | 0.63 | 0.71 | 0.75 | 0.84 | 213.5 | 280.5 | 331 | 369.5 | 414.5 | 288.37 | 353.66 | 384.7 | 381.87 | 417.68 | 0.14 | 0.17 | 0.18 | 0.18 | 0.2 | 70 | 87 | 95 | 100.5 | 114.5 | 506.689 | 641.819 | 710.731 | 736.902 | 814.208 | 0.245 | 0.308 | 0.339 | 0.351 | 0.392
MDA | winter | 89.2 | 44.6 | 66 | 2025: 0.99897; 2025: 25.4014; 2026: 16.7663; 2025: 0.73904; 2025: 39.0535; Forecast Maximum Demand (MVA) 2026: 46.93; Forecast Maximum Demand (MVA) 2027: 47.24; Forecast Maximum Demand (MVA) 2028: 47.5; Forecast Maximum Demand (MVA) 2029: 47.58; Forecast Maximum Demand (MVA) 2030: 47.48; Forecast Maximum Demand (MVA) 2026: 44.4; Forecast Maximum Demand (MVA) 2027: 44.46; Forecast Maximum Demand (MVA) 2028: 44.68; Forecast Maximum Demand (MVA) 2029: 44.73; Forecast Maximum Demand (MVA) 2030: 44.65; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
MLN | summer | 119.7 | 79.8 | 99 | 0.99896 | 83.4903 | 10.7837 | 3.9566 | 101.779 | 132.2 | 136.59 | 145.14 | 152.04 | 156.88 | 116.7 | 120.69 | 128.53 | 134.91 | 139.32 | 46.24% | 36.9 | 7956.3101 | 11426.5703 | 19344.0996 | 27817.6309 | 35189.8086 | 63.78 | 147.65 | 461.3 | 841.37 | 1359.01 | 720 | 967.5 | 1466 | 1894.5 | 2179 | 1807.9399 | 2579.0701 | 4967.1802 | 7580.23 | 10456.71 | 1.3 | 2.33 | 21.92 | 89.07 | 186.29 | 180.5 | 265 | 484 | 684.5 | 846 | 3652.451 | 5233.3201 | 9280.256 | 13651.4502 | 17876.6396 | 20.044 | 45.926 | 153.734 | 314.76 | 538.106
MLN | winter | 131.4 | 83.4 | 99 | 2025: 0.99867; 2025: 83.4903; 2026: 10.7837; 2025: 1.4594; 2025: 76.8955; Forecast Maximum Demand (MVA) 2026: 107.44; Forecast Maximum Demand (MVA) 2027: 112.1; Forecast Maximum Demand (MVA) 2028: 124.11; Forecast Maximum Demand (MVA) 2029: 132.16; Forecast Maximum Demand (MVA) 2030: 139.83; Forecast Maximum Demand (MVA) 2026: 100.27; Forecast Maximum Demand (MVA) 2027: 104.71; Forecast Maximum Demand (MVA) 2028: 116.06; Forecast Maximum Demand (MVA) 2029: 123.69; Forecast Maximum Demand (MVA) 2030: 130.84; Forecast Maximum Demand (MVA) 2026: 0.20228; Forecast Maximum Demand (MVA) 2026: 16.87
MNA | summer | 74 | 37 | 66 | 0.97892 | 28.7887 | 13.1002 | 2.8947 | 44.5696 | 49.81 | 50.28 | 50.47 | 50.5 | 50.25 | 46.07 | 46.51 | 46.67 | 46.69 | 46.41 | 24.51% | 9.07 | 308.62 | 361.23 | 389.27 | 379.12 | 399.93 | 0.15 | 0.17 | 0.19 | 0.18 | 0.19 | 89.5 | 103 | 113.5 | 110.5 | 121.5 | 109.48 | 130.19 | 138.72 | 132.95 | 134.25 | 0.05 | 0.06 | 0.07 | 0.06 | 0.06 | 42.5 | 46.5 | 48.5 | 45.5 | 48 | 169.222 | 199.502 | 213.885 | 206.801 | 213.954 | 0.08 | 0.093 | 0.106 | 0.096 | 0.099
MNA | winter | 85 | 42.5 | 66 | 2025: 0.9902; 2025: 28.7887; 2026: 13.1002; 2025: 1.6691; 2025: 31.7883; Forecast Maximum Demand (MVA) 2026: 37.21; Forecast Maximum Demand (MVA) 2027: 37.61; Forecast Maximum Demand (MVA) 2028: 38.17; Forecast Maximum Demand (MVA) 2029: 38.51; Forecast Maximum Demand (MVA) 2030: 38.77; Forecast Maximum Demand (MVA) 2026: 35.66; Forecast Maximum Demand (MVA) 2027: 36; Forecast Maximum Demand (MVA) 2028: 36.57; Forecast Maximum Demand (MVA) 2029: 36.96; Forecast Maximum Demand (MVA) 2030: 37.23; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
MRO | summer | 36.6 | 18.3 | 27 | 1 | 20.4915 | 3.0484 | 7.4008 | 23.1568 | 24.7 | 24.8 | 24.77 | 24.68 | 24.47 | 22.63 | 22.7 | 22.68 | 22.58 | 22.4 | 23.66% | 4.33 | 525.66 | 582.39 | 605.75 | 574.11 | 568.54 | 0.41 | 0.46 | 0.48 | 0.45 | 0.45 | 321 | 356.5 | 372 | 360.5 | 364 | 146.19 | 159.05 | 162.97 | 147.88 | 144.93 | 0.12 | 0.13 | 0.13 | 0.12 | 0.11 | 107.5 | 115 | 118.5 | 110.5 | 111.5 | 260.031 | 286.052 | 295.804 | 275.749 | 272.013 | 0.207 | 0.229 | 0.235 | 0.219 | 0.212
MRO | winter | 40.4 | 20.2 | 27 | 2025: 0.99763; 2025: 20.4915; 2026: 3.0484; 2025: 1.8986; 2025: 19.2923; Forecast Maximum Demand (MVA) 2026: 21.25; Forecast Maximum Demand (MVA) 2027: 21.19; Forecast Maximum Demand (MVA) 2028: 21.23; Forecast Maximum Demand (MVA) 2029: 21.21; Forecast Maximum Demand (MVA) 2030: 21.21; Forecast Maximum Demand (MVA) 2026: 20.21; Forecast Maximum Demand (MVA) 2027: 20.18; Forecast Maximum Demand (MVA) 2028: 20.26; Forecast Maximum Demand (MVA) 2029: 20.31; Forecast Maximum Demand (MVA) 2030: 20.33; Forecast Maximum Demand (MVA) 2026: 0.000495; Forecast Maximum Demand (MVA) 2026: 0.0099991
NHL | summer | 26 | 13 | 20 | 0.99869 | 12.4066 | 0 | 0.7898 | 10.0165 | 15.87 | 15.9 | 15.78 | 15.67 | 15.4 | 12.68 | 12.65 | 12.54 | 12.37 | 12.15 | - | - | 9.17 | 9.17 | 8.46 | 7.72 | 5.92 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 7.5 | 8 | 8.5 | 8.5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.751 | 2.751 | 2.538 | 2.316 | 1.776 | 0.003 | 0.003 | 0.003 | 0.003 | 0.003
NHL | winter | 32.4 | 16.2 | 20 | 2025: 0.99047; 2025: 12.4066; 2026: 0; 2025: 0.25817; 2025: 7.9121; Forecast Maximum Demand (MVA) 2026: 17.8; Forecast Maximum Demand (MVA) 2027: 17.64; Forecast Maximum Demand (MVA) 2028: 17.54; Forecast Maximum Demand (MVA) 2029: 17.3; Forecast Maximum Demand (MVA) 2030: 16.99; Forecast Maximum Demand (MVA) 2026: 12.69; Forecast Maximum Demand (MVA) 2027: 12.56; Forecast Maximum Demand (MVA) 2028: 12.48; Forecast Maximum Demand (MVA) 2029: 12.31; Forecast Maximum Demand (MVA) 2030: 12.08; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
NKA | summer | 48.8 | 30.5 | 39.5 | 0.99181 | 36.7147 | 1.9815 | 3.5605 | 29.3099 | 35.43 | 36.77 | 36.96 | 36.93 | 36.64 | 30.28 | 31.54 | 31.72 | 31.74 | 31.48 | - | - | 70.87 | 165.85 | 184.03 | 173.62 | 166.96 | 0.12 | 0.27 | 0.3 | 0.28 | 0.27 | 49 | 90.5 | 95.5 | 90.5 | 91.5 | 0 | 1.58 | 1.89 | 1.95 | 1.41 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2.5 | 2.5 | 2 | 21.261 | 50.861 | 56.532 | 53.451 | 51.075 | 0.036 | 0.081 | 0.09 | 0.084 | 0.081
NKA | winter | 57.4 | 30.5 | 39.5 | 2025: 0.99925; 2025: 36.7147; 2026: 1.9815; 2025: 1.0235; 2025: 24.9003; Forecast Maximum Demand (MVA) 2026: 29.04; Forecast Maximum Demand (MVA) 2027: 29.25; Forecast Maximum Demand (MVA) 2028: 29.54; Forecast Maximum Demand (MVA) 2029: 29.49; Forecast Maximum Demand (MVA) 2030: 29.35; Forecast Maximum Demand (MVA) 2026: 27.05; Forecast Maximum Demand (MVA) 2027: 27.33; Forecast Maximum Demand (MVA) 2028: 27.56; Forecast Maximum Demand (MVA) 2029: 27.52; Forecast Maximum Demand (MVA) 2030: 27.38; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
OYN | summer | 32 | 15.2 | 27 | 0.96088 | 4.0186 | 0 | 2.6104 | 7.6391 | 8.57 | 8.55 | 8.49 | 8.4 | 8.27 | 7.9 | 7.88 | 7.82 | 7.75 | 7.62 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OYN | winter | 38.8 | 15.2 | 27 | 2025: 0.86602; 2025: 4.0186; 2026: 0; 2025: 0.38628; 2025: 6.2468; Forecast Maximum Demand (MVA) 2026: 8.93; Forecast Maximum Demand (MVA) 2027: 8.85; Forecast Maximum Demand (MVA) 2028: 8.8; Forecast Maximum Demand (MVA) 2029: 8.69; Forecast Maximum Demand (MVA) 2030: 8.55; Forecast Maximum Demand (MVA) 2026: 6.61; Forecast Maximum Demand (MVA) 2027: 6.55; Forecast Maximum Demand (MVA) 2028: 6.52; Forecast Maximum Demand (MVA) 2029: 6.44; Forecast Maximum Demand (MVA) 2030: 6.34; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
PLD | summer | 44.2 | 22.1 | 32 | 0.99707 | 10.6635 | 0 | 2.9807 | 14.1418 | 17.23 | 17.2 | 17.09 | 16.94 | 16.72 | 15.3 | 15.29 | 15.18 | 15.09 | 14.92 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PLD | winter | 48 | 24 | 32 | 2025: 0.99862; 2025: 10.6635; 2026: 0; 2025: 0.88961; 2025: 16.8318; Forecast Maximum Demand (MVA) 2026: 18.75; Forecast Maximum Demand (MVA) 2027: 18.75; Forecast Maximum Demand (MVA) 2028: 18.85; Forecast Maximum Demand (MVA) 2029: 18.88; Forecast Maximum Demand (MVA) 2030: 18.85; Forecast Maximum Demand (MVA) 2026: 18.19; Forecast Maximum Demand (MVA) 2027: 18.19; Forecast Maximum Demand (MVA) 2028: 18.29; Forecast Maximum Demand (MVA) 2029: 18.3; Forecast Maximum Demand (MVA) 2030: 18.27; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
RVL | summer | 32.8 | 20.4 | 19.5 | 0.99622 | 14.5489 | 4.5726 | 1.2437 | 24.9745 | 35.75 | 37.44 | 37.78 | 37.94 | 37.81 | 25.73 | 27.57 | 27.78 | 27.92 | 27.84 | 26.13% | 5.33 | 1411.52 | 2131.6001 | 2273.53 | 2239.46 | 2330.53 | 5.98 | 17.81 | 21.22 | 22.69 | 21.87 | 434.5 | 638 | 668 | 668.5 | 680.5 | 36.08 | 94.59 | 104.11 | 103.38 | 109.04 | 0.06 | 0.15 | 0.17 | 0.17 | 0.18 | 25 | 50 | 54 | 52 | 55.5 | 448.712 | 705.693 | 754.936 | 744.204 | 775.487 | 1.836 | 5.448 | 6.485 | 6.926 | 6.687
RVL | winter | 35.9 | 22.9 | 19.5 | 2025: 0.9951; 2025: 14.5489; 2026: 4.5726; 2025: 4.7778; 2025: 14.4241; Forecast Maximum Demand (MVA) 2026: 25.76; Forecast Maximum Demand (MVA) 2027: 26.74; Forecast Maximum Demand (MVA) 2028: 27; Forecast Maximum Demand (MVA) 2029: 27.03; Forecast Maximum Demand (MVA) 2030: 26.91; Forecast Maximum Demand (MVA) 2026: 22.62; Forecast Maximum Demand (MVA) 2027: 23.43; Forecast Maximum Demand (MVA) 2028: 23.68; Forecast Maximum Demand (MVA) 2029: 23.72; Forecast Maximum Demand (MVA) 2030: 23.57; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
SA | summer | 124.5 | 81.2 | 93 | 0.99419 | 44.6584 | 9.793 | 4.2454 | 88.4674 | 99.75 | 100.48 | 100.74 | 101.05 | 101.15 | 88.69 | 89.8 | 90.2 | 90.67 | 90.96 | 9.224% | 7.49 | 389.71 | 468.47 | 521.34 | 532.04 | 605.8 | 0.41 | 0.49 | 0.55 | 0.56 | 0.64 | 62.5 | 74 | 83 | 85.5 | 96 | 24.39 | 38.85 | 46.15 | 54.28 | 62.11 | 0.03 | 0.04 | 0.05 | 0.06 | 0.07 | 11 | 13 | 15 | 17 | 20 | 133.986 | 167.736 | 188.707 | 197.608 | 225.217 | 0.144 | 0.175 | 0.2 | 0.21 | 0.241
SA | winter | 137.3 | 89.6 | 93 | 2025: 1; 2025: 44.6584; 2026: 9.793; 2025: 1.6604; 2025: 69.0569; Forecast Maximum Demand (MVA) 2026: 81.18; Forecast Maximum Demand (MVA) 2027: 84.07; Forecast Maximum Demand (MVA) 2028: 87.65; Forecast Maximum Demand (MVA) 2029: 91.16; Forecast Maximum Demand (MVA) 2030: 94.51; Forecast Maximum Demand (MVA) 2026: 76.68; Forecast Maximum Demand (MVA) 2027: 79.42; Forecast Maximum Demand (MVA) 2028: 82.88; Forecast Maximum Demand (MVA) 2029: 86.11; Forecast Maximum Demand (MVA) 2030: 89.27; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
SHL | summer | 55.5 | 36.7 | 40.5 | 0.99257 | 32.6326 | 2.8579 | 2.8522 | 42.5597 | 43.18 | 42.96 | 42.54 | 42.04 | 41.33 | 39.29 | 39.12 | 38.76 | 38.32 | 37.66 | 0.070572 | 2.59 | 69.77 | 63.69 | 52.05 | 38.75 | 27.05 | 0.09 | 0.08 | 0.06 | 0.05 | 0.03 | 35.5 | 35.5 | 30.5 | 22.5 | 18 | 3.98 | 3.36 | 2.22 | 1.16 | 0.5 | 0 | 0 | 0 | 0 | 0 | 4 | 4 | 3 | 2 | 1 | 23.717 | 21.459 | 17.169 | 12.437 | 8.465 | 0.027 | 0.024 | 0.018 | 0.015 | 0.009
SHL | winter | 60.6 | 40.4 | 40.5 | 2025: 0.99262; 2025: 32.6326; 2026: 2.8579; 2025: 0.43652; 2025: 28.0336; Forecast Maximum Demand (MVA) 2026: 29.82; Forecast Maximum Demand (MVA) 2027: 29.55; Forecast Maximum Demand (MVA) 2028: 29.35; Forecast Maximum Demand (MVA) 2029: 28.94; Forecast Maximum Demand (MVA) 2030: 28.47; Forecast Maximum Demand (MVA) 2026: 28.36; Forecast Maximum Demand (MVA) 2027: 28.07; Forecast Maximum Demand (MVA) 2028: 27.88; Forecast Maximum Demand (MVA) 2029: 27.52; Forecast Maximum Demand (MVA) 2030: 27.07; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
SHN | summer | 80 | 40 | 66 | 0.99929 | 27.206 | 2.8579 | 2.7653 | 32.4153 | 36.68 | 37.34 | 37.73 | 37.96 | 37.98 | 34.88 | 35.51 | 35.85 | 36.05 | 36.06 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SHN | winter | 88.2 | 44.1 | 66 | 2025: 0.99905; 2025: 27.206; 2026: 2.8579; 2025: 1.1241; 2025: 29.7589; Forecast Maximum Demand (MVA) 2026: 33.26; Forecast Maximum Demand (MVA) 2027: 33.56; Forecast Maximum Demand (MVA) 2028: 34.17; Forecast Maximum Demand (MVA) 2029: 34.65; Forecast Maximum Demand (MVA) 2030: 35.08; Forecast Maximum Demand (MVA) 2026: 31.61; Forecast Maximum Demand (MVA) 2027: 32; Forecast Maximum Demand (MVA) 2028: 32.61; Forecast Maximum Demand (MVA) 2029: 33.04; Forecast Maximum Demand (MVA) 2030: 33.39; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
SHP | summer | 84.9 | 36.6 | 66 | 0.97927 | 39.3347 | 0 | 7.2038 | 21.0326 | 22.92 | 23.01 | 22.97 | 22.88 | 22.68 | 21.66 | 21.75 | 21.71 | 21.62 | 21.43 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SHP | winter | 91.4 | 41.9 | 66 | 2025: 0.99911; 2025: 39.3347; 2026: 0; 2025: 0.96654; 2025: 16.5234; Forecast Maximum Demand (MVA) 2026: 19.38; Forecast Maximum Demand (MVA) 2027: 19.38; Forecast Maximum Demand (MVA) 2028: 19.49; Forecast Maximum Demand (MVA) 2029: 19.49; Forecast Maximum Demand (MVA) 2030: 19.44; Forecast Maximum Demand (MVA) 2026: 18.35; Forecast Maximum Demand (MVA) 2027: 18.34; Forecast Maximum Demand (MVA) 2028: 18.43; Forecast Maximum Demand (MVA) 2029: 18.43; Forecast Maximum Demand (MVA) 2030: 18.39; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
SSE | summer | 131.8 | 89.7 | 99 | 0.98675 | 26.4458 | 0 | 3.0442 | 68.8116 | 84.48 | 83.92 | 83.16 | 82.23 | 80.91 | 72.26 | 72.79 | 72.5 | 72.27 | 71.8 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SSE | winter | 148.5 | 99 | 99 | 2025: 0.99438; 2025: 26.4458; 2026: 0; 2025: 1.8899; 2025: 59.8799; Forecast Maximum Demand (MVA) 2026: 69.63; Forecast Maximum Demand (MVA) 2027: 70.34; Forecast Maximum Demand (MVA) 2028: 71.56; Forecast Maximum Demand (MVA) 2029: 72.37; Forecast Maximum Demand (MVA) 2030: 73.34; Forecast Maximum Demand (MVA) 2026: 65.73; Forecast Maximum Demand (MVA) 2027: 66.72; Forecast Maximum Demand (MVA) 2028: 68.19; Forecast Maximum Demand (MVA) 2029: 69.4; Forecast Maximum Demand (MVA) 2030: 70.52; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: - | 5.63 | 5.6342 | -0.0042043
STL | summer | 37 | 18.5 | 27 | 0.96098 | 17.53 | 4.0772 | 2.134 | 21.936 | 28.88 | 30.04 | 29.78 | 29.5 | 29.12 | 27.07 | 28.17 | 27.9 | 27.64 | 27.28 | 0.46324 | 8.57 | 3733.24 | 7540.73 | 7494.7202 | 7200 | 6819.3301 | 4.94 | 9.97 | 9.91 | 9.52 | 9.02 | 2068.5 | 3196 | 3157.5 | 3045.5 | 2883.5 | 1606.58 | 3648.55 | 3598.1499 | 3428.23 | 3212.76 | 2.12 | 4.83 | 4.76 | 4.53 | 4.25 | 998.5 | 1977 | 1962 | 1906 | 1807 | 2244.578 | 4816.204 | 4767.121 | 4559.761 | 4294.731 | 2.966 | 6.372 | 6.305 | 6.027 | 5.681 | 21.79 | 21.7908 | -0.00077438
STL | winter | 37.6 | 18.8 | 27 | 2025: 0.97662; 2025: 17.53; 2026: 4.0772; 2025: 0.74454; 2025: 19.2262; Forecast Maximum Demand (MVA) 2026: 28.45; Forecast Maximum Demand (MVA) 2027: 28.31; Forecast Maximum Demand (MVA) 2028: 28.11; Forecast Maximum Demand (MVA) 2029: 27.83; Forecast Maximum Demand (MVA) 2030: 27.53; Forecast Maximum Demand (MVA) 2026: 27.32; Forecast Maximum Demand (MVA) 2027: 27.24; Forecast Maximum Demand (MVA) 2028: 27.08; Forecast Maximum Demand (MVA) 2029: 26.84; Forecast Maximum Demand (MVA) 2030: 26.54; Forecast Maximum Demand (MVA) 2026: 0.45319; Forecast Maximum Demand (MVA) 2026: 8.52 | 14.98 | 14.978 | 0.001976
STN | summer | 112.3 | 61.9 | 79 | 0.99722 | 36.8208 | 0.57158 | 2.8409 | 48.0903 | 59.86 | 60.61 | 60.89 | 61.03 | 60.83 | 52.51 | 53.03 | 53.27 | 53.43 | 53.22 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.45 | 90.4455 | 0.0044785
STN | winter | 114.7 | 61.9 | 79 | 2025: 0.97272; 2025: 36.8208; 2026: 0.57158; 2025: 1.5166; 2025: 37.4067; Forecast Maximum Demand (MVA) 2026: 51.35; Forecast Maximum Demand (MVA) 2027: 51.47; Forecast Maximum Demand (MVA) 2028: 51.83; Forecast Maximum Demand (MVA) 2029: 52.01; Forecast Maximum Demand (MVA) 2030: 52.07; Forecast Maximum Demand (MVA) 2026: 45.3; Forecast Maximum Demand (MVA) 2027: 45.57; Forecast Maximum Demand (MVA) 2028: 46.2; Forecast Maximum Demand (MVA) 2029: 46.65; Forecast Maximum Demand (MVA) 2030: 47.04; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: - | 89.08 | 89.0786 | 0.0013962
SU | summer | 139.5 | 93 | 99 | 0.98809 | 41.8716 | 22.1772 | 3.5023 | 88.278 | 109.12 | 113.06 | 114.47 | 115.33 | 115.86 | 97.15 | 100.85 | 101.6 | 101.9 | 102.25 | 0.044624 | 4.15 | 179.35 | 354.73 | 457.7 | 513.86 | 630.72 | 0.13 | 0.26 | 0.33 | 0.37 | 0.45 | 36.5 | 54.5 | 68 | 74.5 | 92.5 | 3.86 | 19.6 | 27.9 | 32.82 | 38.89 | 0 | 0.01 | 0.02 | 0.02 | 0.03 | 1.5 | 9 | 10.5 | 11.5 | 13 | 56.507 | 120.139 | 156.84 | 177.132 | 216.439 | 0.039 | 0.085 | 0.113 | 0.125 | 0.156 | 30.21 | 30.2095 | 0.00047112
SU | winter | 148.5 | 99 | 99 | 2025: 0.99823; 2025: 41.8716; 2026: 22.1772; 2025: 2.036; 2025: 75.9062; Forecast Maximum Demand (MVA) 2026: 90.35; Forecast Maximum Demand (MVA) 2027: 94.51; Forecast Maximum Demand (MVA) 2028: 96.67; Forecast Maximum Demand (MVA) 2029: 98.87; Forecast Maximum Demand (MVA) 2030: 100.72; Forecast Maximum Demand (MVA) 2026: 87.04; Forecast Maximum Demand (MVA) 2027: 91.09; Forecast Maximum Demand (MVA) 2028: 93.29; Forecast Maximum Demand (MVA) 2029: 95.29; Forecast Maximum Demand (MVA) 2030: 97.28; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: - | 44.01 | 44.0086 | 0.0013657
TNA | summer | 142.8 | 95.2 | 99 | 0.99515 | 111.7199 | 32.1988 | 2.4477 | 128.8869 | 165.57 | 122.91 | 131.75 | 135.14 | 137.7 | 143.06 | 109.21 | 117.88 | 120.56 | 122.98 | 50.27% | 47.86 | 10629.3799 | 729.58 | 1795.2 | 2223.03 | 2989.77 | 182.45 | 0.35 | 0.86 | 1.07 | 1.44 | 770 | 84.5 | 174.5 | 214 | 281 | 2438.4199 | 128.05 | 464.31 | 620.81 | 878.76 | 1.26 | 0.06 | 0.22 | 0.3 | 0.42 | 197.5 | 23.5 | 66 | 74 | 99.5 | 4895.7079 | 308.509 | 863.577 | 1101.476 | 1512.063 | 55.617 | 0.147 | 0.412 | 0.531 | 0.726 | 33.13 | 33.1293 | 0.00067902
TNA | winter | 142.8 | 95.2 | 99 | 2025: 0.99903; 2025: 111.7199; 2026: 32.1988; 2025: 1.644; 2025: 100.1327; Forecast Maximum Demand (MVA) 2026: 149.51; Forecast Maximum Demand (MVA) 2027: 118.54; Forecast Maximum Demand (MVA) 2028: 126.5; Forecast Maximum Demand (MVA) 2029: 132.93; Forecast Maximum Demand (MVA) 2030: 138.73; Forecast Maximum Demand (MVA) 2026: 134.71; Forecast Maximum Demand (MVA) 2027: 109.52; Forecast Maximum Demand (MVA) 2028: 116.67; Forecast Maximum Demand (MVA) 2029: 122.54; Forecast Maximum Demand (MVA) 2030: 127.87; Forecast Maximum Demand (MVA) 2026: 0.41502; Forecast Maximum Demand (MVA) 2026: 39.51 | 12.79 | 12.7875 | 0.0024891
TQY | summer | 99 | 49.5 | 66 | 0.99997 | 27.5025 | 3.8105 | 6.2336 | 36.2545 | 53.29 | 54.92 | 55.79 | 56.58 | 57.1 | 46.52 | 47.66 | 48.33 | 48.97 | 49.38 | - | - | 14.16 | 41.67 | 73.23 | 105.55 | 147.42 | 0.03 | 0.09 | 0.16 | 0.23 | 0.32 | 10 | 24 | 37.5 | 46 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.248 | 12.501 | 21.969 | 31.665 | 44.226 | 0.009 | 0.027 | 0.048 | 0.069 | 0.096 | 15.68 | 15.6781 | 0.0018768
TQY | winter | 99 | 49.5 | 66 | 2025: 0.99507; 2025: 27.5025; 2026: 3.8105; 2025: 0.97697; 2025: 29.9609; Forecast Maximum Demand (MVA) 2026: 40.51; Forecast Maximum Demand (MVA) 2027: 41.2; Forecast Maximum Demand (MVA) 2028: 42.22; Forecast Maximum Demand (MVA) 2029: 43.02; Forecast Maximum Demand (MVA) 2030: 43.71; Forecast Maximum Demand (MVA) 2026: 38.21; Forecast Maximum Demand (MVA) 2027: 38.85; Forecast Maximum Demand (MVA) 2028: 39.8; Forecast Maximum Demand (MVA) 2029: 40.61; Forecast Maximum Demand (MVA) 2030: 41.3; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: - | 2.16 | 2.1588 | 0.0011649
TRG | summer | 58.3 | 19.2 | 46.5 | 0.98177 | 21.2381 | 5.1442 | 1.19 | 16.5381 | 19.62 | 19.85 | 19.92 | 19.97 | 19.74 | 17.89 | 18.11 | 18.2 | 18.25 | 18.08 | - | - | 1.45 | 1.73 | 2.05 | 2.04 | 1.6 | 0 | 0 | 0 | 0 | 0 | 1.5 | 2 | 2 | 2 | 2 | 0.37 | 0.41 | 0.51 | 0.48 | 0.39 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.694 | 0.806 | 0.972 | 0.948 | 0.753 | 0 | 0 | 0 | 0 | 0 | 37.9 | 37.8983 | 0.0017433
TRG | winter | 58.8 | 19.4 | 46.5 | 2025: 1; 2025: 21.2381; 2026: 5.1442; 2025: 0.26115; 2025: 17.3067; Forecast Maximum Demand (MVA) 2026: 21.75; Forecast Maximum Demand (MVA) 2027: 21.82; Forecast Maximum Demand (MVA) 2028: 22.05; Forecast Maximum Demand (MVA) 2029: 21.98; Forecast Maximum Demand (MVA) 2030: 21.77; Forecast Maximum Demand (MVA) 2026: 20.2; Forecast Maximum Demand (MVA) 2027: 20.28; Forecast Maximum Demand (MVA) 2028: 20.48; Forecast Maximum Demand (MVA) 2029: 20.41; Forecast Maximum Demand (MVA) 2030: 20.23; Forecast Maximum Demand (MVA) 2026: 0.041237; Forecast Maximum Demand (MVA) 2026: 0.8 | 39.31 | 39.3138 | -0.0037842
WBE | summer | 123.7 | 82.8 | 99 | 0.9957 | 103.2202 | 8.7642 | 4.3071 | 126.8086 | 144.96 | 131.02 | 133.88 | 136.53 | 138.87 | 132.11 | 120 | 122.05 | 124.15 | 126.06 | 59.55% | 49.31 | 17174.9395 | 7761 | 10726.1699 | 13236.6201 | 16948.4902 | 285.3 | 17.45 | 42.75 | 85.18 | 147.51 | 1393 | 777 | 1013.5 | 1217 | 1461.5 | 4125.6802 | 1794.54 | 2370.6799 | 2911.03 | 3885.3501 | 16.31 | 1.29 | 1.71 | 2.14 | 4.21 | 383 | 181.5 | 253 | 314.5 | 409.5 | 8040.458 | 3584.478 | 4877.3269 | 6008.7071 | 7804.2921 | 97.007 | 6.138 | 14.022 | 27.052 | 47.2 | 28.32 | 28.3232 | -0.0031662
WBE | winter | 137.3 | 92.2 | 99 | 2025: 0.99975; 2025: 103.2202; 2026: 8.7642; 2025: 1.6834; 2025: 87.9351; Forecast Maximum Demand (MVA) 2026: 142.08; Forecast Maximum Demand (MVA) 2027: 133.5; Forecast Maximum Demand (MVA) 2028: 139.16; Forecast Maximum Demand (MVA) 2029: 144.49; Forecast Maximum Demand (MVA) 2030: 149.97; Forecast Maximum Demand (MVA) 2026: 101.37; Forecast Maximum Demand (MVA) 2027: 93.01; Forecast Maximum Demand (MVA) 2028: 98.2; Forecast Maximum Demand (MVA) 2029: 103.3; Forecast Maximum Demand (MVA) 2030: 108.39; Forecast Maximum Demand (MVA) 2026: 0.099458; Forecast Maximum Demand (MVA) 2026: 9.17 | 13.12 | 13.1229 | -0.0029011
WBL | summer | 82 | 49.2 | 79.5 | 0.98679 | 18.4301 | 8.7642 | 6.1131 | 46.5349 | 57.54 | 57.46 | 56.86 | 56.33 | 55.92 | 51.56 | 51.6 | 51.45 | 51.17 | 50.76 | 0.047968 | 2.36 | 165.98 | 186.92 | 162.97 | 130.55 | 121.1 | 0.54 | 0.61 | 0.53 | 0.42 | 0.39 | 71.5 | 81 | 76.5 | 66 | 65 | 2.59 | 3.27 | 3.06 | 2.42 | 1.67 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 2.5 | 3 | 3.5 | 2.5 | 2 | 51.607 | 58.365 | 51.033 | 40.859 | 37.499 | 0.169 | 0.19 | 0.166 | 0.133 | 0.124 | 34.06 | 34.0587 | 0.001255
WBL | winter | 90.7 | 54.8 | 79.5 | 2025: 0.99878; 2025: 18.4301; 2026: 8.7642; 2025: 1.2857; 2025: 49.2065; Forecast Maximum Demand (MVA) 2026: 56.15; Forecast Maximum Demand (MVA) 2027: 56.49; Forecast Maximum Demand (MVA) 2028: 57.19; Forecast Maximum Demand (MVA) 2029: 57.85; Forecast Maximum Demand (MVA) 2030: 58.33; Forecast Maximum Demand (MVA) 2026: 52.3; Forecast Maximum Demand (MVA) 2027: 52.68; Forecast Maximum Demand (MVA) 2028: 53.24; Forecast Maximum Demand (MVA) 2029: 53.81; Forecast Maximum Demand (MVA) 2030: 54.31; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: - | 21.43 | 21.4306 | -0.00061417
WIN | summer | 29.7 | 10.5 | 20.5 | 0.93591 | 12.7618 | 0 | 5.459 | 10.3999 | 11.19 | 11.29 | 11.34 | 11.37 | 11.34 | 10.53 | 10.58 | 10.6 | 10.62 | 10.57 | 0.2857% | 0.03 | 0.09 | 0.24 | 0.5 | 0.73 | 0.83 | 0 | 0 | 0 | 0 | 0 | 1.5 | 2 | 4 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.027 | 0.072 | 0.15 | 0.219 | 0.249 | 0 | 0 | 0 | 0 | 0 | 67.37 | 67.3697 | 0.00030518
WIN | winter | 30.7 | 10.5 | 20.5 | 2025: 0.90717; 2025: 12.7618; 2026: 0; 2025: 2.3954; 2025: 9.9026; Forecast Maximum Demand (MVA) 2026: 11.18; Forecast Maximum Demand (MVA) 2027: 11.27; Forecast Maximum Demand (MVA) 2028: 11.42; Forecast Maximum Demand (MVA) 2029: 11.49; Forecast Maximum Demand (MVA) 2030: 11.55; Forecast Maximum Demand (MVA) 2026: 10.41; Forecast Maximum Demand (MVA) 2027: 10.49; Forecast Maximum Demand (MVA) 2028: 10.64; Forecast Maximum Demand (MVA) 2029: 10.72; Forecast Maximum Demand (MVA) 2030: 10.77; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: - | 36.84 | 36.8386 | 0.0014
WMN | summer | 33 | 17.2 | 46.5 | 0.92358 | 7.2348 | 5.3347 | 6.0762 | 21.9257 | 28.12 | 28.48 | 28.62 | 28.61 | 28.3 | 25.56 | 25.87 | 26.01 | 26 | 25.71 | 48.6% | 8.36 | 955.28 | 1064.95 | 1113.0699 | 1065.64 | 1034.54 | 0.46 | 0.51 | 0.53 | 0.51 | 0.5 | 403.5 | 436.5 | 452 | 440 | 428.5 | 245.69 | 276.58 | 293.19 | 277.8 | 270.18 | 0.12 | 0.13 | 0.14 | 0.13 | 0.13 | 127.5 | 134.5 | 138.5 | 130.5 | 134 | 458.567 | 513.091 | 539.154 | 514.152 | 499.488 | 0.222 | 0.244 | 0.257 | 0.244 | 0.241 | 52.23 | 52.2287 | 0.0013123
WMN | winter | 33 | 20.2 | 46.5 | 2025: 0.92077; 2025: 7.2348; 2026: 5.3347; 2025: 1.5859; 2025: 19.7298; Forecast Maximum Demand (MVA) 2026: 23.01; Forecast Maximum Demand (MVA) 2027: 23.07; Forecast Maximum Demand (MVA) 2028: 23.26; Forecast Maximum Demand (MVA) 2029: 23.13; Forecast Maximum Demand (MVA) 2030: 22.83; Forecast Maximum Demand (MVA) 2026: 20.36; Forecast Maximum Demand (MVA) 2027: 20.42; Forecast Maximum Demand (MVA) 2028: 20.57; Forecast Maximum Demand (MVA) 2029: 20.43; Forecast Maximum Demand (MVA) 2030: 20.17; Forecast Maximum Demand (MVA) 2026: 0.0079208; Forecast Maximum Demand (MVA) 2026: 0.16 | 44.19 | 44.1871 | 0.0029106
WND | summer | 76.6 | 37.5 | 66 | 0.99881 | 24.5774 | 1.1432 | 4.4397 | 24.2955 | 31.18 | 33.42 | 34.12 | 34.7 | 35.11 | 26.07 | 28.28 | 28.93 | 29.53 | 29.94 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.61 | 15.6137 | -0.0036716
WND | winter | 86.4 | 42.7 | 66 | 2025: 0.9988; 2025: 24.5774; 2026: 1.1432; 2025: 1.0123; 2025: 29.0982; Forecast Maximum Demand (MVA) 2026: 38.9; Forecast Maximum Demand (MVA) 2027: 40.1; Forecast Maximum Demand (MVA) 2028: 41.12; Forecast Maximum Demand (MVA) 2029: 41.99; Forecast Maximum Demand (MVA) 2030: 42.74; Forecast Maximum Demand (MVA) 2026: 33.68; Forecast Maximum Demand (MVA) 2027: 34.87; Forecast Maximum Demand (MVA) 2028: 35.94; Forecast Maximum Demand (MVA) 2029: 36.74; Forecast Maximum Demand (MVA) 2030: 37.44; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: - | 52.23 | 52.2345 | -0.0045395
WPD | summer | 96.5 | 56.8 | 79.5 | 0.99614 | 40.8707 | 0.7621 | 6.3989 | 58.8089 | 66 | 67.45 | 68.37 | 69.95 | 71.09 | 58.28 | 60.04 | 61.36 | 62.87 | 64.1 | 0.026056 | 1.48 | 143.6 | 217.71 | 285.04 | 402.19 | 578.17 | 0.15 | 0.22 | 0.29 | 0.41 | 0.59 | 45.5 | 61 | 78.5 | 108.5 | 148.5 | 1.51 | 7.21 | 18.81 | 42.78 | 77.61 | 0 | 0.01 | 0.02 | 0.04 | 0.08 | 1.5 | 7 | 12.5 | 20.5 | 33.5 | 44.137 | 70.36 | 98.679 | 150.603 | 227.778 | 0.045 | 0.073 | 0.101 | 0.151 | 0.233 | 34 | 34.0033 | -0.0032845
WPD | winter | 106.2 | 62.6 | 79.5 | 2025: 0.99977; 2025: 40.8707; 2026: 0.7621; 2025: 1.0629; 2025: 45.8935; Forecast Maximum Demand (MVA) 2026: 54.58; Forecast Maximum Demand (MVA) 2027: 57.45; Forecast Maximum Demand (MVA) 2028: 60.68; Forecast Maximum Demand (MVA) 2029: 63.83; Forecast Maximum Demand (MVA) 2030: 66.92; Forecast Maximum Demand (MVA) 2026: 51.84; Forecast Maximum Demand (MVA) 2027: 54.65; Forecast Maximum Demand (MVA) 2028: 57.8; Forecast Maximum Demand (MVA) 2029: 60.9; Forecast Maximum Demand (MVA) 2030: 63.92; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: - | 44.38 | 44.3827 | -0.0027275
[62 empty] | 62.96 | 62.9583 | 0.0017433
[62 empty] | 30.7 | 30.6968 | 0.0031967
[62 empty] | 47.67 | 47.667 | 0.0030365
[62 empty] | 26.84 | 26.8439 | -0.0038528
[62 empty] | 25.77 | 25.7743 | -0.0042686
[62 empty] | 28.58 | 28.5833 | -0.0033379
[62 empty] | 106.4 | 106.4033 | -0.0033264
[62 empty] | 68.36 | 68.3553 | 0.0047073
[62 empty] | 48.61 | 48.6133 | -0.0033264
[62 empty] | 51.31 | 51.3088 | 0.001152
[62 empty] | 101.78 | 101.779 | 0.00099182
[62 empty] | 44.57 | 44.5696 | 0.0004158
[62 empty] | 23.16 | 23.1568 | 0.0032387
[62 empty] | 10.02 | 10.0165 | 0.0035048
[62 empty] | 29.31 | 29.3099 | 6.2943e-05
[62 empty] | 7.64 | 7.6391 | 0.00092745
[62 empty] | 14.14 | 14.1418 | -0.00177
[62 empty] | 24.97 | 24.9745 | -0.0044556
[62 empty] | 88.47 | 4.2871 | 84.1829
[62 empty] | 42.56 | 42.5597 | 0.0002594
[62 empty] | 32.42 | 32.4153 | 0.0047073
[62 empty] | 21.03 | 21.0326 | -0.0026016
[62 empty] | 68.81 | 68.8116 | -0.0015564
[62 empty] | 21.94 | 21.936 | 0.0040245
[62 empty] | 48.09 | 48.0903 | -0.00033569
[62 empty] | 88.28 | 88.278 | 0.002037
[62 empty] | 128.89 | 128.8869 | 0.003067
[62 empty] | 36.25 | 36.2545 | -0.004467
[62 empty] | 16.54 | 16.5381 | 0.0018654
[62 empty] | 126.81 | 126.8086 | 0.001442
[62 empty] | 46.53 | 46.5349 | -0.0049095
[62 empty] | 10.4 | 10.3999 | 0.00010586
[62 empty] | 21.93 | 21.9257 | 0.0043411
[62 empty] | 24.3 | 24.2955 | 0.0044975
[62 empty] | 58.81 | 58.8089 | 0.0011024
[62 empty] | 5.7569 | 5.7569 | -3.4796e-08
[62 empty] | 17.5759 | 17.5759 | -5.0659e-08
[62 empty] | 14.4728 | 14.4728 | 1.8127e-07
[62 empty] | 87.5758 | 87.5758 | -9.2285e-07
[62 empty] | 79.5431 | 79.5432 | -1.8555e-06
[62 empty] | 20.5718 | 20.5718 | 1.0034e-07
[62 empty] | 35.9443 | 35.9443 | 1.283e-06
[62 empty] | 24.8175 | 24.8175 | -2.7258e-07
[62 empty] | 12.764 | 12.764 | 2.0801e-07
[62 empty] | 12.2199 | 12.2199 | 1.084e-07
[62 empty] | 1.9607 | 1.9607 | 5.0766e-08
[62 empty] | 38.3468 | 38.3468 | 3.8916e-07
[62 empty] | 27.5197 | 27.5197 | -1.8933e-07
[62 empty] | 30.0179 | 29.9719 | 0.046045
[62 empty] | 12.6401 | 12.6401 | 2.9724e-07
[62 empty] | 31.7537 | 31.7537 | 3.5388e-07
[62 empty] | 18.1122 | 18.1122 | 4.2114e-07
[62 empty] | 55.9896 | 55.9896 | 1.2354e-06
[62 empty] | 30.1894 | 30.1894 | 1.4978e-07
[62 empty] | 45.338 | 45.338 | -2.7588e-08
[62 empty] | 37.3181 | 37.3181 | -8.7402e-08
[62 empty] | 13.589 | 13.589 | 4.3707e-07
[62 empty] | 37.0716 | 37.0716 | -1.4648e-08
[62 empty] | 26.2146 | 26.2146 | -4.9756e-07
[62 empty] | 34.9254 | 34.9254 | 1.0791e-07
[62 empty] | 50.0902 | 50.0902 | 5.5664e-07
[62 empty] | 28.4963 | 28.4963 | 1.0938e-07
[62 empty] | 36.6219 | 36.6219 | 9.0088e-08
[62 empty] | 22.6635 | 22.6635 | 4.0747e-07
[62 empty] | 25.2621 | 25.2621 | -1.4624e-07
[62 empty] | 20.7442 | 20.7442 | -3.0872e-07
[62 empty] | 78.7338 | 78.7338 | 2.981e-06
[62 empty] | 65.8978 | 65.8978 | -1.8896e-06
[62 empty] | 28.6302 | 28.6302 | -1.001e-07
[62 empty] | 39.0535 | 39.0535 | 1.7822e-08
[62 empty] | 76.8955 | 76.8955 | 1.6699e-06
[62 empty] | 31.7883 | 31.7883 | -9.5032e-07
[62 empty] | 19.2923 | 19.2923 | 4.8975e-07
[62 empty] | 7.9121 | 7.9121 | 9.1858e-09
[62 empty] | 24.9003 | 24.9003 | 3.3667e-07
[62 empty] | 6.2468 | 6.2468 | -3.8953e-08
[62 empty] | 16.8318 | 16.8318 | 1.1426e-07
[62 empty] | 14.4241 | 14.4241 | 2.2479e-07
[62 empty] | 69.0569 | 2.8783 | 66.1786
[62 empty] | 28.0336 | 28.0336 | -2.0496e-07
[62 empty] | 29.7589 | 29.7589 | 7.2021e-07
[62 empty] | 16.5234 | 16.5234 | -1.8898e-06
[62 empty] | 59.8799 | 59.8799 | -1.4478e-07
[62 empty] | 19.2262 | 19.2262 | 8.0567e-09
[62 empty] | 37.4066 | 37.4066 | 3.2715e-06
[62 empty] | 75.9062 | 75.9062 | 1.0352e-06
[62 empty] | 100.1327 | 100.1327 | -3.3179e-06
[62 empty] | 29.9609 | 29.9609 | -1.6772e-07
[62 empty] | 17.3067 | 17.3067 | 2.4719e-07
[62 empty] | 87.9351 | 87.9351 | 3.2593e-06
[62 empty] | 49.2065 | 49.2065 | 8.4595e-07
[62 empty] | 9.9026 | 9.9026 | -2.002e-08
[62 empty] | 19.7298 | 19.7298 | -4.176e-07
[62 empty] | 29.0982 | 29.0982 | 4.8792e-07
[62 empty] | 45.8935 | 45.8935 | -7.6416e-07