## Intro
Powercor 2025 Distribution System Limitation Template
This Distribution Systems Limitations template is intended to make the Distribution Annual Planning Report (DAPR) limitation data more accessible and usable. Any information provided in this System Limitations template should be read in conjunction with the Powercor 2025 DAPR. It should also be noted that the information in this template and the DAPR are based on high-level risk assessments produced for the DAPR. As such the numbers are indicative and subject to change. Therefore the information in this template should not be used to make investment decisions, and should only be used to assist in discussions with Powercor. Finalised data will be produced in a detailed risk assessment conducted at the RIT-D or business case stage. However Powercor invites interested parties to submit their proposals or to engage in joint planning with Powercor as early as possible in order to defer or avoid the proposed augmentation. Powercor also publishes its own Network Limitation maps in order to assist with the visualisation of the limitation data presented within this template and the DAPR. The data in this template will be updated annually and will be published along with the DAPR. We welcome any feedback to improve the content or usability of this template.

## Powercor Limitations
Owner | Asset Name | Project Name | Asset Code | Network Element | Voltage level (kV) | Rating | [5 empty] | Nameplate Rating | Location |  |  |  | Residential customers affected |  | Business Case | [7 empty] | Demand Reduction required to defer investment by 1 year |  | Emergency Generation |  | Load Transfer capability (MVA) | Power Factor | 10% POE | [14 empty] | 50% POE | [14 empty] | Weighted Expected Energy at Risk (MWh)
[6 empty] | Summer |  |  | Winter |  |  |  | Start |  | End |  |  |  | Constraint Primary Driver | Investment Description | Preferred network investment |  |  |  | Proposed Timing | Annual Deferral Value | [6 empty] | Forecast Minimum Demand (MVA) |  |  |  |  | Maximum Load at risk (MVA) (N-1) |  |  |  |  | Maximum Load at risk (MVA) (N-2) |  |  |  |  | Forecast Minimum Demand (MVA) |  |  |  |  | Maximum Load at risk (MVA) (N-1) |  |  |  |  | Maximum Load at risk (MVA) (N-2)
[6 empty] | N Rating (MVA) | N-1 Rating (MVA) | N-2 Rating (MVA) | N Rating (MVA) | N-1 Rating (MVA) | N-2 Rating (MVA) |  | Longitude | Latitude | Longitude | Latitude | Count | Percent |  |  | capital cost ($) | cost accuracy plus | cost accuracy minus | Operating cost ($) |  |  | (MW) | (MVA) | (MW) | (MVA) |  |  | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030
Note on AD1: Lin, Tim: E.g. contracting backup generators in a hospital to become embedded generators during unuasually high peaks
Note on AA2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Lee Conrad, Angelo use WACC value of 3.5% I left the formula below
Note on Y3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Lee Conrad, Angelo this is 1% of total cost , I left the formula below

## Sub-T Aug Sum
Sub transmission line | Season | Line N Import Rating (MVA) | Line Power Factor at Minimum Demand | Embedded Generation Capacity (MVA) | Load Transfer Capability (MVA) | Hours load is > 95% of Minimum Demand (Hrs) | Actual Minimum Demand (MVA) | 50% POE |  |  |  |  | 50% POE load above N Import Rating (%) | 50% POE load above N Import Rating (MVA) | 50% POE
[8 empty] | Forecast Minimum Demand (MVA) | [6 empty] | Energy at Risk (MWh) |  |  |  |  | Expected Energy at Risk (MWh) |  |  |  |  | Hours at Risk (Hrs)
|  |  | 2025 | 2025 | 2026 | 2025 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2026 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030
ATS-ATD | S | 102.3 | 0.99502 | 0 | - | - | 0 | 4.9 | 28.7 | 54.4 | 62 | 70.6618 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ATS-ATD | W | 130.3 | 0.99502 | 0 | - | - | 0.99 | 13.8 | 43.9 | 60.3 | 62 | 63.7479 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-NRB | S | 52.6 | 0.85944 | 0 | - | - | 34.2 | 82.7 | 82.8 | 82.7 | 82.7 | 82.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-NRB | W | 52.6 | 0.85944 | 0 | - | - | 35.78 | 82.8 | 82.5 | 82.8 | 82.8 | 82.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GTS-GHP | S | 74.3 | 0.98936 | 20.6932 | - | - | 16.38 | 39.6 | 42.1 | 44.6 | 46.6 | 48.6897 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GTS-GHP | W | 87.5 | 0.98936 | 20.6932 | - | - | 14.6 | 37.5 | 39.9 | 41.8 | 43.7 | 45.6864 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BETS-MRO | S | 76.6 | 0.93529 | 20.4915 | - | - | 5.67 | 14.8 | 18.5 | 22.1 | 25.3 | 28.9633 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BETS-MRO | W | 89.2 | 0.93529 | 20.4915 | - | - | 4.9 | 4.2 | 5.3 | 6.2 | 6.9 | 7.679 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HOTS-CHM | S | 26.2 | 0.91304 | 1.583 | - | - | 0 | 1.8 | 1.9 | 2 | 2.1 | 2.205 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HOTS-CHM | W | 35.4 | 0.91304 | 1.583 | - | - | 0.3 | 1.8 | 1.9 | 2 | 2 | 2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KTS-SA1 | S | 116.6 | 0.97635 | 44.6584 | - | - | 5.21 | 13.6 | 20.1 | 27.2 | 33.4 | 41.0132 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KTS-SA1 | W | 122.3 | 0.97635 | 44.6584 | - | - | 5 | 9.7 | 15 | 20.2 | 25.2 | 31.4376 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BGR-ART | S | 45.7 | 0.99342 | 15.7105 | - | - | 0 | 30.4 | 30.4 | 30.5 | 30.4 | 30.3003 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BGR-ART | W | 47.4 | 0.99342 | 15.7105 | - | - | 0.0080021 | 30.5 | 30.4 | 30.4 | 30.4 | 30.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MBN-DTN | S | 74.3 | 0.94521 | 25.4432 | - | - | 0 | 3 | 3.5 | 4 | 4.3 | 4.6225 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MBN-DTN | W | 86.9 | 0.94521 | 25.4432 | - | - | 0.91 | 1.6 | 1.7 | 1.7 | 1.7 | 1.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BETS-CMN | S | 64 | 0.99652 | 33.3596 | - | - | 7.35 | 15.3 | 19.1 | 22.8 | 26.1 | 29.8776 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BETS-CMN | W | 65.2 | 0.99652 | 33.3596 | - | - | 3.4 | 4 | 5.1 | 6 | 6.7 | 7.4817 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
CMN-MRO | S | 26.3 | 0.98252 | 53.8511 | - | - | 0 | 11.2 | 14.2 | 17.1 | 19.6 | 22.4655 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
CMN-MRO | W | 35.4 | 0.98252 | 53.8511 | - | - | 0 | 3.1 | 4 | 4.7 | 5.4 | 6.2043 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HOTS-STL2 | S | 25.7 | 0.99685 | 17.53 | - | - | 4.61 | 15 | 15.7 | 16.5 | 17.1 | 17.7218 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HOTS-STL2 | W | 34.9 | 0.99685 | 17.53 | - | - | 4.3 | 14.5 | 14.9 | 15.3 | 15.8 | 16.3163 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BPA-HTH | S | 17.7 | 0.97297 | 0 | - | - | 0.8 | 1.2 | 1.4 | 1.6 | 1.8 | 2.025 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BPA-HTH | W | 35.4 | 0.97297 | 0 | - | - | 1 | 1.3 | 1.5 | 1.7 | 2 | 2.3529 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HOTS-STL1 | S | 49.2 | 0.99099 | 17.53 | - | - | 9.89 | 20.1 | 21 | 22.1 | 23 | 23.9367 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HOTS-STL1 | W | 57.2 | 0.99099 | 17.53 | - | - | 9 | 19.4 | 20 | 20.6 | 21.2 | 21.8175 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
AL-BLTS | S | 91.4 | 0.87942 | 9.8576 | - | - | 12.2 | 6 | 6.3 | 10.8 | 13.7 | 17.3787 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
AL-BLTS | W | 91.4 | 0.87942 | 9.8576 | - | - | 12.1 | 5.4 | 8.5 | 11 | 11.1 | 11.2009 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BETS-BGO | S | 109.7 | 0.96507 | 21.6087 | - | - | 1.77 | 5.5 | 11.9 | 18.3 | 23.6 | 30.435 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BETS-BGO | W | 114.3 | 0.96507 | 21.6087 | - | - | 1.1 | 3.1 | 8.3 | 12.7 | 16.8 | 22.2236 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RCTS-MDA2 | S | 104 | 0.9247 | 25.4014 | - | - | 4.47 | 3.9 | 6.7 | 9.7 | 12.1 | 15.0938 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RCTS-MDA2 | W | 114.3 | 0.9247 | 25.4014 | - | - | 4.4 | 1.4 | 2.9 | 4.7 | 6.4 | 8.7149 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RCTS-MDA1 | S | 104 | 0.91566 | 25.4014 | - | - | 2.98 | 3.5 | 6 | 8.7 | 10.8 | 13.4069 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RCTS-MDA1 | W | 114.3 | 0.91566 | 25.4014 | - | - | 3 | 1.1 | 2.6 | 4.2 | 5.7 | 7.7357 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HKT-LV | S | 135.5 | 0.97816 | 82.3784 | - | - | 30.6 | 34.7 | 39.9 | 48.6 | 65.4 | 88.0074 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HKT-LV | W | 142.3 | 0.97816 | 82.3784 | - | - | 25.3 | 28.1 | 37.6 | 56.7 | 78.2 | 107.8526 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GTS-FDN | S | 102.9 | 0.95495 | 0 | - | - | 0.79 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GTS-FDN | W | 134.9 | 0.95495 | 0 | - | - | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WETS-WSF | S | 84.6 | 0.99548 | 0 | - | - | 77 | 88.1 | 88 | 88 | 88 | 88 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WETS-WSF | W | 106.3 | 0.99548 | 0 | - | - | 77.8 | 91.5 | 91.4 | 91.5 | 91.9 | 92.3017 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WSF-WMN | S | 31.4 | 0.99548 | 7.2348 | - | - | 0 | 6.1 | 6.2 | 6.3 | 6.4 | 6.5016 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WSF-WMN | W | 43.4 | 0.99548 | 7.2348 | - | - | 0.037724 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ATS-AC | S | 102.3 | 0.88904 | 1.1938 | - | - | 0 | 12.9 | 13.8 | 15 | 15.2 | 15.4027 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ATS-AC | W | 108 | 0.88904 | 1.1938 | - | - | 20 | 13 | 14.1 | 14.7 | 14.8 | 14.9007 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GB-GL | S | 89.7 | 0.94674 | 19.7238 | - | - | 0.65503 | 12.9 | 9.2 | 5.9 | 5.6 | 5.3153 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GB-GL | W | 100.6 | 0.94674 | 19.7238 | - | - | 0 | 14.2 | 10.4 | 7.5 | 5.7 | 4.332 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-SHN2 | S | 88 | 0.99085 | 27.206 | - | - | 5.41 | 5 | 6.2 | 7.3 | 8.1 | 8.9877 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-SHN2 | W | 112 | 0.99085 | 27.206 | - | - | 5.1 | 4.6 | 5.6 | 6.5 | 7.1 | 7.7554 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-HTN | S | 47.4 | 0.84921 | 12.7404 | - | - | 19.4 | 61.4 | 61.9 | 61.8 | 61.8 | 61.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-HTN | W | 48 | 0.84921 | 12.7404 | - | - | 19.37 | 61.8 | 61.6 | 61.4 | 61.6 | 61.8007 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-SHN1 | S | 88 | 0.99085 | 27.206 | - | - | 5.28 | 5 | 6.2 | 7.3 | 8.1 | 8.9877 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-SHN1 | W | 112 | 0.99085 | 27.206 | - | - | 5.1 | 4.6 | 5.6 | 6.5 | 7.1 | 7.7554 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KWF-NHL | S | 44 | 1 | 12.4066 | - | - | 0 | 7.2 | 7.7 | 8.2 | 8.7 | 9.2305 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KWF-NHL | W | 43.4 | 1 | 12.4066 | - | - | 0.060587 | 6.8 | 7.1 | 7.4 | 7.7 | 8.0122 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WETS-BPA | S | 31.4 | 1 | 0 | - | - | 0 | 1.7 | 1.9 | 2.1 | 2.2 | 2.3048 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WETS-BPA | W | 43.4 | 1 | 0 | - | - | 0.32 | 1.9 | 2 | 2.2 | 2.4 | 2.6182 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KRT-PLD1/CWF | S | 40 | 0.9878 | 74.8312 | - | - | 0.0080021 | 25.8 | 26.7 | 27.6 | 28.5 | 29.4293 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KRT-PLD1/CWF | W | 45.7 | 0.9878 | 74.8312 | - | - | 0 | 25.6 | 26.3 | 26.9 | 27.7 | 28.5238 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
NKA-CME | S | 74.3 | 0.98714 | 78.7932 | - | - | 0.13718 | 14.3 | 15.8 | 17.3 | 18.4 | 19.5699 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
NKA-CME | W | 86.9 | 0.98714 | 78.7932 | - | - | 0 | 13.6 | 15 | 16.1 | 17.1 | 18.1621 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ATS-WBE | S | 109.7 | 0.95228 | 103.2202 | - | - | 24.6 | 29 | 35.3 | 43 | 48.6 | 54.9293 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ATS-WBE | W | 134.9 | 0.95228 | 103.2202 | - | - | 24.5 | 24.2 | 27.1 | 31.7 | 36.1 | 41.1107 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-CDN | S | 76.6 | 0.99598 | 19.982 | - | - | 28.8 | 44.7 | 44.2 | 43.6 | 43.1 | 42.6057 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-CDN | W | 85.7 | 0.99598 | 19.982 | - | - | 28.89 | 43.7 | 45.7 | 47.1 | 48.8 | 50.5614 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
NSF-NKA | S | 102.9 | 0.97582 | 36.7147 | - | - | 0 | 104.7 | 105.4 | 104.6 | 105.4 | 106.2061 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
NSF-NKA | W | 114.3 | 0.97582 | 36.7147 | - | - | 0.0080021 | 105.2 | 104.8 | 105 | 104.9 | 104.8001 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MDA-MBN | S | 74.3 | 0.94171 | 50.8447 | - | - | 0 | 5.2 | 6.6 | 7.8 | 8.7 | 9.7038 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MDA-MBN | W | 86.9 | 0.94171 | 50.8447 | - | - | 0.014861 | 2.2 | 2.5 | 2.9 | 3.3 | 3.7552 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BAN-BGR | S | 46.3 | 0.98758 | 63.7025 | - | - | 0 | 62.1 | 62.9 | 64 | 65 | 66.0156 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BAN-BGR | W | 49.7 | 0.98758 | 63.7025 | - | - | 0.0080021 | 61.1 | 61.8 | 62.2 | 62.8 | 63.4058 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ATS-TYA | S | 102.3 | 0.70039 | 0 | - | - | 40.8 | 5.4 | 8.8 | 14.4 | 17.8 | 22.0028 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ATS-TYA | W | 130.3 | 0.70039 | 0 | - | - | 42.63 | 5.8 | 11.9 | 15.3 | 15.7 | 16.1105 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-TNA2 | S | 109.7 | 0.97842 | 111.7199 | - | - | 23.76 | 17.7 | 13.6 | 13.3 | 13.3 | 13.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-TNA2 | W | 134.9 | 0.97842 | 111.7199 | - | - | 23.7 | 14.1 | 13.4 | 13.4 | 14.1 | 14.8366 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KGTS-SHL | S | 40 | 0.9902 | 32.6326 | - | - | 10.8 | 10.3 | 10.6 | 11.3 | 11.8 | 12.3221 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KGTS-SHL | W | 49.7 | 0.9902 | 32.6326 | - | - | 10.85 | 11.9 | 12.5 | 13.1 | 13.6 | 14.1191 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BETS-EHK | S | 111.4 | 0.9587 | 40.6491 | - | - | 3.36 | 5.5 | 11.9 | 18.3 | 23.5 | 30.1776 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BETS-EHK | W | 111.4 | 0.9587 | 40.6491 | - | - | 3.4 | 3 | 8.3 | 12.7 | 16.8 | 22.2236 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GHP-BCG | S | 109.7 | 0.97101 | 20.6932 | - | - | 0.014861 | 32.9 | 33.3 | 33.8 | 34.2 | 34.6047 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GHP-BCG | W | 134.9 | 0.97101 | 20.6932 | - | - | 0 | 32 | 32.7 | 33.3 | 34.1 | 34.9192 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TRG-WBL1 | S | 47.4 | 0.94256 | 39.6682 | - | - | 0.67789 | 12.6 | 14.4 | 16.1 | 17.7 | 19.459 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TRG-WBL1 | W | 49.7 | 0.94256 | 39.6682 | - | - | 0 | 17.1 | 17 | 16.9 | 17 | 17.1006 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TRG-WBL2 | S | 45.7 | 0.98251 | 39.6682 | - | - | 0.11432 | 10.1 | 11.6 | 13 | 14.2 | 15.5108 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TRG-WBL2 | W | 46.3 | 0.98251 | 39.6682 | - | - | 0 | 13.8 | 13.7 | 13.7 | 13.7 | 13.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
AWT-LV | S | 109.7 | 0.97896 | 82.3784 | - | - | 19.88 | 34.7 | 39.9 | 47.7 | 53.7 | 60.4547 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
AWT-LV | W | 134.9 | 0.97896 | 82.3784 | - | - | 19 | 28.1 | 31.8 | 37 | 41.4 | 46.3232 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GTS-GCY | S | 90.3 | 0.94011 | 19.6486 | - | - | 1.55 | 15.4 | 11.7 | 7.8 | 6.2 | 4.9282 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GTS-GCY | W | 96.6 | 0.94011 | 19.6486 | - | - | 1.8 | 16.9 | 13.1 | 9.9 | 7.4 | 5.5313 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FDN-CRO | S | 109.7 | 0.95706 | 6.7197 | - | - | 0.22863 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FDN-CRO | W | 134.9 | 0.95706 | 6.7197 | - | - | 0.2 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BATS-BAN2 | S | 96 | 0.91163 | 63.7025 | - | - | 5.58 | 41.4 | 45 | 50.6 | 55.2 | 60.2182 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BATS-BAN2 | W | 114.3 | 0.91163 | 63.7025 | - | - | 4.9 | 33.6 | 38.4 | 42.2 | 46 | 50.1422 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BATS-BAN1 | S | 96 | 0.91704 | 63.7025 | - | - | 6.53 | 41.6 | 45.3 | 50.9 | 55.5 | 60.5157 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BATS-BAN1 | W | 114.3 | 0.91704 | 63.7025 | - | - | 6.5 | 33.8 | 38.6 | 42.5 | 46.3 | 50.4398 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-SHP | S | 101.7 | 1 | 39.3347 | - | - | 48.76 | 107.6 | 108.4 | 109.6 | 110.7 | 111.811 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-SHP | W | 116 | 1 | 39.3347 | - | - | 48.5 | 103.3 | 104.8 | 105.3 | 106.4 | 107.5115 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BLTS-ATD | S | 97.2 | 1 | 0 | - | - | 1.24 | 5.3 | 28.7 | 54.2 | 61.7 | 70.2378 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BLTS-ATD | W | 125.7 | 1 | 0 | - | - | 1.6 | 13.9 | 43.8 | 60 | 61.8 | 63.654 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
STL-ART | S | 38.3 | 0.96313 | 33.2405 | - | - | 0 | 34.7 | 35.5 | 36.4 | 37.2 | 38.0176 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
STL-ART | W | 43.4 | 0.96313 | 33.2405 | - | - | 0.022863 | 33.8 | 34.3 | 34.9 | 35.4 | 35.9072 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BETS-CTN | S | 26.3 | 0.99163 | 19.1698 | - | - | 18.85 | 23.5 | 24.4 | 25.1 | 25.8 | 26.5195 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BETS-CTN | W | 30.3 | 0.99163 | 19.1698 | - | - | 16.4 | 22.7 | 23.2 | 23.6 | 24.1 | 24.6106 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HOTS-HSM2 | S | 49.2 | 0.99007 | 24.5257 | - | - | 2.9 | 6.2 | 9.4 | 12.6 | 15.3 | 18.5786 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HOTS-HSM2 | W | 52.6 | 0.99007 | 24.5257 | - | - | 2.9 | 5.8 | 8.5 | 10.8 | 13.1 | 15.8898 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HOTS-HSM1 | S | 49.2 | 0.99012 | 24.5257 | - | - | 2.9 | 6.2 | 9.4 | 12.6 | 15.3 | 18.5786 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HOTS-HSM1 | W | 52.6 | 0.99012 | 24.5257 | - | - | 2.9 | 5.8 | 8.5 | 10.8 | 13.1 | 15.8898 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HTH-OYN | S | 17.7 | 0.94118 | 4.0186 | - | - | 1.2 | 1.9 | 2.4 | 2.8 | 3.2 | 3.6571 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HTH-OYN | W | 35.4 | 0.94118 | 4.0186 | - | - | 1.5 | 2.2 | 2.6 | 3.1 | 3.6 | 4.1806 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GTS-CRO | S | 91.4 | 0.95732 | 6.7197 | - | - | 0.27 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GTS-CRO | W | 91.4 | 0.95732 | 6.7197 | - | - | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SHP-KYM | S | 84.6 | 0.88584 | 72.0915 | - | - | 0.014861 | 107.2 | 108.4 | 109.7 | 110.7 | 111.7091 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SHP-KYM | W | 106.3 | 0.88584 | 72.0915 | - | - | 0 | 103.4 | 104.3 | 105.3 | 105.8 | 106.3024 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HCP-WBE | S | 109.7 | 0.98159 | 103.2202 | - | - | 11.4 | 29.2 | 35.6 | 43.4 | 49.2 | 55.7751 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HCP-WBE | W | 134.9 | 0.98159 | 103.2202 | - | - | 11.3 | 24.4 | 27.4 | 32 | 36.4 | 41.405 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-KYM1 | S | 79.4 | 0.998 | 32.7567 | - | - | 40.88 | 59.9 | 61.6 | 63.1 | 64.3 | 65.5228 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-KYM1 | W | 90.3 | 0.998 | 32.7567 | - | - | 39.4 | 58.1 | 59.5 | 61 | 62 | 63.0164 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-KYM2 | S | 79.4 | 0.99802 | 32.7567 | - | - | 42.14 | 61.8 | 63.5 | 65.1 | 66.4 | 67.726 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-KYM2 | W | 90.3 | 0.99802 | 32.7567 | - | - | 41.3 | 60 | 61.4 | 63 | 64 | 65.0159 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
YSW-BMH | S | 36.6 | 0.95469 | 19.1573 | - | - | 0 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
YSW-BMH | W | 37.2 | 0.95469 | 19.1573 | - | - | 0.22291 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-TNA1 | S | 109.7 | 0.98005 | 111.7199 | - | - | 21.4 | 17.7 | 13.6 | 13.3 | 13.3 | 13.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-TNA1 | W | 134.9 | 0.98005 | 111.7199 | - | - | 21 | 14.1 | 13.4 | 13.4 | 14.1 | 14.8366 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WPD-TQY1 | S | 107 | 0.99171 | 68.3733 | - | - | 0 | 7.1 | 9.3 | 11.5 | 13.3 | 15.3817 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WPD-TQY1 | W | 108.6 | 0.99171 | 68.3733 | - | - | 0.69389 | 3.4 | 4.5 | 5.3 | 6.2 | 7.2528 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KYM-ECA2 | S | 45.7 | 0.9975 | 71.0766 | - | - | 8.1 | 14.4 | 16.3 | 18.1 | 19.6 | 21.2243 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KYM-ECA2 | W | 53.2 | 0.9975 | 71.0766 | - | - | 8.1 | 11 | 12.5 | 13.6 | 14.6 | 15.6735 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ATS-AWT | S | 109.7 | 0.97527 | 0 | - | - | 11.12 | 34.6 | 39.8 | 47.6 | 53.5 | 60.1313 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ATS-AWT | W | 134.9 | 0.97527 | 0 | - | - | 11.1 | 28 | 31.7 | 36.8 | 41.3 | 46.3503 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KYM-ECA1 | S | 45.7 | 0.99496 | 71.0766 | - | - | 8.1 | 14.4 | 16.3 | 18.1 | 19.7 | 21.4414 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KYM-ECA1 | W | 52.6 | 0.99496 | 71.0766 | - | - | 8.1 | 11 | 12.5 | 13.7 | 14.7 | 15.773 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KGTS-GSF | S | 48.6 | 0.99485 | 0 | - | - | 46.4 | 58.3 | 59 | 59.7 | 60.3 | 60.906 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KGTS-GSF | W | 52.6 | 0.99485 | 0 | - | - | 46.3 | 60.4 | 61 | 61.6 | 62.1 | 62.6041 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GLE-DDL1 | S | 74.3 | 0.98191 | 84.6323 | - | - | 0.21377 | 18.6 | 24.5 | 30.2 | 35.1 | 40.795 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GLE-DDL1 | W | 86.9 | 0.98191 | 84.6323 | - | - | 0 | 11.4 | 15.1 | 18.2 | 21.1 | 24.4621 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GLE-DDL2 | S | 74.3 | 0.98084 | 84.6323 | - | - | 0.19091 | 18.5 | 24.4 | 30.1 | 34.9 | 40.4654 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GLE-DDL2 | W | 86.9 | 0.98084 | 84.6323 | - | - | 0 | 11.4 | 15.1 | 18.1 | 21 | 24.3646 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GCY-GL | S | 109.7 | 0.96341 | 37.076 | - | - | 0 | 8.7 | 6.5 | 4.3 | 4.5 | 4.7093 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GCY-GL | W | 134.9 | 0.96341 | 37.076 | - | - | 0.0080021 | 8.6 | 6.5 | 4.9 | 3.6 | 2.6449 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GSF-SHL | S | 76.6 | 0.99474 | 32.6326 | - | - | 0.053728 | 9.9 | 10.6 | 11.3 | 11.9 | 12.5319 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GSF-SHL | W | 89.2 | 0.99474 | 32.6326 | - | - | 0.2 | 12 | 12.7 | 13.3 | 13.9 | 14.5271 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
YSF-HTH | S | 17.7 | 0.9434 | 0 | - | - | 0 | 4.5 | 4.4 | 4.4 | 4.3 | 4.2023 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
YSF-HTH | W | 35.4 | 0.9434 | 0 | - | - | 0.045726 | 6.4 | 6.5 | 6.2 | 6.3 | 6.4016 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KRT-PLD2/YWF | S | 29.7 | 0.99422 | 74.8312 | - | - | 0 | 33.6 | 35.9 | 37.7 | 39.3 | 40.9679 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KRT-PLD2/YWF | W | 29.7 | 0.99422 | 74.8312 | - | - | 0.0080021 | 34.2 | 35.4 | 36.3 | 38 | 39.7796 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
CTN-CBW | S | 98.9 | 0 | 19.1698 | - | - | 0.0080021 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
CTN-CBW | W | 106.3 | 0 | 19.1698 | - | - | 0 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ATS-HCP | S | 109.7 | 0.95364 | 0 | - | - | 25.11 | 28.7 | 35 | 42.7 | 48.5 | 55.0878 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ATS-HCP | W | 134.9 | 0.95364 | 0 | - | - | 25 | 23.9 | 26.8 | 31.4 | 35.8 | 40.8166 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KRT-WBL | S | 46.9 | 0.861 | 82.5978 | - | - | 0.0080021 | 33.2 | 34.8 | 36.1 | 37.3 | 38.5399 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KRT-WBL | W | 47.4 | 0.861 | 82.5978 | - | - | 0 | 31.8 | 31.7 | 31.5 | 31.6 | 31.7003 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ATS-SCI | S | 90.8 | 0.78218 | 0 | - | - | 1.8 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ATS-SCI | W | 116 | 0.78218 | 0 | - | - | 1.74 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SBY-GSB2 | S | 76.6 | 0.99273 | 22.7913 | - | - | 5.15 | 22.2 | 28.1 | 33.8 | 38.4 | 43.626 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SBY-GSB2 | W | 89.2 | 0.99273 | 22.7913 | - | - | 5 | 16.5 | 20.7 | 24.1 | 27.4 | 31.1519 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-WNS | S | 91.4 | 0.94373 | 0 | - | - | 0.060587 | 145.3 | 147.2 | 150.4 | 153.4 | 156.4598 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-WNS | W | 91.4 | 0.94373 | 0 | - | - | 0.1 | 133.6 | 134.8 | 136.2 | 137.1 | 138.0059 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RCTS-YSF | S | 84.6 | 0.92661 | 0 | - | - | 78.41 | 85.8 | 85.7 | 85.6 | 85.5 | 85.4001 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RCTS-YSF | W | 106.3 | 0.92661 | 0 | - | - | 77.7 | 88 | 88.1 | 88.2 | 88.2 | 88.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-SU1 | S | 109.7 | 0.96474 | 41.8716 | - | - | 2 | 7.4 | 5.2 | 2 | 2.6 | 3.38 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-SU1 | W | 133.7 | 0.96474 | 41.8716 | - | - | 1.94 | 14 | 12.5 | 9.8 | 7.4 | 5.5878 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GTS-BCG | S | 109.7 | 0.98296 | 0 | - | - | 28.2 | 60.2 | 62.4 | 64.5 | 66.1 | 67.7397 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GTS-BCG | W | 134.9 | 0.98296 | 0 | - | - | 28.7 | 57.9 | 60.2 | 62.1 | 64.1 | 66.1644 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WPD-TQY2 | S | 107 | 0.99171 | 68.3733 | - | - | 0.40353 | 7.1 | 9.3 | 11.5 | 13.3 | 15.3817 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WPD-TQY2 | W | 108.6 | 0.99171 | 68.3733 | - | - | 0.5 | 3.5 | 4.5 | 5.3 | 6.2 | 7.2528 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ATS-LVN | S | 109.7 | 0.97111 | 19.9175 | - | - | 4 | 16.3 | 14.9 | 14.5 | 17.2 | 20.4028 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ATS-LVN | W | 134.9 | 0.97111 | 19.9175 | - | - | 4.33 | 18.7 | 17.1 | 16.3 | 16.1 | 15.9025 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GTS-GB | S | 135.5 | 0.92883 | 2.2964 | - | - | 0.85 | 15.3 | 11.4 | 7.4 | 5.6 | 4.2378 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GTS-GB | W | 142.3 | 0.92883 | 2.2964 | - | - | 1 | 16.8 | 12.9 | 9.6 | 7 | 5.1042 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
COB-CDN | S | 49.2 | 1 | 28.5118 | - | - | 0.4 | 33.4 | 32.8 | 31.8 | 30.9 | 30.0255 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
COB-CDN | W | 57.2 | 1 | 28.5118 | - | - | 0.0080021 | 32.4 | 33.5 | 34.5 | 35.7 | 36.9417 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KSF-RVL | S | 84.6 | 0.97382 | 14.5489 | - | - | 0 | 6.6 | 4.9 | 5 | 5.2 | 5.408 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KSF-RVL | W | 106.3 | 0.97382 | 14.5489 | - | - | 0.045726 | 4.6 | 4.5 | 4.8 | 4.9 | 5.0021 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BCG-WIN | S | 91.4 | 0.97877 | 12.7618 | - | - | 0.022863 | 94.5 | 93.7 | 92.9 | 92.2 | 91.5053 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BCG-WIN | W | 91.4 | 0.97877 | 12.7618 | - | - | 0 | 95.1 | 96 | 96.8 | 98.1 | 99.4175 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
CPL-AL | S | 91.4 | 0.8864 | 9.8576 | - | - | 0 | 6.1 | 5.7 | 8.3 | 10.7 | 13.794 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
CPL-AL | W | 91.4 | 0.8864 | 9.8576 | - | - | 0.054871 | 5.5 | 7.9 | 11 | 11.8 | 12.6582 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SBY-GSB1 | S | 51.4 | 0.99638 | 22.7913 | - | - | 7.19 | 22.2 | 28.1 | 33.7 | 38.3 | 43.5279 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SBY-GSB1 | W | 69.7 | 0.99638 | 22.7913 | - | - | 7.1 | 16.6 | 20.7 | 24.1 | 27.4 | 31.1519 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GTS-SRC | S | 109.7 | 0.95731 | 0 | - | - | 7.1 | 12.1 | 11.9 | 11.6 | 10.8 | 10.0552 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GTS-SRC | W | 134.9 | 0.95731 | 0 | - | - | 7.11 | 16.1 | 16.2 | 15.1 | 13.8 | 12.6119 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BLTS-TYA | S | 88 | 0.7305 | 0 | - | - | 19.8 | 6.2 | 7 | 12.3 | 16 | 20.813 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BLTS-TYA | W | 112 | 0.7305 | 0 | - | - | 19.77 | 5.6 | 9.8 | 13.2 | 13.6 | 14.0121 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BCG-WPD | S | 91.4 | 0.99036 | 40.8707 | - | - | 0.4 | 53.3 | 52.3 | 51.3 | 50.4 | 49.5158 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BCG-WPD | W | 91.4 | 0.99036 | 40.8707 | - | - | 0.31208 | 54.8 | 54.7 | 54.7 | 55 | 55.3016 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BATS-YSW/BGL | S | 36.6 | 0.9973 | 0 | - | - | 30.1 | 30.1 | 30.2 | 30.3 | 30.3 | 30.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BATS-YSW/BGL | W | 37.1 | 0.9973 | 0 | - | - | 30.4 | 30.1 | 30.1 | 30.1 | 30.2 | 30.3003 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BATS-BAS1 | S | 83.5 | 0.97587 | 116.0329 | - | - | 7.62 | 13.3 | 16.2 | 17.2 | 21 | 25.6395 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BATS-BAS1 | W | 102.9 | 0.97587 | 116.0329 | - | - | 7.6 | 10.1 | 7.7 | 13.2 | 16.5 | 20.625 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ATS-HKT1 | S | 135.5 | 0.9711 | 0 | - | - | 3.57 | 14.2 | 13.05 | 24.4 | 32.95 | 44.496 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ATS-HKT1 | W | 142.3 | 0.9711 | 0 | - | - | 3.6 | 14.2 | 13.05 | 24.4 | 32.95 | 44.496 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KTS-SSE1 | S | 89.7 | 0.93416 | 26.4458 | - | - | 2.89 | 8.3 | 5.5 | 2.6 | 1.6 | 0.98462 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KTS-SSE1 | W | 94.3 | 0.93416 | 26.4458 | - | - | 3 | 12.4 | 9.8 | 7.5 | 5.3 | 3.7453 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-NSF | S | 98.3 | 0.95254 | 0 | - | - | 93.58 | 163.7 | 165.7 | 169 | 171.8 | 174.6464 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-NSF | W | 114.3 | 0.95254 | 0 | - | - | 88.5 | 152 | 153.5 | 154.6 | 155.8 | 157.0093 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HOTS-KWF | S | 44 | 0.69173 | 0 | - | - | 28.17 | 38.7 | 39.2 | 39.7 | 40.1 | 40.504 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HOTS-KWF | W | 43.4 | 0.69173 | 0 | - | - | 25.4 | 38.4 | 38.7 | 39 | 39.3 | 39.6023 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KTS-SA2 | S | 108 | 0.97525 | 44.6584 | - | - | 8.27 | 13.6 | 20.1 | 27.2 | 33.4 | 41.0132 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KTS-SA2 | W | 122.3 | 0.97525 | 44.6584 | - | - | 8.2 | 9.7 | 15 | 20.2 | 25.2 | 31.4376 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
NRB-HTN | S | 52.6 | 0.84651 | 12.7404 | - | - | 0.35095 | 62 | 62 | 62 | 62 | 62 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
NRB-HTN | W | 53.2 | 0.84651 | 12.7404 | - | - | 0.5 | 62 | 62 | 62 | 62 | 62 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GSB-WND2 | S | 46.3 | 1 | 47.3687 | - | - | 3.5 | 11 | 13.2 | 15.3 | 17 | 18.8889 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GSB-WND2 | W | 49.7 | 1 | 47.3687 | - | - | 1.1 | 8.3 | 9.8 | 11 | 12.2 | 13.5309 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KGTS-CHA | S | 31.4 | 0.94771 | 36.5961 | - | - | 25.81 | 37.5 | 38.3 | 39.3 | 40.1 | 40.9163 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KGTS-CHA | W | 43.4 | 0.94771 | 36.5961 | - | - | 24.3 | 29.5 | 30.3 | 31.1 | 31.6 | 32.108 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GSB-WND1 | S | 109.7 | 1 | 47.3687 | - | - | 3.42 | 11.1 | 13.3 | 15.4 | 17.2 | 19.2104 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GSB-WND1 | W | 114.3 | 1 | 47.3687 | - | - | 1.9 | 8.3 | 9.8 | 11.1 | 12.3 | 13.6297 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KTS-SSE2 | S | 89.4 | 0.93544 | 26.4458 | - | - | 3.86 | 8.3 | 5.5 | 2.6 | 1.6 | 0.98462 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KTS-SSE2 | W | 100.6 | 0.93544 | 26.4458 | - | - | 4 | 12.4 | 9.8 | 7.5 | 5.3 | 3.7453 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-DLF1 | S | 87.5 | 0.88448 | 0 | - | - | 1.27 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-DLF1 | W | 87.5 | 0.88448 | 0 | - | - | 1.3 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MDA-BNG | S | 104 | 0.93779 | 25.4014 | - | - | 0 | 2.8 | 3.2 | 3.6 | 3.9 | 4.225 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MDA-BNG | W | 114.3 | 0.93779 | 25.4014 | - | - | 0.0080021 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GTS-GLE2 | S | 109.7 | 0.92421 | 32.1632 | - | - | 7.52 | 20.6 | 28.5 | 36.2 | 42.9 | 50.8401 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GTS-GLE2 | W | 133.7 | 0.92421 | 32.1632 | - | - | 7.3 | 11.7 | 17.1 | 21.7 | 26.1 | 31.3922 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GTS-GLE1 | S | 109.7 | 0.9539 | 32.1632 | - | - | 12.23 | 20.7 | 28.6 | 36.4 | 43 | 50.7967 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GTS-GLE1 | W | 133.7 | 0.9539 | 32.1632 | - | - | 10 | 11.7 | 17.1 | 21.8 | 26.3 | 31.7289 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MGW-CLC | S | 74.3 | 0.9912 | 16.06 | - | - | 0 | 66.4 | 66.4 | 66.3 | 66.3 | 66.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MGW-CLC | W | 86.9 | 0.9912 | 16.06 | - | - | 0.0034295 | 67.7 | 68.2 | 68.6 | 69 | 69.4023 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BATS-BAS2/BGF | S | 93.2 | 0.9727 | 116.0329 | - | - | 10.51 | 13.2 | 16.1 | 17.1 | 20.9 | 25.5444 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BATS-BAS2/BGF | W | 94.9 | 0.9727 | 116.0329 | - | - | 9.3 | 10.1 | 7.7 | 13.2 | 16.4 | 20.3758 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
STN-MNA | S | 48.6 | 0.95758 | 65.6095 | - | - | 0 | 5.6 | 7.4 | 9.3 | 11.2 | 13.4882 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
STN-MNA | W | 52.6 | 0.95758 | 65.6095 | - | - | 0.0080021 | 4.9 | 5.9 | 7 | 8.1 | 9.3729 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-KRT2 | S | 97.2 | 0.85901 | 64.1676 | - | - | 12.13 | 27.7 | 29.6 | 31.2 | 32.6 | 34.0628 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-KRT2 | W | 116 | 0.85901 | 64.1676 | - | - | 12 | 28.8 | 28.6 | 28.5 | 28.6 | 28.7004 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-KRT1 | S | 44 | 0.97879 | 64.1676 | - | - | 7.45 | 21.6 | 23.1 | 24.4 | 25.6 | 26.859 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-KRT1 | W | 44.6 | 0.97879 | 64.1676 | - | - | 7.1 | 22.5 | 22.4 | 22.3 | 22.4 | 22.5004 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GTS-WPD | S | 108 | 0.97242 | 40.8707 | - | - | 29 | 60.2 | 62.5 | 64.8 | 66.5 | 68.2446 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GTS-WPD | W | 135.5 | 0.97242 | 40.8707 | - | - | 29.3 | 57.9 | 60.2 | 62.2 | 64.3 | 66.4709 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BGO-EHK | S | 48.6 | 0.96325 | 62.2578 | - | - | 0 | 3.5 | 6.9 | 10.3 | 13 | 16.4078 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BGO-EHK | W | 49.2 | 0.96325 | 62.2578 | - | - | 0 | 3.1 | 5.3 | 7.2 | 9.2 | 11.7556 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WNS-NKA | S | 91.4 | 0.97094 | 36.7147 | - | - | 0.11432 | 121.2 | 122.1 | 122.9 | 124.9 | 126.9325 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WNS-NKA | W | 91.4 | 0.97094 | 36.7147 | - | - | 0.1 | 115.4 | 115.2 | 115.8 | 116.3 | 116.8022 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-STN | S | 91.4 | 0.94565 | 36.8208 | - | - | 8.62 | 10.3 | 13.1 | 16.8 | 20.3 | 24.5292 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-STN | W | 91.4 | 0.94565 | 36.8208 | - | - | 8 | 8.7 | 10.2 | 11.9 | 13.8 | 16.0034 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-SU2 | S | 109.7 | 0.96182 | 41.8716 | - | - | 0 | 7.4 | 5.2 | 2 | 2.6 | 3.38 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-SU2 | W | 133.7 | 0.96182 | 41.8716 | - | - | 0.03 | 14 | 12.5 | 9.8 | 7.4 | 5.5878 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RVL-BSP | S | 84.6 | 0.99451 | 14.5489 | - | - | 0 | 7.3 | 6.9 | 5.7 | 6.7 | 7.8754 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RVL-BSP | W | 106.3 | 0.99451 | 14.5489 | - | - | 0 | 6.2 | 6.1 | 6.3 | 6.4 | 6.5016 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WIN-MGW | S | 98.3 | 0.96369 | 12.7618 | - | - | 0.0011432 | 93.8 | 93.9 | 94.1 | 94.3 | 94.5004 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WIN-MGW | W | 99.5 | 0.96369 | 12.7618 | - | - | 0 | 92.8 | 93.3 | 93.7 | 94.5 | 95.3068 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-MNA | S | 88 | 0.93277 | 28.7887 | - | - | 3.89 | 10.3 | 13.1 | 16.8 | 20.2 | 24.2881 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-MNA | W | 114.4 | 0.93277 | 28.7887 | - | - | 3.4 | 8.7 | 10.1 | 11.9 | 13.8 | 16.0034 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BLTS-SCI | S | 97.2 | 0.99738 | 0 | - | - | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BLTS-SCI | W | 125.7 | 0.99738 | 0 | - | - | 0.0080021 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-MLN2 | S | 109.7 | 0.95473 | 83.4903 | - | - | 27.04 | 27.2 | 30.8 | 33.7 | 30 | 26.7062 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-MLN2 | W | 134.9 | 0.95473 | 83.4903 | - | - | 26.9 | 14.2 | 15.7 | 9.3 | 10.6 | 12.0817 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
CDN-CLC | S | 74.3 | 0.99274 | 36.042 | - | - | 0.030865 | 66.7 | 66.7 | 66.6 | 66.5 | 66.4002 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
CDN-CLC | W | 86.9 | 0.99274 | 36.042 | - | - | 0 | 59.7 | 62.1 | 63.7 | 65.7 | 67.7628 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-COB | S | 109.7 | 0.98614 | 8.5298 | - | - | 11.1 | 28.4 | 27.7 | 26.7 | 25.8 | 24.9303 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-COB | W | 116 | 0.98614 | 8.5298 | - | - | 11.12 | 29.3 | 30.5 | 31.5 | 32.7 | 33.9457 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-DLF3 | S | 87.5 | 0.88448 | 0 | - | - | 0.84 | 1.7 | 1.7 | 1.8 | 1.7 | 1.6056 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FBTS-DLF3 | W | 87.5 | 0.88448 | 0 | - | - | 0.9 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BSP-BBD | S | 65.2 | 0.95804 | 1.0882 | - | - | 0 | 5.5 | 5.5 | 5.6 | 5.6 | 5.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BSP-BBD | W | 67.4 | 0.95804 | 1.0882 | - | - | 0.030865 | 3.8 | 3.8 | 3.9 | 3.9 | 3.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BLTS-LVN | S | 109.7 | 0.97121 | 19.9175 | - | - | 6.61 | 9.6 | 10.5 | 13.4 | 16.7 | 20.8127 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BLTS-LVN | W | 122.3 | 0.97121 | 19.9175 | - | - | 4.5 | 11.8 | 13 | 14.3 | 14.7 | 15.1112 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GTS-FNS | S | 88 | 0.96039 | 41.0865 | - | - | 8.7 | 12.1 | 11.9 | 11.6 | 10 | 8.6207 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GTS-FNS | W | 112 | 0.96039 | 41.0865 | - | - | 7.69 | 16.1 | 16.2 | 15.1 | 13.8 | 12.6119 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-TRG2 | S | 91.5 | 0.98752 | 21.2381 | - | - | 0.38 | 18.6 | 21.8 | 24.8 | 27.7 | 30.9391 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-TRG2 | W | 91.5 | 0.98752 | 21.2381 | - | - | 0 | 20.6 | 20.5 | 20.5 | 20.5 | 20.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-TRG1 | S | 91.5 | 0.98752 | 21.2381 | - | - | 0.27 | 18.6 | 21.8 | 24.8 | 27.7 | 30.9391 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TGTS-TRG1 | W | 91.5 | 0.98752 | 21.2381 | - | - | 0 | 20.6 | 20.5 | 20.5 | 20.5 | 20.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RCTS-MBN | S | 97.2 | 0.91562 | 25.4432 | - | - | 2.55 | 3.9 | 5.1 | 6.2 | 7.1 | 8.1306 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RCTS-MBN | W | 114.3 | 0.91562 | 25.4432 | - | - | 1 | 1.6 | 2.1 | 2.7 | 3.4 | 4.2815 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RCTS-KSF | S | 84.6 | 0.97423 | 0 | - | - | 88.64 | 98.5 | 96.6 | 96.8 | 97 | 97.2004 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RCTS-KSF | W | 106.3 | 0.97423 | 0 | - | - | 86.5 | 96.3 | 96.2 | 96.4 | 96.6 | 96.8004 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
AC-CPL | S | 102.9 | 0.89246 | 1.1938 | - | - | 0 | 12.9 | 13.8 | 15.1 | 15.2 | 15.3007 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
AC-CPL | W | 108 | 0.89246 | 1.1938 | - | - | 0.045726 | 13 | 14.1 | 14.7 | 14.8 | 14.9007 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FNS-SRC | S | 109.7 | 0.94715 | 41.0865 | - | - | 0 | 10.7 | 10.7 | 10.8 | 10.8 | 10.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FNS-SRC | W | 125.7 | 0.94715 | 41.0865 | - | - | 0.0080021 | 11.8 | 11.8 | 11.9 | 11.9 | 11.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WETS-BSP | S | 84.6 | 0.94235 | 0 | - | - | 66.24 | 87.7 | 86.2 | 85.9 | 86.4 | 86.9029 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WETS-BSP | W | 106.3 | 0.94235 | 0 | - | - | 65.6 | 91.4 | 91.4 | 91.6 | 91.8 | 92.0004 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-BMH | S | 32.6 | 0.94985 | 19.1573 | - | - | 2.8 | 29.2 | 29.3 | 29.3 | 29.4 | 29.5003 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-BMH | W | 37.7 | 0.94985 | 19.1573 | - | - | 2.3 | 28.4 | 27.6 | 26.8 | 26.1 | 25.4183 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ATS-HKT2 | S | 135.4637 | 0.9711 | 0 | - | - | 0 | 14.2 | 13.05 | 24.4 | 32.95 | 44.496 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ATS-HKT2 | W | 142.3226 | 0.9711 | 0 | - | - | 0 | 14.2 | 13.05 | 24.4 | 32.95 | 44.496 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-MTC1 | S | 135.3494 | 0.95473 | 0 | - | - | 113.6 | 27.2 | 30.7 | 33.6 | 30 | 26.7857 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DPTS-MTC1 | W | 142.3226 | 0.95473 | 0 | - | - | 10.9 | 14.2 | 15.7 | 9.3 | 10.6 | 12.0817 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
LSF-KYM | S | 79.4492 | 0.99802 | 112.7567 | - | - | 0 | 59.9 | 61.6 | 63.1 | 64.3 | 65.5228 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
LSF-KYM | W | 90.3091 | 0.99802 | 112.7567 | - | - | 0 | 58.1 | 59.5 | 61 | 62 | 63.0164 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MTC-MLN | S | 135.3494 | 0.95473 | 83.4903 | - | - | 17.1 | 27.2 | 30.7 | 33.6 | 30 | 26.7857 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MTC-MLN | W | 142.3226 | 0.95473 | 83.4903 | - | - | 2.7 | 14.2 | 15.7 | 9.3 | 10.6 | 12.0817 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-LSF | S | 79.4492 | 0.99802 | 80 | - | - | 38.34 | 59.9 | 61.6 | 63.1 | 64.3 | 65.5228 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SHTS-LSF | W | 90.3091 | 0.99802 | 80 | - | - | 27.3 | 58.1 | 59.5 | 61 | 62 | 63.0164 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -

## ZSS Aug Sum
Zone Substation | Season | Station N Export Rating (MVA) | Station N-1 Export Rating (MVA) | Station Nameplate Rating (MVA) | Station Power Factor at Minimum Demand | Embedded Generation Capacity (MVA) | Load Transfer Capability (MVA) | Generation Headroom (MVA) | Hours load is > 95% of Minimum Demand (Hrs) | Actual Minimum Demand (MVA) | 50% POE |  |  |  |  | % 50% POE load below N-1 Export Rating | 50% POE
[11 empty] | Forecast Minimum Demand (MVA) | [5 empty] | Energy at Risk (MWh) |  |  |  |  | Expected Energy at Risk (MWh) |  |  |  |  | Hours at Risk (Hrs)
[5 empty] | 2025 | 2025 | 2026 | 2025 | 2025 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030
AC | summer | -40 | -20 | 40 | 0 | 1.1938 | 0 | 18.8062 | 0.17703 | 0 | -1.0977 | -1.1069 | -1.1069 | -1.0977 | -1.0977 | -
AC | winter | -40 | -20 | 40 | 0.74049 | 1.1938 | 0 | 18.8062 | 0.025959 | 0.49697 | -1.0662 | -1.0662 | -1.057 | -1.0439 | -1.0347 | -
AL | summer | -30 | 0 | 30 | 0.94759 | 9.8576 | 0 | 0 | 0.3798 | -1.6127 | -0.51245 | -0.51245 | -1.1399 | -1.7763 | -2.5245 | 100% | -0.8878 | -0.81905 | -3.5008 | -6.0393 | -10.6314 | -0.000831 | -0.000766 | -0.003276 | -0.005651 | -0.009947 | 2.5 | 2 | 6.5 | 6 | 9.5
AL | winter | -30 | 0 | 30 | 0.63481 | 9.8576 | 0 | 0 | 3.2319 | 1.639 | 2.5698 | 2.2079 | 1.7541 | 1.2513 | 0.74953 | -
ART | summer | -20 | -10 | 20 | 0.84702 | 15.7105 | 1.1432 | 0 | 1.8437 | -7.4497 | -5.3775 | -6.0258 | -6.8047 | -7.6056 | -8.5373 | -
ART | winter | -20 | -10 | 20 | 0.88312 | 15.7105 | 1.1432 | 0 | 1.4886 | -6.4892 | -4.8192 | -5.4246 | -6.0582 | -6.7364 | -7.4986 | -
BAN | summer | -120 | -80 | 120 | 0.95393 | 63.7025 | 12.9557 | 16.2975 | 0.66597 | -4.8327 | 5.3571 | 2.5581 | -2.3554 | -3.6114 | -7.8561 | -
BAN | winter | -120 | -80 | 120 | 0.99518 | 63.7025 | 12.9557 | 16.2975 | 1.7348 | 6.7324 | 15.0746 | 11.9379 | 8.8326 | 5.0183 | 1.5059 | -
BAS | summer | -99 | -66 | 99 | 0.99641 | 116.0329 | 12.7652 | 0 | 0.93519 | -14.0103 | -9.21 | -10.7695 | -15.2442 | -17.8817 | -22.7164 | -
BAS | winter | -99 | -66 | 99 | 0.99378 | 116.0329 | 12.7652 | 0 | 0.73129 | -5.5981 | -1.609 | -4.9551 | -8.5695 | -13.6657 | -16.6923 | -
BBD | summer | -66 | -33 | 66 | 0.2211 | 1.0882 | 0 | 31.9118 | 0.36434 | 1.9448 | -6.51 | -5.7872 | -5.6627 | -5.5766 | -5.4716 | -
BBD | winter | -66 | -33 | 66 | 0.85902 | 1.0882 | 0 | 31.9118 | 0.33987 | -0.38416 | -2.4645 | -2.0594 | -2.0181 | -1.9988 | -1.9479 | -
BGO | summer | -66 | -33 | 66 | 0.58957 | 21.6087 | 12.4985 | 11.3913 | 0.90104 | -1.1308 | 2.9262 | 1.8659 | -1.9881 | -3.7305 | -5.9396 | -
BGO | winter | -66 | -33 | 66 | 0.84456 | 21.6087 | 12.4985 | 11.3913 | 2.0015 | 2.1788 | 3.2249 | 2.0164 | -1.6274 | -1.6634 | -2.7772 | -
BMH | summer | -27 | -13.5 | 27 | 0.91923 | 19.1573 | 3.0484 | 0 | 0.079308 | -4.2246 | -4.5539 | -5.8415 | -7.4471 | -9.0699 | -10.904 | -
BMH | winter | -27 | -13.5 | 27 | 0.84198 | 19.1573 | 3.0484 | 0 | 0.33194 | -3.3611 | -2.4774 | -3.2032 | -4.1736 | -5.3057 | -6.6264 | -
CDN | summer | -20 | -10 | 20 | 0.94298 | 19.982 | 0 | 0 | 0.32835 | -4.3161 | -5.674 | -6.3205 | -6.9876 | -7.6651 | -8.4129 | -
CDN | winter | -20 | -10 | 20 | 0.64819 | 19.982 | 0 | 0 | 0.72723 | -2.3244 | -4.1101 | -4.5849 | -5.0792 | -5.6155 | -6.1613 | -
CHA | summer | -27 | -13.5 | 27 | 0.90913 | 36.5961 | 1.9053 | 0 | 3.0862 | -7.9019 | -1.7773 | -2.1979 | -2.6932 | -3.203 | -3.7254 | -
CHA | winter | -27 | -13.5 | 27 | 0.94343 | 36.5961 | 1.9053 | 0 | 5.168 | -0.88585 | -1.122 | -1.4223 | -1.793 | -2.212 | -2.6207 | -
CHM | summer | -33 | 0 | 33 | 0.77869 | 1.583 | 0 | 0 | 0.67888 | -0.34922 | -0.48083 | -0.60465 | -0.75133 | -0.92477 | -1.1037 | 100% | -8.0018 | -19.7159 | -43.2112 | -87.7722 | -154.3998 | -0.001923 | -0.004739 | -0.010386 | -0.021096 | -0.037111 | 84.5 | 148.5 | 287 | 467.5 | 695
CHM | winter | -33 | 0 | 33 | 0.28646 | 1.583 | 0 | 0 | 0.18534 | -0.24552 | -0.42012 | -0.52498 | -0.65192 | -0.79158 | -0.93231 | 100%
CLC | summer | -79 | -46 | 79 | 0.91693 | 16.06 | 0 | 29.94 | 1.5921 | 6.649 | 7.9967 | 9.9774 | 8.4614 | 6.9121 | 5.1806 | -
CLC | winter | -79 | -46 | 79 | 0.90813 | 16.06 | 0 | 29.94 | 2.6164 | 8.813 | 12.7465 | 12.0194 | 10.9749 | 9.7121 | 8.3738 | -
CME | summer | -40.5 | -27 | 40.5 | 0.96738 | 42.0785 | 0.53347 | 0 | 1.8708 | -13.3556 | -14.5008 | -15.5908 | -16.8215 | -17.956 | -19.0726 | -
CME | winter | -40.5 | -27 | 40.5 | 0.94648 | 42.0785 | 0.53347 | 0 | 1.9867 | -13.7773 | -13.4007 | -14.4185 | -15.3226 | -16.2602 | -17.1134 | -
CMN | summer | -66 | -33 | 66 | 0.99999 | 33.3596 | 0 | 0 | 0.30816 | -4.9601 | -14.1624 | -16.896 | -18.906 | -20.9795 | -23.1355 | -
CMN | winter | -66 | -33 | 66 | 0.98669 | 33.3596 | 0 | 0 | 0.025783 | -3.2803 | -10.0641 | -11.7984 | -13.5229 | -15.259 | -16.9184 | -
COB | summer | -26 | -10 | 26 | 0.42265 | 8.5298 | 1.7147 | 1.4702 | 0.91337 | -5.4655 | -6.7532 | -6.7602 | -6.7182 | -6.6697 | -6.6146 | -
COB | winter | -26 | -10 | 26 | 0.32624 | 8.5298 | 1.7147 | 1.4702 | 1.3046 | -6.0793 | -7.0843 | -7.0454 | -7.006 | -6.9665 | -6.9277 | -
CRO | summer | -60 | -27 | 60 | 0.9472 | 6.7197 | 11.4315 | 20.2803 | 0.54409 | 2.6742 | -3.1443 | -3.3734 | -3.4431 | -3.6025 | -3.9016 | -
CRO | winter | -60 | -27 | 60 | 0.96952 | 6.7197 | 11.4315 | 20.2803 | 0.72522 | 5.2733 | 1.1377 | 1.1557 | 1.1557 | 1.0708 | 0.97985 | -
CTN | summer | -39.5 | -26 | 39.5 | 0.90337 | 19.1698 | 0 | 6.8302 | 0.79426 | -7.3248 | -5.8941 | -3.6695 | -4.4396 | -5.4259 | -6.4817 | -
CTN | winter | -39.5 | -26 | 39.5 | 0.87533 | 19.1698 | 0 | 6.8302 | 0.88919 | -6.7552 | -4.4225 | -3.3883 | -3.9579 | -4.6205 | -5.3975 | -
DDL | summer | -66 | -33 | 66 | 0.99746 | 52.4691 | 4.5726 | 0 | 1.3661 | -17.5945 | -19.2928 | -22.7306 | -26.8371 | -31.2373 | -35.7661 | -
DDL | winter | -66 | -33 | 66 | 0.97713 | 52.4691 | 4.5726 | 0 | 0.86593 | -10.1927 | -11.7557 | -14.2685 | -17.077 | -20.0615 | -23.0723 | -
ECA | summer | -40.5 | -27 | 40.5 | 0.92563 | 38.3199 | 4.9537 | 0 | 1.9107 | -10.8251 | -10.6652 | -11.7638 | -13.1723 | -14.6011 | -15.9902 | -
ECA | winter | -40.5 | -27 | 40.5 | 0.91559 | 38.3199 | 4.9537 | 0 | 1.0292 | -10.536 | -9.5338 | -10.5333 | -11.5071 | -12.4527 | -13.453 | -
EHK | summer | -54 | -27 | 54 | 0.54976 | 40.6491 | 17.4521 | 0 | 0.74834 | -5.5148 | 2.97 | 3.314 | 2.0841 | -3.0349 | -5.1123 | -
EHK | winter | -54 | -27 | 54 | 0.76521 | 40.6491 | 17.4521 | 0 | 0.9203 | -3.3552 | 8.5296 | 7.9014 | 4.6931 | 3.3321 | 2.4515 | -
FNS | summer | -99 | -66 | 99 | 0.77708 | 41.0865 | 0 | 24.9135 | 1.5878 | -1.896 | 7.7554 | 12.8513 | 11.2843 | 9.6285 | 7.7554 | -
FNS | winter | -99 | -66 | 99 | 0.30915 | 41.0865 | 0 | 24.9135 | 3.7502 | 1.1321 | 16.4306 | 15.9602 | 14.6701 | 13.4615 | 12.4541 | -
GB | summer | -37.5 | -25 | 37.5 | 0.90275 | 2.2964 | 0 | 22.7036 | 1.2628 | 1.6505 | -1.1114 | -1.1165 | -1.1428 | -1.165 | -1.1822 | -
GB | winter | -37.5 | -25 | 37.5 | 0.97715 | 2.2964 | 0 | 22.7036 | 5.5431 | 2.1014 | 2.6101 | 2.6201 | 2.5902 | 2.5803 | 2.5407 | -
GCY | summer | -66 | -33 | 66 | 0.99487 | 19.6486 | 16.7663 | 13.3514 | 2.9573 | 8.8703 | 10.2629 | 9.047 | 7.472 | 5.7944 | 4.0299 | -
GCY | winter | -66 | -33 | 66 | 0.99739 | 19.6486 | 16.7663 | 13.3514 | 26.109 | 10.44 | 11.835 | 10.7365 | 9.4777 | 8.1767 | 6.9352 | -
GHP | summer | -66 | -33 | 66 | 0.9393 | 20.6932 | 0 | 12.3068 | 0.74932 | -3.9249 | -7.4397 | -8.8128 | -10.4106 | -12.0243 | -13.7511 | -
GHP | winter | -66 | -33 | 66 | 0.75564 | 20.6932 | 0 | 12.3068 | 0.32111 | -2.1527 | -4.0762 | -5.2957 | -6.4933 | -7.7372 | -8.9057 | -
GL | summer | -80 | -40 | 80 | 0.33255 | 17.4274 | 17.4522 | 22.5726 | 0.55297 | 1.283 | 5.0683 | 5.6601 | 4.1774 | 2.8484 | -2.4656 | -
GL | winter | -80 | -40 | 80 | 0.92022 | 17.4274 | 17.4522 | 22.5726 | 5.1803 | 3.5173 | 9.6872 | 8.7556 | 7.4492 | 6.0632 | 4.6101 | -
GLE | summer | -79.5 | -46.5 | 79.5 | 0.80823 | 32.1632 | 6.0968 | 14.3368 | 0.15653 | -3.419 | 5.8222 | 7.0729 | 4.8884 | 3.211 | -3.2659 | -
GLE | winter | -79.5 | -46.5 | 79.5 | 0.44166 | 32.1632 | 6.0968 | 14.3368 | 1.9063 | 2.0137 | 12.5269 | 11.1524 | 9.4375 | 7.6729 | 5.8657 | -
GSB | summer | -66 | -33 | 66 | 0.99737 | 22.7913 | 0 | 10.2087 | 1.2659 | -7.1387 | -5.8536 | -7.6352 | -9.7771 | -11.9662 | -14.2739 | -
GSB | winter | -66 | -33 | 66 | 0.97478 | 22.7913 | 0 | 10.2087 | 0.057526 | -3.5188 | -2.7011 | -4.0693 | -5.5372 | -7.173 | -8.8986 | -
HSM | summer | -40.5 | -27 | 40.5 | 0.91087 | 24.5257 | 6.6303 | 2.4743 | 0.0041982 | -5.2258 | -2.1408 | -3.2294 | -5.2598 | -7.4945 | -9.916 | -
HSM | winter | -40.5 | -27 | 40.5 | 0.47959 | 24.5257 | 6.6303 | 2.4743 | 1.1074 | -3.1833 | 2.2328 | -1.9148 | -2.9974 | -4.72 | -6.5554 | -
HTN | summer | -39.5 | -26 | 39.5 | 0.7409 | 12.7404 | 0 | 13.2596 | 0.71752 | 1.2507 | 1.2732 | -0.20125 | -1.9021 | -3.7411 | -5.8007 | -
HTN | winter | -39.5 | -26 | 39.5 | 0.98225 | 12.7404 | 0 | 13.2596 | 1.9221 | 2.932 | 2.0824 | 0.77524 | -0.6463 | -2.2322 | -3.9115 | -
KRT | summer | -40.5 | -27 | 40.5 | 0.89016 | 64.1676 | 3.1627 | 0 | 1.595 | 3.177 | 4.245 | 3.4406 | 2.5857 | 1.7804 | 1.1456 | -
KRT | winter | -40.5 | -27 | 40.5 | 0.95943 | 64.1676 | 3.1627 | 0 | 3.2281 | 5.793 | 6.0253 | 5.6939 | 5.207 | 4.6375 | 3.952 | -
KYM | summer | -40.5 | -27 | 40.5 | 0.61637 | 32.7567 | 0 | 0 | 0.25551 | -6.9337 | -5.6109 | -7.6509 | -8.3045 | -8.9789 | -9.7037 | -
KYM | winter | -40.5 | -27 | 40.5 | 0.64784 | 32.7567 | 0 | 0 | 0.59577 | -5.0871 | -5.3615 | -5.658 | -5.994 | -6.4022 | -6.8722 | -
LV | summer | -99 | -66 | 99 | 0.98479 | 82.3784 | 14.2513 | 0 | 0.43831 | -30.7171 | -26.7175 | -26.3699 | -31.8669 | -37.2293 | -42.4079 | -
LV | winter | -99 | -66 | 99 | 0.97829 | 82.3784 | 14.2513 | 0 | 0.10552 | -23.3367 | -14.3073 | -16.4119 | -19.7965 | -23.012 | -26.1427 | -
LVN | summer | -129 | -96 | 129 | 0.87611 | 19.9175 | 4.9537 | 76.0825 | 1.9013 | 14.569 | 25.1814 | 25.9831 | 25.5137 | 24.9763 | 24.4298 | -
LVN | winter | -129 | -96 | 129 | 0.94055 | 19.9175 | 4.9537 | 76.0825 | 11.9822 | 18.7614 | 31.0864 | 30.8353 | 30.6039 | 30.3745 | 30.0137 | -
MBN | summer | -59 | -27 | 59 | 0.99301 | 25.4432 | 13.7178 | 1.5568 | 0.36001 | -7.2289 | -5.787 | -6.8586 | -8.1969 | -9.4685 | -10.6977 | -
MBN | winter | -59 | -27 | 59 | 0.99766 | 25.4432 | 13.7178 | 1.5568 | 0.18586 | -4.428 | -5.2587 | -6.2346 | -7.1772 | -8.1309 | -8.9903 | -
MDA | summer | -66 | -33 | 66 | 0.94208 | 25.4014 | 16.7663 | 7.5986 | 0.089367 | -3.747 | 1.0602 | 0.71028 | -1.1302 | -3.0101 | -4.96 | -
MDA | winter | -66 | -33 | 66 | 0.82388 | 25.4014 | 16.7663 | 7.5986 | 0.3664 | -2.4114 | 3.6003 | 2.12 | 0.58078 | -1.0002 | -2.5001 | -
MLN | summer | -99 | -66 | 99 | 0.9951 | 83.4903 | 10.7837 | 0 | 0.64791 | -29.3204 | -23.224 | -22.7139 | -23.5324 | -24.4207 | -27.1566 | -
MLN | winter | -99 | -66 | 99 | 0.98924 | 83.4903 | 10.7837 | 0 | 0.63996 | -23.0548 | -6.7574 | -6.1565 | -4.3958 | -4.9394 | -5.5142 | -
MNA | summer | -66 | -33 | 66 | 0.76148 | 28.7887 | 13.1002 | 4.2113 | 0.52839 | -6.9733 | -5.4242 | -5.8981 | -6.796 | -7.945 | -9.1806 | -
MNA | winter | -66 | -33 | 66 | 0.44245 | 28.7887 | 13.1002 | 4.2113 | 0.14546 | -4.7614 | -5.4321 | -5.3793 | -5.5916 | -6.0319 | -6.6592 | -
MRO | summer | -27 | -13.5 | 27 | 0.94901 | 20.4915 | 3.0484 | 0 | 0.71195 | -6.0695 | -4.3756 | -5.6552 | -7.1179 | -8.5832 | -10.1795 | -
MRO | winter | -27 | -13.5 | 27 | 0.94301 | 20.4915 | 3.0484 | 0 | 0.49322 | -5.3693 | -3.4422 | -4.5991 | -5.8466 | -7.0745 | -8.3534 | -
NHL | summer | -20 | -10 | 20 | 0.85819 | 12.4066 | 0 | 0 | 0.48835 | -6.7079 | -5.9527 | -6.3205 | -6.7481 | -7.2553 | -7.8231 | -
NHL | winter | -20 | -10 | 20 | 0.89078 | 12.4066 | 0 | 0 | 2.7092 | -6.455 | -6.0539 | -6.2235 | -6.4595 | -6.7727 | -7.1347 | -
NKA | summer | -39.5 | -26 | 39.5 | 0.97128 | 36.7147 | 1.9815 | 0 | 2.2453 | -13.9422 | -19.1306 | -18.8706 | -19.8406 | -20.8405 | -21.7805 | -
NKA | winter | -39.5 | -26 | 39.5 | 0.94297 | 36.7147 | 1.9815 | 0 | 2.4489 | -12.0633 | -15.5044 | -16.0823 | -16.8505 | -17.61 | -18.3905 | -
OYN | summer | -27 | -13.5 | 27 | 0.36225 | 4.0186 | 0 | 9.4814 | 0.099073 | -0.80622 | -1.17 | -1.307 | -1.5557 | -1.8983 | -2.3224 | -
OYN | winter | -27 | -13.5 | 27 | 6.0011e-17 | 4.0186 | 0 | 9.4814 | 0.026065 | -1.0117 | -1.1732 | -1.444 | -1.7851 | -2.1991 | -2.6369 | -
PLD | summer | -32 | -16 | 32 | 0.99852 | 10.6635 | 0 | 5.3365 | 0.63018 | -1.1442 | -0.79076 | -1.7548 | -2.9828 | -4.272 | -5.7215 | -
PLD | winter | -32 | -16 | 32 | 1 | 10.6635 | 0 | 5.3365 | 0.86572 | 0.0087608 | 0.52612 | -0.35355 | -1.2774 | -2.3345 | -3.5116 | -
RVL | summer | -19.5 | -13 | 19.5 | 0.93863 | 14.5489 | 4.5726 | 0 | 1.5652 | -8.6296 | -7.5353 | -5.6868 | -5.6967 | -5.7558 | -5.8247 | -
RVL | winter | -19.5 | -13 | 19.5 | 0.93908 | 14.5489 | 4.5726 | 0 | 3.5156 | -6.5951 | -5.1591 | -4.9092 | -5.0011 | -5.0472 | -5.086 | -
SA | summer | -93 | -60 | 93 | 0.90793 | 44.6584 | 9.793 | 15.3416 | 0.015754 | -11.0471 | -10.5031 | -13.6405 | -17.5384 | -22.0611 | -27.0082 | -
SA | winter | -93 | -60 | 93 | 0.67638 | 44.6584 | 9.793 | 15.3416 | 0.7681 | -7.3134 | -6.3727 | -8.5221 | -11.5109 | -14.9261 | -18.7799 | -
SHL | summer | -40.5 | -27 | 40.5 | 0.99363 | 32.6326 | 2.8579 | 0 | 1.7491 | -11.7985 | -17.2302 | -18.0426 | -18.7237 | -19.5032 | -20.3335 | -
SHL | winter | -40.5 | -27 | 40.5 | 0.99526 | 32.6326 | 2.8579 | 0 | 3.5676 | -13.782 | -15.8217 | -16.4388 | -17.1068 | -17.7653 | -18.4459 | -
SHN | summer | -66 | -33 | 66 | 0.9796 | 27.206 | 2.8579 | 5.794 | 1.437 | -10.3174 | -7.3698 | -7.9591 | -9.008 | -10.0472 | -11.0266 | -
SHN | winter | -66 | -33 | 66 | 0.958 | 27.206 | 2.8579 | 5.794 | 0.27541 | -9.1472 | -4.47 | -5.2148 | -5.9624 | -6.711 | -7.3498 | -
SHP | summer | -66 | -33 | 66 | 0.88648 | 39.3347 | 0 | 0 | 2.5942 | -26.1973 | -41.1319 | -41.9677 | -42.5349 | -43.0126 | -43.5401 | 24.64% | -74.8842 | -92.4025 | -104.6696 | -116.6523 | -132.4657 | -0.035993 | -0.044413 | -0.050309 | -0.056069 | -0.06367 | 27 | 32.5 | 35 | 40.5 | 47.5
SHP | winter | -66 | -33 | 66 | 0.92014 | 39.3347 | 0 | 0 | 4.4178 | -26.6264 | -36.9926 | -37.4841 | -37.7458 | -38.0165 | -38.318 | 12.1%
SSE | summer | -99 | -66 | 99 | 0.97523 | 26.4458 | 0 | 39.5542 | 1.0719 | 4.8672 | 7.2524 | 5.5692 | 3.4376 | 1.2035 | -1.8405 | -
SSE | winter | -99 | -66 | 99 | 0.99894 | 26.4458 | 0 | 39.5542 | 4.8513 | 10.2776 | 14.1741 | 12.6709 | 11.0302 | 9.2452 | 7.1145 | -
STL | summer | -27 | -13.5 | 27 | 0.054824 | 17.53 | 4.0772 | 0 | 1.3159 | 5.7153 | 6.4139 | 6.5634 | 5.9624 | 5.374 | 4.862 | -
STL | winter | -27 | -13.5 | 27 | 0.39279 | 17.53 | 4.0772 | 0 | 5.7599 | 5.7197 | 7.7665 | 7.5773 | 7.1754 | 6.7587 | 6.3307 | -
STN | summer | -79 | -46 | 79 | 0.7996 | 36.8208 | 0.57158 | 9.1792 | 0.63556 | -9.8357 | -4.2648 | -4.7486 | -5.9303 | -7.2089 | -8.7475 | -
STN | winter | -79 | -46 | 79 | 0.8951 | 36.8208 | 0.57158 | 9.1792 | 1.792 | -6.7957 | -4.1346 | -4.2716 | -4.7915 | -5.574 | -6.5395 | -
SU | summer | -99 | -66 | 99 | 0.82208 | 41.8716 | 22.1772 | 24.1284 | 1.1417 | -1.0948 | 8.4972 | 8.7709 | 6.3945 | 3.8829 | -1.8201 | -
SU | winter | -99 | -66 | 99 | 0.99843 | 41.8716 | 22.1772 | 24.1284 | 5.3669 | 16.3131 | 23.4618 | 23.3523 | 21.3594 | 19.5082 | 17.3917 | -
TNA | summer | -99 | -66 | 99 | 0.99803 | 111.7199 | 32.1988 | 0 | 1.3624 | -35.8068 | -17.98 | -8.4885 | 10.6949 | 9.9704 | 9.3627 | -
TNA | winter | -99 | -66 | 99 | 0.9735 | 111.7199 | 32.1988 | 0 | 0.54277 | -26.395 | -8.9093 | 19.342 | 19.7363 | 19.7183 | 19.9069 | -
TQY | summer | -66 | -33 | 66 | 0.93035 | 27.5025 | 3.8105 | 5.4975 | 0.60975 | -8.3087 | -8.2886 | -8.9467 | -10.5987 | -12.3662 | -14.2588 | -
TQY | winter | -66 | -33 | 66 | 0.63857 | 27.5025 | 3.8105 | 5.4975 | 0.60923 | -5.0895 | -4.3527 | -5.0801 | -6.1028 | -7.2381 | -8.4037 | -
TRG | summer | -46.5 | -13.5 | 46.5 | 0.94984 | 21.2381 | 5.1442 | 0 | 1.1006 | -4.8815 | -6.9773 | -5.7365 | -6.3067 | -6.918 | -7.5604 | -
TRG | winter | -46.5 | -13.5 | 46.5 | 0.65307 | 21.2381 | 5.1442 | 0 | 0.89097 | -6.0126 | -6.9773 | -4.6388 | -5.0593 | -5.5003 | -6.0031 | -
WBE | summer | -99 | -66 | 99 | 0.99998 | 103.2202 | 8.7642 | 0 | 0.11054 | -24.337 | -26.8348 | -30.55 | -36.1202 | -41.0178 | -45.9123 | -
WBE | winter | -99 | -66 | 99 | 0.98717 | 103.2202 | 8.7642 | 0 | 0.11888 | -21.7012 | -9.0879 | -11.2959 | -14.6838 | -17.7786 | -20.7099 | -
WBL | summer | -79.5 | -46.5 | 79.5 | 0.98001 | 18.4301 | 8.7642 | 28.0699 | 1.8115 | 12.3979 | 11.6352 | 10.3434 | 8.6974 | 6.9005 | 4.9357 | -
WBL | winter | -79.5 | -46.5 | 79.5 | 0.99824 | 18.4301 | 8.7642 | 28.0699 | 3.6597 | 12.0879 | 13.903 | 12.9372 | 11.83 | 10.5956 | 9.177 | -
WIN | summer | -20.5 | -7 | 20.5 | 0.50077 | 12.7618 | 0 | 0 | 1.0889 | -4.0204 | -5.2475 | -6.4689 | -6.816 | -7.1815 | -7.5646 | -
WIN | winter | -20.5 | -7 | 20.5 | 0.27818 | 12.7618 | 0 | 0 | 0.65081 | -3.9423 | -4.9394 | -5.0261 | -5.1265 | -5.2805 | -5.4985 | -
WMN | summer | -46.5 | -13.5 | 46.5 | 1 | 7.2348 | 5.3347 | 6.2652 | 1.355 | 0.066344 | -4.4807 | -4.5206 | -4.5007 | -4.4608 | -4.4109 | -
WMN | winter | -46.5 | -13.5 | 46.5 | 0.99977 | 7.2348 | 5.3347 | 6.2652 | 0.18731 | -1.407 | -3.4286 | -3.4347 | -3.4253 | -3.4132 | -3.3825 | -
WND | summer | -66 | -33 | 66 | 0.99847 | 24.5774 | 1.1432 | 8.4226 | 1.5458 | -7.0508 | -10.0629 | -10.101 | -12.0406 | -14.0712 | -16.1759 | -
WND | winter | -66 | -33 | 66 | 0.8987 | 24.5774 | 1.1432 | 8.4226 | 0.22966 | -3.0934 | -4.5156 | -5.0983 | -6.6278 | -8.1327 | -9.7621 | -
WPD | summer | -79.5 | -46.5 | 79.5 | 0.9475 | 40.8707 | 0.7621 | 5.6293 | 1.2691 | -11.3066 | -11.8528 | -13.8978 | -16.3212 | -18.7993 | -21.363 | -
WPD | winter | -79.5 | -46.5 | 79.5 | 0.8729 | 40.8707 | 0.7621 | 5.6293 | 0.041685 | -7.6955 | -6.1741 | -7.3848 | -8.6894 | -10.1001 | -11.5369 | -